## Table1_Responsibility
Project Name | Transmission Owner | Cost ($M) | Year | Driver Categories | Load Growth Evidence | PG&E | SCE | SDG&E | Other
Tulucay-Napa #2 60 kV Line Capacity Increase | PG&E | 7.5 | 2020 | equip_aging¦load_growth | Overload appears starting in 2024 (not in 2021 baseline) and worsens in high CEC forecast sensitivity, indicating that increasing load is driving the P0 overload on top of the existing equipment rating gap. | 1 | 0 | 0 | 0
Gamebird 230/138 kV Transformer Upgrade Project | VEA / GLW | 4.9 | 2020 | load_growth¦voltage | The report explicitly states: 'Load growth in the VEA area was found to be the primary driver behind this reliability issue.' VEA is identified as the area with the highest load growth in CAISO. Overloads appear in 2021 baseline and worsen in higher-load sensitivity scenarios, confirming load growth as the cause. | 0 | 0 | 0 | 1
Coppermine 70 kV Reinforcement Project | PG&E | 23.7 | 2022 | equip_aging¦load_growth¦voltage | Project need date is 'P0 overloads based on historical data' with future local demand growth in the area driving the need for permanent reinforcement beyond the temporary operational measure. | 1 | 0 | 0 | 0
San Jose Area HVDC Lines | PG&E | 417.5 | 2022 | load_growth | Report explicitly states the forecasted overall San Jose area load is beyond the capacity of 115 kV lines, with ~500 MW (~75%) load increase in SVP service area driving the need for entirely new transmission infrastructure. | 1 | 0 | 0 | 0
Series Compensation on Los Esteros-Nortech 115 kV Line | PG&E | 12.5 | 2022 | load_growth | The series compensation is explicitly an interim solution for the SVP area load growth issue while the San Jose HVDC project is built. The same load growth (~500 MW, ~75% in SVP area) drives both projects. | 1 | 0 | 0 | 0
Garberville Area Reinforcement | PG&E | 153 | 2023 | equip_aging¦load_growth¦voltage | Overloads on the Humboldt 60 kV system identified starting 2024 in both near-term and long-term planning horizons, consistent with load in a remote area growing into a constrained corridor. | 1 | 0 | 0 | 0
Tulucay-Napa #2 60 kV line Reconductoring project | PG&E | 10.95 | 2023 | load_growth | The original project mitigates overloads through 2027; the expansion is needed because overloads reappear by 2032 as load continues to grow beyond the original project's capacity. | 1 | 0 | 0 | 0
Banta 60 kV Bus Voltage Conversion (Central Valley Area) | PG&E | 13.25 | 2023 | load_growth | Report explicitly states 'Due to potential load growth, there will be overload on the Vierra-Tracy-Kasson 115 kV in long term under P6.' | 1 | 0 | 0 | 0
Redwood City 115kV System Reinforcement | PG&E | 83.1 | 2023 | load_growth¦equip_aging | Appendix explicitly states project objectives include 'provide transmission capacity to meet future local demand growth.' | 1 | 0 | 0 | 0
Los Banos 70 kV Area Reinforcement | PG&E | 45 | 2023 | load_growth¦equip_aging | Report explicitly states: 'the overloads are increasing due to additional new distribution customer driven load increases at the Canal, Ortiga, Santa Nella and Wright 70 kV substations starting 2024 further requiring system upgrades.' | 1 | 0 | 0 | 0
North East Kern 115 kV Line Reconductoring | PG&E | 192 | 2023 | load_growth | Appendix explicitly states: 'To mitigate new load driven overloads in the North East Kern area.' | 1 | 0 | 0 | 0
Coolwater A 115/230 kV Bank Project | SCE | 47 | 2023 | voltage¦load_growth | The Coolwater 1A Bank is also needed for the Brightline West High Speed Rail project to energize, representing a significant new retail load interconnection in the North of Lugo area. | 0 | 1 | 0 | 0
Martin-Millbrae 60 kV Area Reinforcement project | PG&E | 30 | 2024 | load_growth¦equip_aging | Report states: 'The load forecast indicates high load growth in this area due to multiple business load requests.' PG&E plans to expand load serving capacity at Sneath Lane substation due to increased demand. | 1 | 0 | 0 | 0
Camden 70 kV reinforcement project | PG&E | 75 | 2024 | load_growth¦equip_aging¦voltage | Report states: 'Operations has observed over 90% loading on Camden-Kingsburg 70 kV line during peak conditions due to the local load growth.' PG&E distribution load forecast indicates additional loads will be transferred to Camden substation, resulting in P0 overloads and low voltages in all near-term and long-term scenarios. | 1 | 0 | 0 | 0
Rio Oso-W. Sacramento Reconductoring Project | PG&E | 97.4 | 2024 | equip_aging¦load_growth | Report states 'substantial distribution load interconnections have been requested in this area,' contributing to the need for higher capacity beyond what re-rating could provide. | 1 | 0 | 0 | 0
Cortina #1 60 kV Line Reconductoring Project | PG&E |  | 2024 | load_growth¦equip_aging¦voltage | PG&E received a near-term 10 MW load interconnection request at Dunnigan substation; 0.7 MW already online in 2023, 4.2 MW in queue for 2024, plus 0.5 MW agricultural pump and 0.4 MW EV charging station applications. Even under only normal distribution load growth, P0 thermal overload at 113% appears by 2035. | 1 | 0 | 0 | 0
Salinas Area Reinforcement Project | PG&E | 339.2 | 2024 | load_growth¦equip_aging¦voltage | PG&E Distribution Planning received 'a large number of load interconnection applications near Spence.' Load at Spence substation forecast: 23.3 MW in 2023, 50.8 MW in 2025, 84.6 MW in 2035. Report states: 'Due to load growth in the area, the previously approved Salinas-Firestone #1 and #2 reconductor project... is insufficient to address these overloads.' | 1 | 0 | 0 | 0
Tejon area Reinforcement Project | PG&E | 42 | 2024 | load_growth¦equip_aging | Report explicitly states: 'The projected local load growth, including an additional 50 MW load at San Bernard substation and 45.5 MW load at Tejon 70kV substation... results in thermal overloads.' All near-term and long-term scenarios show P3 overloads driven by these additional loads. | 1 | 0 | 0 | 0
French Camp Reinforcement Project | PG&E | 63.15 | 2024 | equip_aging¦load_growth | Report states: 'Significant distribution load interconnections have been requested in this area.' Weber substation is at maximum capacity, and new load requests are driving the need for a fundamentally new supply path. | 1 | 0 | 0 | 0
Coronado Island Reliability Reinforcement Phase I | SDG&E | 42 | 2025 | load_growth¦equip_aging | The US Navy submitted a load interconnection request to SDG&E that will add 95 MVA of load at North Island Metering substation from 2023 to 2042. P1 and P3 contingency overloads were observed in the near term and long term planning horizons driven by this additional load. | 0 | 0 | 1 | 0
Coronado Island Reliability Reinforcement Phase II | SDG&E | 66 | 2025 | load_growth¦equip_aging | All P1 contingency overloads in Phase II are 'driven by the additional US Navy load' of 95 MVA at North Island Metering substation, same as Phase I. | 0 | 0 | 1 | 0
Tortilla 115kV Capacitor Replacement | SCE | 5 | 2025 | load_growth¦voltage | Report explicitly states: 'The decline in post-contingency voltage is primarily driven by the significant increase in load at Tortilla and Edwards substations.' | 0 | 1 | 0 | 0
Kramer-Coolwater 115kV Line Looping into Tortilla 115kV Substation | SCE | 37 | 2025 | load_growth¦equip_aging¦voltage | Report explicitly states: 'The decline in post-contingency voltage is primarily driven by the significant increase in load at Tortilla and Edwards substations.' Load growth is the stated driver for both thermal and voltage concerns. | 0 | 1 | 0 | 0
West Fresno 115 kV Voltage support Project | PG&E | 45 | 2025 | load_growth¦voltage | Report states: 'With growing distribution level forecast, low voltages at West Fresno are expected to continue and worsen if not mitigated.' Low voltages worsen progressively in near-term to long-term scenarios driven by growing distribution load. | 1 | 0 | 0 | 0
Cortina #3 60 kV Reconductoring Project | PG&E | 41.65 | 2025 | load_growth¦equip_aging¦voltage | EV charging distribution project expected to add 3 MW by 2025, 10 MW by 2028, and 20 MW by 2030 at Williams substation. The entire project is driven by this planned load increase. | 1 | 0 | 0 | 0
Gold Hill-El Dorado Reinforcement | PG&E |  | 2025 | equip_aging¦load_growth | Objectives state: 'provide enough transmission capacity to meet future local demand.' The project increases operating flexibility and load serving capability to accommodate projected growth in El Dorado County. | 1 | 0 | 0 | 0
San Miguel New 70kV Line Project | PG&E |  | 2025 | load_growth¦voltage | Alternatives analysis notes: 'Voltage Support at San Miguel... is insufficient for projected load growth.' A new line is needed to accommodate anticipated demand increases beyond what reactive support alone can address. | 1 | 0 | 0 | 0
San Mateo 230/115 kV Transformer Bank Addition Project | PG&E | 82.5 | 2025 | load_growth¦equip_aging | Report states overloads worsen from 20% in 2026 to 38% in 2034, driven by 'distribution customers in San Francisco and the Peninsula, the increasing demand for electric vehicle (EV) charging, electrification loads, and the interconnection of large customer loads.' AATE and AAFS loads will further increase overloads beyond 2034. | 1 | 0 | 0 | 0
North Oakland Reinforcement Project | PG&E | 845.5 | 2025 | load_growth¦equip_aging | Report states: 'this area is experiencing rapid load increase due to industrial and commercial growth and the rise in the EV Charging and Electrification loads.' Demand projected to increase from 376.7 MW (2024) to 458.2 MW (2039). The previously approved OCEI project is no longer sufficient due to this load growth. | 1 | 0 | 0 | 0
South Oakland Reinforcement Project | PG&E | 187.5 | 2025 | load_growth¦equip_aging | Report states: 'Significant load growth is anticipated at San Leandro, Edes, Oakland J, and Grant 115 kV Substations.' Data center load interconnection projects totaling more than 300 MW are actively being studied near East Shore substation. | 1 | 0 | 0 | 0
Greater Bay Area 500 kV Transmission Reinforcement | PG&E | 600 | 2025 | load_growth¦economic | LCR deficiency of nearly 5,000 MW in 2039 scenario. South Bay projected 2.5 GW load growth between 2026 and 2039. Report states: 'The anticipated increase in load significantly surpasses the available transmission resources and internal generation capacity.' | 1 | 0 | 0 | 0
Metcalf 500/230 kV Transformer Bank Addition Project | PG&E | 136.5 | 2025 | load_growth¦equip_aging | Report states project 'will provide additional transmission capacity to meet the future local demand.' Demand driven by 'Silicon Valley area and newly interconnected large load, such as data centers.' Multiple companion projects (500 kV line, HVDC) are being proposed simultaneously to address the same explosive load growth. | 1 | 0 | 0 | 0
New San Jose B-NRS 230 kV line | PG&E | 162.5 | 2025 | load_growth | Long-term San Jose area load forecast increased from 2,100 MW in the 2021-2022 TPP to ~3,400 MW (base) and ~4,200 MW (sensitivity) in the 2024-2025 TPP—a 62-100% increase. The previously approved HVDC projects were re-scoped and this new line was added as a complement. | 1 | 0 | 0 | 0
South Bay Reinforcement Project | PG&E | 325.5 | 2025 | load_growth¦equip_aging | Objectives explicitly cite 'the aggressive ramp-up in load trends reflected in the current load forecast.' South Bay hosts many AI/data-driven companies. Previously approved projects were re-scoped because load forecast significantly increased since their approval. | 1 | 0 | 0 | 0
Metcalf-Piercy & Swift and Newark-Dixon Landing 115 kV Upgrade (re-scope) | PG&E | 186 | 2025 | load_growth¦equip_aging | Objectives explicitly state 'to prevent system overloads due to the aggressive ramp-up in load trends reflected in the current load forecast.' The project required re-scoping specifically because load forecast increases made the original reconductoring insufficient. | 1 | 0 | 0 | 0

## Table2_ShareRatio
Project Name | Transmission Owner | Cost ($M) | Year | Driver Categories | Allocation Method | PG&E | SCE | SDG&E | Others
Tulucay-Napa #2 60 kV Line Capacity Increase | PG&E | 7.5 | 2020 | equip_aging¦load_growth | HV TAC Gross Load Share | 42.656 | 43.6711 | 9.5621 | 4.1107
Gamebird 230/138 kV Transformer Upgrade Project | VEA / GLW | 4.9 | 2020 | load_growth¦voltage | HV TAC Gross Load Share | 42.656 | 43.6711 | 9.5621 | 4.1107
Coppermine 70 kV Reinforcement Project | PG&E | 23.7 | 2022 | equip_aging¦load_growth¦voltage | HV TAC Gross Load Share | 44.0231 | 42.6611 | 9.3226 | 3.9932
San Jose Area HVDC Lines | PG&E | 417.5 | 2022 | load_growth | HV TAC Gross Load Share | 44.0231 | 42.6611 | 9.3226 | 3.9932
Series Compensation on Los Esteros-Nortech 115 kV Line | PG&E | 12.5 | 2022 | load_growth | HV TAC Gross Load Share | 44.0231 | 42.6611 | 9.3226 | 3.9932
Garberville Area Reinforcement | PG&E | 153 | 2023 | equip_aging¦load_growth¦voltage | HV TAC Gross Load Share | 44.4901 | 43.7465 | 8.4937 | 3.2697
Tulucay-Napa #2 60 kV line Reconductoring project | PG&E | 10.95 | 2023 | load_growth | HV TAC Gross Load Share | 44.4901 | 43.7465 | 8.4937 | 3.2697
Banta 60 kV Bus Voltage Conversion (Central Valley Area) | PG&E | 13.25 | 2023 | load_growth | HV TAC Gross Load Share | 44.4901 | 43.7465 | 8.4937 | 3.2697
Redwood City 115kV System Reinforcement | PG&E | 83.1 | 2023 | load_growth¦equip_aging | HV TAC Gross Load Share | 44.4901 | 43.7465 | 8.4937 | 3.2697
Los Banos 70 kV Area Reinforcement | PG&E | 45 | 2023 | load_growth¦equip_aging | HV TAC Gross Load Share | 44.4901 | 43.7465 | 8.4937 | 3.2697
North East Kern 115 kV Line Reconductoring | PG&E | 192 | 2023 | load_growth | HV TAC Gross Load Share | 44.4901 | 43.7465 | 8.4937 | 3.2697
Coolwater A 115/230 kV Bank Project | SCE | 47 | 2023 | voltage¦load_growth | HV TAC Gross Load Share | 44.4901 | 43.7465 | 8.4937 | 3.2697
Martin-Millbrae 60 kV Area Reinforcement project | PG&E | 30 | 2024 | load_growth¦equip_aging | HV TAC Gross Load Share | 44.2171 | 43.8055 | 8.6528 | 3.3246
Camden 70 kV reinforcement project | PG&E | 75 | 2024 | load_growth¦equip_aging¦voltage | HV TAC Gross Load Share | 44.2171 | 43.8055 | 8.6528 | 3.3246
Rio Oso-W. Sacramento Reconductoring Project | PG&E | 97.4 | 2024 | equip_aging¦load_growth | HV TAC Gross Load Share | 44.2171 | 43.8055 | 8.6528 | 3.3246
Cortina #1 60 kV Line Reconductoring Project | PG&E |  | 2024 | load_growth¦equip_aging¦voltage | HV TAC Gross Load Share | 44.2171 | 43.8055 | 8.6528 | 3.3246
Salinas Area Reinforcement Project | PG&E | 339.2 | 2024 | load_growth¦equip_aging¦voltage | HV TAC Gross Load Share | 44.2171 | 43.8055 | 8.6528 | 3.3246
Tejon area Reinforcement Project | PG&E | 42 | 2024 | load_growth¦equip_aging | HV TAC Gross Load Share | 44.2171 | 43.8055 | 8.6528 | 3.3246
French Camp Reinforcement Project | PG&E | 63.15 | 2024 | equip_aging¦load_growth | HV TAC Gross Load Share | 44.2171 | 43.8055 | 8.6528 | 3.3246
Coronado Island Reliability Reinforcement Phase I | SDG&E | 42 | 2025 | load_growth¦equip_aging | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
Coronado Island Reliability Reinforcement Phase II | SDG&E | 66 | 2025 | load_growth¦equip_aging | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
Tortilla 115kV Capacitor Replacement | SCE | 5 | 2025 | load_growth¦voltage | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
Kramer-Coolwater 115kV Line Looping into Tortilla 115kV Substation | SCE | 37 | 2025 | load_growth¦equip_aging¦voltage | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
West Fresno 115 kV Voltage support Project | PG&E | 45 | 2025 | load_growth¦voltage | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
Cortina #3 60 kV Reconductoring Project | PG&E | 41.65 | 2025 | load_growth¦equip_aging¦voltage | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
Gold Hill-El Dorado Reinforcement | PG&E |  | 2025 | equip_aging¦load_growth | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
San Miguel New 70kV Line Project | PG&E |  | 2025 | load_growth¦voltage | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
San Mateo 230/115 kV Transformer Bank Addition Project | PG&E | 82.5 | 2025 | load_growth¦equip_aging | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
North Oakland Reinforcement Project | PG&E | 845.5 | 2025 | load_growth¦equip_aging | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
South Oakland Reinforcement Project | PG&E | 187.5 | 2025 | load_growth¦equip_aging | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
Greater Bay Area 500 kV Transmission Reinforcement | PG&E | 600 | 2025 | load_growth¦economic | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
Metcalf 500/230 kV Transformer Bank Addition Project | PG&E | 136.5 | 2025 | load_growth¦equip_aging | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
New San Jose B-NRS 230 kV line | PG&E | 162.5 | 2025 | load_growth | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
South Bay Reinforcement Project | PG&E | 325.5 | 2025 | load_growth¦equip_aging | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307
Metcalf-Piercy & Swift and Newark-Dixon Landing 115 kV Upgrade (re-scope) | PG&E | 186 | 2025 | load_growth¦equip_aging | HV TAC Gross Load Share | 44.3347 | 42.9606 | 9.374 | 3.3307