## JLE-1
CPP | CPP Description | Project Category | Project Description | Project Cost Jan 2019 to Sep 2023
TA2013007 | 2013/2014 Asset Replacement | System Restoration | This program covered rehabilitation projects in AEP Texas service area. Some of the work performed under this program included the following: - New DICM installed at DuPont - Line relays on Whitepoint - Rincon - Breaker at Victoria Dupont | 4689192.53
TA2020025 | 2020 ERCOT Region NIP | Reliability | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -34.63
TA2019517 | 2020 TCC GE/SEL Relay Upgrade | Reliability | This project replaced electromechanical relays in the AEP Texas region. The identified relays replaced under this program were obsolete, no longer supported, out of warranty, or had numerous service notices that described vulnerabilities and high risk of failure. The modules within these relay panels were necessary for replacement in order to sustain grid resilience, performance, and stability. To address these conditions, this project replaced 101 GE relays and 155 SEL relays in 50 stations in the AEP Texas region. | 2706538.97
TA2020072 | 2021 GE/SEL Relay Upgrades | Reliability | This project replaced obsolete GE and SEL relays throughout the AEP Texas service area. The identified relays were obsolete, no longer supported, out of warranty, or had numerous service notices that describe vulnerabilities and high risk of failure. The modules within these relay panels had to be replaced in order to sustain grid resilience, performance, and stability. General Electric (GE) and Sweitzer Engineering Laboratories (SEL) have agreed to supply replacement modules, at a discounted price, in strategically-identified GE and SEL protective relay panels. Overall, this project replaced 145 GE relays and 337 SEL relays in 172 stations throughout the AEP Transmission footprint. | 1306113.25
GENPLTCAP | 2023 General Capital Plant Blanket | Customer Service & Other | This blanket program covers for individual projects that are under $2,000,000 and of a general nature, such as building equipment, HVAC, roofs, paving, security, storeroom and fleet tools that are required for facilities that are the responsibility of Real Estate and Workplace Services, Physical Security, Supply Chain and Fleet. | 194585.65
TECHCBKT | 2023 Telecommunication Capital Blanket | Telecom | This blanket provides for the loaded cost of Telecommunication projects not included in programs. The blankets are for projects each not exceeding $2,000,000 for small asset improvements and asset replacements due to failures. | 796645.43
TREESTX | 2023 Transmission and Distribution Forestry Program | Customer Service & Other | This 2023 program covered danger tree removal and widening the rights-of-way for AEP Texas. | 23891.95
ABTXDCR17 | Abilene DACR 2017 | Distribution Driven Transmission | The Distribution Automation Circuit Reconfiguration (DACR) project for the Abilene district automated distribution feeder breakers and station regulators at multiple substations in the Laredo area as part of the Smart Grid initiative for AEP Texas. Upgrading to a Smart Grid System because it will allow for a more reliable distribution system, improve response times for outages, and better monitor and control the distribution system. | 2342252.32
TP2018082 | Abilene NW Breaker Replacement | RTO | This project replaced breakers at the Abilene Northwest Station. The Company replaced two circuit breakers and upgraded any associated equipment at Abilene Northwest Station. | 833425.28
TP2021743 | Abilene NW Interconnect | Customer Service & Other | The Company constructed an underground 138kV tie-line from Abilene Northwest Station to outside of Lancium Station (a customer station), installed a dead-end structure, and installed one 138kV breaker at Abilene Northwest Station. Additionally, revenue meters, RTU, and SCADA were installed at the station, and the Drop In Control Module was expanded. | -468355.2
TP2021743 | Abilene NW Interconnect | Customer Service & Other | This customer driven project was placed into service during a previous rate case, and the credit in the plant in service file is due to customer reimbursement of project costs. | -468355.2
TA2021525 | Abilene NW Rehab | Reliability | This project intends to replace aging equipment at the Abilene Northwest station. There are six old oil breakers that are becoming too difficult to maintain due to lack of oil containment and spare parts. There are also electromechanical relays in the control house that no longer have vendor support or spare parts. | 330.19
TP2014055 | Abilene South to Abilene West | RTO | To mitigate potential overload, the Company rebuilt the Abilene South-Abilene West Texas Gulf Tap 69 kV line as 138 kV. Major components of this project included rebuilding the 2.15 mile 69 kV section from Abilene South-Abilene West Texas Gulf Tap with 138 kV construction with double circuit capable structures, retiring existing 2.15 mile section of Abilene South-Abilene West Texas Gulf tap 69 kV line, Constructing new 138 kV point of delivery (POD) box bay with new three motor operated air breakers (MOAB) switches, and installation of supervisory control and data acquisition systems (SCADA). | 115690.15
TA2019374 | Abilene Telecom Modernization | Telecom | This program included Transmission Telecommunication Modernization Program (TTMP) which will provide a robust telecommunication network in the Abilene, Texas area. This program built 115 miles of AEP-owned fiber that provides connectivity to ten stations, increases resiliency at six stations, provides resiliency via new fiber ring topology to four stations while laying the groundwork for resiliency in the future. | 6406299.54
TA2018807 | AEP Texas Failure Program | Reliability | This program covers reactive station and line work due to failures of various transmission assets. Some of the station assets replaced under this program included a failed switch at Fort Chadbourne, a circuit breaker at LonHill, a cap bank failure at Del Mar, a circuit breaker at Red Creek, a circuit breaker at White Point, and a reactor at Red Creek. Tansmission line repairs and replacements were also performed on the Uvalde - La Pryor, Eagle Pass - CFE Piedras, Hall Acres - S. Mcallen, Hamilton Road - TNC Tie, and Lon Hill - CPSB Spruce transmission lines, among others. | 13312456.58
TA2018607 | AEP Texas Region Line Program | Reliability | This program included projects that were placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -70776.84
TA2018707 | AEP Texas Region Station Rehab | Reliability | This program replaced station infrastructure at a number of AEP Texas stations to improve system reliability and dependability. Among the improvements, the program included rehabilitation of 82 aging transmission circuit breakers and 6 transmission transformers. The program also included associated work such as remote end relaying and line work necessary to accommodate some of the main station improvements and 6 new drop in control modules. This project rebuilt, improved, or replaced equipment at the following stations: Abilene Industrial Park, Airline, Anson, Clyde Magnolia, Cross Plains, Del Sol, Elm Creek, Garza, Joslin, Kenedy Switch, Laguna, Lon Hill, Naval Base, Pleasanton, Putnam, Radium, Rebecca Lane, Refugio, Rising Star, San Angelo Power Station, Sigmor, Twilight Trails, Vernon Main, Victoria Dupont, Victoria Plant, and Wylie. | 76538980.7
TA2014049 | AEP Texas SCADA Upgrades | Reliability | This project enhanced supervisory control and data acquisition (SCADA) penetration across the AEP Texas service area. The implementation of SCADA systems will provide transmission operations (TOPS) with the tools needed to make critical decisions during real time operations. This will result in fewer customer interruptions, reduced outage durations, and increased local reliability. The Company installed SCADA at the following stations: Magruder, Portland, Santo Nino, Wesmer, Downie (Customer Station), Javelina, Equistar Bay City, Wadsworth, Walnut Street, Paducah, Walnut Street Switch #4543, Acme Bestwall, and Over Street. | 3780180.59
TP2014195 | AEPTCC Pharr 138 kV Loop | RTO | The ERCOT 2013 Regional Transmission Planning (RTP) identified the North Edinburg - Azteca - South Edinburg - Pharr 138 kV line exceeds the emergency rating under N-1 conditions. To alleviate the overload, the Company another 138 kV source to Pharr 138kV line by tapping the North Edinburg to North McAllen line via a 2.2 mile line. This created a loop feed. | 39575.87
TP2020197 | Air Liquide Station: Pass Thru | Customer Service & Other | This customer driven project was placed into service during a previous rate case, and the credit in the plant in service file is due to customer reimbursement of project costs. | -212981.62
TP2015195 | Airline - Holly New Circuit | RTO | The Company added a new line between the Airline and Holly substations as well as expanded and upgraded both stations. | 169060.61
TP2015196 | Airline - Westside Reconductor | RTO | The Company rebuilt and re-conductored the Airline - Cabaniss 138 kV transmission line. The line is 6.3 miles long; 2.3 miles that are steel double circuit structures were re-conductored and 4 miles that are wood H-frame structures were rebuilt. In addition, station equipment was upgraded to accommodate the 3000 amp path between Airline Station and Westside Station. | 26685.33
TP2014013 | Albany Foundry-Putnam 69KvLine | RTO | The Company rebuilt approximately a 23 mile section of the existing Albany-Putnam 69 kV line as recommended by ERCOT. In addition, a 138 kV insulated point of delivery box bay at Hulltown was constructed and the Albany Foundry through path was upgraded to 138 kV standards. | 14978.66
DISTBLKTX | Distribution Blankets - AEP TX | Distribution Driven Transmission | This project covered various distribution projects in the AEP Texas service area. Some of these projects included associated transmission work on either transmission lines or on transmission station equipment. Associated transmission work under this program included work the following: - Mars Solar - Dimmit Station - Catarina - LaHuerta - Pueblo Station - Zapata Station - Catarina Station - Cherry Creek Station - Alexis Solar | 1367215.73
TP2020088 | Alice-Falfurrias 69 kV Rebuild | RTO | This project rebuilt approximately 3 miles of the 37-mile Alice-Falfurrias 69 kV line. The line was designed to 138 kV standards, but operated at 69 kV. Rebuilding the line to 138 kV standards allows for future conversion when the Falfurrias transformer is retired. The portion of the line that was rebuilt under a previous project, approximately 35 miles transmission line, were already 138 kV capable. | 7718169.19
TP2018209 | Angstrom 345 kV Station SDI In | Customer Service & Other | This was an industrial customer project that was going to add 400 MW of load in the area. The Company built a greenfield 345 kV Angstrom Station with a 3 breaker ring bus. A 0.5 mile cut-in from the STP - Whitepoint 345 kV line was built as single circuit 345 kV design standard steel structures. Approximately 0.9 miles of a 345 kV line was constructed to the point of interconnection (POI). | 9581989.17
TP2020038 | Anson-Radium 69kV Line Rebuild | RTO | This project rebuilt the 7.7-mile Anson-Radium 69 kV line to address NERC reliability standards. The Company rebuilt the Anson - Radium 69 kV line to 138 kV standards but the line is currently operating at 69 kV. This will allow for future growth in the area. This project also included station upgrades at Radium 138 kV Station and Anson 69 kV Station. | 8365217.73
RGTXDCR17 | RGV DACR Workplan | Distribution Driven Transmission | The Distribution Automation Circuit Reconfiguration (DACR) project for the Rio Grande Valley district automated distribution feeder breakers and station regulators at multiple substations in the Edinburg, Mission, and Raymondville area as part of the Smart Grid initiative for AEP Texas. | 1600926.87
TP2021066 | Appaloosa Run Wind | IPP | This was an interconnection project to a 175 MW wind generating facility. The greenfield 138 kV Palouse Station was constructed as a 3 breaker ring bus. The Big Lake - North McCamey 138 kV line had a 0.04 mile cut-in to Palouse completed that was designed single circuit 138 kV steel structures. Approximately 0.04 miles of a 138 kV line was constructed to the generator’s point of interconnection (POI). | 7691913.37
TP2013115 | Aransas Pass - Rockport Improv | IPP | The Company converted the Aransas Pass - Rockport 69 kV line to 138 kV operation to address NERC reliability standards. While the existing line was already constructed to 138 kV standards, major expansion was needed at Aransas Pass and Rockport stations to establish 138 kV ring busses. The addition of a second 138/69 kV transformer at Rockport, retermination of various transmission lines, relocation of distribution lines, and remote end relaying upgrades were included in the project scope. | 82997.67
TP2018187 | Aransas Pass-Seawall 69 kV | RTO | This project rebuilt approximately 3 miles of the Aransas Pass - Seawall line to address NERC reliability standards. The Company rebuilt portions of the Aransas Pass - Seawall 69 kV line to 138 kV standards but is currently operated at 69 kV. The Company also completed associated station upgrades at Seawall and Aransas Pass Stations. | 9473454.4
TP2014121 | Asherton - Carrizo Springs 69 | RTO | This project rebuilt the Asherton to Carrizo Springs 69 kV line. The 2013 ERCOT RTP study identified this line overloading with the loss of the Crystal City to Uvalde 69 kV line. | 55878.67
DP18X0013 | Asherton Sub Upgrade | Distribution Driven Transmission | The Comapny reconstructed the Asherton distribution lowside of the substation with a 69kV/138kV-13.09kV, 10/12.5 MVA transformer, two distribution feeder breakers and approximately 3 miles of feeder reconductor. | 458313.53
TA2018024 | Asphalt Mines Station Rebuild | Reliability | This project was created to rebuild the Asphalt Mines station. A phase to ground fault caused by a raccoon resulted in the entire station burning down driving the need for a complete rebuild. | 1007279.42
TP2019228 | Avenger 69kV Permanent Station | Customer Service & Other | Two customers requested an interconnect to TEC's Atwell Station in Callahan County, Texas for 2 MW of new load. To accommodate the request, the Company installed a new Point of Delivery (POD) (Avenger) approximately 9.5 line miles south of the Putnam 69 kV Station on the Putnam-Cross Plains 69 kV line near structure 10/11 with three switches, a remote terminal unit (RTU), and supervisory control and data acquisition (SCADA). Avenger is a 69 kV phase-over-phase (POP) switch designed to 138 kV to accommodate future load growth in the area. AEP will also install low side metering on the customer's Atwell Station. | 1646263.19
TA2021012 | Ballinger - Santa Anna Rehab | Reliability | This project mitigated 96 conditions identified during inspection of Ballinger-Santa Anna 138 kV line in Runnels and Coleman Counties, Texas. The conditions identified are deterioration of components which include rotten or woodpecker-holed poles, rotten or woodpecker-holed crossarms, and woodpecker-holed X-braces. Two of the 361 structures on the line were completely replaced. | 814883.27
TP2012203 | Barney Davis to Naval Base: New 138kV Line Phase 2 | RTO | This project was created to construct a new 138 kV line between Barney Davis and Naval Base. The plant in service amounts included in ther review period for the current case are trailing charges that occurred after the last base case. | 463.27
TP2015180 | Barrilla Improvements | RTO | The Company rebuilt 37 of 54 miles on the Barrilla Junction/Solstice - Permian Basin 138 kV transmission line with single circuit steel structures to address NERC reliability standards. The bus work was upgraded, existing switches were replaced, and installation of a static var compensator (SVC) at Lotebush Station. | 21947060.37
TP2017123 | Basin 138 kV | Customer Service & Other | ONCOR Electric Delivery Company, LLC (ONCOR) requested a Point of Delivery (POD) on the Solstice to Yucca Drive 138 kV Line to service a 48.5 MW load. To meet the request, the Company installed a new 138 kV box bay, consisting of three line switches, metering, and associated equipment. ONCOR's tap station will be located adjacent to AEP&#39;s right of way and ONCOR will be responsible for constructing the 138 kV transmission line connecting our station to theirs. | 2209954.38
TA2014075 | Bates - Garza 138 kV, Relocate | Customer Service & Other | Texas Department of Transportation (TXDoT) constructed a US 83 relief route. The road's right of way expanded to encompasstwo 138 kV structures. To accommodate TXDOT's request, this projec relocated and raised two 138 kV structures, and added two additional 138 kV support structures. This project was a 100% reimbursable public relocation project. | 153558.1
TP2016001 | Bates - Wormser Increase MOT | RTO | This project increased the line size of the Bates - Wormser line from 795 ACSR to 1272 ACSR and upgrade station equipment so as not to limit the increased line rating MOT of 150 C. | 1065149.92
TP2019190 | Bay City-Lane City 138 kV Line | RTO | The Company rebuilt the 15-mile Bay City-Magill-Lane City 138 kV line to address NERC reliability standards. This project also included associated station work at Lane City, Magill, and Bay City Stations. | 33081680.24
TP2016027 | BayCity&McGillCapBanks | RTO | This rebuild is needed due to the Jourdanton to Pleasanton 69 kV line exceeding its emergency rating for single outages when South Texas Electrical Cooperative&#39;s (STEC) Fowlerton 345/138 kV autotransformer is out of service. The Jourdanton 69 kV Station experiences low voltages for the loss of the Jourdanton to Pleasanton 69 kV line. These issues were identified in the ERCOT 2015 Regional Transmission Planning (RTP) and Western Transmission Planning (WTP) annual assessment. Prior period costs relate to pre-engineering.<br /> | 3511.96
TA2014072 | NERC Physical Security - TX | RTO | NERC issued CIP-014-1 that required AEP to identify and protect Transmission substations critical to the operation of the grid. AEP Transmission developed a 4-Tier approach to the classification of each of its stations. Transmission sponsored phase one of this project to include all work for the currently identified station assets applicable to the NERC CIP-014-1. This program included work on four substations, including low visibility, no-cut fencing, ballistic walls, security cameras, and other physical protection equipment for substations critical to system reliability. | 57349490.95
TA2018010 | Beeville to Goliad 69 kV Line | Reliability | This project rebuilt 25 miles of the Beeville-Goliad 69 kV line to address NERC reliability standards. The line was rebuilt to 138 kV single circuit standards but is currently operated at 69 kV to allow for future load growth in the area. As part of this project, the Company also installed two new station assets. The first is a box bay that was built on existing Company property at Berclair, which was built to 138 kV standards but is currently operated at 69 kV. The second Station asset is the new Baez 69 kV Station, which is a four breaker ring bus expandable to six breakers. | 34019673.21
TP2017245 | Bessel Area Improvement | Customer Service & Other | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -189511
TA2018040 | Big Foot to Dilley | Reliability | This project intends to rebuild and convert the Big Foot to Dilley 69 kV circuit to 138 kV. This circuit will be rebuilt due to age, condition, maintenance burden, and reliability. Most of the issues are caused by aging wooden structures. The conversion is needed to support future load growth in the area. | 16031.13
TP2020095 | Big Foot to Moore rld | RTO | This project rebuilt the 6.1 mile Big Foot-Moore 138 kV line in Frio County, Texas. This project also included associated station upgrades. | 6418744.27
TP2016097 | Bison Station | RTO | Prior to the execution of this project, 14.5 MW of load was served from the radially-fed Powell Field Tap on the Big Lake - McCamey 69 kV Line. The load was transferred from the Big Lake - McCamey 69 kV Line to the Big Lake - Santa Rita 138 kV Line. There was a normally open switch at Powell Field which prevents the load from being networked to the Big Lake - Ozona 69 kV Line. This switch could not be closed with Owls Station in-service because it would have created a three terminal configuration. This project created a new 69 kV three breaker ring bus (Bison Station) at the existing Powell Field Junction Tap. This allowed the normally open switch to be closed, resulting in reduced outages and improved customer quality of service. | 6190904.08
DR20X0004 | Black Cat Construct Station | Distribution Driven Transmission | This project constructed the new Black Cat Substation with a 138 kV / 13.09 kV non-LTC transformer and four feeder breakers and replaced six miles of conductor. The Black Cat Substation was tied into the Bay City/Conoco 138 kV Line. | 3005938.54
TP2019287 | Blackjack Creek Wind Farm | Customer Service & Other | This was an interconnection project to a 240 MW wind generating facility. The existing 345kV Grissom Station was was built out to include a third rung with two breakers added on the third rung and two breakers added to the second rung to convert from a ring bus to a breaker and a half configuration. The Coleto Creek - Grissom 345 kV line was reterminated into one of the new 345 kV terminals. Approximately 0.02 miles of a 345 kV line was constructed to the generator’s point of interconnection (POI). | 12014591.74
TP2019289 | Blessing - Bay City Pump Rebui | RTO | The Company rebuilt 10.8 miles of the Blessing to Bay City Pump #3 69 kV line between Blessing and Markham Tap to address NERC reliability standards. It was designed as steel 138 kV structures but remains currently operating at 69kV. | 16687487.65
TA2021191 | Blessing - Lane City 138 kV | Reliability | This project will rebuild the Blessing to Lane City 138 kV circuit. This circuit is targeted to get rebuilt due to age, condition, maintenance burden, and reliability. Most of the issues are caused by aging wooden structures. | 595.96
TP2020166 | Blessing-Lolita 138kV Rebuild | RTO | This project rebuilt the Blessing to Lolita 138 kV circuit. | 7072.28
TP2015121 | Bobcat Hills Interconnection | IPP | A customer requested a new Point of Interconnection outside AEP's Rio Pecos 138 kV Station to interconnect a 138 kV transmission line that serves as the interconnecting facility to a 109 MW solar plant. The Company added two 138 kV breakers, associated switches, terminal equipment at Rio Pecos Station, and one span of 138 kV transmission line from the station to the dead-end structure outside the station fence. | 2675705.63
TP2018245 | Bond Road Permanent 69kV Switc | Customer Service & Other | Customer requested to interconnect 10 MW of new load in Sutton County, Texas. To accommodate this request, the Company expanded the Bond Road station to accommodate a new switched tap to serve the new customer. The Company installed a remote terminal unit (RTU), metering, supervisory control and data acquisition (SCADA) relays, and a line trap. | 1587014.12
TP2017041 | Brackettville - Escondido | RTO | The Company expanded the Brackettville 138 kV Station, expanded the Escondido 138 kV Station, and constructed a new forty-two mile 138 kV line from Escondido Station to Brackettville Station. The amounts included in the review period for this base case are trailing charges that occurred after the end of the last AEP Texas base case. | 10666.7
TP2019264 | Bravepost Interconnection | IPP | This project provided a Point of Interconnection for a 200 MW solar generator facility in Tom Green County, Texas. In order to meet the customer request, the Company expanded Red Creek Station and installed one 345 kV circuit breaker, added ERCOT Polled Settlement (EPS) metering sub synchronous oscillation (SSO) relays, expanded the drop-in control module, and installed a dead-end structure outside the Red Creek Station fence. | 43.88
TA2015707 | Replace/Refurbish - Texas | Reliability | The projects under this program are part of an on-going, multi-year effort to improve system reliability and dependability by replacing failed assets and assets in danger of imminent failure, and by strategically replacing selected, obsolete assets (both station equipment and transmission line components) that have reached the end of their serviceable lives or that can no longer be properly maintained due to non-availability of parts. During the review period, this program included, but is not limited to, the following work: - Install DICM and replace breakers at Rincon Station - Replace electromechanical relay at EL Campo Station - Circuit breaker and relay replacement at Alice Station - Replace circuit breakers at Equistar Victoria Station - Install Data Fault Recorder at Westside Station - Upgrade equipment at Javelina - Rebuilt 69 kv Station at Aspermont - Rebuild Rule Station to 138 kV | 46733437.34
TA2020250 | Brownsville to La Palma RBLD | Reliability | This project will rebuild the Brownsville Switch to La Palma 69 kV circuit. This circuit is targeted to get rebuilt due to age, condition, maintenance burden, and reliability. Most of the issues are caused by aging wooden structures. | 48515.26
TP2021260 | BRP Antlia BESS Interconnect | IPP | This project was an interconnection to a 70 MW storage farm in Val Verde County, Texas. To accommodate the request, the Company installed a breaker terminal at the Maxwell 138 kV Station along with EPS metering, constructed a dead-end structure outside of the station along with the first span of the 138 kV gen-tie line, installed dual fiber, and installed WSL meters at the generator's collector station. | 1438405.38
TA2022025 | Bruni-Crestonio138 kV, Rep Ins | Reliability | The Company replaced deteriorated polymer insulators on the Bruni-Crestonio 138 kV line to address equipment material condition, performance, and risk as well as operational flexibility and efficiency in Webb and Duval Counties, TX. The Company also added bird guards on 113 structures. | 389607.68
TP2016093 | Build Belknap Station | Reliability | The Company built the greenfield 69 kV Belknap Station with a three breaker ring bus. The Albany - Fort Griffin 69 kV line was terminated into Belknap with a 0.09 miles cut-in. Rainey Creek - Spillway and was terminated into Belkanp with a 0.23 mile cut-in. | 8414811.08
TP2018164 | Build Goodlett Station | RTO | This project built a new 69/12 kV Goodlett Station and retired the Acme Bestwall Station approximately 5 miles west of Quanah, Texas. Customer requested relocation of AEP facilities due to Customer's unground mining activities. | 2937239.67
BUILDING | BUILDING | Customer Service & Other | The new Abilene Transmission Office was acquired under this project. This office was added to accommodate the increase in personnel and equipment needed to support the operation and maintenance of AEP Texas's new customer load growth and aging transmission and station assets. | 1079923.41
DP21X0016 | Bull Moose Skid Project | Distribution Driven Transmission | Two customers requested a combined 16 MVA of additional load for the Sinton location at the SDI site to support customer construction and production. In order to support this additional load, a double circuit feeder was constructed from a skid transformer located on leased property located in Sinton near the Lon Hill to Warburton 138 kV line. This project included installation of a temporary 30 MVA skid transformer and 4 sets of 333 KVA regulators and construction of approximately 4.5 miles of new distribution line. | 61710.26
TP2017237 | Bunsen 138 kV Station | Customer Service & Other | Customer requested 21 MW peak load with 10 MW - 15 MW of transmission service for its facility located near Bunsen 138 kV Station. To accommodate the customer request, the Company acquired right-of-way and constructed a double circuit 138 kV transmission line from Bunsen Station to Customer's station, Texstar. Two 138 kV breakers were installed at Bunsen Station in addition to metering and relaying. | 1532681.66
TP2016096 | Burma Switch Station | RTO | The Company built the greenfield Burma 69kV Station with a 3 breaker ring bus. The Grape Creek - North San Angelo 69 kV line was reterminated for 0.03 miles into the new station and designed as single circuit 138 kV steel structures but operated at 69 kV. The College Hills - Sterling City 69 kV line was cut-in 0.7 miles to the new station. It was designed as single circuit 138 kV steel structures. | 9482250.24
TA2019700 | Burma to Sterling City 69 kV | Reliability | This project rebuilt portions of the Burma-Sterling City 69 kV line in the Sterling City, Texas area. When complete, this project will rebuild approximately 32 miles of 69 kV transmission line from Burma to Sterling City. Portions of the line were placed into service during the review period for this rate case, and the remaining portions of the line will be completed and placed into service at a later date. | 3747218.18
DP19X0008 | Cabaniss Sub- Add second bank | Distribution Driven Transmission | The Company constructed a second transformer bank at the existing Cabaniss Substation in Corpus Christi, TX, installed a 138kV/13.09kV 30 MVA transformer, three distribution feeder breakers, and approximately four miles of feeder work. | 530462.29
TP2017050 | Cactus Flats Perm Interconnect | IPP | This project created an interconnection to a 150 MW wind generation facility on the 138 kV line between San Angelo Power Station (SAPS) and Yellowjacket. This project constructed a new 138 kV switch station (Treadwell) for a permanent interconnection on the SAPS - Yellowjacket 138 kV line. | 7021517.68
TP2016143 | Cactus Flats Temp Interconnect | IPP | This customer driven project was placed into service during a previous rate case, and the credit in the plant in service file is due to customer reimbursement of project costs. | -14301.98
DX17X0001 | Callicoatte Sub-Construct sub | Distribution Driven Transmission | Transmission operations requested two feeders to serve the new Transmission Operations Center near the existing Lon Hill Switchyard in Corpus Christi, Texas. Each feeder needs to be from a separate substation and from a different transmission line in order to meet the North American Electric Reliability Corporation Critical Infrastructure Protection requirements. In order to meet these needs, a feeder extension from Hearn Rd 9665 was built for the first feed. In order to provide the second feed, a new distribution substation was constructed on previously purchased property. It was constructed with a 138/13.09 KV transformer and 3 feeder breakers. The new substation is off of the existing Lon Hill-Warburton Creek transmission line. | 1543447.8
TP2013184 | Campbellton: Whitsett sub | Reliability | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -1491.48
DP17X0005 | Carancahua-Upgrade bank | Distribution Driven Transmission | This project was created to support the upgrade of distribution facilities to serve AEP Texas distribution load. | 82512.21
TP2016025 | CarrizoSprings-CrystalCity69kV | RTO | The Company rebuilt approximately 13.5 miles of the Carrizo Springs - Crystal City 69 kV line to address NERC reliability standards. It was designed as steel 138 kV structures but remains currently operating at 69kV. | 16309691.59
TP2016059 | Carver: New 138 kV Station | RTO | The Company built a greenfield 138 kV Carver Station in close proximity with 138 kV Sonora Station. Carver Station was built with a 4 breaker ring bus, a DICM and two capacitor banks. There was station work completed at the existing Sonora 138 kV Station. Three Transmission lines were reterminated from Sonora Station into Carver Station. There was a bus tie built from the Sonora 138 kV bus to the Carver 138 kV bus. | 15964994.8
TP2013100 | Cassava: New 3 bkr 69kV Sta | RTO | This was one of three projects in West Texas to address voltage issues caused by the load growth from oil and gas production facilities. The other projects are Yucca Area Improvements and Cassava to Yucca line rebuild (TP2012201 and TP2014047 respectively). This program constructed a three breaker ring bus near the Barnhart Phillips Tap. This allowed the Barnhart Phillips Tap to be retired, and the ring bus provides additional sectionalization to reduce exposure from contingencies. | 64356.6
DP21X0022 | Catarina - La Huerta DG | Distribution Driven Transmission | A Customer requested a 10 MW generation facility to be fed off of a new feeder at the Catarina substation. The Company installed a new distribution and transmission remote terminal units to get customer data points and system status points. The Distribution Generation is tied to the new feeder. | 36274.97
DR18X0002 | Causeway Substation | Distribution Driven Transmission | This project added a second transformer at the existing Causeway Substation in Port Isabel, Texas. The Company installed one transformer, one breaker, two circuit breakers, one bus tie breaker, replaced the drop in control module (DICM) and breaker/transformer relays, installed circuit switcher, extended transmission bus work, installed motor operated air break switch (MOAB), and upgraded transmission remote terminal unit (RTU). | 2047268.8
DP19N0002 | Cedar Gap Increase Capacity | Distribution Driven Transmission | This project was created to support the upgrade of distribution facilities to serve AEP Texas distribution load. | 1041213.31
TP2018117 | Chalupa WF Interconnection | IPP | This was an interconnection project to a 174 MW wind generating facility. The greenfield 138 kV Kelvin Station was constructed as a 3 breaker ring bus and a DICM was installed. The La Palma - Rio Hondo 138 kV line had a 0.08 mile cut-in to Kelvin completed that was designed double circuit 138 kV steel structures. Approximately 0.04 miles of a 138 kV line was constructed to the generator’s point of interconnection (POI). | 8579386.68
TP2014064 | Champlin 138 kV Station Expans | RTO | The Company expanded the Champlin (Citgo West) 138 kV Station and reconfigured the existing configuration to a 4 breaker ring bus and a DICM was installed. The Champlin - Lon Hill 138 kV line was reterminated into the station. | 13912079.03
TP2020087 | Champlin to Weil Tract Rebuild | RTO | The Company replaced a guyed structure on the Clarkwood-Champlin West 138 kV line to accommodate the rebuild of the Electric Transmission Texas (ETT) Champlin-Weil Tract 138 kV line and to address equipment material condition, performance, and risk in Corpus Christi, TX. The Company replaced structure 13/1 with a self-supporting steel pole and removed six structures on an abandoned section of line that is supporting the overhead guy span to the west. | 421.43
TP2018010 | Chaparrosa 69kV Box Bay | Customer Service & Other | This project provided a point of delivery to add 9.5 MW of new load in Zavala County, Texas. To accommodate the customer request, the Company constructed a POD box bay that was cut in to the Turtle Creek-La Pryor Tap-Uvalde 69 kV line and included the box bay, three switches, metering, and associated equipment. | 3055256.08
TP2017019 | Cheniere LNG Interconnect | Customer Service & Other | This customer driven project was placed into service during a previous rate case, and the credit in the plant in service file is due to customer reimbursement of project costs. | -277615.99
TP2013082 | Cheniere LNG Project | Customer Service & Other | This customer driven project was placed into service during a previous rate case, and the credit in the plant in service file is due to customer reimbursement of project costs. | -22740.11
DP18N0001 | Cherry Creek Tap - Incr Cap | Distribution Driven Transmission | This project reconstructed the Cherry Creek Station with a 69 x 138 kV / 13.09 kV transformer, two distribution feeder breakers, reconductor 3 miles of feeder, and 3 miles of feeder with 556 aluminum. Only those portions of the project related to transmission assets have been included in this transmission plant in service. | 1676279.39
DP20X0001 | Chocolate Bayou-Upgrade XFMR | Distribution Driven Transmission | The Company upgraded a transformer bank at Chocolate Bayou Substation. The new transformer is a 138kV/13.09kV, 18/24/30 MVA non-LTC transformer. | 478542.5
TA2021002 | Ckt 39 STP to WAP LOC's | Reliability | This project rebuilt the South Texas Project (STP) Corridor-HL&P 345 kV line in Wharton County, Texas to remove five locations of concern (LOC). To resolve these violations, AEP Texas coordinated with WCEC to lower its distribution line assets impacting four of the LOCs and replaced structure 136/1 to resolve the fifth LOC. | 1551808.18
DP18X0001 | Closner Substation | Distribution Driven Transmission | To adequately serve the load in this area and provide better reliability, the new Closner Station was built to offload SE Edinburg and North Edinburg Substations. The substation include two 138kV/13.09kV transformers, six regulators, four breakers, two totalizer breakers, and one bus tie breaker. | 5622609.42
TP2019244 | Conan 69 kV Box Bay | Customer Service & Other | This project was needed to address additional load for a pipeline customer to the Conan Tap located on the Cross Plains-Santa Anna 69 kV line in Callahan County, Texas. The customer was fed from a hard tap on the Cross Plains-Santa Anna 69 kV line via an approximately 3.3 mile radial line. The Company removed the Dressy hard tap and installed a permanent box bay station (Conan) that was built to 138 kV but is currently operated at 69 kV. This project also rebuilt a 0.3-mile section of the Cross Plains-Santa Anna line to 138 kV design to match the rest of the Cross Plains-Santa Anna 138 kV line that was rebuilt as part of a previous project. | 4162015.2
TP2020065 | Concho Valley Solar | IPP | This was an interconnection project to a 150 MW solar generating facility. The greenfield 138 kV Maddux Station was constructed as a 5 breaker ring bus. The Menard - San Angelo 138 kV line had a 0.1 mile cut-in to Maddux completed that was designed single circuit 138 kV steel structures. The San Angelo Power - Eldorado Live Oak 138 kV line had a 0.07 mile cut-in to Maddux completed that was designed single circuit 138 kV steel structures. Approximately 0.06 miles of a 138 kV line was constructed to the generator’s point of interconnection (POI). | 14682196.13
DR18X0003 | Continental Sub - Rebuild Sub | Distribution Driven Transmission | This project rebuilt the Continental Substation to bring it up to current standards. The Intellirupters and existing relaying and breaker system were inadequate and had to be replaced. Because the existing steel and foundations were not able to sustain the installation of the new equipment necessary to bring the substation to current standards, the new Continental Substation was built in the clear on the existing property. | 1114042.32
TP2017093 | Convert Solstice-Ft Stockton-R | RTO | The Company rebuilt 16.5 miles of the Barrilla Junction-Ft. Stockton Sw 69 kV line to 138 kV, converted 45 miles of the Ft. Stockton Sw-Rio Pecos 69 kV line to 138 kV, and built a greenfield Ft. Stockton Sw 138 kV ring bus station to address NERC reliability standards. As part of the conversion, new in and out stations with 138 kV switches and 138/12 kV transformers will be installed at Sun Valley, Masterson Field, and Pecos Valley. In addition, because the existing Ft. Stockton Sw Station is a 69 kV station, a new greenfield 138 kV ring bus station was built near the existing Ft. Stockton Sw Station and both converted lines were terminated into the new station. | 37983882.73
TP2018143 | Corichi 138kV POP: Gray Oak | Customer Service & Other | Customer requested an interconnect for an 11.5 MW load to the El Campo-Victoria 138 kV line in Wharton County, Texas. To address the customer request, the Company constructed a Corichi 138 kV POP switch approximately 13 line miles south of the El Campo Station on the El Campo-Victoria 138 kV line at structure 43/6. | 2273358.15
TA2019371 | Corpus Area Telecom Modernizat | Telecom | This project covered the AEP Texas Transmission Telecommunication Modernization Program (TTMP), which built out a robust telecommunication network to support the transmission system. This program built 27.2 miles of AEP-owned fiber that provides connectivity to nine stations, increases resiliency at nine stations, and provides resiliency via new fiber ring topology to nine stations. This program replaced one obsolete RX1000 router and eliminated nearly $14K in annual lease line expenses while enhancing the telecommunication reliability by addressing single points of failure throughout the fiber network. | 4602581.1
CCTXDCR17 | Corpus Christi DACR Workplan | Distribution Driven Transmission | The Distribution Automation Circuit Reconfiguration (DACR) project for the Corpus Christi district automated distribution feeder breakers and station regulators at multiple substations in the Corpus Christi, Victoria, and Rockport areas as part of the Smart Grid initiative for AEP Texas. | 1697062.67
TP2018159 | Crane Area Improvement | RTO | The Company built the new 138/69 kV Heron Station, rebuilt and converted approximately 2 miles 69 kV line, and upgraded Kinnison and Sage Stations to address planning criteria violations, equipment material condition, performance, and risk as well as customer service in the Crane County, TX area. The Company built the new Heron 138/69 kV Station by installing one 138/69 kV transformer, three 138 kV breakers, and one 69 kV breaker, rebuilt Kinnison 138 kV Station by installing one 138/69 kV transformer, three 138 kV breakers, and four 69 kV breakers, modified Sage Station by removing three 69 kV switches, and rebuilt ~2.0 miles of existing 69 kV line between Heron and Ollin Stations and converted to 138 kV | -5.56
TP2018109 | Cranell WF Interconnect | IPP | This was an interconnection project to a wind generating facility. The 345 kV Grissom Station was constructed with a breaker and half configuration and a DICM . This project also included cutting 0.3 miles 345 kV single circuit steel structures from the Lon Hill - Coleto Creek 345 kV Line into the new Grissom Station. One span of the 345 kV single circuit line was constructed outside the station fence to the generator’s point of interconnection (POI). | 26702687.07
TP2020182 | Creosote 138 kV Station | Customer Service & Other | The Company built a greenfield 138 kV Creosote Station. Creosote Station was built with a 4 breaker ring bus. The Lotebush - Pig Creek 138 kV line had a 0.08 mile cut-in to Creosote Station completed that was designed single circuit 138 kV steel structures. Approximately 0.04 miles of a 138 kV line was constructed to the generator’s point of interconnection (POI). | 11227439.76
TP2018020 | Crossover 138 kV Box Bay | Customer Service & Other | This project constructed a new box bay, Crossover, and approximately 1800 feet of transmission line to serve a new customer point of delivery for approximately 10 MW of new load. The new box bay was cut in to the North McCamey - Santa Rita 138 kV Line. | 3327154.51
TA2019150 | Crowell - Lake Pauline | Reliability | The Company rebuilt the 23-mile the Crowell-Lake Pauline 69 kV line using a 138 kV design (operated at 69 kV), constructed the Argurita Tap Switching Station to replace Liberty Tap, and performed jumper replacement at Crowell Station. | 72.22
TP2021587 | Cruce 345 kV Station Property | RTO | This project purchased property for the planned Cruce 345 kV Station as part of the Lower Rio Grande Valley (LRGV) System Enhancements project to address operational flexibility and efficiency, infrastructure resilience, and system needs in Duval County, TX. This project was a standalone project completed before the station build project because AEP needs control of the property before filing CCNs for the upcoming LRGV System Enhancement project. AEP Texas purchased enough property (75 acres) to facilitate a four-rung, 345 kV breaker-and-a-half station near the county lines between Duval, Brooks, and Jim Hogg Counties. | 5375.01
TP2022033 | Cruce to Reforzar 345 kV | RTO | This project was created to construct a new 345 kV line between Cruce and Reforzar. As part of the Lower Rio Grande Valley (LRGV) System Enhancement Project study, ERCOT identified system improvements were needed by 2027 due to a combination of load growth, limited conventional generation, and limited transmission infrastructure. Outages on one of the three 345 kV circuits serving the LRGV or one of the large conventional generators could result in under voltage load shedding, major congestion, and/or strain on GTCs. Adding a fourth 345 kV line to the LRGV and tying it to three sources significantly improves service and reliabilit for the LRGV area. | 95.14
TP2017222 | Cryo 138 kV Substation | Customer Service & Other | This was an industrial customer project that was going to add 50 MW of load in the area. The Company built a greenfield 138 kV Cryo Station with a 3 breaker and a half, a 138 kV/12 kV transformer, and DICM. A 5 mile 138 kV greenfield line from Cryo - Saragosa was built as a single circuit 138 kV design standard steel structures. Approximately 0.07 miles of a 138 kV line was constructed to the point of interconnection (POI). | 12149147.76
DP18X0009 | Darst Creek- LCRA Rebuild | Distribution Driven Transmission | The Company constructed the new Darst Creek Substation on Lower Colorado River Authority (LCRA) purchased land with two 69kV/13.09kV 25 MVA transformers, five distribution feeder breakers, and approximately 2 miles of feeder reconductor. | 784396.53
DP18X0016 | Del Mar-Upgrade Transformers | Distribution Driven Transmission | The Company reconstructed the Del Mar Substation with two 138/13.09 kV 40 MVA transformers, replaced six distribution breakers and reconductored 1.5 miles of feeders | 461116.88
TP2018043 | Dilley -Charlotte 69kV line | RTO | The Company rebuilt approximately 45 miles of the Dilley-Charlotte 69 kV line to address NERC reliability standards. The line was rebuilt to 138 kV standards but still operating at 69 kV. This project also included associated station work at both the Dilley 69 kV Station and the Jourdanton 69 kV Station. Dilley had to upgrade buswork. | 43579512.7
TA2018070 | Live Oak to Sonora | Reliability | This project rebuilt approximately 24 miles of the Live Oak-Sonora 69 kV line in Live Oak, Texas. The Company rebuilt the existing 69 kV line to 138 kV standards, but the line will initially be operated at 69 kV. This provides a high capacity future 138 kV path at minimal cost. This project also included buiding a new station, rebuilding the Shell Bailey Tap, and upgrading the Sonora Station. | 2984011.66
TP2019020 | Dobbin 138 kV Station Skid Tap | Customer Service & Other | This project was created to construct a new 138 kV hard tap to serve a new 6 MW industrial load. A hard tap was selected due to the timeline requested by the customer. | 37987.32
TP2018027 | Dolan Creek 138kV | Customer Service & Other | This project built the new Dolan Creek 138 kV Station to serve a new transmission point of delivery to serve 9.5 MW of load. The new delivery point is supplied from the Maxwell-Sonora 138 kV line. Dolan Creek Station included a box bay with motor-operated switches. | 5764959.7
TP2022135 | Dupont to LGE 138 kV | RTO | This project was placed in service during a previous rate case review period and the amount reflected in transmission capital is a trailing charge. | 26.74
DP19X0006 | Dustdevil Const New Stattion | Distribution Driven Transmission | The Company constructed a new distribution station, Dustdevil Substation, on an Electric Transmission Texas (ETT) owned 138 kV transmission line with one 138/13.09 kV 40 MVA transformer, three distribution breakers and two miles of feeders. This project alleviated the overload at University Substation and will allow for future residential and commercial growth capacity in the area. | 395862.31
TA2022036 | E Munday - Lake Pauline | Reliability | The Company rehabed 40 issues identified during inspection of the East Munday-Lake Pauline 138 kV line to address equipment material condition, performance, and risk as well as operational flexibility and efficiency in Knox and Haskell Counties, TX. The conditions identified were deterioration of components which include rotten poles, rotten, split, or woodpecker holed crossarms, and woodpecker holed X-braces. The Company replace four structures out of the 475 structures in the line. | 284903.84
TA2022037 | E Munday - Paint Creek #1 Reha | Reliability | This project mitigated 169 issues identified during inspection of the East Munday-Paint Creek Station 1 138 kV line in Knox and Haskell Counties, Texas. The conditions identified are deterioration of components which include rotten poles, rotten, split, or woodpecker holed crossarms, and woodpecker holed X-braces. To address known conditions, this project will replace 16 structures out of the 227 structures in the line. This is a Class 4 estimate (+50%/-30%).</p> | 860513.14
TA2020082 | Eagle Pass Substation | Reliability | This project removed the Eagle Pass high-voltage direct-current (HVDC) facility in the Maverick County, TX area. This project is driven by the need to remove aging HVDC infrastructure that is no longer in use at the Eagle Pass 138 kV Station. The HVDC facility chillers and building cooling system contain glycol, which is considered an environmental contaminant. Removal of the HVDC facility will reduce the risk of environmental contamination and future O&M expenses. The Block Load Transfer relaying was upgraded to allow the Block Load Transfer on the Mexico Comision Federal de Electricidad line to operate. The project installed the smallest DICM to house relaying, and the existing HVDC equipment and control building was removed. | 2429814.6
TP2014050 | EF 90 (Lorentz): Temporary Tap | Customer Service & Other | This customer driven project was placed into service during a previous rate case, and the credit in the plant in service file is due to customer reimbursement of project costs. | -5436.59
TP2020068 | El Algodon Interconnection | IPP | This was an interconnection project to a 200 MW wind generating facility. The greenfield 345 kV Katoen station was constructed as a 3 breaker ring bus and included a DICM in the fence. The Lon Hill - Goddard 345 kV line had a 0.09 mile cut-in to Katoen completed that was designed single circuit 345 kV steel structures. One span of the 345 kV line was constructed outside the station fence to the generator’s point of interconnection (POI). | 16734076.24
TA2017960 | El Campo - Lane City Pump 138 | Customer Service & Other | The Company relocated transmission line structures on the El Campo-Lane City Pump 138 kV line to accomodate the Texas Department of Transportation (TxDOT) road modification project. TxDOT requested AEP relocate structures on the El Campo-Lane City Pump 138 kV line to accomodate its Texas US 59 Overpass project in Wharton County, TX. The Company removed and replaced the existing structures on the El Campo-Lane City Pump 138 kV line. | 18678.25
TP2021023 | El Sauz Wind Interconnection | IPP | This project installed equipment to accommodate a new interconnection for a 302 MW wind farm in Willacy County, Texas. This project included retermination of the Ajo 345 kV line to a new 345 kV terminal at Cebolla Station and repurposed the existing Ajo 345 kV line terminal to accommodate the new El Sauz Ranch gen-tie line. | 6922288.45
TP2020061 | Enterprise Lake Low Side Meter | Customer Service & Other | Two Customers requested to increase capacity from 7.5 MW to 28.5 MW at the delivery point in the Paint Rock, TX area. One Customer added an additional interconnection at the station known as Enterprise Lake Ivie that required the Company to add low side metering. The meter is a check meter. | 25231.24
TA2021055 | Eola Tap 69 kV Line Rebuild | Reliability | The Company rebuilt 12 miles of the Eola Tap 69 kV line using 138 kV design and 69 kV operation. In addition, there is a nearby customer-owned line that was converted to 138 kV operation. | 74.03
TA2020059 | Equistar Island Scheme Upgrade | Customer Service & Other | The Company installed an uninterruptible power supply (UPS) to serve the existing Military Highway Static Synchronous Compensator (STATCOM) and upgraded the STATCOMs human machine interface (HMI). | 2622.6
TA2020728 | ERCOT 2020 TCC-Storm Recovery | System Restoration | On July 27, 2020, the Category 1 Hurricane Hanna swept through the valley area of Texas, causing many power outages across the region. A large amount of congestion was due to an ~2-mile section of the North Edinburg-North McAllen 138 kV line having fallen during the storm. This particular line also has a second circuit, the North Edinburg-McColl Road circuit, causing even more strain on the system. The 2-mile section of line in question was comprised of 35 double circuit, single-wood pole structures that were broken. These structures were replaced with single, concrete pole structures with double circuit, braced posts insulators. This restoration project included the replacement of utility poles, line structures, station equipment, and fences to restore service. | 5401214.04
TA2020132 | ERCOT CIP-002 IROL Mitigation | RTO | Effective October 1, 2020, ERCOT designated Interconnection Reliability Operating Limits (IROL) for 14 stations owned and operated by AEP Texas. The Company updated station equipment at each of the stations to meet NERC compliance. The Company installed physical security (card readers and cameras), electronic security (firewalls), and device level measures such as the installation of SDR computers, segregation of LAN network segments, and upgrading of station protection and control devices and/or firmware. | 2222509.82
TA2019045 | Port Lavaca Area Upgrades | Reliability | The Company rebuilt 46 miles of line and rebuilt/upgraded stations and lines to address planning criteria violations, equipment condition and risk, and operational flexibility in Calhoun County, TX.The Company rebuilt the 12-mile Carbide-Port Lavaca 69 kV line at 138kV, 12 miles of Carbide-Joslin a 138 kV, 2 miles of Point Comfort-Caranchua 69 kV, 0.05 miles of Blessings-Palacios 69 kV, 2.0 mile Port-Brookhollow 69 kV line, and 18 miles of Port Lavaca-Victoria 69 kV at 138 kV. The Port Lavaca 69 kV Station was be rebuilt as the 138/69 kV Cangrejo Station, Placedo Station was rebuilt as the 138/12 kV Beecher Station, and a new Dacosta 138 kV Station was built on the Dupont-Joslin 138 kV line on newly-acquired land. | 2319243.28
TA2016921 | ERCOT Region Major Eq/Spare Pr | Reliability | This three-year program (2017-2019) included of specific asset replacement projects, replacement of failed equipment, and the purchase of major spare and mobile equipment for the transmission and distribution systems. The program is part of an on-going effort to improve system reliability and dependability by replacing equipment that has reached the end of its serviceable life, and by purchasing long-lead-time equipment that will become system spares. The equipment purchased mainly consist of capital spare transformers, spare reactors, spare circuit breakers, mobile transformer stations, and spare transmission line towers. | 5073308.86
TA2019130 | Munday - Throckmorton | Reliability | This project rebuilt approximately 35 miles of the Munday-Throckmorton 69 kV line and performed select station upgrades in the Knox and Throckmorton Counties, Texas area. The Munday-Throckmorton 69 kV line was rebuilt to 138 kV standards but will continue to operate at 69 kV ratings which will both facilitate a long-term plan for the area by creating a 138 kV loop as well as increase the MVA rating, load expansion, and generation serving capability in the area. Additionally, this project will rebuilt 1.3 miles of an existing double circuit section of the East Munday-Painted Creek 2 138 kV line which shares transmission structures with Munday-Throckmorton 69 kV. As part of this project, the Company also installed a new 69 kV breaker, associated switches, an RTU installed with a new DICM at the Throckmorton Station and two SCADA-controlled motor operated switches installed at the Woodson Oil Station. | 4776135.16
TA2019508 | TX - Meter Modernization 2021 | Reliability | The ERCOT Meter Modernization Initiative (MMI) addressed metering points across the Transmission system that were impacted by poor physical condition or obsolete equipment. Additionally, it sought to ensure that regional transmission organization (RTO) accuracy standards are followed across the AEP system. This program addressed communication issues at Acacia, B.P. Chemical, Campwood, Carbide, Citgo N. Oak Park, Coffee Port, Coleto Creek, Formosa/Formosa Plastics, McAdoo, Pelican, Randado, Rio Hondo, Spur, and Victoria Plant Stations. It also proposes to upgrade meters and/or meter panels at B.P. Chemical, Campwood, Coffee Port, George West, and Rio Hondo Stations. Additionally, instrument transformers will be upgraded at B.P. Chemical, Formosa/Formosa Plastics, and Rio Hondo Stations. | 1467004.55
TA2019090 | Escondido - Hamilton Road | Reliability | The Company rebuilt the 54-mile Escondido-Hamilton Road 138 kV line to address equipment material condition, performance, and risk, as well as, infrastructure resilience and customer service in the Eagle Pass, TX area, and made necessary related upgrades at Escondido, Ganso, Maverick, and Hamilton Road 138 kV Stations | 34660.11
TP2015099 | Escondido-Eagle Pass Line Rebu | RTO | This project was created to rebuild the Eagle Pass to Escondido 138 kV circuit #1 line. The 2014 ERCOT RTP study identified this line overloading with the loss of the Eagle Pass to Escondido 138 kV circuit #2 line by the summer of 2015. | 53.75
TP2012201 | Esmeralda to Yucca | RTO | The Company constructed a new distribution substation, Fincas, along Hwy 359 in East Laredo, with one 138/13.09 kV 25 MVA transformer, three distribution breakers and constructed 1.5 miles of feeders. | 2754.02
TP2018048 | Esperanza 138 kV Substation | Customer Service & Other | An industrial customer requested 50 MW of new load for an industrial facility. To accommodate the customer request, the Company built a greenfield 138 kV three-breaker ring bus, installed a DICM, two capacitor banks with breakers, and installed 0.64 miles of double circuit greenfield 138 kV Experanze Extension to cut the new station in from the Blessing - Celanese 138 kV line. A DICM was installed at the Celanese 138 kV station with some other station upgrades completed as well. | 16547916.61
TP2012157 | Euler Station | RTO | This project constructed a greenfield 138 kV station at Euler to address NERC reliablity standards. The new station is a three breaker ring bus. The Company also constructed a greenfield 55-mile double circuit capable 138 kV line between Coleto Creek and Tuleta and performed associated station upgrades at Coleto Creek Switching Station and Tuleta Station. | 72375513.4
TP2016070 | Exxon GCGV Project Perm Power | Customer Service & Other | A customer requested approximately 230 MW of new industrial load in the area near the Dupont - Whitepoint 138 kV line. To meet the customer need, AEP Texas acquired property and built the new Gibbs 138 kV substation, a six breaker ring bus expandable to a three rung substation. Relay settings were updated and relay panels were installed at the McCampbell 138 kV Substation and Whitepoint 138 kV Switching Station. This project also included construction of approximately 0.9 miles of transmission line to cut in the new Gibbs 138 kV Station to the existing McCampbell - Whitepoint 138 kV line. | 4524174.89
DP19X0001 | Falfurrias Sub Rebuild | Distribution Driven Transmission | This project rebuilt the distribution station at Falfurrias Substation with two 138/13.09kV transformers, four distribution breakers and reconductored three miles of feeders. The transmission costs included in the review period are for associated transmission work performed to accommodate this project. | 1520751.08
TA2020141 | Falfurrias to North Edinburg | Reliability | The Company modified the existing monopole structure delta design of the 65-mile Falfurrias-North Edinburg 138 kV line by replacing 623 structure davit arms with brace post construction. | 7036326.24
TP2015181 | Far West Project | RTO | This station and transmission line project was part of the larger Far West Texas project endorsed by ERCOT. This project included approximately 40 miles of new double-circuit 345 kV line between Solstice and Bakersfield stations and a major expansion at the Solstice Station. The 345 kV Solstice Station was expanded to accommodate four 345 kV circuits, two 345 kV auto transformers, one 345 kV bus shunt reactor. The cost of the Far West project was allocated between the Company and other operators. | 123843329.02
DP20X0016 | Fincas-Construct New Station | Distribution Driven Transmission | The Company installed a 28.8 mega volt ampere reactive (MVAR) shunt capacitor at Magill 138 kV station and a 14.4 MVAR switched shunt capacitor at Bay City 138 kV station in Matagorda County | 2817.94
TA2021052 | Flomot Tap 69 kV Line Rebuild | Reliability | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -5788.26
TP2019195 | Flomot Tap Improvement | Reliability | This project installed a new motor operated switch with SCADA controls on the radial side of Flomot Tap. The Flomot load is served by a 7-mile radial line tapped off the main line. This radial line between Flomot Tap and Flomot is very old, in poor condition, and has experienced numerous outages over the years. There is not a switch on the radial side of the tap, so whenever maintenance is performed on the radial, the loads at Turkey Lighthouse and Turkey lose their source. Those loads cannot be picked up by SPP because the normally open portion between Estelline and Turkey is in such bad shape, it cannot be safely energized. To remediate this issue, the Company installed a new motor-operated switch with SCADA controls on the radial side of Flomot Tap, which will allow the main line to be energized while maintenance is being performed on the 7-mile radial line to Flomot. | 1373802.47
TP2014063 | Fort Mason to Mason Rebuild | RTO | This project rebuilt the Fort Mason to Mason 69 kV line and upgraded the Fort Mason 138/69 kV autotransformer to address NERC reliability standards. The new autotransformer was installed at Mason Station, and the new line was constructed and operated at 138 kV. | 7125299.84
TP2018163 | Foxtail Station Reactor | RTO | This project added a 50 mega volt - amperes reactive (MVAR) reactor at Foxtail Station on the Oklaunion-Mulberry Creek 345 kV line. In May 2015, a tornado damaged several structures between the Foxtail and Oklaunion Stations, which isolated Foxtail Station from Oklaunion line reactor. When the Oklaunion-Foxtail 345 kV line is out of service and area wind farms are offline, Foxtail Station experienced extremely high voltages, which caused the generators to trip during startup. To mitigate these high voltages, AEP Texas will add a 50 MVAR reactor to Foxtail Station. | 4524423.47
TP2020080 | Foxtrot Wind | IPP | This was an interconnection project to a 504 MW wind generating facility. The greenfield 345kV Tango Station was constructed as a 3 breaker ring bus and included a DICM in the fence. The Goddard - Pawnee 345kV line had a 0.13mi cut-in to Tango completed that was designed single circuit 345kV steel structures. One span of the 345 kV line was constructed outside the station fence to the generator’s point of interconnection (POI). | 18228257.54
TP2022897 | Frontera Interconnection | IPP | This project was created to provide a point of interconnection for a 535 MW combined cycle generating facility near the Frontera 138 kV station. AEP Texas and Customer signed an interconnection agreement to connect the generating facility to the grid. | 1165134.99
TP2018023 | Ft Stockton Pt to Solstice MOT | RTO | This project replaced thirty-two structures on the Ft. Stockton Plant - Solstice 138 kV Line to address NERC reliability standards. The load forecast in Pecos and Reeves Counties in West Texas continue to increase due to the aggressive oil and gas activity in the Delaware Basin. | 1604977.95
TP2015187 | Ft. Griffin Station | RTO | The Company built a new 69 kV station, Ft. Griffin, near the existing 69 kV Albany Station as recommended by ERCOT. The existing Rainey Creek and Putnam 69 kV lines that terminated in the Albany Station were re-terminated into the new Ft. Griffin Station and the 69 kV line sections between Albany and Ft. Griffin were rebuilt to the existing Albany Station to support the existing distribution load. | 287655.86
TA2019047 | Ft.Griffin- Albany Foundry 69 | Reliability | The Company rebuilt the entire 4.66 mile Albany Foundry - Fort Griffin 69 kV line for single circuit 138 kV steel structures but operated at 69 kV. A greenfield Salt Prong 138 kV box bay was installed on the line at the previous Hubbard Tap #1 location that currently operates at 69 kV. | 8305226.58
TP2016131 | Ganso Three Breaker Ring | Reliability | The Company construcedt a new station (Ganso) near Eagle Pass hydro in Maverick County, TX.The Company purchased approximately 5 acres for the new 138 kV three breaker ring bus substation in line with the Escondidio to Hamilton Road line located beside the existing Eagle Pass hydro tap poin.The Company constructed a new three breaker ring bus to improve the reliability of service to the generator as well as system reliability. | 312529.06
TA2018044 | Garza Station | Reliability | This project upgraded assets at Garza Station in the area of Rio Grande City, Texas. The Company expanded the yard to replace four 69 kV and two 138 kV circuit breakers, installed a 69 kV transformer low side circuit breaker, replaced the transformer high side circuit switcher, installed a new DICM, and upgraded the existing electromechanical relays and associated equipment at Garza Station. | 7115036.65
TA2020034 | TNC Abilene 2023 TTMP | Telecom | This project cover the AEP Texas Transmission Telecommunication Modernization Program (TTMP) in the Abilene area, which built out a robust telecommunication network to support the transmission system. | 444252.4
TP2019231 | Gila-Whitepoint 138 kV Upgrade | Customer Service & Other | This customer driven project was placed into service during a previous rate case, and the credit in the plant in service file is due to customer reimbursement of project costs. | -2739.7
TP2017004 | Gillrina 69 kV Sub:STEC | Customer Service & Other | This was an interconnection project with STEC and the new Gillrina 69 kV Station. The greenfield Gillrina Station was constructed as a 3 breaker ring bus and a DICM. The Stadium - Calallen 69 kV line had a greenfield 0.09 mile cut-in to Gillrina completed that was designed single circuit 138 kV steel structures but operating at 69 kV. | 8191510.88
TP2015170 | Goliad 69 kV Station Upgrade | Telecom | The Company converted the Goliad 69 kV Station to a 138 kV capable station to improve reliability and reduce affected customers by any future outages. To mitigate the reliability concerns of this line, the Company did the following: Added a 138 kV design box bay with two breakers, expandable to three breakers and operated at 69 kV. Expanded the existing drop in control module to 16x27 to accommodate additional relay requirements. Re-terminated the Beeville - Goliad 69 kV line into Goliad breaker position. Re-terminated the Goliad - Fannin 69 kV line into Goliad breaker position. | 98574.4
TP2017040 | GVEC Interconnect:138kV Box By | Customer Service & Other | Customer requested to interconnect to the Coleto Creek-Kenedy 138 kV line in Goliad County, Texas. In order to accommodate the new Point of Delivery (POD), the Company constructed a new Rosata permanent 138 kV POD switch ~15 line miles west of the Coleto Creek 138 kV Station and tied it into the Coleto Creek-Kenedy 138 kV line. Relays were replaced at Coleto Creek Station as part of this project. | 1867826.79
DP19X0018 | Haisley add second bank | Distribution Driven Transmission | The Company installed a 138kV/13.09kV, 15/30MVA non-LTC substation transformer to the Haisley substation with an urban bay distribution bus designed for four feeder breakers, installed two-1200A circuit breakers, totalizer and circuit switcher, and three-1000/1120kVA regulators. The Company also reconfigured feeders to the existing customer | 508069.59
TP2017036 | Hamilton Rd - Picacho 138 kV | RTO | This project rebuilt the entire 8.7 miles of the Hamilton Road - Picacho 138 kV line with single circuit 138 kV steel structures to address NERC reliability standards. The Company also completed associated station work at Hamilton Road and Picacho Stations. | 8606935.77
TP2017043 | Harlingen SS - Raymondville #2 | RTO | This project increased line and station capacity to address NERC reliability standards. The Company converted the Raymondville #1 - Raymondville #2 69 kV line to 138 kV standards and is currently operating the line at 138 kV. Raymondville #1 69 kV Station was converted to 138 kV. The Raymondville #2 Station was rebuilt to a ring bus and a new DICM was installed. The Harlingen #1 Station had all 69 kV breakers replaced. The Harlingen Switching Station moved the Harlingen SS - Raymondville #2 line from the 69 kV position to the empty 138 kV position. A new 138 kV breaker was added to maintain the ring configuration as well as the replacement of three 69 kV breakers. With the new ring bus at Raymondville #2, there was retermination of the lines: Harlingen SS - Raymondville #2 138 kV, Raymondville #2 - Armstrong 138 kV, Raymondville #2 - STEC La Sara 138 kV, and Ramondville #2 - Rio Hondo 138kV. | 20590191.02
TP2014137 | Hawley Tap-Onyx SW Rebuild | RTO | The Company rebuilt approximately five miles of transmission line as 138 kV from Hawley Tap Station to Onyx Station and upgraded the associated limiting series equipment. The rebuild contained sections of distribution underbuild that went through the town of Hawley on the same centerline.The Company also added motor operators and supervisory control and data acquisition (SCADA) to the switches being replaced at Hawley Tap and Onyx Station to sectionalize the line. Hawley Tap was replaced with Zelo Station, a point of delivery box bay station asset with three switches and SCADA; Onyx Station had three switches replaced and new motor operators and SCADA were installed | 10278.91
TP2019050 | Hayter: Box Bay 138 kV | Customer Service & Other | A customer requested new 138 kV service to add 10 MW of new load in Pecos County, Texas. In order to meet the customer need, the Company constructed a 138 kV POD station (Hayter) approximately 1.8 line miles south of the Solstice 138 kV Station on the Alamito Creek-Solstice 138 kV line at retired structure 2/6. | 3197810.35
TP2019164 | Hecker-Whitepoint 138kV Recond | RTO | The Company reconductored 5.7 miles of the double circuit Hecker - Whitepoint 138 kV line to address NERC reliability standards. The existing structures were left in place and new insulator and conductor was installed for both circuits on the line. | 8396198.12
DP18X0015 | Heines Sub- Construct new Sub | Distribution Driven Transmission | This project constructed the new Heines Substation on previously purchased land. The new substation included two 138kV/13.09kV transformers, five distribution feeder breakers, and approximately 7 miles of feeder reconductor. Only those portions of the project related to transmission assets have been included in this transmission plant in service. | 1834428.77
TP2014039 | Hindes: STEC Interconnection | Customer Service & Other | This customer driven project was placed into service during a previous rate case, and the credit in the plant in service file is due to customer reimbursement of project costs. | -57865.92
TP2021285 | House Mountain BESS 69 kV | IPP | Customer requested to interconnect its 62.32 MW battery storage facility to the AEP transmission system in Brewster County, Texas. To accommodate the request, the Company installed a new station terminal with one 69 kV breaker, disconnect switches, and EPS metering at Bronco 69 kV Station. | 2493957.07
TP2021070 | Hyperion 345 kV station | Customer Service & Other | This was an interconnection project to a new 200 MW wind generating facility in Dickens County, Texas. In order to facilitate this request, the Company constructed a 345 kV fenced station as an extension of the customer-owned Helios 345 kV Station. The Company installed a slack span from the Wind Energy Transmission Texas dead-end structure leading to the metering facilities within the AEP-owned Hyperion Station and a slack span from the metering facilities with the AEP station to a dead-end structure located outside of the Hyperion Station. The dead-end structure is owned by and was installed by the IPP and will be the demarcation of ownership between the Company and the IPP. | 1601097.21
TP2020066 | Install Capacitor Bank at Magn | RTO | This project installed a 15.4 MVAR capacitor bank and a 138 kV circuit breaker at Magnolia Station. Additional upgrades are being made to Magnolia Station on a separate Distribution project (DP20X0018) to install a new transformer to support 8MW of load. | 1104676.03
DP20X0002 | James Rowe Substation | Distribution Driven Transmission | The Company constructed the new James Rowe Substation to relieve loading on West McAllen Substation. The substation includes two - 138 kV/13.09 kV 24/32/40 MVA transformers, six - 2000 kVA regulators, four - 1200 amp breakers, two - 3000 amp totalizer breakers, and one - 2000 amp bus tie breaker. There was also 4.35 miles of distribution line work (2.39 miles new installation and 1.96 miles reconductoring) accompanying the new station install. | 397.04
TP2012155 | Javelina Wind Farm Inter | IPP | This project was created to provide a temporary point of interconnection for a generating facility. Javelina is a 250 MW wind generating facility near the Wormser Road to Zapata 138 kV line. AEP Texas and Customer signed an interconnection agreement to connect the generating facility to the grid. The PUCT substantive rules mandate that the TSP construct interconnection facilities for new generation. | 550.94
TP2016026 | Jourdanton-Pleasanton69kVline | RTO | The Company rebuilt the Jourdanton to Pleasanton 69 kV transmission line (approximately 5 miles) and upgraded the Jourdanton Station. The line was rebuilt to 138 kV specifications and operats at 69 kV currently until more load is required; Additionally the Company installed two switched shunt capacitors at Jourdanton 69 kV Station. | 3648.87
TA2021013 | Junction - Mason Sw Rehab | Reliability | The Company replaced nine out of the 676 structures on this line. | 596468.09
TP2017068 | Junction Station Rebuild | RTO | This project rebuilt the Junction Station as a new 69 kV box bay station with two 69 kV circuit breakers. | 3355594.03
TP2018067 | Kaiser Creek Interconnection | IPP | This project was created to provide a point of interconnection for a generating facility. Kaiser Creek is a 100 MW wind generating facility near the East Abilene to Putnam 138 kV line. AEP Texas and Customer signed an interconnection agreement to connect the generating facility to the grid. The PUCT substantive rules mandate that the TSP construct interconnection facilities for new generation. | 6.19
TP2018044 | Karankawa II WF Interconnect | IPP | Customer requested a second interconnection on a wind generating facility totaling 200 MW. To accomodate this customer request, the Company installed one 345 kV circuit breaker, as well as a new line terminal for the interconnection. | 2446229.64
TP2017249 | Karankawa l Interconnection | IPP | This was an interconnection project to a 200 MW wind generating facility. The greenfield 345 kV Goddard Station was constructed as a 3 breaker ring bus and included a DICM in the fence. The Goddard - Pawnee 345 kV line had a 0.13mi cut-in to Goddard completed that was designed single circuit 345 kV steel structures. Two single spans of the 345 kV line was constructed outside the station fence to the generator’s point of interconnection (POI). | 18908123.27
TP2016042 | Katz area improvements | RTO | The Katz Area Improvements project was completed to address NERC reliablity standards. The Company built the greenfield 138 kV Tardis Station, conversion of the Benjamin 69 kV Station to 138 kV operation, and a rebuild of the existing 69 kV Benjamin radial line for 138 kV to connect Tardis and Benjamin. This project also constructed the Company's portion of the new 138 kV line from the Benjamin Station (AEP Texas) to the new Katz Station (Brazos Electric Cooperative). | 29456027.6
TP2012049 | Kenedy SS to Tuleta | RTO | This project rebuilt the Kenedy Switch to Pettus 69 kV circuit as a double circuit with 138 kV insulation. This circuit was rebuilt due loading issues caused by increased customer load in the area. | 43050.34
TA2017961 | Kleberg - Loyola 138 kV, Reloc | Customer Service & Other | This project removed eleven transmission poles and installed thirteen transmission poles as part of a relocation to accommodate Texas Department of Transportation's (TxDOT) construction project on US Highway 77. In Kleberg County, TxDOT acquired right of way on the east side of US 77 and rebuit a bridge that caused the need to relocate a portion of the Kleberg-Loyola 138 kV line. As a result, AEP Texas removed eleven transmission poles and installed thirteen transmission poles to accommodate TxDOT's request. A Standard Utility Agreement has been executed. This project was 100% reimbursable. | 81314.55
DP18X0006 | Kleimann Sub-LCRA Conversion | Distribution Driven Transmission | This project constructed the new Kleimann Substation on Lower Colorado River Authority (LCRA) purchased land with a 138 kV/13.09 kV transformer, two distribution feeder breakers, and approximately two miles of feeder reconductor. The LCRA 69 kV Glidden - Altair transmission line was converted to 138 kV. TLCRA has purchased property and is building a ring bus and AEP must build a new substation at this new location to continue serving customers. AEP will have a perpetual easement on which to build and maintain this new substation. | 856791.29
TP2021588 | La Palma 345 kV Expansion | RTO | The Company expanded the La Palma 345 kV Station to a three-breaker 345 kV ring bus in Cameron County, TX. The The Company constructed ~3.5 miles of double circuit 345 kV line, acquiring all new ROW. Remote end work was also completed at Gulch and Stewart Road 345 kV Stations. Sharyland Utilities constructed the remaining ~3.5-mile 345 kV line between LaPalma and Palmito Stations and built a new Kingfisher 345 kV Station on the Stewart Road-Palmito 345 kV line. | 4535.02
TP2016071 | La Palma SVC | RTO | This project installed two Static Var Compensators (SVC) at the La Palma Yard. Additionally, the La Palma Yard was expanded in order to accommodate the two new SVCs. Continued growth in peak customer demand throughout the Lower Rio Grande Valley (LRGV) and the scheduled switch of the Frontera generation out of ERCOT to Federal Electricity Commission (CFE)/Mexico have created a need for additional transmission import capacity to serve the region. This ERCOT endorsed project increased reliability criteria in the LRGV. | 1274581.52
DR20X0005 | La Pryor Substation | Distribution Driven Transmission | The Company added a (69kV/138kV)/13.09kV, 10/12.5 MVA non-LTC transformer to the La Pryor Substation with an Urban bay distribution bus designed for 4 feeder breakers, and Installed 2-1200A circuit breakers, 3-667/747kVA regulators and totalizer breaker. The Company also installed a Drop In Control Module extension with a Distribution Remote Terminal Unit panel 61.05. | 403519.57
TA2018030 | Lake Pauline Replace Transform | Reliability | This project replaced the auto transformer and two 138 kV circuit breakers at Lake Pauline 138 kV Station. | 3761436.27
TP2017107 | Lake Pauline-Vernon Taps | RTO | This project rebuilt the Lake Pauline to Vernon Main Street 69 kV line and replaced 69 kV switches and facilities to address NERC reliability standards. The Company rebuilt portions of the Lake Pauline - Chillicothe 138 kV line and completed station upgrades at Lake Pauline, Chillicothe, and Vernon Main Street Stations. | 10145595.41
TP2015044 | LaPalma 345/138kV Auto#2 | RTO | This project was placed in service during a previous rate case review period and the amount reflected in transmission capital is a trailing charge. | 397.08
TP2022078 | Laredo Area Cap Banks | Reliability | This project installed capacitor banks at Santo Nino, Wormser Road, and Molina Stations in Webb and Zapata Counties, Texas. The Company installed a 23 MVAR capacitor bank and a 138 kV breaker at both Santo Nino and Wormser Road Stations and installed a 15.4 MVAR capacitor bank and 138 kV breaker at Molina Station. | 1182783.66
TA2019372 | Laredo Area Telecom Modernizat | Telecom | This program covered the Laredo, Texas area Transmission Telecommunication Modernization Program (TTMP) which built out a robust telecommunication network. To meet the ever expanding bandwidth demands across the AEP Texas regional footprint, this program built 46 miles of AEP-owned fiber that provides connectivity to a station, provides resiliency via new fiber ring topology to 15 stations, and laid the groundwork for resiliency at seven stations in the near future. | 2457378.2
TP2015144 | Laredo Breaker Addition | RTO | The Company added new breakers to sectionalize and allow the STATCOM and capacitor banks to be operated independently. Optical ground wire (OPGW)was added between the STATCOM yard and the Laredo power station yard reconductored the transmission line with aluminum conductor composite core trapezoidal wires. | 151655.91
LATXDCR17 | Laredo DACR Workplan | Distribution Driven Transmission | The Distribution Automation Circuit Reconfiguration (DACR) project for the Laredo district automated distribution feeder breakers and station regulators at multiple substations in the Laredo area as part of the Smart Grid initiative for AEP Texas. Upgrading to a Smart Grid System because it will allow for a more reliable distribution system, improve response times for outages, and better monitor and control the distribution system. | 2377862.29
TA2018263 | Laredo Rehab | Reliability | The existing static synchronous converter (STATCOM) at Laredo Station was originally installed in 2000. The Human Machine Interface (HMI) computer and alarm system has reached the end of the usable life and needs to be upgraded in order for maintenance personnel to safety and effectively operate the STATCOM. The antiquated hardware and operating system for the existing HMI is no longer supported by any vendors in the market, so finding replacement parts to keep the HMI running is no longer possible. In order to allow the STATCOM to be operated as designed, an upgrade of the HMI is required. This project will be a turn-key project that will be sole sourced to the vendor who originally installed the STATCOM (Siemens). When AEP approached other vendors with flexible alternating curren transmission system (FACTS) experience and capability, no other vendors were willing to do a replacement of the HMI. They will only bid on a total replacement of the STATCOMs which is not planned to be done for five or more years. | 337553.55
TP2020072 | Laredo VFT-North Laredo rebuil | RTO | The Company rebuilt 11.7 miles of the Laredo VFT North-North Laredo Switch 138 kV line to address planning criteria violations, operational flexibility, and customer service in the Laredo, TX area. The Company acquired ROW and rebuilt ~8.8 miles of the Laredo VFT North-North Laredo Switch 138 kV single circuit line and ~2.9 miles of double circuit line, added a breaker at Milo Station, and upgraded the limiting elements at Las Cruces, Milo, Mines Road, and North Laredo Switch Stations. Additionally, the Company upgraded the limiting elements at Laredo VFT North Station via a separate requisition. | 733483.55
TP2019034 | Las Lomas WF interconnection | IPP | This was an interconnection project to a 200 MW wind generating facility. The greenfield 138 kV Revilla Station was constructed as a 3 breaker ring bus. The Lopeno - Falcon 138 kV line had a 0.3 mile cut-in to Revilla completed that was designed single circuit 138 kV steel structures. Approximately 0.1 miles of the 138 kV line was constructed to the generator’s point of interconnection (POI). | 16016565.8
TP2018031 | Las Majadas Interconnection | IPP | The Company built a greenfield 9 mile 345 kV line and installed a 345 kV terminal at Rio Hondo Station to interconnect a 272 MW wind farm. To accommodate the interconnection request, AEP Texas constructed 9 miles of single circuit 345 kV generation tie line from the generator's collector station (Majadas) to Rio Hondo 345 kV station. A new 345 kV circuit breaker was installed at Rio Hondo Station. | 27530122.16
TP2018152 | Lemay 138 kV Box Bay | Customer Service & Other | A customer requested 15 MW of new load on the North Laredo-Reveille 138 kV line in La Salle County, Texas. To accommodate the customer request, AEP Texas constructed a 138 kV POD switching box bay (Lemay) approximately 2 line miles south of the Reveille 138 kV Station on the North Laredo-Reveille 138 kV line. | 1394584.74
TP2018151 | Lemay POD: EPIC Hard Tap | Customer Service & Other | This project constructed a new 138 kV hard tap to serve a new 15 MW oil and gas load. A hard tap was selected due to the timeline requested by the customer. | 100932.36
TP2018205 | Lipton Temp Tap 138kV | Customer Service & Other | This project was created to construct a new 138 kV hard tap to serve a new 11.5 MW industrial load. A hard tap was selected due to the timeline requested by the customer. | 13758.76
TA2020036 | TCC Corpus Christi 2023 TTMP | Telecom | This project cover the AEP Texas Transmission Telecommunication Modernization Program (TTMP) in the Corpus Christi area, which built out a robust telecommunication network to support the transmission system. | 27824.27
TP2017046 | Live Oak to Sonora 69kV | Reliability | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -102.09
TA2021017 | Lon Hill - CPSB Spruce Rehab | Reliability | This project rehabilitated 44 structures on the Lon Hill-CPSB Spruce 345 kV line in Nueces, San Patricio, Live Oak, and Bee Counties, TX. An inspection of the Lon Hill-CPSB Spruce line identified 44 structures with deterioration of the tower legs from rust. This project improved those structures by adding a three foot concrete reveal above the ground line. | 1151920.83
TA2018060 | Lon Hill to Warburton (STEC) | Reliability | The Company rebuilt 57.3 miles of the single circuit Lon Hill - Warburton (STEC) 138 kV line, replacing aged wooden structures with new steel poles. The line was rebuilt to 138 kV standards, but currently operated at 69 kV. This will accommodate future load growth in the area. | 53754237.28
TA2020095 | Lon Hill Training Center | Reliability | This project included upgrades to the Lon Hill Training Center to support transmission personnel. | 86700.23
DP22X0008 | Los Fresnos- Whipple DG | Distribution Driven Transmission | This project was placed in service during a previous rate case review period and the amount reflected in transmission capital is a trailing charge. | 1856.83
TP2018018 | Lotebush 138 kV Station #2 | Customer Service & Other | This project expanded the Lotebush Station to accommodate additional customer load and generation interconnect study results. The Company installed two capacitor banks and three additional circuit breakers, bringing the station to a total of eleven breakers. Additionally, the Company installed deadend structures outside of the station fence for the customer lines exiting the station, as well as wavetraps at Musquiz and County Road 101 Stations to maintain signal integrity. | 1626150.61
TP2015156 | Lotebush 138kV Switch Station | Customer Service & Other | This project constructed a new 138 kV substation on the Pig Creek to Permian Basin line to serve new load from Texas New Mexico Power Company (TNMP) and Oncor. The substation is expandable to allow an additional rung to be added for future static VAR compensator (SVC) connection. | 1157249.64
TP2012150 | Loxley 138kV Station:STEC | Customer Service & Other | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -157855.77
TP2017226 | Lynx - Rio Pecos Line Rebuild | RTO | To resolve a NERC reliability issue, the Company rebuilt two miles of the Lynx - Rio Pecos 138 kV Line, and terminated the line into Lynx Station. | 3596725.57
TP2015185 | Lynx Station | RTO | The Company built a greenfield 138kV Lynx Station. Lynx Station was built with six breakers laid out as a breaker and half configuration. The Fort Stockton PS - Rio Pecos 138 kV line was terminated into the new station with a 0.1 miles cut-in. The Lynx - Rio Pecos 138 kV line was rebuilt for 2 miles with double circuit capable steel structures but only a single circuit installed. Woodward Tap #1 was reterminated for 0.32 miles into the Lynx Station and Woodward Tap #2 was reterminated for 0.09 miles with 138 kV standard design and steel structures. | 10692432.15
TP2018168 | Lynx Station Phase 2 | RTO | This project added equipment at Lynx Station to accommodate a new interconnection request. AEP Texas added a third rung to Lynx Station in a breaker-and-half configuration, added three breakers and associated terminal equipment, constructed approximately 0.2 miles of new line span to the two new Point Of Interconnections to terminate into the Lynx Station, and added tie line metering on the 16th Street and Rio Pecos lines. | 4867675.41
TP2015091 | Magic Valley II Permanent | IPP | This was an interconnection project to a 250 MW wind generating facility. The 345 kV Cebolla Station was greenfield 345 kV station for a 3 breaker ring bus. This project also included a greenfield 0.5 mile cut-in from the Ajo - Rio Hondo 345 kV to the new station. A 1.4 mile 345 kV single circuit tie line was constructed from Cebolla Station to the generator’s point of interconnection (POI). | 20790742.7
TP2015041 | Magic Valley II Temporary Tap | IPP | This customer driven project was placed into service during a previous rate case, and the credit in the plant in service file is due to customer reimbursement of project costs. | -51874.02
TP2020008 | Martina 138 kV Box Bay | Customer Service & Other | Two customers requested a new POD to interconnect 10 MW of load in Upton County, Texas. To meet the needs of the customers, the Company constructed a new 138 kV station (Wolfcamp) that has three motor operated switches, 3000A equipment, and a wavetrap as well as install low side metering at the customer station. The Company installed a dead-end structure at Wolfcamp Station that will be the point of interconnection. | 2948356.86
TA2020940 | Mason SW to Yellowjacket | Reliability | The Company rebuilt 26.5 miles from Mason Switch-Yellowjacket using 138 kV design, operating at 69 kV, and acquired supplemental ROW as needed | 1188.55
TA2020941 | Mason to Mason SW | Reliability | This project rebuilt 12.2 miles of the Mason-Mason Switch-North Brady 69 kV line and constructed a new Seaquist switching station in the Mason, Texas area. To construct this project, the Company acquired supplemental ROW and rebuilt the 10.3-mile Mason-Mason Switch 69 kV single and double circuit line as well as the 1.9-mile Mason-North Brady 69 kV line, using a 138 kV capable design. The Company constructed a new Seaquist switching station at the Mason Phillips Tap to replace the existing line switches and added a new circuit breaker, DICM, and relaying equipment at the Mason Switch Station. | 1281.62
TA2022131 | Mason-Fredricksburg LCRA Rehab | Reliability | The Company rehabed 193 issues identified during inspection of the Mason-Fredricksburg 69 kV line to address equipment material condition, performance, and risk as well as operational flexibility and efficiency in Mason and Gillespie Counties, TX. The conditions identified were deterioration of components which include rotten or woodpecker holed poles, rotten, split, or woodpecker holed crossarms, broken arresters, broken insulators, damaged conductor, and broken ground lead. FThe Company replaced two structures out of the 392 structures in the line. | 427297.68
DP20X0012 | Mayo Sub Add Second Bank | Distribution Driven Transmission | The Company installed a second bank at the Mayo substation, as well as two feeder exits will be constructed from Mayo substation's second bank. The Company installed 138kV/13.09kV, 40MVA non-LTC transformer, Urban bay distribution bus designed for 4 feeders. Install 2-1200A feeder breakers, 3-2000kVA regulators, totalizer breaker, expanded&nbsp;DICM, and site and grading work. | 546215.53
DP18X0014 | McColl Rd - Upgrade #2 Bank | Distribution Driven Transmission | The Company upgraded the existing McColl Rd Substation. The upgrade involved replacing existing #2 transformer bank (28 MVA) with one 40 MVA transformer, and upgrading the distribution station with a new circuit breaker and feeder to help alleviate load from the #1 transformer. | 724599.57
TP2018126 | McKenzie-Westside Line Rebuild | Reliability | The Company replaced telecommunication equipment to accommodate the rebuild of the Electric Transmission Texas (ETT) McKenzie-Westside 138 kV line to address equipment material condition, performance, and risk in the Corpus Christi, TX area. ETT rebuilt the line and replaced fiber on 10.9 miles of the 11.5 miles of the McKenzie-Westside 138 kV line on a separate project (ETT-157). | 511038.36
TP2015088 | Melon Creek Substation | RTO | This project constructed the new 138/69 kV Melon Creek Station on the Airco - Rincon 138 kV line and the Refugio - Tatton 69 kV line to address NERC reliability standards. In addition to the station work, this project also rebuilt and upgraded approximately 1.4 miles and upgraded limiting equipment on the Refugio - Rincon transmission line. | 5655624.91
TA2022028 | Menard - Fort Mason 138kV, RC | Reliability | This project completed rehab on the Menard-Fort Mason 138 kV line in Menard and Mason Counties, Texas. To address 369 known structure component conditions, this project replaced fourteen complete structures on the Menard-Fort Mason 138 kV line as well as replaced identified poles, crossarms, and X-braces. | 1862514.8
DP17X0019 | Mesquite Substation | Distribution Driven Transmission | The Company constructed the new Mesquite Substation to offload Rangerville Substation. The new substation includes two - 138 kV/69 kV/13.09 kV transformers, six - regulators, four - breakers, and a 12.47 kV/ 25 kV step-up transformer | 8266.26
DP19N0001 | Miles Increase Capacity | Distribution Driven Transmission | This project replaced equipment at Miles Substation. The Company replaced the existing transformer and regulators and installed one new distribution feeder breaker. | 1567868.76
TA2018262 | Military Highway HMI Replaceme | Reliability | The existing static synchronous converter (STATCOM) at Military Highway Station was originally installed in 2000. The Human Machine Interface (HMI) computer and alarm system has reached the end of the usable life and needed to be upgraded in order for maintenance personnel to safety and effectively operate the STATCOM. In order to allow the STATCOM to be operated as designed, an upgrade of the HMI was required. This project was a turn-key project that was sole sourced to the vendor who originally installed the STATCOM (Siemens). | 365566.24
TP2016061 | Military Highway UPS | RTO | The Company replaced the Rankin #2, 69/4 kV, 4.5 MVA transformer with a 69/12 kV, 12.5 MVA transformer. The Rankin #2 transformer low-side bus work was rebuilt for 12 kV clearances, with two new circuit breakers and a new drop in control module (DICM). | 2677.01
DP19X0007 | Mines Road 2nd Bank | Distribution Driven Transmission | This project upgraded equipment at the Mines Road Substation in Laredo, Texas by adding a second 15/20/25/28 MVA transformer bank with 3 distribution feeder breakers and 5 miles of reconductor. | 2060756.94
TA2020058 | Albany-Throckmorton 69kV Rehab | Reliability | The Company rebuilt the 32-mile Albany-Throckmorton 69kV line to address equipment material condition, performance and risk as well as operational flexibility and customer service in the Throckmorton County, TX area. To address those issues, the 32-mile Albany-Throckmorton 69 kV line was rebuilt to 138 kV standards, but will continue to operate at 69 kV ratings, which will both facilitate a long-term plan for the area by creating a 138 kV loop as well as increase the MVA rating, load expansion, and generation serving capability in the area. | 336192.18
TP2012053 | Munday to Munday (BEC) | RTO | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -5461.64
TP2017250 | Musquiz/Utah 138kV | Customer Service & Other | A Customer requested a wholesale point of delivery (POD) to serve a retail customer that is located in their certified service territory. The Company installed a supervisory control and data acquisition (SCADA) controlled motor-operated switch, wave trap, jumpers on the southeast side of the existing box bay, and check metering in the customer's tap station. The Customer's Utah Station is located adjacent to the Company's right of way, and the Customer constructed the 138 kV transmission line connecting the Company's station to theirs and installed the metering in their station. | 30569.08
TP2019110 | N McCamey Breaker Replacement | RTO | The Company replaced poorly performing station equipment at North McCamey Station to address equipment material condition, performance, and risk in the McCarney, TX area. Based on AEP's Annual Planning Assessment of Facilities utilizing a System Protection Working Group (SPWG) 2021 case, the 138 kV circuit breaker 4195 at North McCamey Station was identified of being at risk of exceeding the interrupting fault capability. The Company removed the breaker 4195 along with the associated switches 4194, 4196 and 4197 and installed arresters, new line jumpers and insulators to re-connect the LCRA's North McCamey Station to the 138 kV bus at the Company's North McCamey Station. | 169560.62
TA2020051 | NATOC & Roanoke TOC Upgrade | Reliability | In support of the Transmission SCADA Network (TSN), the following infrastructure upgrades were made: 1) At New Albany TOC, upgrade two existing 1G firewall appliances with 10G firewalls to alleviate a bandwidth bottleneck. 2) At Roanoke Data Center, upgrade two existing 1G firewall appliances with 10G firewalls and upgrade two 1G network switches with 10G to alleviate a bandwidth bottleneck. 3) At Abilene Service Center, install two Ciena 5170 network switches to support the AEP Multi Enterprise Network (AMEN). 4) At Arsenal Hill Command Center, provide 0.2 miles of conduit through which AT&amp;T will install fiber optic cable to deliver a 10G circuit providing diversity to the AMEN network. 5) At Tulsa general Office, install fiber optic cable in the existing conduit to connect a third party circuit from Windstream (via the existing Ciena 5170 switch) providing diversity to the AMEN network. | 124519.23
TA2018050 | Naval Base to North Padre 69kV | Reliability | The Company rebuilt the original Naval Base-North Padre Island 69 kV line with a steel pole 138 kV design to address NERC reliability standards. This project consisted of rebuilding 5.1 miles of single-circuit line, reconductoring 3.8 miles of double-circuit line, and replacing and upgrading equipment at the North Padre Island 69 kV Station. | 33404241.69
TA2022038 | Nelson Sharpe Radiator Rplmnt | Reliability | This project removed and replaced radiators on transformer T1 and refurbish other parts at the Nelson Sharpe III 345 kV/138 kV Station to address equipment material condition, performance, and risk in Corpus Christi, Texas. This project also drained the transformer and load tap changer, conducted internal inspection and oil processing, and completed commission testing. | 1003155.99
TA2020921 | ERCOT Spare Equipment Program | Reliability | This program covered major equipment and spares in the ERCOT region. The Transmission sparing strategy is based on a probability model that predicts failures based on AEP-specific transformer data, historical failure rates, and material lead times across every operating company. This strategy creates a required target for spares for AEP Texas based on current inventory, voltage class, and failure rates. Items identified as part of this program are deemed as critical sparing needs in the ERCOT region. | 11754028.14
TP2019167 | North Edinburg 138 Fault Duty | RTO | This project added and replace equipment at the North Edinburg Station This project added two reactors on the low side of the 345/138 kV transformers. It also replaced bus insulators, added additional bus structures, added surge arrestors, and expanded the ground grid to bring the fault current rating of the entire 138 kV yard up to 63 kA. | 5740631.03
TP2019168 | North Edinburg 345-new rung | RTO | This project built a new 345 kV rung at North Edinburg Station to address planning criteria violations as well as operational flexibility and efficiency in the Edinburg, Texas area. The Company installed a new 345 kV rung with two 345 kV breakers at North Edinburg Station and relocated the Lon Hill terminal to this new rung. Additionally, two 50 MVAR 345 kV shunt reactors were installed at the station. | 12981765.6
TA2018054 | North Edinburg Relay Replace | Reliability | The Company completed work at the North Edinburg 345 kV/138 kV/69 kV/12 kV Station. A DICM was installed in the 138 kV yard. There also was multiple relays and metering worked on as well as CCVTs and a RTU installed. | 12325667.85
TP2020148 | North Edinburg-Redgate (STEC) | RTO | The Company constructed a new 138 kV station, Esmeralda, arranged in a four breaker ring bus. Esmeralda taps the existing Big Lake to Friend Ranch line. A new 138 kV line was constructed from Esmeralda to Yucca Station via a 14.7-mile line. This will allow Yucca Station to be converted to 138 kV; if a 138/12 kV transformer is added. | 2656.58
TA2019034 | North McCamey Rehab | Reliability | The Company replaced poorly performing station equipment at North McCamey Station to address equipment material condition, performance, and risk in the McCamey, TX area. The Company replaced a total of three switches: circuit switcher 6538 with a 138 kV circuit switcher, 3000A, 34.2 kA, switch 6547 with a new 138 kV switch, and switch 4192. Additionally, the project removed switches 3578 and 4189. | 779711.71
DP21X0002 | North Weslaco Substation | Distribution Driven Transmission | This project supported transmission line work on the North Weslaco Substation distribution project. | 262068.57
TA2020017 | NorthPadre-PortAransasShieldRp | Reliability | This project replaced approximately 15 miles of Optical Ground Wire (OPGW) shield wire on the North Padre Tap-Port Aransas 69 kV line to increase reliability. The existing OPGW shield wire was breaking and unraveling and mounting hardware was corroding due to the coastal environment. The existing OPGW shield wire could no longer be used by Telecom for communication and was barely serviceable as a shield wire | 1582424.91
TP2016067 | Nueces Area 69 kV Reinforcemen | RTO | The Company built a 1.6 mile greenfield 138kV line from Champlin to Valero East 69kV Substation to address NERC reliability standards. The Company also rebuilt a 0.4 mile portion of the Champlin - Weil Tract 138kV line with double circuit steel structures. As part of this project, the Company also reterminated the Valero East - Valero West 69kV line into the Valero East Substation, expanded the Valero East 69kV Substation by adding a new 138kV Box Bay, and added an additional breaker to the Champlin Substation to accept the Valero East 138kV terminal. | 15228522.48
TA2018043 | Nueces Bay - Avery Point, Remo | Customer Service & Other | The United States Army Engineer District (USAED), Galveston, planned construction of the congressionally directed deepening and widening of the Corpus Christi Ship Channel. AEP Texas was directed to remove three conduits were in the channel from the Nueces Bay-Avery Point 69 kV lines. The lines were decommissioned in the 1990s and the cable and dielectric fluid was removed from the conduits in 2013. This project will remove the remaining conduits from the Corpus Christi Ship Channel. | 376491.25
DP18X0011 | Odem Sub Upgrade | Distribution Driven Transmission | This project upgraded Odem #2 transformer to a 69/138kV / 13.09kV transformer, installed one additional distribution feeder breaker, replaced three distribution feeder breakers and reconductored approximately 3 miles of feeder to 556 all aluminum conductor. | 2514324.09
TP2018140 | Ollin 69 kV Substation | Customer Service & Other | Two customers requested to interconnect 16 MW of new load and 20 MW of new load, respectively, in Crane County, Texas. To accommodate the customer requests, the Company constructed a six-breaker ring bus station (Ollin) expandable to a breaker and a half configuration. Some associated transmission line work was also performed under this project. | 2924312.08
TP2016099 | Owls Station | RTO | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -5132.11
TA2021011 | Paducah-West Childres Rehab | Reliability | This project was used to mitigate 344 conditions identified during inspection of Paducah Clare Street-West Childress 138 kV line in Cottle and Childress Counties, Texas. The conditions identified are deterioration of components which include rotten poles, rotten, split, or woodpecker-holed crossarms, and woodpecker-holed X-braces. Nine of the 321 structures on the line were completely replaced. | 1251934.03
TA2018025 | Paint Creek Station Rehab | Reliability | This project replaced aging equipment at Paint Creek Station. The Company replaced eight 138 kV oil breakers, the associated disconnect switches, six 69 kV switches, all cap and pin insulators, and associated switches and cooper bus tubing. | 4558144.91
DP20X0007 | Pantera Sub | Distribution Driven Transmission | The Company built the new Pantera Substation with two 138kV/13.09kV non-LTC transformers, six regulators, four breakers, and urban-design distribution bus with eight bays and disconnects. The project also included installing transformer metering, overload and differential relaying, a new drop-in control module (DICM), and two circuit switchers, as well as a transmission bus in and out of the substation and 138kV breakers. | 3355179.01
TP2017235 | Patriot Gen Interconnect | IPP | Independent Power Producer requested interconnection for their 180 MW wind facility into the Nelson Sharpe 345 kV Station. To accommodate the interconnection request, AEP built a 345 kV connection into the Nelson Sharpe 345 kV Station and installed remote terminal unit (RTU), station data repository (SDR), and phaser measurement unit (PMU) equipment in the generator's collector station. The Company also installed metering and sub-synchronous oscillation (SSO) equipment in the Nelson Sharpe Station to monitor the generator from the point of interconnection (POI). | 1543778.21
TP2018030 | Pavlov 138 kV Substation | Customer Service & Other | This project constructed the new Pavlov 138/12 kV Station and constructed a 1-mile transmission line cut-in on the Blessing-Lane City 138 kV line to the new station. Transmission facilities installed at the new station include three 138 kV switches and associated equipment. | 3827361.07
TP2019002 | Pershing 138 kV Box Bay | Customer Service & Other | This project was in response to accommodate 11.5 MW of new customer load in Taylor county, Texas. The Company constructed a new POD 138 kV box bay approximately 14.5 line miles northeast of Oak Creek 138 kV Station on the Abilene Northwest-Oak Creek 138 kV line. | 2468860.1
TP2019001 | Pershing 138 kV Temp Tap | Customer Service & Other | Two Customers requested an interconnect in Taylor County, TX for an 11.5 MW load. The Customers constructed a temporary tap approximately 14 miles northeast of the Oak Creek 138 kV Station and approximately 50 feet southwest of structure 33/3 on the Company's existing Abilene Northwest-Oak Creek 138 kV line. The Company installed jumpers to connect to Customer lines to the temporary tap. | 38906.83
TP2016073 | Pharr SVC | RTO | This project installed two +150/-75 MVAR Static Var Compensators (SVC) at the Pharr yard to address NERC reliability standards. The Pharr yard was expanded in order to accommodate the two new +150/-75 MVAR SVCs. Continued growth in peak customer demand throughout the Lower Rio Grande Valley (LRGV) and the scheduled switch of the Frontera generation out of ERCOT to Federal Electricity Commission (FEC)/Mexico have created a need for additional transmission import capacity to serve the region. | 4816121.25
DP18X0005 | Picacho- Construct New Station | Distribution Driven Transmission | This project constructed a distribution station at Picacho Switch Substation with a new transformer and three distribution breakers and reconductor 7 miles of feeders. The transmission costs included in the review period are for associated transmission work performed to accommodate this project. | 1097758.85
TP2018145 | Pig Creek Expansion & Tarbush | Customer Service & Other | This project expanded Pig Creek 138 kV Station to provide a new point of delivery for a customer.TNMP has requested a new delivery point to serve 20 MW of load at its Tarbush Station. To accommodate the customer, Pig Creek 138 kV Station will be expanded to a three rung breaker and a half configuration. TNMP will construct a radial transmission line from Tarbush Station to a point of interconnect owned by AEP outside of Pig Creek Station. TNMP's Flat Top 138 kV line will be re-terminated to the third rung, so that Tarbush Station can be terminated to the second rung. | 4807452.47
TP2015023 | Pig Creek Staion | Customer Service & Other | The Company constructed a 3 breaker ring bus station to serve a Customer. A temporary tap was installed to serve the customer while the station was engineered and constructed. | 38548.8
DP16X0004 | Pirate Substation | Distribution Driven Transmission | This project constructed the new Pirate Substation in Sinton, Texas. The new substation included a transformer with 3 distribution feeder breakers and 4 miles of reconductor. Only those portions of the project related to transmission assets have been included in this transmission plant in service. | 1784642.11
TP2014158 | Pleasanton138/69kVAutoUpgrade | RTO | This project was created to upgrade the 138/69 kV autotransformer at Pleasanton. The 2013 ERCOT RTP study identified this autotransformer overloading in the base case by the summer of 2016. | 177674.02
TP2019166 | Port Aransas undersea cable rp | Customer Service & Other | The Company replaced 0.48 miles of its undersea cable/conduit on the Port Aransas - Seawall 69 kV line. It was designed single circuit 138 kV but has remained operating at 69 kV. | 12754820.5
TA2021050 | GE SEL 2022/2023 Relay Upgrade | Reliability | The Company replaced obsolete GE and SEL relays throughout the AEP Transmission footprint to address equipment material condition, performance, and risk as well as infrastructure resilience and customer service. This project replaced 71 GE relays and 342 SEL relays in 138 stations throughout the AEP Transmission footprint. | 635047.65
DP19X0012 | Primera Substation | Distribution Driven Transmission | This project constructed the new Primera Substation on the Harlingen - Rio Hondo 138 kV Line. The project included installation of a 138 kV/69 kV/13.09 kV non-LTC transformer, three feeder breakers, and reconductor of 5 miles of primary reconductor to 556 AL wire. | 4273040.64
TA2022039 | Proactive Polymer MOV Replmnt | Reliability | This project replaced the porcelain Metal Oxide Varistors (MOV) from phases A, B, and C Series Capacitor with new polymer-type MOVs at North Edinburg 345 kV Station. Porcelain-type MOVs are more subject to failure, and Transmission Field Services recommend proactive replacement of porcelain MOVs with polymer MOVs. | 2776558.12
DP20X0009 | Progreso - Construct Station | Distribution Driven Transmission | This project constructed the new Progreso Substation with a 138/69/13.09 kV transformer, three feeder breakers, and reconductor for six miles of primary reconductor to 556 AL wire. The Progreso Substation will be tied into the La Palma/Stewart Road 69 kV line. | 2405640.67
TA2019032 | Pt Lavaca-Victoria 69kV Rehab | Reliability | This project rehabilitated the Lavaca - Victoria 69 kV transmission line. | 10798.58
TA2012102 | Purchase/Rebuild Maj Eqp Trans | System Restoration | This three-year program (2012-2014) is for the purchase of major spare equipment for the transmission and distribution systems. The projected expenditures are based on typical average failure rates. A three-year program is recommended due to longer equipment lead times, with EHV equipment requiring a 1.5 to 2 year advance commitment. The equipment purchased will mainly consist of capital spare transformers, spare reactors, spare circuit breakers, mobile transformer stations, and spare transmission line towers. A three-year program allows the Company to secure equipment contracts to leverage our purchases and obtain the best prices for the needed equipment. | 1505529.92
TP2015189 | Quaint Station | RTO | The Company identified and replaced two switches at the Delk tap to allow full interrupting capability. The Company constructed a new four breaker ring station between the Delk and Onyx taps. | 404195.84
DP20X0015 | Quintana Substation | Distribution Driven Transmission | This project was constructed to meet a customer request for approximatley 2 MVA of power for a pump site. To meet the customer request, the Company constructed the new Quintana substation with 138kV/13.09kV transformer, installed two breakers, three regulators, and new DICM. | 3200692.03
TP2013080 | Rangerville (STEC) Line | RTO | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -1385708.88
TP2021056 | Rangerville STEC Asset Purchas | Customer Service & Other | After renegotiating the Interconnection Agreement between South Texas Electric Cooperative, Inc. (STEC) and AEP Texas Inc., the Company purchased the high side equipment of the Rangerville STEC 138 kV Station. The Rangerville STEC Station is currently owned by STEC and operated by AEP. Rangerville STEC is electrically positioned on the La Palma-Luna 138 kV line. By AEP taking ownership of the high side of the station, it will lead to long-term efficiencies for TFS field personnel and system operations personnel. AEP-owned equipment will be maintained and upgraded as needed, while STEC operates and maintains its own equipment. | 1476959.54
DP15N0001 | Rankin 4kV Upgrade | Distribution Driven Transmission | The Company constructed Las Cruces Substation, a new Greenfield substation, with a 25 MVA transformer, distribution bus, transmission bus, and three distribution feeders | 2770.4
TP2018029 | Raymond Wind Permanent Connect | IPP | This was an interconnection project to a 201 MW wind generating facility. The greenfield 345 kV Bonilla Station was constructed as a breaker and a half with four breakers. The North Edinburg - Rio Hondo 345 kV line had a 1.0 mi cut-in to Bonilla completed that was designed single circuit 345 kV steel structures. One span of the 345 kV line was constructed outside the station fence to the generator’s point of interconnection (POI). | 27176864.76
TP2018186 | Rayos Del Sol | IPP | This was an interconnection project to a 150 MW wind generating facility. The greenfield 345 kV Luna Station was constructed as a 3 breaker ring bus. The Rangerville - Weslaco 138 kV line had a 0.43 mile cut-in to Luna completed that was designed double circuit 138 kV steel structures. Approximately 0.06 miles of a 138 kV line was constructed to the generator’s point of interconnection (POI). | 9207115.68
DP18X0004 | Reading Substation | Distribution Driven Transmission | The Company constructed the new Reading Substation with a 15/20/25 MVA transformer and three distribution feeder breakers in North East Uvalde, Texas. | 2182184.47
TP2016048 | Rebuild Abilene NW-Elm Creek | RTO | The Company rebuilt the existing Abilene Northwest to Elm Creek 69 kV line as a 138 kV (operated at 69 kV) in addition to breaker replacement and terminal equipment upgrades at Abilene Northwest and Elm Creek stations. | 13641.3
TA2020140 | Rebuild Matador to Turkey | Reliability | This project rebuilt 27 miles of the Matador-Turkey 69 kV line to address equipment material condition, performance, and risk and operational flexibility in Motley and Hall Counties, Texas. This project acquired ROW as needed and rebuilt the 27-mile Matador-Turkey line with a 138 kV design. In preparation for looped transmission service, the line was designed for 138 kV operation to facilitate interconnecting the AEP Texas transmission system to the 345 kV CREZ system. Adding a 345/138 kV transformation where the 345 kV and 138 kV lines cross provides the northern part of the AEP Texas system with looped service for increased reliability and will yield an additional 370 MW of load and 358 MW of generation serving ability. | 15927.83
TP2016049 | Rebuild sections of Crane Loop | RTO | This project rebuilt and upgraded the Crane Loop to address NERC reliablity standards. To complete these upgrades, the Company rebuilt 2.7 miles of the Sage - Texas New Mexico Pipe 69 kV line to 138 kV steel structures and 2.3 miles of the Crane - McElroy 69 kV line with 138 kV steel structures, both currently operating at 69 kV. Associated station upgrades were completed at TXNM Pipe, Cardona, Kelton, Crane, and McElroy Stations. | 10435835.96
TP2017091 | Rebuild Solstice-Saragosa | RTO | The Company rebuilt the existing 19 mile Barilla Junction - Saragosa 69 kV line to 138 kV standards to address NERC reliability standards. Saragosa Station built a greenfield 4 breaker ring bus, DICM, 138 kV/13 kV distribution transformer and 138 kV/69 kV autotransformer. There were station upgrades at Solstice Station and a DICM expansion completed. There were station upgrades completed at Barrilla Junction Station. | 25491557.73
TA2021014 | Red Creek - Oak Creek Rehab | Reliability | The Company replaced four out of the 359 structures identified with conditions during inspection of Red Creek-Oak Creek 138 kV line in Coke, Runnels, and Tom Green Counties, TX. The conditions identified are deterioration of components which include rotten or woodpecker-holed poles, rotten, split, or woodpecker-holed crossarms, and broken or woodpecker-holed X-braces. | 797662.64
TP2012052 | Red Creek Replace Autos | RTO | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -57617.96
TP2021714 | Reforzar 345 kV Station Proper | RTO | This project is subject of a proforma adjustment and will not be included in rates. | 677430.15
TP2017209 | Refugio Auto&Conversion to 138 | RTO | This project installed a 138/69/12 kV autotransformer and associated equipment at Refugio 69 kV Station on the Melon Creek line terminal to address NERC reliability standards and ERCOT RTP-identified needs. | 3693164.11
TP2017085 | Refugio-Rincon MLSE Upgrades | RTO | This project rebuilt approximately 1.4 miles of the Rincon-Refugio 69 kV Line and replaced most limiting series element equipment on this line and the Refugio-Victoria 69 kV line to address NERC reliability standards. The Refugio-Rincon 69 kV Line and Refugio-Victoria 69 kV Line both serve load in Refugio County. Upgrading the Refugio-Rincon 69 kV Line to 243 MVA and bringing a third source to the Refugio 69 kV Station eliminated the overloads while also improving voltage stability in the area. | 5231001.27
TA2014065 | Relocate for Harbor Bridge | Customer Service & Other | Texas Department of Transportation (TxDOT) is constructing a new Harbor Bridge in Corpus Christi, Texas approximately 0.5 mile west of the existing location. The Company's structures were in the road right of way and needed to be moved to accommodate the TxDOT project. The Company removed ten existing single-pole wood structures, along Sam Rankin Street and crossing the proposed Harbor Bridge Hwy 181. Six new single-pole galvanized steel structures were installed. | 1873108.49
TA2017024 | Relocate for TxDOT, US 181 & S | Customer Service & Other | At the request of the Texas Department of Transportation, the Company raised and relocated structures on the Gregory-Aransas Pass 69 kV and Whitepoint-Dupont double circuit 138 kV lines to accommodate a highway improvement project in the San Patricio County, Texas area. | 2875019.17
TA2021227 | TNC 2022 TTMP | Telecom | This project covered the AEP Texas Transmission Telecommunication Modernization Program (TTMP) in the Abilene area, which built out a robust telecommunication network to support the transmission system. This program built 152 miles of AEP-owned fiber that increases resiliency at nine stations and provides resiliency via new fiber ring topology to six additional stations. | 6444438.73
DP19X0002 | Resaca Substation | Distribution Driven Transmission | This project constructed the new Resaca Substation on the La Palma - Brownsville 69 kV Line. The new station includes a 138kV/69kV/13.09kV transformer, three 1200A feeder breakers, one 2000A totalizer breaker and 2.5 miles of 556 primary conductor. | 4580568.04
TA2021228 | TCC 2022 TTMP | Telecom | This was the Telecommunication Modernization Program (TTMP) in the Corpus Christi area that installed approximately 100 miles of fiber and subsequent work at termination points. The Company installed fiber for the following pathes: Arcadia Station - Corpus Christi HOB, Arcadia - Westside, Weil Tract - Westside, Bishop Celanese - Stratton TS, Lon Hill - Stratton, North Victoria - Thomaston, Victoria Plant - Lolita, Haisley Station - Pirate Station, and Mayo - Whiepoint. | 15627292.98
TP2020131 | Rincon-Whitepoint 138 kV Rebld | RTO | This project rebuilt the Rincon - Whitepoint 138 kV line to address NERC reliability standards. The Company reconductored 3.2 miles of the Rincon - Whitepoint 138 kV line. It is a double circuit line and both circuits of conductor were replaced. The remaining 4.6 miles of line were rebuilt as single circuit 138 kV standard design steel structures. | 7792557.36
TA2019373 | Rio Grande Telecom Modernizati | Telecom | This program covered the Rio Grande Valley, Texas area Transmission Telecommunication Modernization Program (TTMP) which built out a robust telecommunication network. To meet the ever expanding bandwidth demands across the AEP Texas regional footprint, this program built 93 miles of AEP-owned fiber that provides connectivity to five stations, increases resiliency at six stations, and provides resiliency via new fiber ring topology to 18 stations. This program replaced three obsolete RX1000 routers and eliminated nearly $19,842 in annual lease line expenses while enhancing the telecommunication reliability by addressing single points of failure throughout the fiber network. | 7597087.11
TP2020026 | Rio Hondo - STEC E. Rio Hondo | RTO | The Company upgraded the East Rio Hondo 138 kV line terminal at Rio Hondo Station to a minimum of 2000A to address NERC reliability standards. The Company also replaced jumpers, breaker switches, CCVT, and removed an unused metering CT that was replaced in another project (A19508024). | 615240.19
TA2018068 | Rio Pecos - Crane 138 kV, Relo | Customer Service & Other | The Company replaced three structures to accommodate the Texas Department of Transportation's (TxDOT) road widening project. TxDOT widened United States Highway 385 where the Rio Pecos-Crane 138 kV line crosses over. Two structures were relocated to clear the new proposed right of way and replaced with larger steel dead-end structures in order to support the longer span over the highway. The third structure was replaced with a taller wooden H-frame structure due to the uplift caused from the larger dead-end structures | 10631.52
TP2017064 | Rio Pecos CB and Bus Diff | RTO | To address stability issues in the area, the Company installed a second breaker on the rung for the Fort Stockton 138 kV line. Furthermore, the addition of a redundant bus differential protection scheme along with two bus tie breakers brought the Rio Pecos 138 kV Station into alignment with current Protection and Control standards. This project also installed two 138 kV bus tie breakers, installed additional 138 kV breaker at Fort Stockton position to complete the rung, and added bus differential relays at Rio Pecos Station. | 3151036.97
TA2018015 | Rio Pecos Rehab | Reliability | This project included replacement of equipment at the Rio Pecos 138 kV Station. The Company replaced the existing 138/69 kV autotransformer #1 and 69/12 kV distribution cap bank with a new supervisory control and data analytic (SCADA) controlled autotransformer with load tap changer (LTC) and a dual winding distribution bank. | 2354778.15
DP19X0004 | Rockport Sub- Upgrade Xfmr | Distribution Driven Transmission | The Company rebuilt the existing distribution substation in order to accommodate the new transformer upgrade in Rockport, TX. This included upgrades to the existing transformer to 138/69/13.09 kV 18/24/30 MVA transformer, installing four distribution feeder breakers, and constructing approximately four miles of feeder work. Rebuilding the existing substation and installing a larger transformer provides increased reliability and would allow for future load growth. | 394332.12
TP2014135 | Roserock Permanent Interconnec | Customer Service & Other | This project built out infrastructure necessary to connect a new generating facility. The new solar farm is located approximately 4.5 miles east of the existing Barrilla Junction Substation. This project included installation of a breakered terminal for the solar farm to tie into the existing transmission system. | 6281854.87
TA2020217 | RTU Reliability ERCOT - 2020 | Reliability | This project replaced Remote Terminal Units and associated protection and control equipment at eight stations in Texas. | 3748719.3
TA2017217 | RTU Reliability Program ERCOT | Reliability | This project replaced Remote Terminal Unit (RTU) equipment and associated protection and control equipment at nine stations, including, Falcon, Brownsville, Roma Tap, Roma, DuPont, Cantwell, West McAllen, Fronterra SW, and Elsa Stations. | 3092724.71
TP2016056 | Russek Street: Add Breakers | RTO | The Russek Street Station was added on the Big Lake to Twin Buttes 138 kV line 0.1 mile east of Big Lake Station because there was no room within the Big Lake Station to add two distribution banks The station was added without circuit breakers. As a result, the load being served by the distribution banks at Russek Street experiences momentary outages from the line between Big Lake to Twin Buttes, which is about 65 miles in length. The Company added two circuit breakers, and expanded the drop in control module (DICM) at Russek Street Station, upgraded the relaying at Big Lake Station towards Russek Street Station, and added fiber between Big Lake Station and Russek Street Station. | 141.12
TP2016085 | S & N McAllen MLSE Upgrades | RTO | This project upgraded the North McAllen and South McAllen Stations to address NERC reliability standards. The Company replaced the 138 kV Bus #1, three circuit breakers, installed a new DICM, and replaced all limiting elements at South McAllen Station. The Company also replaced two circuit breakers, installed a new DICM, and replaced all limiting elements at North McAllen Station. | 10164188.36
TP2018162 | SA Concho to Live Oak MLSEs | RTO | The Company rebuilt 3 miles of the San Angelo Concho - Live Oak 69 kV line with designed single circuit 138 kV steel structures and upgraded station equipment to address NERC reliability standards in the area. The 40-mile 69 kV line was terminated into 6 stations, all of which were upgraded as part of the reliability need. Work was performed at the San Angelo, Christoval, Arrott, Hudale, Pave Paws, Eldorado Live Oak, and Lake Nasworthy Stations. The San Angelo Concho - Mathis Field 69 kV line was terminated into the Lake Nasworthy Substation. The switches at Lake Nasworthy were removed and a POD Boxbay was installed. A switch at Christoval was replaced. The station work at Arrott included the removal of three switches and replaced 2 of them with motor operated switches, one updated switch, and new buswork. The Hulldale and Pave Paws Substation had its switches removed and a POD Boxbay installed in their places. | 18221474.17
TP2021610 | Salvare Interconnection | Customer Service & Other | This project was created to facilitate the interconnection of a 600 MW data center load to ETT's Salvare 345 kV station. AEP's portion of the work involved installing metering and a portion of the tie line for the customer at the ETT station. | 1240473.13
TP2007090 | Salvation Interconnection | Reliability | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -2007.41
SATXDCR17 | San Angelo DACR 2017 | Distribution Driven Transmission | The Distribution Automation Circuit Reconfiguration (DACR) project proposed for the San Angelo district seeks to automate distribution feeder breakers and station regulators at multiple substations in the San Angelo area as part of the Smart Grid initiative for AEP Texas. Upgrading to a Smart Grid System because it will allow for a more reliable distribution system, improve response times for outages, and better monitor and control the distribution system. This portion of the project covers only associated transmission work that was done to implement the DACR project. | 1883007.49
TA2021229 | TCC Laredo TTMP 2022 | Telecom | This project covered the AEP Texas Transmission Telecommunication Modernization Program (TTMP) in the Laredo area, which built out a robust telecommunication network to support the transmission system. This program built 118 miles of AEP-owned fiber that increases resiliency at eight stations and provides connectivity to eight stations. | 7816618.76
TP2015113 | San Roman Perm Interconnect | IPP | A Customer requested to interconnect their 105 MW wind farm to the Port Isabel-Laureles 138 kV circuit. A temporary interconnection was completed under a separate planning project due to the requested in service date.The Company then constructed a 138 kV station, Marconi Station, arranged in a 3 breaker ring bus. The new station taps into the Port Isabel-Laureles 138 kV line via a 0.6 mile 138 kV line. | 197.92
DP20X0008 | Sand Crab Substation | Distribution Driven Transmission | This project constructed the new Sand Crab Substation with two 138kV/13.09kV transformers, six regulators, and five breakers. | 2529687.87
TP2017090 | Sand Lake-Solstice 345 kV Line | RTO | This station and transmission line project was part of the larger Far West Texas project endorsed by ERCOT to address NERC reliability standards. This portion of the project included approximately 40 miles of greenfield double circuit 345 kV line between the Sand Lake and Solstice Stations. The cost of the Far West project was allocated between the Company and the operator of the Sand Lake Substation. | 51100904.94
TA2020208 | Santa Anna Station Rehab | Reliability | This project was created to replace aging equipment at the Santa Anna 138/69 kV station. AEP replaced one autotransformer, one circuit breaker, one circuit switcher, and various relays. The aging equipment was at risk of failing, had limited spare parts, and was a risk to reliability. | 53571.92
DP20X0010 | Santo Nino - Station Upgrade | Distribution Driven Transmission | This project rebuilt the distribution station at Santo Nino Substation, and this portion of the project covers the associated transmission work required for that distribution substation project. The Company installed two 138/13.09 kV 40 MVA transformers, seven distribution breakers and construct one mile of distribution feeder. | 2845279.97
TP2018130 | Schottky 69 kV POP | Customer Service & Other | Customer requested an interconnect for a 34 MW load to the Pleasanton-Three Rivers 69 kV line in Live Oak County, Texas. To accommodate the customer request, approximately 0.21 miles of the Pleasanton-Three Rivers 138 kV line was rebuilt to enable capacity to serve the additional load. This project installed a POP point of delivery to serve this load. The Schottky POP was designed and built at 138 kV and operated at 69 kV. | 1837664.93
TA2018257 | SDR Replacements - TNC/TCC | RTO | The Substation Data Repository (SDR) system performs the functions of recording, collecting and analyzing substation data, which consists of oscillography, sequence of events, fault reports, dynamic disturbances, transmission line trending, transformer trending, carrier level trending, and circuit breaker trending. Microsoft stopped supporting Windows XP leaving the substations vulnerable to cybersecurity attack. As a result, SDR Window XP units at extra high voltage (EHV) and 138 kV substations in the AEP Texas region were replaced with SEL 3355/Windows 10 units. | 86926.92
TP2018198 | Shakes Solar Interconnection | IPP | This project created a new interconnection to a 200 MW solar farm at Asherton Station in Zavala County, Texas. In order to accommdate the customer request, the Company expanded Asherton 138 kV Station, added a 138 kV circuit breaker, added metering equipment, and re-terminated the Escondido line. | 4040740.47
TP2018022 | Sharyland Stillman Station | Customer Service & Other | This project reterminated the La Palma-Loma Alta 138 kV line, the Union Carbide-Loma Alta 138 kV line, and existing fiber optic lines into Sharyland's new Stillman Station. | 5124115.45
TP2019230 | Solanum 138 kV Box Bay | Customer Service & Other | Customers have requested a new 138 kV point of delivery in Callahan County, Texas to serve 11.5 MW of load. To meet the needs of the customers, the Company constructed the new Solanum 138 kV box bay near structure 25/3 on the South Abilene-Putnam 138 kV line by installing three motor operation switches and 3000A associated equipment on newly acquired property. | 2678315.91
TP2019229 | Solanum 138 kV Temp Hard Tap | Customer Service & Other | This project constructed a new 138 kV hard tap to serve a new 11.5 MW GSEC industrial load. A hard tap was selected due to the timeline requested by the customer. | 51990.93
TP2017089 | Solstice 345 kV Reactor | RTO | This station project was part of the larger Far West Texas project endorsed by ERCOT. This portion of the project installed a 345 kV bus shunt reactor at the Solstice Station to mitigate the risk of voltage violations. The addition of a 50 Mvar 345 kV bus shunt reactor mitigates the overload and provides Transmission Operations (TOPS) better control of the voltage at Solstice Station. The cost of the Far West project was allocated between the Company and other operators. | 2693705.65
TP2018237 | Solstice PST | RTO | This project upgraded equipment at the Solstice Station to address NERC reliability standards. The Company installed a phase shifting transformer on the Fort Stockton Plant - Solstice 138 kV line at Solstice Station. A capacitor bank was installed in Solstice on the 138 kV bus and a DICM expansion was completed. | 7951224.75
TA2018100 | Sonora/Carver Rehab | Reliability | The original Sonora Station was 138 kV and 69 kV station that had a single bus configuration next to a hill, which made expanding the station impractical. Because expansion was not possible, a previous transmission project was approved to build a new ring bus station (Carver) to be expandable in the future to a standard breaker-and-a-half layout. To remediate identified risk, Carver Station will have a new 138/69 kV autotransformer and 69 kV circuit breaker installed and Sonora Station will have two 12 kV circuit breakers replaced in addition to the removal of the existing autotransformer and breakers. | 5068112.89
TP2020136 | Sparta Solar Interconnection | IPP | This project created an interconnection to a 255 MW solar generating facility on the Goddard - Pawnee 345 kV line in Bee County, Texas. The Company constructed a breaker terminal at the new 345 kV Tango Station and a line span from the 345 kV terminal to Point of Interconnection (POI). | 3636713.76
TA2018009 | Stadium 69 kV Station | Customer Service & Other | The Company expanded the Stadium 69 kV Station to accommodate equipment replacement. | 612241.68
DP18X0007 | Stafford Hill Substation | Distribution Driven Transmission | The Company upgraded the Stafford Hill substation from 69kV/13.09kV to 138kV/13.09kV to continue to serve existing customers.The Company reconstructed with a 69-138kV/13.09kV, 10/12.5MVA non-load tap changer transformer, two distribution breakers and require approximately 4 miles of feeder reconductor to 556 aluminum (AL). | 761432.92
TA2021231 | San Angelo TNC TTMP 2022 | Telecom | This project covered the AEP Texas Transmission Telecommunication Modernization Program (TTMP) in the San Angelo area, which built out a robust telecommunication network to support the transmission system. This program built 82 miles of AEP-owned fiber that increases resiliency at seven stations and provides resiliency via new fiber ring topology to ten additional stations. | 5546389.38
TP2015177 | Stewart Road | RTO | This ERCOT-endorsed project was designed to accommodate growing demand in the West Lower Rio Grande Valley and address NERC reliability standards. The overall project included work on the Edinburg - SU Palmito 345 kV circuit, expanding the station at Stewart Road, constructing a five breaker ring bus, and installing two 345/138 autos to connect to the Steward Road 138 kV yard. For its part of this project, AEP Texas purchased additional property and expanded the Steward Road Station to accommodate a 345 kV interconnection. The Company installed four new breakers, a new 345 kV yard with buswork and four line terminals in ring bus configuration, six new 345 kV breakers, one new 345 kV shunt reactor, one new DICM, and new metering equipment. It also completed associated station work at North Edinburg and Palmito Stations, and relocation and retermination of a portion of the Stewart Road - Welaco 138 kV line to make room for the 345/138 auto tie. | 38446396.24
TA2017044 | Storm Recovery- Harvey 8-2017 | System Restoration | On August 25, 2017, Hurricane Harvey made landfall in Rockport, Texas, as a Category 4 hurricane. Over 700 transmission poles were damaged or destroyed. This project covered the cost of emergency restoration activities, including replacement of poles, conductor, and equipment for dozens of lines and stations. This project included restoration work at the following stations: Tatton Station, Fulton Station, Live Oak Station, Mustang Island Station, Rockport Station, and Port Aransas Station. The project included restoration of the line switch structures on the Heard Tap-Heard 69 kV, Heard Tap-Refugio 69 kV, and Woodsboro-Heard Tap 69 kV lines. This project also included restoration and removal costs on the Whitepoint - STP (South Texas Project Electric Generating Station) 345 kV and Port Aransas - Seawall 69 kV transmission lines. | 6334691.53
TP2016050 | SW Vernon: Replace Auto | RTO | The Company replaced the Southwest Vernon 138/69 kV autotransformer as recommended by ERCOT to a rating of at least 130 mega volt ampre (MVA) to address NERC reliability standards. Additional property was purchased to expand and rebuild the Southwest Vernon 138/69 kV Station, and install a 138 kV box bay. This project is mandatory in the ERCOT 5-year plan. | 369589.64
TP2011078 | T/TCC/Midway Farm Wind Interco | IPP | This project was created to provide a point of interconnection for a generating facility. Midway Farm is a 160.2 MW wind generating facility near the Whitepoint 138 kV station. AEP Texas and Customer signed an interconnection agreement to connect the generating facility to the grid. The PUCT substantive rules mandate that the TSP construct interconnection facilities for new generation. | 79899.73
TA2013217 | T/TCC/TNC/Telecom Upgrades | Telecom | This program covered a 5-year effort to replace obsolete equipment that will no longer be supported by telecommunication companies by replacing analog leased lines, frame relay circuits (obsolete digital leased line), and tone telemetry installations (obsolete 2-point system alarms). Telecom providers are phasing out these older technologies, which they will no longer support, and which the Company will no longer be able to support due to lack of expertise and unavailability of parts. This upgrade also required the replacement of related station equipment such as older model RTUs that will not support newer technology, and, in the case of obsolete tone telemetry, RTUs will need to be added to support the newer Telecom technology. | 744241.91
TA2013207 | T/Texas/Asset Health Program | Reliability | The Company installed asset health monitoring equipment for select station equipment related to the AEPSC Asset Health Center (AHC). The retrofit of monitoring equipment to existing station assets will afford them the same level of monitoring and protection as is available on new state-of-the-art equipment resulting in improved asset condition awareness, prediction and prevention of equipment failure and related cost saving, otimized effectiveness of O&M effort and spend, improved system operational performance and reliability, and prioritized asset renewal decisions. | 541.6
TP2018160 | Taygete Interconnection | IPP | This project provided a point of interconnection (POI) for a 250 MW solar farm in Pecos County, TX. In order to accommodate this connection, the Company added one 138 kV breaker, Subsynchronous Oscillation (SSO) relaying, and metering equipment at Pig Creek Station. | 2162038.06
TP2019109 | Taygette Solar II | IPP | This project provided a point of interconnection for a new customer for a 256 MW solar farm in Pecos County, Texas. To accommodate this connection, the Company added one 138 kV breaker, Subsynchronous Oscillation (SSO) relaying, and ERCOT Polled Settlement (EPS) metering at Pig Creek. | 1860754.94
TA2022031 | Texas Cap Bank Replacements | Reliability | This project is a Transmission capacitor bank replacement project for 13 stations in the Texas region. This project will replace 16 failed units with the new standard high-margin grounded-wye design capacitor banks. The new units have a modular design that includes surge arrestors, series reactors to help mitigate outrush transients, a high margin can design that can handle higher over-voltage stresses, current transformers in each capacitor string to provide more reliable relay protection, and targeted can failure information to help in reducing O&M trouble-shooting activities. | 8237252.97
TA2022807 | ERCOT Failure Program | Reliability | This program covers reactive station and line work due to failures of various transmission assets. Some of the station assets replaced under this program included an auto transformer failure at West Childress, an auto transformer at Big Foot SW, a circuit breaker at Lon Hill, and a circuit breaker at Dupont SW. Transmission line repairs and replacements were also performed on the La Palma - Pt Isabel, Encinal - Cotulla, Gohlke - Joslin, Naval Base - N. Padre Tap, Hamilton Road - Maverick, and N. Edinburg - N. McAllen transmission lines, among others. | 12828577.11
TA2020037 | TCC Laredo 2023 TTMP | Telecom | This program included Transmission Telecommunication Modernization Program (TTMP) which will provide a robust telecommunication network in the Laredo, Texas area. This program built out AEP-owned fiber that provides connectivity to stations and increases resiliency. | 1002815.17
TA2022921 | ERCOT Spare/Major Equi Program | Reliability | This three-year program purchased major equipment and spares for AEP Texas. The Transmission sparing strategy is based on a probability model that predicts failures based on AEP-specific transformer data, historical failure rates, and material lead times across every operating company. The strategy limits the sharing of spares across operating companies and Transcos as well as territories (East/West). This strategy creates a required target for spares for each operating company based on current inventory, voltage class, failure rates, and other factors. Items identified as part of this program are deemed as critical sparing needs in the ERCOT region. This program purchased major spare and mobile equipment to replenish spare equipment utilized to address failures or emerging projects as needed. The program is part of an ongoing effort to improve system reliability and resiliency by having an adequate stock of spare equipment available for use during unforeseen and emergency situations. | 2670672.88
DP17X0006 | TCC/Las Cruces - New station | Distribution Driven Transmission | This project constructed the Las Cruces Substation, a new Greenfield substation, with a 25 MVA transformer, distribution bus, transmission bus and three distribution feeders. | 3298.23
DP17X0001 | TCC/Unitec - Construct New Sub | Distribution Driven Transmission | The Company constructed the Unitec Substation, a greenfield (new) substation with a 25 MVA transformer, distribution bus, transmission bus and three distribution feeders. | 9762.44
TA2015715 | Telecom Fiber Build Out - TX | Telecom | This program expanded the AEP Texas fiber network to existing stations and transitioned the Company's operations to a private network. Several key initiatives in Transmission such as Asset Health, Physical Security, Supervisory Control and Data Acquisition (SCADA), and enhanced protection and controls technology required additional bandwidth that could not be supported by the existing fiber infrastructure. Additionally, other business units can benefit from the increased bandwidth to install gridSMART automation technologies such as Volt Var Optimization and Advanced Metering Infrastructure. This program added approximately 1,500 miles of fiber to the existing infrastructure on more than 85 different lines and completed termination work on more than 90 substations. | 85276868.89
TP2015201 | Tennyson 138kV | Customer Service & Other | A Customer requested a new Tennyson 138 kV delivery point. The new delivery point was supplied from the Nicole to Red Creek 138 kV line. AEP constructed a new 138 kV box bay, consisting of three motor operated line switches and loop the line into the box bay. The Customer constructed a 138 kV tap line and 138/4 16 kV station. A | 14091.73
TBLANKTTX | Trans Capital Blanket - Texas | Reliability | This program includes projects with costs of less than $3,000,000 for: (1) asset improvements, including the cost of work on transmission lines and transmission and distribution stations, and asset replacements due to failures, (2) facility relocation changes in all existing types of transmission plant made mandatory by the alteration, construction, reconstruction, and relocation of all public projects carried out by any governmental body, (3) customer service projects including facilities for new customers or for additional facilities to serve increased load of existing customers, (4) storm recovery costs for minor storm events and (5) pre-engineering costs. | 89881661.5
TA2021064 | Texas HB4150-ERCOT (TFS) | Customer Service & Other | This program included inspection and identification of capital projects designed to mitigate any violations of Texas House Bill 4150, which requires utilities to inspect and analyze transmission lines utilizing LiDAR surveying and mitigate any violations that result from the analysis. Projects identified under this program may have included raising conductors, replacing structures, reconductoring, and partial rebuilds. | 1430187.77
TA2021057 | Texas House Bill 4150 Mitigati | Customer Service & Other | This program included inspection and identification of capital projects designed to mitigate any violations of Texas House Bill 4150, which requires utilities to inspect and analyze transmission lines utilizing LiDAR surveying and mitigate any violations that result from the analysis. Projects identified under this program may have included raising conductors, replacing structures, reconductoring, and partial rebuilds. | 2908454.93
TA2017947 | Texas Line Rebuild Program | Reliability | This program consists of multiple projects to be completed in multiple phases that are part of an on-going initiative to improve the AEP Texas system reliability and dependability. For the review period, this program partially or fully rebuilt 8 circuits in the AEP Texas service area, including, but not limited to the following: - 34.5 mile rebuild on the Alice - Falfurrias 69 kV line - 29.6 mile rebuild on the Calallen - Stadium 69 kV line - 51.8 mile rebuild on the Cedar Hill - Miles 69 kV line - 44.8 mile rebuild on the Fort Stockton Switch - Rio Pecos 69 kV line - 4.3 mile rebuild on the Gregory - Rincon 69 kV line - 21.4 miles rebuild on the Refugio - Tatton 69 kV line - 7.0 mile rebuild on the Sabinal - Uvalde 69 kV line - 32.2 mile rebuild on the Turtle Creek - Uvalde 69 kV line | 215887558.26
TA2017957 | Texas Line Rebuild Program | Reliability | This program consists of multiple projects to be completed in multiple phases that are part of an on-going initiative to improve the AEP Texas system reliability and dependability. For the review period, this program partially or fully rebuilt 5 circuits in the AEP Texas service area, including the following: - 31.8 mile rebuild on the Blessing - Port Lavaca 69 kV line - 40.0 mile rebuild on the Concho - Live Oak 69 kV line - 16.5 mile rebuild on the Concho - Miles 69 kV line - 28.1 mile rebuild on the Cross Plains - Santa Anna 69 kV line - 40.5 mile rebuild on the Pleasanton - Three Rivers 69 kV line | 165149558.56
TA2017927 | Texas Line Rebuild Program | Reliability | This program consists of multiple projects to be completed in multiple phases that are part of an on-going initiative to improve the AEP Texas system reliability and dependability. For the review period, this program partially or fully rebuilt 6 circuits in the AEP Texas service area, including the following: - 37.4 mile rebuild on the Ballinger - Eden 69 kV line - 29.9 mile rebuild on the Friend Ranch - Sonora 69 kV line - 5.0 mile rebuild on the Goliad - Fannin 69 kV line - 27.7 mile rebuild on the Junction - Yellowjacket 69 kV line - 23.1 mile rebuild on the Lake Pauline - Vernon 69 kV line - 22.1 mile rebuildon the Refugio - Rincon 69 kV line | 138509259.98
TA2017996 | Texas Line Rehab Program | Reliability | This program includes four proactive line rehabilitation projects that were originally opened under the transmission capital blanket release for the Texas region. All four projects exceeded the $500K threshold for blanket work orders. These line rehabilitation projects address the proactive replacement of multiple (twelve) transmission line structures and another line was re-insulated to prevent future failures that may lead to unplanned outages for our customers. The four lines included in this IR are Airco-Rincon 138 kV, North Edinburg-Rachal 138 kV, Naval Base-North Padre Tap 69 kV, and Hamilton Road-Maverick 138 kV. | 500666.3
TA2018076 | Texas SEL/GE Relay Upgrade Pro | Reliability | Some legacy microprocessor/digital relays at various substations in the AEP Texas region were in need of replacement due to asset performance, condition, and risk. The identified relays were either obsolete, no longer supported, out of warranty, or had numerous service notices that described vulnerabilities and high risk of failure. The modules within these relay panels are necessary for replacement in order to sustain grid resilience, performance, and stability. | 2065769.04
TA2019375 | Texas Telecom Modernization | Telecom | The San Angelo, Texas area Transmission Telecommunication Modernization Program (TTMP) built out a robust telecommuncation network. To meet the ever expanding bandwidth demands across the TNC regional footprint, this program built 47.6 miles of AEP-owned fiber that provides connectivity to 12 stations, increases resiliency at 12 stations, provides resiliency via new fiber ring topology to 12 stations while laying the groundwork for resiliency in the future. | 2063038.77
TA2016002 | Texas T-Line Rebuild Program | Reliability | This program consists of multiple projects to be completed in multiple phases that are part of an on-going initiative to improve the AEP Texas system reliability and dependability. For the review period, this program partially or fully rebuilt 17 circuits in the AEP Texas service area including, but not limited to the following: - 16 mile rebuild on the Abiliene NW - Anson 69kV line - 15.5 mile rebuild on the Albany - Rainey Creek 69 kV line - 8.9 mile rebuild on the Alpine - Barrilla Junction 69 kV line - 39.9 miles rebuild on the Anson - Paint Creek PS 69 kV line, partially double circuit structures from Anson - STR 1/16, 138 kV single circuit steel structures from Structure 1/17 - 10/18, and 138 kV double circuit steel structures from 11/1 - Paint Creek - 23.4 mile rebuild on the Big Lake - Mathis Field 69 kV line - 5 miles rebuild on the Bishop - Stratton 69 kV line - 25.4 mile rebuild on the Crowell - Munday 69 kV line - 23.2 mile rebuild on the Ely Tap - Eskota 69 kV line, designed as 138 kV single circuit steel structures for 20.4 miles and 138 kV double circuit steel structures for 2.8 miles, but operating at 69 kV - 20.2 mile rebuild of the Jayton - Rotan 69 kV line was rebuilt for 20.2 miles - 13.6 mile rebuilt of the Port Isabel - South Padre Island 138 kV line - 7.7 miles rebuild of the Rockport - Fulton 69 kV line | 297831105.11
TA2019050 | TFS TX Line Rehab Program | Reliability | Inspections identified three lines in the AEP Texas region that were at risk of failure due to their conditions, the Blessing-South Texas Project (STP) 345 kV, Aransas Pass-Seawall 69 kV, and STP Tap-Celanese 138 kV lines. Conditions identified included issues with rotten poles, rusty insulators, rotten crossarms, and rusty davit arms. The company remediated the identified conditions on these three lines in the Texas region to improve reliability. | 2048601
TP2014028 | Three Rivers Sta: Replace Auto | RTO | This project was created to upgrade the Three Rivers 138/69 kV autotransformer. The 2013 ERCOT RTP study identified this autotransformer overloading with the loss of the Kenedy Switch 138/69 kV autotransformer by the summer of 2018. | 11143.99
TP2020032 | Thrush Low Side Meter | Customer Service & Other | Two Customers requested to increase capacity at the Tennyson delivery point from 7.5 MW to 28.5 MW. To accommodate the additional load, the Company installed low side metering at the new Customer Tennyson East Station. | 41378.47
TP2018136 | Tinsley 138kV POD: Phillip 66 | Customer Service & Other | Customer requested an interconnect for a 19.5 MW load in Sutton County, Texas. To meet the customer request, the Company constructed the Tinsley POP with three motor-operated switches with SCADA control, RTU, and EPS metering approximately 1.3 line miles south of Carver 138 kV Station on the Maxwell-Carver 138 kV line between structures 2/5 and 2/6. | 2079949.86
TP2014129 | Beeville Area Improvements | RTO | This project upgraded the transmission facilities in the Live Oak County area. The upgrades included adding a 138/69 kV autotransfomer at a new station in the Beeville area, constructing a new 138/69 kV circuit between Beeville and Tuleta, and rebuilding and converting the Beeville to Three Rivers 69 kV line to 138 kV. | 52421143.77
TP2020020 | Apogee Wind Interconnect | IPP | This was an interconnection project to a 451.5 MW wind generating facility. The greenfield 345 kV Perigee Station was constructed as a 3 breaker ring bus. The Foxtail - Mulberry Creek 345 kV line had a 0.1 mile cut-in to Perigee completed that was designed single circuit 345 kV steel structures. Approximately 0.15 miles of a 345 kV line was constructed to the generator’s point of interconnection (POI). | 15571098.86
TA2020104 | TNC Abilene 2024 TTMP | Telecom | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -2134.36
TA2020035 | TNC San Angelo 2023 TTMP | Telecom | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -3011.74
TA2019447 | TNC/TCC Meter Modernization | Reliability | This project covered the Electric Reliability Council of Texas (ERCOT) Meter Modernization Initiative (MMI) to address metering points across the Transmission system that are impacted by poor physical condition or obsolete equipment. This program ensures that regional transmission organization (RTO) accuracy standards are followed across the AEP system. The MMI program addressed primarily communication problems at Brownsville, Las Pulgas, Rio Hondo Southwest, and Santa Anna Brownwood Stations. It also upgraded meters, meter panels, and communication at Lane City, North Edinburg, Turtle Creek, and University Stations. Additionally, instrument transformers were upgraded at Dilley Southwest, Equistar, Military Highway, and San Miguel Southwest Stations. | 2220096.56
TP2014107 | Tortuga 138 kV Station and POD | Customer Service & Other | This was an industrial customer project that was going to add 20 MW of load in the area. The Company built a greenfield 138 kV Tortuga Station with a 3 breaker line bus. A 138 kV termination from the Upriver - Gila was built as a single circuit 138 kV design standard steel structures. The station was built in-line with the existing line so the terminations installed new dead end structures. Approximately 0.21 miles of a 138 kV line was constructed to the point of interconnection (POI). | 10495150.41
TP2018146 | Toyana 138kV Sub: CoralApache | Customer Service & Other | This project was created to construct a new 138 kV station to serve a new 40 MW industrial load. A ring bus was selected due to the size of the load and the need to install two capacitor banks to support the voltage in the area. | 689.69
TP2009001 | TPCO American Steel Mill Proje | Customer Service & Other | This project was created to construct a new 138 kV station to serve a new 120 MW industrial load. | 948885.53
DP19X0005 | Trade Zone Substation | Distribution Driven Transmission | This project constructed Trade Zone Substation to offload South McAllen Substation. The substation included one 138 kV/69 kV/13.09 kV transformer, three 1200A feeder breakers, and approximately 2 miles of 556 Aluminum primary wire and 4/0 All Aluminum Alloy Conductor neutral wire. | 2659408.95
TP2020082 | Brightside Permanent Interconn | IPP | This was an interconnection project to a 58.8 MW solar generating facility. The greenfield 138 kV Charter Station was constructed as a 3 breaker ring bus and a DICM was installed. The Poesta - Three Rivers 138 kV line had an in-line 0.05 mile cut-in to Charter completed that was designed single circuit 138 kV steel structures. Approximately 0.03 miles of a 138 kV line was constructed to the generator’s point of interconnection (POI). | 8213246.56
TA2017938 | Transmission Access Control | Reliability | The Company implemented an access control system across all of AEP's Transmission and Distribution stations to standardize security architecture and help facilitate internal AEP security management and communications. The new security access system, ABLOY PROTEC CLIQ, is a new lock technology system that integrates electronics and mechanics and allows for a standardized system with the ability to change access rights to stations within the Company system. | 2696537.17
TA2019376 | Transmission TCC DWDM TTMP | Reliability | This Transmission Telecommunication Modernization Program (TTMP) which will provide a robust telecommunication network in the AEP Texas service area. This program built 16.1 miles of AEP-owned fiber that increased resiliency at 33 stations, provides resiliency via new fiber ring topology to four stations while laying the groundwork for resiliency in the future. | 5909737.25
TA2019377 | Transmission TNC DWDM TTMP | Telecom | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -2459.33
TP2019312 | Tres Bahias Interconnection | IPP | This project created a new interconnection to a 195 MW solar farm in Calhoun County, Texas. In order to accommodate the customer request, the Company installed a new 138 kV terminal at the Joslin 138 kV Station, EPS metering (primary and backup), fiber, and one 138 kV span outside of Joslin to the gen-tie line point of interconnection (POI). In order to make room for the gen-tie line on the Joslin property, the Company also reterminated the existing Dupont-Joslin 138 kV line to the new terminal, reterminated the existing Formosa-Joslin 138 kV line to the old Dupont terminal, and interconnected Tres Bahias at the old Formosa terminal. | 4063711.6
TA2019057 | Tuscola to Winters Rehab | Reliability | The Comapny replaced jumpers at Winters and Tuscola Stations to support new structure design of the Tuscola-Winters 69 kV line rebuild being completed on ETT-901. The Company rebuilt the 19.34 mile Tuscola-Winters 69 kV line based on the outage history, equipment condition, and outdated design. While this line is an ETT-owned asset, AEP owns the Tuscola and Winters Stations. To accommodate the new structure design, AEP replaced jumpers at Tuscola and Winters Stations.The jumpers at ETT-owned Steamboat Station were replaced on ETT-901. | 144846.08
TP2020209 | Starr Solar Interconnection | IPP | Customer requested to interconnect a new 136 MW solar generating facility at the Roma Tap 138 kV Station in Starr County, Texas. In order to accommodate the new generation facility, the Company constructed a new 138 kV terminal at the Roma Tap 138 kV Station and the first span of the gen-tie line. | 2062790.99
TA2018507 | TX CIP Firewall Install | RTO | Cisco Industrial Security Appliance (ISA) Firewall device at medium impact stations were installed. Pilot installation was performed in July 2018 and subsequent testing and configurations yielded positive results on the mitigation plan. | 169982.63
TA2019787 | TX Line Rehab Program | Reliability | This program covered partial rebuild on eight transmission lines in the Texas region. Assets were replaced to address issues like rotting poles, broken arms, and flashed insulators. | 4709837.62
TA2021015 | UnionCarbide-Port Isabel Rehab | Reliability | This project was used to mitigate 199 conditions identified during inspection of this line in Cameron County, Texas. The conditions identified are deterioration of components which include rotten poles, rotten crossarms, and rusty static arms. One out of the 106 structures on the line was completely replaced. | 928483.45
TP2014131 | Uvalde - Campwood 69kV Rebuild | RTO | This project rebuilt 37 miles of the single circuit Uvalde - Campwood 69 kV line to address NERC reliability standards. The line was rebuilt to 138 kV standards, but is currently operated at 69 kV to allow for future growth in the area. This project also included associated equipment upgrades at Uvalde Station and installation of a four breaker ring bus, a new 138 kV/69 kV auto transformer, and a 138 kV/12 kV distribution transformer at Campwood Station. | 39327496.11
TP2012020 | Val Verde WindFarm Interconnect | IPP | A Customer requested to interconnect a wind generating facility called Val Verde Wind totaling 180 MW to the Company's transmission system. This project provided a temporary and permanent connection. The permanent connection is a new 138 kV station, called Maxwell (TCC). The 138 kV station is a three breaker ring bus expandable to a six breaker ring in the future. Communication and metering equipment was installed at Maxwell station on the terminal to Fermi station. | 38169.41
DP18X0018 | Valadez - Construct Substation | Distribution Driven Transmission | This project constructed the new Valadez Substation on previously purchased land. The new substation included two 138kV/13.09kV transformers, four distribution feeder breakers, and approximately 6.5 miles of feeder reconductor. Only those portions of the project related to transmission assets have been included in this transmission plant in service. | 1819602.4
TP2020106 | Vancourt Solar Interconnection | IPP | Customer requested to interconnect a 50 MW solar generating facility in Cameron County, Texas. To accommodate the customer request, the Company built the new Luna Station located along the LaPalma-Wesmer 138 kV line. The Company installed a new 138 kV terminal at the Luna Station and installed primary and backup EPS metering, fiber, and one 138 kV span outside of Luna Station for the gen-tie line. | 1642415.59
DP17N0001 | Verhalen - Incr Capacity | Distribution Driven Transmission | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -16664.31
TP2016046 | Vernon Main:Add capacitor bank | RTO | The Company installed two 138 kV 14.4 mega volt amps (MVAR) capacitor banks at the Vernon Main Street 138 kV bus. This project was identified in the 2015 Regional Transmission Plan study. | 268101.87
TP2018033 | Victoria City Interconnection | IPP | This project created an interconnection to a 100 MW thermal generating facility in Victoria County, Texas. The Company intalled a remote terminal unit, station data repository, disturbance monitoring equipment, sub-synchronous oscillation relay, and added a breaker terminal along with ERCOT Polled Settlement metering at Victoria Power Plant Station. | 3435216.29
TP2018242 | Victoria City Replace Breaker | RTO | This project replaced a circuit breaker at Victoria Plant Station. This replacement requirred expansion of the control house and installation of new relay panels. To accommodate likely future projects, the control building expansion is large enough to ensure the control house does not need to be re-expanded in the foreseeable future. | 1302448.17
TP2020195 | Victoria Port 2 Permanent | IPP | A Customer requested to interconnect a new 100 MW thermal generating facility called "Ruple" in Victoria County, TX. Per the Public Utility Commission of Texas substantive rules, the Transmission Service Provider (TSP) is required to build all direct interconnection facilities to interconnect the generator to the transmission system. The original project scope for the Victoria-DuPont Switch station breaker and relaying upgrade project was driven by the interconnection of a 100 MW thermal generating facility (TP2018014). Customer has notified the Company of two additional generator units at its location. To accommodate the new generation facility,the Company updated relay settings and panels at Victoria-DuPont Switch as well the remote ends of Victoria-DuPont Switch line terminals. | 144413.29
TP2018014 | Victoria Port Permanent | IPP | This project created an interconnection to a 100 MW thermal generating facility in Victoria County, Texas. To accommodate the new interconnection request, the Company removed a temporary tap outside Dupont Switch Station (Victoria), installed five breakers, and added a permanent line (Dupont Switch Station-Rupley) with sub-synchronous oscillation relays. | 7220948.47
TP2018013 | Victoria Port Temp Tap | IPP | This project created an interconnection for a 100 MW thermal generating facility in Victoria County, TX. The requested interconnection to the ERCOT transmission system was temporary tap on the Dupont SW-Victoria 138 kV Line. AEP Texas connected a temporary tap at the collector station and installed a remote terminal unit (RTU), disturbance monitoring equipment (DME), and ERCOT - Polled Systems (EPS) metering at the generator's collector station. | 1122398.07
TP2014145 | Victoria-Fannin69kV Line Rebui | RTO | This project was either placed in service during a previous rate case review period or canceled, and the amount reflected in transmission capital is a credit. | -3220.29
TA2018052 | Weaver Rd - Greenlake 69 kV | Customer Service & Other | The Port Authority of Victoria requested the relocation of a portion of the Weaver Road - Greenlake 69 kV Line due to the widening of the adjacent road (McCoy) from State Highway 185 to the Victoria Bridge Canal. The Company removed three existing wood pole structures along McCoy Road that are crossing the widended area. The Company installed a new three-pole self-supporting dead-end structure and two pole tangents. All poles are galvanized steel. | 549340.82
TP2012106 | Welsh HVDC Tie | RTO | This project installed new harmonic filters and reactors at the Welsh HVDC facility to address NERC reliability standards. When the generators at Monticello were offline there was no voltage regulation in the area of the HVDC tie, which led to high voltages. The reactors will lower the voltage and enable parallel operation of the harmonic filters. | 2845647.15
TA2021140 | Wesmer-Weslaco Unit 138kV Reha | Reliability | This project rehabilitated the Wesmer-Weslaco Unit 138 kV line in Hidalgo County, TX. An inspection of the Wesmer-Weslaco Unit 138 kV line has identified 74 open conditions related to the deterioration of components such as rotten poles, rusty davit arms, rusty insulators, and rusty static hardware. To address these issues and to avoid unplanned outages at Mesquite and Wesmer Stations, Transmission Field Services replaced 11 of the 114 structures on this line as well as replaced needed components and hardware. | 1044366.4
TP2019197 | West Raymond Wind | IPP | This project created a point of interconnection for a 240 MW wind farm in Sebastian, Texas. The interconnection to the Company system is at the new 345 kV Bonilla Station located on the North Edinburg-Rio Hondo 345 kV line. This project included installation of two breakers and a dead-end structure outside of the new Bonilla Station to provide a point of interconnect for the Customer. After the addition of the two breakers, Bonilla Station has a six breaker, two rung, breaker and a half configuration. | 6373141.81
TP2019219 | Whitepoint 138 kV 345 kV Auto | Customer Service & Other | This project expanded the Whitepoint 345 kV and 138 kV Stations, added a fifth rung with two new 138 kV breakers to the 138 kV bus, expanded the 345 kV bus from a three to four breaker ring bus configuration, and added the second 345/138 kV transformer. Portions of the Pelican-Whitepoint and Nueces-Mayo-Whitepoint 138 kV lines were relocated to accommodate the station expansion. | 3001483.24
TP2020034 | Whitepoint 138 kV Line Reactor | RTO | This project replaced the existing Whitepoint 138 kV series reactors to address NERC reliability standards. The Company replaced the two existing 10 ohm series reactors on the Gila-Whitepoint 138 kV and Nueces Bay-Whitepoint 138 kV lines with 19.8 ohm series reactors. | 2578758.12
TP2019179 | Whitepoint Area 138kV Imprvmt | RTO | This project was created to LiDAR multiple lines in the Ingleside area to determine if their MOT could be increased. An increased MOT leads to a higher rating for lines. A higher rating is needed to help support the new industrail load that has signed in the area. | 0.1
TP2016128 | Wolfgang Three Breaker Ring | Reliability | The Company replaced the three line switches at the Clairmont Tap with a 138 kV phase over phase switch structure. At the Wolfgang Tap, the greenfield 69 kV Wolfgang Station was constructed as 3 breaker ring bus and a DICM was installed. The Jayton - Rotan 138 kV line had a 0.05 mile cut-in to Wolfgang. The line was also reterminated into the new switch structure at Clairmont Tap. These were designed as 69 kV single circuit steel structures. Approximately 400 feet of a 138 kV line was constructed to the generator’s point of interconnection (POI). | 12318975.18
TP2009082 | Yellowjacket to Heartland 69 kV line build | RTO | The Company built the greenfield Heartland 69 kV Substation and 30 miles of single circuit transmission line, constructed at 138 kV and operated at 69 kV, from the Yellow Jacket Station to the newly built Heartland Station. This project was constructed to address NERC reliability standards. | 31368031.92
TA2016809 | Yosemite Line Relocation | Customer Service & Other | This customer driven project was placed into service during a previous rate case, and the credit in the plant in service file is due to customer reimbursement of project costs. | -284389.08
DP15X0016 | Young Sub - Construct New Sub | Distribution Driven Transmission | This project constructed the new Young Substation to offload Polk Ave Substation and Pharr Substation feeders. The substation included two 138 kV/13.09 kV transformers, six 2000kVA regulators, five 1200A breakers, two 2000A totalizer breakers, and One 2000A bus tie breaker. The new substation was constructed on existing AEP land purchased in 2017. | 2645996.74
TA2021018 | Zapata - Randado Rpl two strs | Reliability | This project replaced two three-pole structures that are deteriorated from rot in Zapata and Jim Hogg Counties, Texas. | 858580.61
3070266935.86