## Energy Loss Factor
WP/II-H-1.3/1
Page 1 of 3
2021 TEST YEAR DATA
Oncor Electric Delivery Company LLC
Unadjusted Test Year Load Data
For the Test Year Ended December 31, 2021
Sponsor: D.E. Nelson
System Line Loss Calculation
Energy Loss Factor Calculation
Line
No.
(a) | (b) | (c) | (d)
1 | System Net Consumed, MWh (as Calculated page 3) |  | 119258130.5031
2
3 | Booked Sales and Energy Losses by Voltage Level, MWh
4 | (Booked Sales and Energy Losses Page 3):
5 |  | Energy | Booked
6 |  | Losses | Sales
7 | Substation | 680634.8252 | 6412195
8 | Primary | 1030222.1777 | 17209450
9 | Secondary | 2002628.5002 | 91923000
10 | Total | 3713485.5031 | 115544645
11
12 | Percent Losses Calculation Procedure
13 | Substation:
14 | Input to Distribution Substation Transformation System, MWh |  | 119258130.5031
15 | Substation Losses, MWh |  | 680634.8252
16 | Substation Sales, MWh |  | 6412195
17 | Remainder to Distribution Primary System, MWh |  | 112165300.6779
18 | Percent Losses (Line 15/Line14) |  | 0.5707%
19 | Primary:
20 | Input to Distribution Primary System, MWh |  | 112165300.6779
21 | Primary Losses, MWh |  | 1030222.1777
22 | Primary Sales, MWh |  | 17209450
23 | Remainder to Distribution Secondary System, MWh |  | 93925628.5002
24 | Percent Losses (Line 21/Line 20) |  | 0.9185%
25 | Secondary:
26 | Input to Distribution Secondary System, MWh |  | 93925628.5002
27 | Secondary Losses, MWh |  | 2002628.5002
28 | Secondary Sales, MWh |  | 91923000
29 | Percent Losses (Line 27/Line 26) |  | 2.132%
30
31 | Loss Factors
32 | Loss Element by Voltage Level (1 - (Percent Losses/100):
33 | Substation |  | 0.99429
34 | Primary |  | 0.99082
35 | Secondary |  | 0.97868
36
37 | Factor by Voltage Level :
38 | Substation (1.0/Line 33) |  | 1.0057
39 | Primary (Line 38/Line 34) |  | 1.0151
40 | Secondary (Line 39/Line 35) |  | 1.0372

## Demand Loss Factor
WP/II-H-1.3/1
Page 2 of 3
2021 TEST YEAR DATA
Oncor Electric Delivery Company LLC
Unadjusted Test Year Load Data
For the Test Year Ended December 31, 2021
Sponsor: D.E. Nelson
System Line Loss Calculation
Demand Loss Factor Calculation
Line
No.
(a) | (b) | (c) | (d)
1 | System Peak Demand, MW (as Calculated Page 3) |  | 23735.7517
2
3 | Coincident Demand and Demand Losses, MW
4 | (Coincident Demands and Demand Losses Page 3):
5 |  | Demand | Coincident
6 |  | Losses | Demand
7 | Substation | 150.2397 | 766.781
8 | Primary | 309.2799 | 2197.9
9 | Secondary | 364.6011 | 19946.95
10 | Total | 824.1207 | 22911.631
11
12 | Percent Losses Calculation Procedure
13 | Substation:
14 | Input to Distribution Substation System, MW |  | 23735.7517
15 | Substation Losses, MW |  | 150.2397
16 | Substation Demand, MW |  | 766.781
17 | Remainder to Distribution Primary System, MW |  | 22818.731
18 | Percent Losses (Line 15/Line 14) |  | 0.633%
19 | Primary:
20 | Input to Distribution Primary System, MW |  | 22818.731
21 | Primary Losses, MW |  | 309.2799
22 | Primary Demand, MW |  | 2197.9
23 | Remainder to Distribution Secondary System, MW |  | 20311.5511
24 | Percent Losses (Line 21/Line 20) |  | 1.355%
25 | Secondary:
26 | Input to Distribution Secondary System, MW |  | 20311.5511
27 | Secondary Losses, MW |  | 364.6011
28 | Secondary Demand, MW |  | 19946.95
29 | Percent Losses (Line 27/Line 26) |  | 1.795%
30
31 | Loss Factors
32 | Loss Element by Voltage Level (1 - (Percent Losses/100):
33 | Substation |  | 0.99367
34 | Primary |  | 0.98645
35 | Secondary |  | 0.98205
36
37 | Factor by Voltage Level :
38 | Substation (1.0/Line 33) |  | 1.0064
39 | Primary (Line 38/Line 34) |  | 1.0202
40 | Secondary (Line 39/Line 35) |  | 1.0388

## 2021 Stats
WP/II-H-1.3/1
Page 3 of 3
2021 TEST YEAR DATA
Oncor Electric Delivery Company LLC
Unadjusted Test Year Load Data
For the Test Year Ending December 31, 2021
Sponsor: D.E. Nelson
2021 Analysis of System Losses
Calculated Losses Using 2015 Oncor Integrated Power System Loss Analysis
| MWh |  | MW
Retail Sales from Service Drop | 91923000 |  | 19946.95
Service Drop Factor * | 1.0031 |  | 1.0038
Output from Secondary | 92211638.22 |  | 20022.9479
Secondary Conductor Loss Factor * | 1.001 |  | 1.0019
Output from Line Transformers | 92303849.8582 |  | 20060.7913
Line Transformer Loss Factor * | 1.0176 |  | 1.0125
Input to Line Transformers | 93925628.5002 |  | 20311.5511
Sales from Primary | 17209450 |  | 2197.9
Output from Primary Lines | 111135078.5002 |  | 22509.4511
Primary Line Loss Factor * | 1.0093 |  | 1.0137
Output from Distribution Substations | 112165300.6779 |  | 22818.731
Sales from Substations | 6412195 |  | 766.781
Total Output from Distribution Substations | 118577495.6779 |  | 23585.512
Distribution Substation Loss Factor * | 1.0057 |  | 1.0064
Input to Distribution Substations | 119258130.5031 |  | 23735.7517
Total System Losses | 3713485.5031 |  | 824.1207
NOTE:
2021 Annual Energy from company records and Demand at ERCOT's 2021 annual peak
* For Loss Factors, refer to WP/II-H-1.3/2