## Schedule VI-M-2.1
| Project Name | Portions of Planning Studies that Support Need for Project 1 | Load growth rate in area to be served by project during each of 5 calendar years immediately before project was energized | Load growth rate in area served by project during each calendar year starting with year project initially energized | Peak Load projected to be served by project as forecasted by applicant and consistent with planning study | Peak Load served by project during each year since project was initially energized | Identify types of load the project was planned to serve (Industrial, Commercial, Residential, others) | Identify Customers if project was planned to serve a limited number of Customers with relatively large loads 2
1 | 17T63019 -- MAVERICK DRAW SUB: ESTABLISH 138-21.6 KV 28 MVA XFMR & 1 FDR BKR | Customer A and Customer V have requested 13 MW total of distribution service over the next 2 years to serve oil fields and a cryogenic processing plant. The customers are adjacent to Oncor Permian to Culberson 138 kV Transmission Line in Culberson County. The requested in-service date is April 15, 2018. In addition the area is Oncor singly certified. There are currently no distribution facilities in this area. The distance to this new load, which is virtually all motor load, from Screwbean substation is 69,300 ft. or 13.2 miles. In order to serve the load, it is proposed to establish Culberson Co. FM 2119 substation (now knows as Maverick Draw Sub) with 1-28 MVA 138-21.6 kV substation transformer and two 21.6 kV feeder breakers. The new station will be located along FM 2119 and west of the Culberson-Reeves County Line. Completion of this work will provide service to Customer A, Customer V, and expand the distribution capabilities on this single certified area. | 2014: -23.19% 2015: 24.53% 2016: 45.45% 2017: 52.08% 2018: 63.70% | 2019: 37.66% 2020: 38.60% 2021: -24.62% | 6.5 MW | 2019: 3.3 MW 2020: 5.6 MW 2021: 5.6 MW | Commercial | Customer A Customer V
2 | 17T63008 -- SALT LAKE SUB: ESTABLISH 138-12.5 KV STATION | Customer C has requested 8.7 MW distribution service over the next five years to an oil field immediately adjacent to Oncor’s Spraberry Switch switching station in Midland County. The requested in-service date is March 1, 2017. The current distribution to this area is served from Tex Harvey 1621. The distance to this new load, which is virtually all motor load, from Tex Harvey Substation is 88,000 ft. or 16.7 miles. A study of the Distribution system has determined that an acceptable motor starting capacity cannot be provided at this requested point of service due to the distance. An acceptable voltage level cannot be maintained over this distance, and coordination is not possible due to extremely low available fault currents. In order to serve the Customer C load, it is proposed to install Salt Lake Substation with 1-28.0 MVA 138-12.5 kV substation transformer and two 12.5 kV feeder breakers. The new station will be located across CR 1160 from Spraberry Switch. It is anticipated that Customer C will request a substation rate PME at the new substation, however Distribution Planning recommends that one of the new feeder also be tied to existing distribution in the area, and also load be transferred from Tex Harvey 1621 to the new feeder. Completion of this work will provide service to the Customer C Oil Field, provide load relief for Tex Harvey Substation, and will improve reliability, voltage stability, motor starting capabilities, and coordination in this area. | 2012: 12.77% 2013: 3.77% 2014: 7.27% 2015: 30.51% 2016: 6.49% | 2017: 14.63% 2018: 82.98% 2019: 2.91% 2020: -6.78% 2021: -24.74% | 6.5 MW | 2017: 1.7 MW 2018: 8.5 MW 2019: 7.8 MW 2020: 7.1 MW 2021: 8.1 MW | Commercial Industrial | Customer C
3 | 19T63013 -- CASTILE HILLS SUBSTATION: ESTABLISH STATION W/ 47MVA TRANSFORMER | Black River Substation has received a 25.5 MW of distribution service request with buildout over the next 2 years. This request along with area growth will load Black River Substation, a 1-28 MVA transformer station to 45.5 MVA, which is 163% over the 28 MVA transformer name plate rating. In order to correct this problem it is proposed to establish Castile Hills Substation by installing Transformer #1, (1) 46.7 MVA 138-21.6 kV, and (2) 21.6 kV feeder breakers with 1,000 AL feeder exits. Establish two primary points of delivery for the Customer to transfer their load form Black River Substation to Castle Hills Substation. The completion of this project will correct the normal loading problem at BLKRV Substation Transformer #1 | 2014: 52.94% 2015: 24.36% 2016: 30.93% 2017: 22.05% 2018: 22.58% | 2019: 50.53% 2020: 4.55% 2021: 22.10% | 25.5 MW | 2019: 14.2 MW 2020: 15.7 MW 2021: 16.7 MW | Industrial | Customer D
4 | 0PT40938 -- HARRY HINES SUB : ESTABLISH SUBSTATION WITH 1–46.7MVA, 138-13.8 KV TRANSFORMER AND A SWITCHGEAR BUILDING WITH TWELVE CIRCUIT BREAKERS FOR EIGHT FEEDERS. | Customer E has requested 14 MVA dual feed service with a third, redundant feeder in Dallas. The 2020/2021 projected winter load on Reagan Street 0015 is 12.0 MVA which is 148.1% of its 8.1 MVA rating. In addition, the 2020/2021 projected winter load on Reagan Street 0016 is 13.5 MVA, which is 103% of its 13.1 MVA rating. In order to correct these problems, it is proposed to establish Harry Hines Substation with 1- 46.7 MVA, 138 - 13. 8 kV transformer and a switchgear building with twelve circuit breakers for eight feeders. The completion of this project will correct the loading problems on Reagan Street 0015 and 0016 and provide additional backstand capacity to feeders in the area. | 2015: 0.00% 2016: 0.00% 2017: 0.00% 2018: -5.88% 2019: -6.94% | 2020: 66.42% 2021: -14.54% | 14 MW | 2020: 1.5 MW 2021: 1.9 MW | Commercial | Customer E
5 | 0PT04398 -- THORNTONVILLE SUB: INSTALL 1-28 MVA AND 2-12.47KV FEEDER | Monahans Substation has received a 6.8 MW of distribution service request with buildout over the next 2 years. The customer requested in-service date is October 15, 2019. This request along with area growth will load Monahans Substation transformer #2, a 22.4 MVA transformer, to 25.8 MW, which is 116% over the transformer name plate rating. In addition, the substation will be loaded to 39.8 MW which is 142% over its 28 MVA substation rating. Lastly, the projected load on Monahans substation feeder 1912 is 19 MW which is 142% over the 13.8 MVA Feeder Maximum Continuous rating. In order to correct this problem it is proposed to establish Thortonville Substation by installing Transformer #1, (1) 28 MVA 138/69-12.47 kV, and (2) 12.47 kV feeder breakers with 1,000 AL feeder exits. Install approximately 9,000’ of 3-795 AAC, two 900 amp ABS and perform feeder switching. The completion of this project will correct the normal loading problem at Monahans Substation Transformer #2 and correct feeder loading of Monahans substation feeder 1912. | 2014: 5.51% 2015: 6.62% 2016: 4.25% 2017: -7.84% 2018: 30.27% | 2019: 13.94% 2020: -2.75% 2021: -16.01% | 11 MW | 2019: 0.5 MW 2020: 10.6 MW 2021: 6.8 MW | Commercial Industrial Residential | Customer F
6 | 0PT04144 -- KYLE RANCH: ESTABLISH SUBSTATION WITH 2-46.7 MVA 138-21.6KV TRANSFS AND FOUR FEEDER BREAKERS | ELMAR Substation has received 83.4 MW and MASON substation has received 70MW of distribution service requests with buildout over the next 2 years. These requests along with area growth will load ELMAR Substation a 2-46.7 MVA transformer station to 111.7 MVA which is 191% over the 58.4 MVA Substation Rating. In addition, ELMAR Substation transformer #2 will be loaded to 66.7 MVA which is 143% over its 46.7 MVA nameplate rating. MASON substation transformer #3 will be loaded to 42.0MVA which is 150% over its 28.0 MVA rating Lastly, Substation feeders ELMAR 3222 and MASON 3413 will be loaded to 30.2 MVA and 31.0 MVA, which is 120% and 116% of their 25.2 and 26.8 MVA maximum continuous ratings, respectively. In order to correct this problem it is proposed to establish KYLE Ranch Substation with (2) 46.7 MVA 138-21.6 kV Substation Transformer and (4) 21.6 kV feeder breakers with 1,000 AL feeder exits. In addition, install approx. 15,000' of 3-795 AAC, 4,000' of double circuit 3-795, (3) 900 AMP ABS, relocate 1 NOVA recloser, remove 1 NOVA recloser and perform feeder switching. The completion of this project will correct the normal loading problem at ELMAR and MASON Substations and relieve its distribution feeders. | 2015: -14.29% 2016: 31.90% 2017: 14.38% 2018: 70.10% 2019: 30.57% | 2020: 14.67% 2021: 8.23% | 56 MW | 2020: 14.6 MW 2021: 29.6 MW | Commercial Industrial | Customer G Customer W Customer X
7 | 0PT39579 -- HILL CREST (BIG SPRING GULF SUB) : ESTABLISH STATION WITH 138-12.5KV, 46.7MVA TRANSFORMER AND TWO FEEDER BREAKERS | The 2020 projected summer load on Big Spring Gulf Substation Transformer Bank #1 is 12.8MVA which is 341% of the 3.75 MVA maximum rating for this transformer bank. This overload is caused by two customers who are Customer H’s 3.9 MW added load to their existing 1.7MW load and Customer I’s 5.2MW added load to their existing 2.0 MW load. The customer’s requested in-service date is May 1, 2020. In addition the 2020 projected load on Big Spring Switch Substation is 34.1 MVA which is 136% of the 25 MVA backstand rating for this substation. In order to correct this problem, the original Plan Story proposed to replace the existing transformer at Big Spring Gulf substation with a 138kV-12.47kV 1-47MVA transformer with 3 feeder breakers. Also install two 795AAC overhead feeder exits for two substation rate customers and another 795AAC overhead feeder exit for a new feeder connecting to Big Spring Switch. The new feeder will require reconductoring approx. 10,000 ft. of existing single phase line to 3-795AAC and installing two N.O. switches. The completion of this project will correct the overload at Big Spring Gulf Substation and substation rating overload at Big Spring Switch substation. The actual project constructed differed from the recommendation after detailed engineering analysis performed by Oncor’s Transmission Engineering group determined that no additional room was available to accommodate the transformer change-out, and therefore, additional property was acquired and the new substation (Hill Crest Substation) was constructed on acquired property. | 2015: 5.34% 2016: 0.68% 2017: 7.05% 2018: 7.84% 2019: -0.58% | 2020: -4.97% 2021: -0.14% | 12.8 MW | 2020: 1.5 MW 2021: 13 MW | Industrial | Customer H Customer I
8 | 18T63115 -- YARBROUGH SUB: ESTABLISH STATION | Customer J has requested 7.2 MW of distribution service over the next years served by a single PME from Judkins Substation. This request load Judkins Substation Transformer #1 to 11.3 MVA, which is 108% of its 10.5 MVA nameplate rating. Also, the Autotransformer will be loaded to 8 MVA, which is 107% of its 7.5MVA nameplate rating. In addition, Monahans Substation is projected to be loaded at 34.5 MVA or 123% of its backstand rating. In order to correct this problem it is proposed to establish Yarbrough Substation by installing a 28 MVA 138-21.6 kV Substation Transformer, (2) 21.6 kV feeder breakers with 1,000 Cu feeder exits, approx. 34,800 feet of 3-795, (1) 900 AMP ABS and perform feeder switching. The completion of this project will correct the normal loading problem at Judkins substation transformer #1 and backstand loading of Monahans substation. | 2013: 1.87% 2014: 2.10% 2015: 7.46% 2016: 3.35% 2017: -9.49% | 2018: 23.02% 2019: 15.18% 2020: -22.02% 2021: 4.23% | 12 MW | 2018: 0.1 MW 2019: 0.1 MW 2020: 0.9 MW 2021: 3.0 MW | Commercial Industrial | Customer J
9 | 16T63020 -- MARIENSFIELD 138-25 KV SUBSTATION: ESTABLISH STATION | Customer K has requested 7.6 MW of added load at the existing Cross Bar North and Cross Bar South PMEs M County. Customer K currently has 2 PMEs with a total load of approximately 4.6 MW for the total of 12.2 MW. The earliest possible in-service date is March 15, 2019.The current distribution to this area is served from Midland Farm Feeder 2131. There are ties to both Adobe Meadows 6532 and Alkali Lake 4221. The distance to this new load, which is virtually all motor load, from Midland Farms Substation is 80,000 ft. or 15.1 miles. A study of the Distribution system has determined that an acceptable motor starting capacity cannot be provided at this requested point of service due to the distance. An acceptable voltage level cannot be maintained over this distance, and coordination is not possible due to extremely low available fault currents. MDFRM2131 is a GT 300 Enhancement Feeder. In order to serve the Customer K load, it is proposed to install Marienfield Substation with 1-47.0 MVA 138-21.6 kV substation transformer and three 21.6 kV feeder breakers. The new station will be located approximately 5 miles west of the State Hwy 349. It is proposed to create three new feeders. Feeder one will serve west to Customer K’s two PMEs, which will require approximately 1000 ft. of 3-795 kcmil AAC primary with #4/0 AAAC neutral to the intersection with the current MDFRM 2131, Reconductor approximately 9000 ft. of 3-#4/0 ACSR with 3-795 kcmil AAC, installing 2-1200 KVAR capacitor banks, removing 3-1200 KVAR capacitor banks from MDFRM 2131, installing two air break switches, removing 3-200 amp regulators, and transferring approximately 12.1 MW of load from MDFRM 2131 to MRNFD feeder 1. The second feeder will consist of installing approximately 1000 ft. 3-795 kcmil with 4/0 AAAC neutral and reconductoring approximately 2,000 ft. of 3-#4/0 ACSR with 3-795 kcmil AAC, installing 1-900 amp air break switch, relocating a NOVA recloser, and transferring approximately 7 MW from ADMDS 6532 to MRNFD feeder 2. The third feeder will consist of installing approximately 1000 ft. 3-795 kcmil AAC w #4/0 AAAC neutral, and reconductoring 8,000 ft. 3-#1/0 ACSR with 3-795 kcmil AAC, removing 6-200 amp regulators, removing 1 NOVA recloser, and transferring approximately 6 MW from ADMDS 6532 to MRNFD feeder 3. Completion of this work will provide service to the Customer K Cross North and Cross South PMEs, provide load relief for Adobe Meadows Substation feeder 6532, and will improve reliability, voltage stability, motor starting capabilities, and coordination in this area. This work will also be an enhancement of a GT300 Feeder. | 2014: 96.67% 2015: 80.51% 2016: -12.21% 2017: 75.40% 2018: 20.73% | 2019: -3.28% 2020: 15.93% 2021: -18.91% | 10 MW | 2019: 1.5 MW 2020: 4.2 MW 2021: 2.4 MW | Commercial Residential | Customer K
10 | 0PT39591 -- WILLOW WELLS SUB : INSTALL A 46.7 MVA TRANSFORMER AND TWO FEEDER BREAKERS | Loving Substation has received 1.7 MW and 10.0 MW of distribution service requests for Customer O and Customer P (ultimate load is 45.5 MW), respectively. These requests along with area growth will load Loving transformer #2, a 28 MVA bank to 32.0 MVA in the 2020 summer, which is 114% over the 28.0 MVA transformer name plate rating and Loving Substation to 57.2 MVA in the 2020 summer, which is 163% of the 35.0 MVA substation rating. In order to correct this problem it is proposed to establish Willow Wells Substation by installing Transformer #1, (1) 46.7 MVA 138-21.6 kV, and (2) 21.6 kV feeder breakers with a 795 AAC OH feeder exit and a 1000 Cu UG exit, and Transformer #2, (1) 46.7 MVA 138-21.6 kV, and (2) 21.6 kV feeder breakers. Establish one primary point of delivery for the Customer P’s substation rate and install 10,000 ft. of 3-795 AAC primary and reconductor 9500 ft. of 3-#1/0 ACSR primary with 795 AAC conductor, and transfer loads from Loving Substation to Willow Wells Substation. The completion of this project will correct the normal loading problems at Loving Substation. | 2015: 45.59% 2016: 39.39% 2017: 33.33% 2018: 58.70% 2019: 70.55% | 2020: 1.41% 2021: 2.93% | 13 MW | 2020: 15.4 MW 2021: 13.9 MW | Commercial Industrial Residential | Customer O Customer P
11 | 0PT37618 -- HORSEHEAD DRAW SUB (FORMERLY MENTONE SOUTHWEST SUB) : ESTABLISH STATION WITH (1) 46.7 MVA 138-21.6 KV SUBSTATION TRANSFORMER AND (3) 21.6 KV FEEDER BREAKERS | ELMAR Substation has received 83.4 MW of distribution service requests with buildout over the next 2 years. These requests along with area growth will load ELMAR Substation a 2-46.7 MVA transformer station to 99.4 MVA which is 170% over the 58.4 MVA Substation Rating. In addition, ELMAR Substation transformer #1 will be loaded to 51.9 MVA which is 111% over its 46.7 MVA nameplate rating. In addition, MASON Substation feeder 3412 is projected to be loaded to 11 MW, there is currently no backstand capability for this feeder. In order to correct this problem it is proposed to establish Mentone Southwest Substation with (1) 46.7 MVA 138-21.6 kV Substation Transformer and (3) 21.6 kV feeder breakers with 1,000 AL feeder exits. In addition, install approx. 8,000’ of double circuit 3-795 AAC, and 4,000’ of 3-795 AAC, (3) 900 AMP ABS, (1) 7500 kVA 22 to 12 KV Auto, and perform feeder switching. The completion of this project will correct the normal loading problem and mitigate the backstand loading problem at ELMAR Substation and create backstand capabilities for MASON feeder 3412. | 2014: 210.34% 2015: -38.89% 2016: 32.12% 2017: 41.74% 2018: 106.80% | 2019: 30.99% 2020: 12.31% 2021: 2.28% | 21.2 MW | 2019: 3.6 MW 2020: 12.0 MW 2021: 13.0 MW | Commercial Industrial | Customer Q Customer R Customer S
12 | 0PT37461 -- MOOREHEAD SUB (CAMPBELL SUB) : ESTABLISH STATION WITH TWO 138-24.9 KV, 47 MVA TRANSFORMERS AND FIVE 24.9 KV FEEDER BREAKERS. | Customer T has requested a 40 MW dual-feed service near Garland Telecom Substation. With this load the 2019 projected winter load on Garland Telecom 3805 is 44.4 MW which is 329% of its 13.5 MW maximum continuous rating. The 2019 projected winter load on Garland Telecom Pkwy #1 is 57.2 MW which is 122% of its 46.7 MVA nameplate rating. Requested in-service date for the added load is June 15, 2019. In addition, the 2019 projected summer load on Murphy Rd Substation Transformer #3 is 48.1 MVA which is 103% of the 46.7 MVA nameplate rating. In order to serve this load and correct the loading problem at Murphy Substation, it is proposed to establish Campbell (renamed Moorehead) Substation with two 138-24.9 kV, 46.7 MVA transformers and five 24.9 kV feeder breakers with 1000Cu feeder exits, install 500 ft. of 8E6 duct bank, install two 900 Amp air-break switches and transfer 10 MW from Murphy 2756 to Campbell (renamed Moorehead) Substation. The completion of this project will serve Customer T and correct the loading problem at Murphy Rd Substation. | 2014: 0.00% 2015: 0.00% 2016: 0.00% 2017: 0.00% 2018: 100.00% | 2019: 100.00% 2020: -15.21% 2021: -5.67% | 20 MW | 2019: 5.1 MW 2020: 9.0 MW 2021: 8.0 MW | Commercial Residential | Customer T
13 | 0PT04138 -- OWL HILLS SUB: ESTABLISH SUBSTATION WITH 2-46.7 MVA 138-21.6KV TRANSFORMERS AND FOUR FEEDER BREAKERS | Customer U has requested 54 MW of distribution service from Screwbean substation with an in-service date of October 2019. This request along with area growth will load Screwbean Substation, a 1-28 MVA transformer station to 81.5 MVA, which is 295% over the 28 MVA transformer name plate rating. In order to correct this problem it is proposed to establish Owl Hills Substation by installing Transformers #1 and #2, (2) 46.7 MVA 138-21.6 kV, and (4) 21.6 kV feeder breakers with overhead 795 AAC and underground 1000 AL feeder exits. Install approximately 12,000’ of double circuit, 3-795 AAC, install one 900 AMP ABS and perform feeder switching. The completion of this project will correct the normal loading problem at Screwbean Substation Transformer #1 and provide service to Customer U. | 2015: 24.53% 2016: 45.45% 2017: 52.08% 2018: 63.70% 2019: 23.85% | 2020: 129.73% 2021: -8.33% | 54 MW | 2020: 28.0 MW 2021: 33.6 MW | Commercial Industrial | Customer U
14 | 0PT04140 -- LONESOME DRAW SUB: ESTABLISH SUBSTATION WITH (2) 47 MVA TRANSFORMERS AND (5) 25 KV FEEDER BREAKERS | Upton substation has received a 60 MW distribution service request from Customer U for service in April 2019. The 2019 projected summer load at Upton substation with this request is 88 MVA which is 314 % over Upton’s nameplate rating of 28 MVA. In order to correct this problem it is proposed to establish HWY 2594 Substation (now known as Lonesome Draw Sub) with (2) 46.7 MVA 138-25 kV Substation Transformers, (5) 25 kV feeder breakers, and (5) 1000Cu feeder exits. Customer U will receive (4) 25 kV feeders for their facility. In addition 3.6 miles of 12.5 kV to 25 kV voltage conversion, install 1,000 ft. of new 3-795AAC, reconductor 1000 ft. of #2ACSR with 3-795AAC, install (2) 7500 kVA autotransformers, and switching devices as shown. The completion of all this work will satisfy the customer’s request for service and greatly improve reliability and motor starting requirements in the area. | 2014: 0.00% 2015: -52.58% 2016: 189.13% 2017: 7.52% 2018: 22.38% | 2019: -2.86% 2020: 357.65% 2021: -38.46% | 54.2 MW | 2019: 59.8 MW 2020: 60.5 MW 2021: 62.4 MW | Commercial Industrial Residential | Customer U
15 | 0PT04142 -- SHIPWRECK SUB : ESTABLISH SUBSTATION WITH (2) 47 MVA TRANSFORMERS AND (5) 25 KV FEEDER BREAKERS | Glasscock substation has received a 60 MW distribution service request from Customer U for service in September 2019. The 2019 projected summer load at Glasscock substation with this request is 80 MVA which is 286 % over Glasscock’s nameplate rating of 28 MVA. In order to correct this problem it is proposed to establish Shipwreck Substation with (2) 46.7 MVA 138-25 kV Substation Transformers, (5) 25 kV feeder breakers, and (5) 1000Cu feeder exits. Customer U will receive (4) 25 kV feeder for their facility. In addition installing 2,700 ft. of 3-795AAC, enabling load to be moved from Hadacol Corner substation and Canal road to this substation. The completion of all of this work will satisfy the customer’s request for service and greatly improve reliability and motor starting requirements in the area. | 2014: 0.00% 2015: -17.11% 2016: -14.29% 2017: 31.48% 2018: 57.75% | 2019: -5.36% 2020: 510.38% 2021: 15.97% | 61.2 MW | 2019: 4.5 MW 2020: 53.8 MW 2021: 66.2 MW | Commercial Industrial Residential | Customer U
16 | 0PT37562 -- ALLIGATOR DRAW SUB : ESTABLISH STATION WITH TWO 47 MVA, 138-21.6 KV TRANSFORMERS AND (2) 21.6 KV FEEDER BREAKERS. | Customer U has requested 54 MW of distribution service from Black River Substation with an in-service date of September 15 of 2019. This request along with area growth will load Black River Substation, a 1-28 MVA transformer station to 74 MVA, which is 264% over the 28 MVA transformer name plate rating. In order to correct this problem it is proposed to establish Alligator Draw Substation by installing Transformer #1 and #2, (2) 46.7 MVA 138-21.6 kV, and (2) 21.6 kV feeder breakers with overhead 795 AAC feeder exits and (1) 21.6 kV feeder breaker with 1000 AL underground feeder exit. Establish two primary points of delivery rated for 27 MVA each for Customer U. Install ~4000’ of 3-795 AAC, (1) 900 AMP ABS and perform feeder switching. The completion of this project will correct the normal loading problem at BLKRV Substation Transformer #1. | 2015: 24.36% 2016: 30.93% 2017: 22.05% 2018: 22.58% 2019: -24.21% | 2020: 152.78% 2021: 16.41% | 54 MW | 2020: 22.2 MW 2021: 26.9 MW | Commercial Industrial | Customer U
17 | TPSU.14.005772 --GLASS RANCH SUBSTATION | Refer to Section 3.20 of Exhibit JBN-3 | 2014: 78.8% | 2015: 4.7% 2016: -0.7% 2017: 44.8% 2018: 44.3% 2019: 39.7% 2020: -7.9% | 48.7 MW | 2016: 23.7 MW 2017: 46.3 MW 2018: 65.2 MW 2019: 69.5 MW 2020: 71.5 MW | Industrial | NTU Customer A
18 | TPSU.14.005706 --ROCKY ROAD 138KV SUBSTATION | Refer to Section 3.21 of Exhibit JBN-3 | 2014: 71.3% | 2015: 36.2% 2016: -15.3% 2017: -11.2% 2018: 24.3% 2019: 20.1% 2020: -8% | 9.9 MW | 2015: 3.9 MW 2016: 4.9 MW 2017: 4 MW 2018: 5.1 MW 2019: 8.2 MW 2020: 7 MW | Industrial | NTU Customer B
19 | TPSU.15.006030 --PRONGHORN SUBSTATION | Refer to Section 3.30 of Exhibit JBN-3 | 2014: -10.7% 2015: 11.6% | 2016: 0.3% 2017: 69.4% 2018: -1.6% 2019: 103.4% 2020: 2.9% | 11.6 MW | 2017: 7.1 MW 2018: 13.7 MW 2019: 22.8 MW 2020: 26.4 MW | Industrial Residential | NTU Customer C
20 | TPSU.13.005631 --CONSTRUCT TALL CITY SUBSTATION NORTH MIDLAND | Refer to Section 3.17 of Exhibit JBN-3 | 2014: 12.7% | 2015: 34.5% 2016: -20.7% 2017: 14.7% 2018: 22.3% 2019: 56.7% 2020: -1.4% | 3.5 MW | 2015: 16.6 MW 2016: 9.95 MW 2017: 15.5 MW 2018: 15.7 MW 2019: 32.4 MW 2020: 34.7 MW | Industrial Residential | NTU Customer D
21 | TPSU.14.005813 --NATURAL DAM 138/25KV SUBSTATION | Refer to Section 3.27 of Exhibit JBN-3 | 2014: 27.1% 2015: 48.5% | 2016: 12.8% 2017: 38.9% 2018: 103.5% 2019: 22.8% 2020: 29.3% | 22.4 MW | 2016: 3.1 MW 2017: 8.1 MW 2018: 19.4 MW 2019: 25.5 MW 2020: 28.9 MW | Industrial | NTU Customer E
22 | TPSU 14.005802 --CARTERVILLE 138KV SUBSTATION | Refer to Section 3.24 of Exhibit JBN-3 | 2014: 141.2% | 2015: 28.7% 2016: 19.9% 2017: 33.2% 2018: 107.7% 2019: -0.1% 2020: 5.7% | 3.9 MW | 2016: 2.1 MW 2017: 2.3 MW 2018: 6.9 MW 2019: 5.3 MW 2020: 3.5 MW | Industrial | NTU Customer F
23 | TPSU.15.006054 --RINGO SUBSTATION | Refer to Section 3.31 of Exhibit JBN-3 | 2014: 18.3% 2015: 27.4% | 2016: -10.7% 2017: 18.8% 2018: 24.4% 2019: 38.4% 2020: 17.8% | 9.5 MW | 2017: 4.4 MW 2018: 7.1 MW 2019: 9.2 MW 2020: 15.8 MW | Industrial | NTU Customer G
24 | TPSU.15.005908 --BLUE ACRES 138/12.5KV SUBSTATION | Refer to Section 3.29 of Exhibit JBN-3 | 2014: 5.9% 2015: 3.6% | 2016: -9.1% 2017: 8.1% 2018: 30.8% 2019: 56.8% 2020: 3.5% | 20.2 MW | 2016: 0.8 MW 2017: 2.5 MW 2018: 10.1 MW 2019: 15.4 MW 2020: 21.5 MW | Industrial | NTU Customer H
25 | 0PT39915 -- NTUSU SAINT LAWRENCE SUB : REMOVE EQUIPMENT FOR ESTABLISHING BLISSARD SUB | The 2020 projected summer loading on the Saint Lawrence substation is 24.6 MW which is 110% over the name plate rating of 22.4 MVA of the transformer. In order to correct this problem, the original proposal was to install Saint Lawrence #2 with a 138-25 kV 47 MVA transformer and (2) 25 kV feeder breakers. In addition, it is proposed to move feeders 2102 and 2104 from transformer #1 to transformer #2. Customer U has a large facility in this area it is proposed to move this facility from ESTIL 2103 to STLWC 2102 (on XFMR #2) to provide growth opportunities while keeping ESTIL 2103 as backstand. The completion of this work will allow for increased growth for the oil fields, provide backstand to a single transformer station, and solve the overloading issues. The actual project constructed differed from the recommendation after detailed engineering analysis performed by Oncor’s Transmission Engineering group determined that construction of the project as recommended would be less economical. It was decided to instead, build Blissard Substation on the adjacent property to avoid a total rebuild of the existing station. | 2015: -43.44% 2016: -7.25% 2017: 7.03% 2018: -1.46% 2019: 2.96% | 2020: 6.47% 2021: -7.13% | 11.9 MW | 2020: 3.7 MW 2021: 5.4 MW | Commercial Industrial Residential | Not Applicable
26 | 0PT40871 -- BLISSARD SUB : ESTABLISH A NEW 138-25KV SUBSTATION NEXT TO THE EXISTING SAINT LAWRENCE SUB | The 2020 projected summer loading on the Saint Lawrence substation is 24.6 MW which is 110% over the name plate rating of 22.4 MVA of the transformer. In order to correct this problem, the original proposal was to install Saint Lawrence #2 with a 138-25 kV 47 MVA transformer and (2) 25 kV feeder breakers. In addition, it is proposed to move feeders 2102 and 2104 from transformer #1 to transformer #2. Customer U has a large facility in this area it is proposed to move this facility from ESTIL 2103 to STLWC 2102 (on XFMR #2) to provide growth opportunities while keeping ESTIL 2103 as backstand. The completion of this work will allow for increased growth for the oil fields, provide backstand to a single transformer station, and solve the overloading issues. The actual project constructed differed from the recommendation after detailed engineering analysis performed by Oncor’s Transmission Engineering group determined that construction of the project as recommended would be less economical. It was decided to instead, build Blissard Substation on the adjacent property to avoid a total rebuild of the existing station. | 2015: -43.44% 2016: -7.25% 2017: 7.03% 2018: -1.46% 2019: 2.96% | 2020: 6.47% 2021: -7.13% | 11.9 MW | 2020: 3.7 MW 2021: 5.4 MW | Commercial Industrial Residential | Not Applicable
27 | 0PT42368 -- SHIFTING SANDS (FORMERLY KEYSTONE) SUB : ESTABLISH STATION BY INSTALLING A 138/69-21.6 KV 46.7 MVA TRANSFORMER WITH TWO FEEDER BREAKERS | With the added load of 6.4 MW of Customer CR, the projected load on Keystone Feeder 1021 is 15.4 MW which is 197% of the 7.8 maximum continuous rating of this feeder. In addition, the projected load on Keystone Substation Transformer #1 is 22.4 MW which is 112% of the 20 MVA nameplate rating of this transformer. Keystone Substation is a single transformer substation. In order to correct this problem, it is recommended to establish a substation at 22 kV with a138/69-22 kV 47 MVA transformer and two feeder breakers at Keystone Substation. It is also recommended to construct various distribution facilities in order to transfer loads to the new feeder breakers. The completion of this work will correct the overloads that have been identified due to the added load of Customer CR. | 2016: -23.46% 2017: 9.68% 2018: 44.12% 2019: 46.94% 2020: 22.22% | 2021: -45.86% | 18.4 MW | 2021: 2.2 MW | Commercial Industrial Residential | Customer CR
28 | 0PT43523 -- MOORES MILL SUB : ESTABLISH SUBSTATION WITH A 138-12.5KV 46.7MVA TRANSFORMER AND 4 FEEDER BREAKERS | Customer CQ has signed an FEA for 19.7 MW with 4 MW to be online by 2021 and the rest in 2022. With the added load of 4.0 MW, the projected 2021 winter load on Temple North substation feeder 1603 is 16.5 MVA, which is 126% of the 13.1 MVA maximum continuous rating of this feeder. In addition, the projected 2021 winter load on Temple North Substation is 59.0 MVA which is 101% of the 58.4 MVA backstand rating for this substation. In order to correct this problem, it is recommended to establish Moores Mill Substation with a 138-12.5 kV 46.7 MVA transformer and 4 feeder breakers with 1000 Cu exits. Two feeder breakers will be used in 2021 and the other feeder breakers will be used in 2022. It is also recommended to construct various distribution facilities in order to transfer load to the substation. The completion of this work will correct the overloads that have been identified due to the added load of Customer CQ in Temple. | 2016: 10.83% 2017: 4.37% 2018: 3.2% 2019: 0.95% 2020: 1.18% | 2021: 0.47% | 18.5 MW | 2021: 0.2 MW | Commercial Industrial Residential | Customer CQ
29 | 0PT01074 -- PARKS BELL RANCH SUB: ESTABLISH SUBSTATION WITH (1) 47 MVA TRANSFORMER AND (3) 12.5KV FEEDER BREAKERS | The 2019 summer projected load on GLNHV3953 is 15.8, which is 120% of the 13.1 MVA maximum continuous rating. The 2019 summer projected load on Glenhaven Transformer #3 is 48.9 MVA which is 105% of the 46.7 MVA transformer’s nameplate rating, the 2019 summer projected load on Glenhaven Substation is 104.1 MVA which is 133% of this substation’s 78.4 MVA rating and the 2019 summer projected load on Grandview Odessa Substation is 78.6 MVA which is 135% of this substation’s 58.4 MVA rating. It is proposed Parks Bell Boulevard Substation with a 46.7 MVA, 138-12.5 kV transformer and three 12.5 kV feeder breakers with 1000 Cu exits. In addition, it is proposed to install 23,700 ft. of 3-795 AAC primary, reconductor 18,850 ft. of small conductor primary with 3-795 AAC, and transfer load among feeders using existing and proposed switches. The completion of this work will correct the overloads at Glenhaven and Grandview Odessa Substations. | 2014: 2.85% 2015: 3.22% 2016: 4.14% 2017: -2.30% 2018: 16.76% | 2019: 0.00% 2020: -7.15% 2021: -6.03% | 27.2 MW | 2019: 7.0 MW 2020: 17.4 MW 2021: 17.2 MW | Commercial Residential | Not Applicable
30 | 0PT01087 -- SALADO SOUTH SUBSTATION: ESTABLISH SALADO SOUTH SUBSTATION WITH A 28.0 MVA 138-12.5 KV TRANSFORMER AND TWO FEEDER BREAKERS | The 2019/2020 projected winter load on Salado Switch Substation is 35.4 MW which is 122% of this substation's 29.1 MVA backstand rating. The 2019/2020 projected winter load on Salado Switch feeder 3001 is 14.7 MW which is 109% of this feeder's 13.5 MVA maximum continuous rating. In order to correct these problems it is proposed to install Salado South Substation with 1-28 MVA 138-12.5 kV transformer and (2) 12.5 kV feeder breakers. Completion of this work will correct substation and feeder loadings at Salado Switch Substation | 2015: -13.57% 2016: 5.24% 2017: 5.97% 2018: 20.66% 2019: -16.73% | 2020: 46.26% 2021: -27.95% | 9.7 MW | 2020: 4.0 MW 2021: 5.5 MW | Commercial Industrial Residential | Not Applicable
31 | 0PT01906 -- SCATTER BRANCH SUBSTATION: ESTABLISH NEW SUBSTATION WITH ONE 28 MVA TRANSFORMER AND TWO 25 KV FEEDER BREAKERS | The 2017/2018 projected winter load on Neylandville substation is 5.8 MVA which is 116% of the 5.0 MVA transformer nameplate rating. In order to correct this problem, it is proposed to establish Scatter Branch substation with 1-28 MVA, 138/69-24.9 kV, substation transformer and two 25 kV feeder breakers with one 1000 kcmil Cu feeder exit. In addition, it is proposed to reconductor 9200 ft. of 1-#4 ACSR and 2-#4 ACSR to 3-#4/0 ACSR, install one 7500 kVA auto stepdown transformer, install one Kyle Nova recloser with Form 6 controls, close one NO 300 A overhead disconnect to transfer 4.96 MW from Neylandville 1201 to the new Scatter Branch feeder, transfer 345 kW from Neylandville 1202 to the new Scatter Branch feeder, convert the former Neylandville 1202 feeder to 24.9 kV, and open both Neylandville feeder disconnects to remove all load from Neylandville substation. The completion of this project will correct the overload problems at Neylandville substation. | 2015: -6.12% 2016: -19.57% 2017: 35.14% 2018: 10.00% 2019: -10.91% | 2020: 32.65% 2021: -26.77% | 5.8 MW | 2020: 2.7 MW 2021: 0.47 MW | Commercial Industrial Residential | Not Applicable
32 | 0PT04151 -- FLOWER GROVE SUB: ESTABLISH SUBSTATION WITH A 138-24.9 KV 46.7 MVA TRANSFORMER AND TWO FEEDER BREAKERS | The 2019 summer projected load on Brown feeder 1101 is 18.6 MVA. This is 143% of the feeder’s 13 MVA rating. The summer projected 2019 load on feeder 1102 is 15.2MVA which is 117% of the feeder’s 13 MVA rating. Also Brown, a single-transformer substation, has a 47.5 MVA rating based upon 95% of the 50 MVA nameplate rating for the transformer. With 2019 summer loading at 47.1 MVA, Brown substation will be at 99% of its 47.5 MVA rating and 94% of the 50 MVA nameplate rating. Additionally, the 2019 summer projected load on Knott 5221 is 27.3 MVA which is 101% of this feeders 27.2 MVA rating. In order to correct these overloads, it is proposed to establish Flower Grove Substation with 1-46.7 MVA transformer and 2-25 kV feeder breakers. It is proposed in install/reconductor approximately 13,000 ft. of 3-795 AAC, Install 5,200 ft. of 3-#4/0 AAC, install 3 switches, install a 5 MVA 25/12kV auto, install one Kyle Nova Recloser, install 2 sets of 25 kV regulators, and perform switching to transfer 15.8 MVA off Brown Substation with 9.1 MVA off feeder 1101 and 6.3 MVA off 1102 and 3.5 MVA off Knott Feeder 5211. The completion of this work will correct the feeder overloads on Brown and Knott Substations. | 2014: -4.86% 2015: 13.14% 2016: -30.97% 2017: 1.87% 2018: 100.92% | 2019: 85.84% 2020: 37.35% 2021: -2.57% | 18.9 MW | 2019: 1.8 MW 2020: 8.7 MW 2021: 12.3 MW | Commercial Industrial Residential | Not Applicable
33 | 0PT04155 -- BLAGG SUB: ESTABLISH SUBSTATION WITH A 47 MVA 138-24.9 KV TRANSF. AND TWO FEEDER BREAKERS | The 2019/2020 projected winter load on Krugerville Sub transformer Bank #1 is 33.3 MVA which is 119% of the 28 MVA transformer rating. There is no adjacent transformer to transfer load to relieve this problem. In the event of a fault on the new Blagg St south feeder, there would be no back stand for 6.8 MW of the projected 2019/2020 winter load of 10.9 MW on Blagg St Sub, resulting in an extended outage. In order to correct this problem, it is proposed to establish Blagg Substation with 1-46.7 MVA 138-24.9 kV transformer, and two 24.9 kV feeder breakers. The completion of this project will correct the overload problems at Krugerville Sub | 2015: -2.55% 2016: -21.83% 2017: 40.78% 2018: 23.81% 2019: -18.59% | 2020: 10.24% 2021: -31.48% | 9.8 MW | 2020: 5.1 MW 2021: 5.3 MW | Commercial Industrial Residential | Not Applicable
34 | 0PT04157 -- BIRD NEST SUB FORMERLY (PFLUGERVILLE SOUTH SUBSTATION) | The 2019 projected summer load on Pflugerville 2001 is 31.8 MVA which is 118% of the 26.9 MVA maximum continuous rating for this feeder. The 2019 projected summer load on Pflugerville 2007 is 25.6 MVA which is 105% of the 24.4 MVA maximum continuous rating for this feeder. The 2019 projected summer load on Pflugerville 2004 is 25 MVA which is 102% of the 24.4 MVA maximum continuous rating for this feeder. The 2019 projected summer load on Pflugerville Substation Transformer #3 is 47.6 MVA which is 102% of the 46.7 MVA nameplate rating of this transformer. The 2019 projected summer load on Pflugerville Substation is 128 MVA which is 110% of the 116.8 rating for this substation. In order to correct these problems, it is proposed to establish Bird Nest Substation and install a 138-25KV, 46.7 MVA transformer with two 24.9 KV feeder breakers. The completion of this project will correct the loading problems at Pflugerville Substation. | 2014: 2.32% 2015: 8.02% 2016: 4.83% 2017: -2.34% 2018: 11.97% | 2019: -5.86% 2020: 32.45% 2021: -6.37% | 31 MW | 2019: 9.8 MW 2020: 39.6 MW 2021: 44.0 MW | Commercial Industrial Residential | Not Applicable
35 | 0PT04281 -- RENTAL CAR SUB: ESTABLISH SUBSTATION WITH 2-46.7 MVA, 138-24.9 KV TRANSFORMERS AND 4 FEEDERS | The 2019 projected summer load on DFWSW Substation is 52.3 MVA, which is 111% of the 47 MVA substation rating. DFWSW Substation Bank #1 is reserved for CTA load only while Bank #2 is to serve quadrant load. In addition, the 2019 projected summer load on DFWSW Feeder 2326 is 27.7 MVA, which is 114% of the maximum continuous rating for this feeder. In order to correct this problem, it is proposed to establish Rental Car Substation by installing 2- 47 MVA, 138-24.9 kV transformers, 4- 25 kV circuit breakers, 5390 ft. of 6-1000 MCM Cu cable in 8E6 duct bank. The completion of this project will solve the loading problems on DFWSW Substation and Feeder 2326. | 2014: 1.82% 2015: 21.19% 2016: -17.73% 2017: -18.56% 2018: 0.37% | 2019: -7.33% 2020: 20.95% 2021: 52.35% | 40.6 MW | 2019: 4.3 MW 2020: 4.1 MW 2021: 10.7 MW | Commercial | Not Applicable
36 | 0PT39269 -- CHINA LAKE SUB : ESTABLISH SUBSTATION WITH 1-47 MVA TRANSFORMER AND 1-22 KV FEEDER BREAKERS | The 2020 projected summer load on Coyanosa Northwest Bank #1 is 34.0 MVA, which is 121% of its 28 MVA rating. In addition, the 2020 projected summer load on Coyanosa Northwest Substation is 55.6 MVA, which is 159% of the 35 MVA substation backstand rating. In order to correct this issue, it is proposed to establish China Lake Substation with 1-47 MVA, 138-21.6 kV transformer and 2-21.6 kV feeder breaker with 3-1000 Cu feeder exit. In addition, it is proposed to install 8,700 ft. of 3-795 kcmil AAC, reconductor 2,650 ft. of 1-#2 ACSR to 3-795 kcmil AAC, reconductor 6,200 ft. of 3-#2 ACSR to 3-795 kcmil AAC, relocate the existing 1000 kVA autotransformer north, convert a small portion of the feeder to 21.6 kV and install one 900 Amp ABS, P-NO. The completion of this project will correct the transformer overload and mitigate the substation backstand overload. | 2015: 0.00% 2016: 0.00% 2017: 0.00% 2018: 46.91% 2019: 191.60% | 2020: -36.02% 2021: 21.66% | 16.5 MW | 2020: 0.8 MW 2021: 1.8 MW | Industrial | Not Applicable
37 | 0PT39275 -- DOOLEY SUB : REBUILD EXISTING NORTHWARD SUB BY ESTABLISH STATION WITH 46.7 MVA, 69/22 KV TRANSFORMER | The projected summer 2020 load on Northward substation is 11 MW, which is 105% of the maximum continuous rating of the 10.5 MVA transformer. Also, the projected load on a 7500 kVA autotransformer is 10.3 MW, which is 137% of the maximum continuous rating. In order to correct this issue, the original proposal was to replace the 10.5 MVA, 69/12.5 kV, transformer at Northward substation with a 46.7 MVA, 69/22 kV, transformer and convert approximately 5 Points of Delivery and 571 kVA of transformation to 22 kV. It is also proposed to relocate the 7500 kVA auto. The completion of this project will resolve the overloads at Northward Substation. The actual project constructed differed from the recommendation after detailed engineering analysis performed by Oncor’s Transmission Engineering group determined no additional room was available to accommodate the transformer change-out, and therefore, additional property was acquired and the new substation (Dooley Substation) was constructed on acquired property. | 2015: 0.00% 2016: -6.25% 2017: 13.33% 2018: 0.00% 2019: 23.53% | 2020: 228.57% 2021: -6.84% | 11 MW | 2020: 6.9 MW 2021: 6.4 MW | Industrial | Not Applicable
38 | 0PT39276 -- FATE SUB : ESTABLISH SUBSTATION WITH 46.7 MVA 138-24.9KV TRANSFORMER AND TWO FEEDER BREAKERS | The 2020 projected summer load on Rockwall feeder 1203 is 29.8 MVA which is 110% of the 27.2 MVA feeder rating. In addition, the projected summer load on Rockwall Transformer #1 is 49.0 MVA, which is 105% of the 46.7 MVA rating. In addition, the projected summer load on Rockwall substation is 86.6 MVA which is 148% of the 58.4 MVA substation backstand rating. In addition, the projected summer load on Rockwall East substation is 68.7 MVA which is 117% of the 58.75 MVA substation backstand rating. In order to correct this problem, it is proposed to establish Fate substation with 1-46.7 MVA, 138-24.9 kV, transformer and two 25 kV feeder breakers with 1000 kcmil Cu feeder exits. In addition, it is proposed to install 7100 ft. of overhead 3-795 kcmil AAC, install 650 ft. of 1000 kcmil Al, reconductor 15300 ft. of various small wire to 3-795 kcmil AAC overhead conductor, relocate 1 recloser, remove 1 recloser, relocate 1 autotransformer, remove 2-7500 kVA autotransformers, install 2-3750 kVA autotransformers, install 3-900A air break switches, convert 170 customers from 12.5 to 24.9 kV, transfer 13.8 MW from Rockwall 1203 and Rockwall 1201 to the new Fate west feeder, transfer 3.2 MW from Rockwall 1203 to Rockwall 1201, transfer 1.4 MW from Rockwall East 3321 to the new Fate West feeder, and transfer 11.0 MW from Rockwall East 3326 to the new Fate east feeder. The completion of this project will correct the overload problems at Rockwall substation and Rockwall East substation. In addition, establishing Fate substation increases the available capacity and feeder routes in a fast-growing and dual-certified area which includes the Wood Creek development, future Montarra development, and Rockwall Technology Park economic development zone. | 2015: 7.74% 2016: 9.58% 2017: -10.64% 2018: 11.04% 2019: -2.56% | 2020: 4.15% 2021: -0.70% | 23.4 MW | 2020: 15.6 MW 2021: 17.6 MW | Commercial Industrial Residential | Not Applicable
39 | 0PT39278 -- JACK RABBIT SUB : ESTABLISH SUBSTATION WITH A 47 MVA, 138-12.5 KV TRANSFORMER, AND THREE 12.5 KV FEEDER BREAKERS | The 2020 summer projected load on feeder Odessa 0212 is 14.9MVA which is 103% of the 14.5 MVA rating of the feeder. Additionally, Odessa substation transformer #1 is projected to be loaded at 47.6 MVA which is 102% of the 46.7MVA nameplate rating of this transformer. Feeder Glenhaven 3942 will be loaded to 13.7MVA which is 110% of the 12.4MVA rating of the feeder. Also the 2020 summer projected load on Odessa Substation is 89.2 MVA which is 153% of the 58.4 MVA substation rating. It is proposed to establish Jack Rabbit Substation with 46.7MVA, 138-12.5kV transformer and three 12.5kV feeder breakers with 1000 Cu exits. Also, it is proposed to install approximately 14000ft of 3-795AAC conductor and install 5-900 air switches to transfer load. Approximately 4800ft of existing conductor will needed to be replaced with 3-795AAC. The completion of this work will correct the overloads at Odessa and Glenhaven Substations. | 2015: 1.89% 2016: -0.46% 2017: 2.66% 2018: 14.15% 2019: -1.02% | 2020: -15.11% 2021: -1.58% | 24.5 MW | 2020: 5.8 MW 2021: 13.8 MW | Commercial Industrial Residential | Not Applicable
40 | 0PT39486 -- LAKECREST SUB (FISH CREEK) : ESTABLISH SUBSTATION WITH 46.7 MVA TRANSFORMER AND THREE FEEDER BREAKER | The 2019 projected Summer load on Grand Prairie Substation is 83.2 MVA which is 143% of the 58.4 MVA Summer rating for this substation. In addition, the projected feeder loading on Grand Prairie 0811 and 0842 is 10.1 and 18.4 MVA respectively which is 101 and 163% of the 10.0 and 11.3 MVA rating. In order to correct this problem, it is proposed to establish Lakecrest Substation with one 138-12.5 kV 46.7 MVA substation transformer and three 12.5 kV feeder breakers. The completion of this project will correct the loading problems on Grand Prairie Substation. | 2015: -0.60% 2016: 7.90% 2017: 1.41% 2018: 1.11% 2019: -4.81% | 2020: 15.58% 2021: -12.78% | 14.5 MW | 2020: 5.3 MW 2021: 13.6 MW | Commercial Industrial Residential | Not Applicable
41 | 0PT40126 -- BRELYN SUB (COAHOMA WEST SUB) : ESTABLISH SUBSTATION WITH A 138-21.6KV 46.7MVA TRANSFORMER WITH 2-21.6KV FEEDER BREAKERS | The 2020 projected summer load on Coahoma #2 (21.6 kV) is 10.4 which is111% of the transformer 9.375 MVA nameplate rating. This is treated as a single transformer substation because Coahoma #1 has different distribution voltage (12.5 kV) and there is no low voltage bus tie between the two transformers. In addition, the 2020 projected summer load on Bulldog Substation is 23.0 MVA which 103% of the 22.4 MVA nameplate rating. Bulldog Substation is a single transformer substation. In order to correct these loading problems, it is proposed to establish the Brelyn Substation with a 1-46.7 MVA 138-21.6 kV transformer and 2-21.6 kV feeder breakers with 795 AAC overhead feeder exits. Install approx. 6700 ft. of 3-795 AAC for two feeders and connecting to existing feeders. Install two 21.6 kV – 12.47 kV 7.5 MVA Auto Transformers to pick up load from COHMA1111. Additionally install four air break switches, one NOVA Recloser, and one Trip Saver, relocate an existing recloser, remove an existing recloser, and reconductor 500 ft. of 3-#4 ACSR with 4/0 ACSR primary. The completion of this project will correct the loading problems at Coahoma and Bulldog Substations. | 2015: 8.16% 2016: 26.42% 2017: 31.34% 2018: 121.59% 2019: 24.10% | 2020: 9.50% 2021: -17.88% | 10.2 MW | 2020: 6.0 MW 2021: 10.2 MW | Commercial Industrial Residential | Not Applicable
42 | 0PT40344 -- BEALS CREEK (FORMERLY ANDREWS HIGHWAY) SUB : ESTABLISH WITH TWO 138-24.9 KV 46.7 MVA TRANSFORMERS AND 3-24.9 KV BREAKERS | The 2020 summer projected load on Natural Dam Substation Transformer #1 is 83.4 MVA. This is 149% of the transformer nameplate’s 56 MVA rating. The 2020 projected summer load on Coyote Substation Transformer #1 is 71.0 MVA which is 127% of the transformer nameplate’s 56 MVA rating. Additionally. The 2020 projected summer loads for the Natural Dam feeders are: 2103 - 20 MVA, 2104 - 35 MVA, 2106 - 28.4 MVA. The overloaded feeders are 2104 and 2106 will have 35 MVA on a 25 MVA maximum continuous rating which is an overload of 140% and 28.4 MVA on a 25 MVA maximum continuous rating which is an overload of 114%. There is a 2020 projected summer load of 30.0 MVA on CYOTE 2104 which is 160% of the 18 MVA feeder maximum continuous rating. In order to correct these overloads, it is proposed to establish the Andrews Highway Substation with 2-46.7 MVA transformer and 3-25 kV feeder breakers. Install approximately 39,000 ft. of 3-795 AAC, 6-N.O. ABS, and 1-400 amp 25 kV Regulator. Reconductor 1/0ACSR and #4 ACSR to 795AAC for 21,000 ft. Convert 1-Ph to 3-Ph for 2400 ft. Perform switching to transfer 37 MVA off Natural Dam Substation with 19.5 MVA off feeder 2104 and 17 MVA off feeder 2106. Also perform switching to transfer 24 MVA off Coyote Substation with 15 MVA from feeder 2103 and 9 MVA from feeder 2104. Loading after switching will be Coyote: 47 MVA, Andrews HWY #1: 30 MVA, Andrews HWY #2: 26 MVA, and Natural Dam: 48.4 MVA. The completion of this project will correct transformer overloads on Natural Dam and Coyote Substations as well as feeder overloads on both substations. | 2015: 38.64% 2016: 27.05% 2017: 40.00% 2018: 129.49% 2019: 6.63% | 2020: 17.70% 2021: 13.33% | 56 MW | 2020: 0.6 MW 2021: 5.5 MW | Commercial Industrial Residential | Not Applicable
43 | 0PT41685 -- COTTONFIELD SUB : ESTABLISH SUBSTATION WITH 138-25 KV 47 MVA TRANSFORMER AND 2-25 KV FEEDER BREAKERS | The 2020 projected winter load on South Midland substation is 59 MW which is 105% of the substation's 56 MVA rating. In order to correct this issue, it is proposed to establish Cotton Fields Substation with a 138-25 kV 47 MVA transformer and 2-25 kV feeder breakers. Utilize two feeder exits to tie into existing SMLND feeder 2104. Four 900A ABS will be used to transfer 28 MW from SMLND to Cotton Fields Substation. The completion of this work will correct the substation loading issue at South Midland Substation | 2015: 153.85% 2016: 27.27% 2017: -3.57% 2018: 6.17% 2019: 55.04% | 2020: 30.50% 2021: -26.33% | 28 MW | 2020: 7.6 MW 2021: 15.0 MW | Commercial Industrial | Not Applicable
44 | 16T62004 -- WHITE SETTLEMENT WEST SUBSTATION: ESTABLISH STATION | The 2017/18 projected winter load on Western Hills Substation Transformer #1 is 49.8 MVA which is 106% of the 47.0 MVA nameplate rating for this transformer. In addition, the 2017/18 projected winter load on Banks #1 and #2 is 92.2 MVA and the 2017/18 projected winter load on Banks #2 and #3 is 66.4 MVA which is 157% and 113% of the 58.75 substation rating for these transformers, respectively. In order to correct these problems, it is proposed to establish the White Settlement West Substation with one 47 MVA 138-24.9 kV transformer and two feeder breakers with 1000 Cu feeder exits, install 5700 ft. of 3-795 kcmil AAC conductor, reconductor 16,800 ft. of small wire with 3-795 kcmil AAC, install one 140 amp WV recloser, relocate two SCADA sectionalizer switches, install one air switch and transfer load using new and existing facilities. The completion of this project will correct the loading problems on this substation. | 2012: -5.10% 2013: -0.80% 2014: 25.81% 2015: -6.68% 2016: -24.44% | 2017: 35.32% 2018: 7.39% 2019: -10.72% 2020: -8.11% 2021: 47.81% | 28 MW | 2017: 4 MW 2018: 30.9 MW 2019: 28.7 MW 2020: 27.5 MW 2021: 45.6 MW | Industrial Residential | Not Applicable
45 | 16T62052 -- PANTHER ISLAND SUB: RELOCATE THE NORTH MAIN SUBSTATION TO THE SOUTH OF HERITAGE SUB AND NORTH MAIN SWITCH | The 2019 projected summer peak on North Main Substation is 44.6 MW. The Trinity River Vision Project in the City of Fort Worth will bring a large amount of additional load to the North Main Substation area. The existing location of the North Main Substation is not conducive to expansion of the facilities for load growth. In addition, the facilities at North Main Substation are old. In anticipation of these concerns, it is recommended that the North Main Substation be relocated with new facilities to an area that allows for additional capacity to be added. It is proposed to relocate the North Main Substation with two 138-12.5 kV 46.7 MVA transformers and eight feeder breakers to a 5.52 acre tract just south of the existing location. In addition, it is proposed to install duct system with eight 1000 Cu exits as required. | 2015: -1.89% 2016: 1.93% 2017: -4.49% 2018: 6.68% 2019: -6.03% | 2020: 61.73% 2021: -35.64% | 44.6 MW | 2020: 26.0 MW 2021: 42.5 MW | Commercial Industrial Residential | Not Applicable
46 | 16T64089 -- CAMINO SUB: ESTABLISH NEW 138 KV - 13.2 KV DISTRIBUTION YARD | The projected 2017 winter load on Nacogdoches Substation is 44.7 MVA which is 143% of this stations 31.25 MVA substation rating. In addition, the transformers at Nacogdoches Substation are inaccessible during replacement. In order to correct his problem it is proposed to relocate Nacogdoches Substation (now knowns as Camino Substation) by installing 2-47 MVA 138-12.47 kV transformers. In addition, relocate existing six overhead feeder exits with underground 1000 Al feeder exits. Install an additional feeder breaker to split NCDCH 1204 load. The final configuration will have 3 feeders in bank #1 and 4 feeders in bank #2. The completion of this project will correct the substation rating problem and provide accessibility to the substation transformers for replacement. | 2012: -7.23% 2013: -3.64% 2014: -7.55% 2015: 15.16% 2016: 16.20% | 2017: 13.51% 2018: -30.90% 2019: -5.28% 2020: 0.00% 2021: -4.54% | 44.7 MW | 2017: 52.1 MW 2018: 36.0 MW 2019: 34.1 MW 2020: 34.1 MW 2021: 32.6 MW | Commercial Industrial Residential | Not Applicable
47 | 16T65007 -- ANNA SOUTHEAST SUBSTATION: ESTABLISH STATION | The 2018 projected summer load on Van Alstyne Substation is 24.2 MVA, which is 180% of the 13.5 MVA summer backstand rating. In addition, the 2018 projected summer load on McKinney (24.9 kV) Substation and McKinney #4 is 93.4 MVA and 53.9 MVA which is 160% and 115% of its 58.4 MVA summer backstand rating and 46.7 MVA nameplate rating. In order to correct these problems, it is proposed to build Anna SE substation in Melissa and install a 47.0 MVA 138-24.9 kV transformer with two 24.9 kV circuit breakers and approx. 2300 ft. of 8E6 duct bank with 3-1000 AL feeder exits, build two 3-795 Kcmil AAC circuits for an estimated 15,000 ft. each, reconductor 8800 ft. of 3-#1 Cu with 3-795 AAC, convert an area of Van Alstyne substation feeder 2412 from 12.5kV to 24.9kV, remove one capacitor bank, relocate one WVE 280 amp recloser, Install four 65 amp fuses, replace all fuses in an area of Van Alstyne substation feeder 2412 with 40 amp fuses, replace one set of 200 amp regulators, relocate a 3,750kVA autotransformer, balance feeder load and perform one switching operation to transfer 10 MW of load from Van Alstyne substation feeder 2412 to a new Anna SE substation feeder. Additionally , it is proposed to convert an area of McKinney substation feeder 1252 from 12.5 kV to 24.9 kV, replace a 2,500 kVA autotransformer with a 3,750 autotransformer from Van Alstyne substation feeder 2412, remove another 2500 kVA autotransformer, reconductor 13,800 ft. of small conductor with 3-795 kcmil AAC, install a 3-795 kcmil AAC double circuit for an estimated 500 ft., install one dead span, install a 600 amp Air Break Switch, remove a set of 200 amp regulators, remove two capacitor banks and install two capacitor banks to correct low voltage, relocate a 630 amp Nova recloser, remove a 560 amp recloser, and perform two switching operations to transfer 15.0 MW of load from McKinney substation feeder 1252 to a new Anna SE substation feeder. In order to convert these two feeders from 12.5 kV to 24.9 kV two 600 kVAR 12.5 kV capacitor banks will be replaced with two 900 kVAR 24.9 kV capacitor banks, a 750 kVA 12.5 pad mounted transformer will be replaced with a 24.9 kV pad mounted transformer, and 1,217 kVA of 12.5 kV overhead transformer capacity will be replaced with 24.9 kV transformers. The completion of this project will correct the backstand loading problems at Van Alstyne and McKinney Substations. | 2013: -7.31% 2014: 3.07% 2015: 7.65% 2016: 2.39% 2017: -12.13% | 2018: 14.96% 2019: -0.36% 2020: -0.73% 2021: 2.85% | 25 MW | 2018: 16.7 MW 2019: 24.1 MW 2020: 25.7 MW 2021: 25.4 MW | Commercial Industrial Residential | Not Applicable
48 | 16T65129 -- ESTABLISH NORTH NETWORK OVERHEAD SUBSTATION | The 2017 projected summer load for Bryan 0004 is 15.7 MW, which is 120% of its 13.1 MW feeder rating. In addition, the 2017/2018 projected winter loads for Bryan 0005 and East Network Overhead 0004 are 14.8 MW and 11.6 MW, which is 113% of Bryan 0005’s 13.1 MW feeder rating and 106% of East Network Overhead 0004’s 10.9 MW feeder rating. Finally, the 2017 projected summer load for Lemmon Avenue Substation is 73.6 MW, which is 126% of its 58.4 MW substation rating. In order to correct these problems, it is proposed to establish the North Network Overhead substation with one 138-13.2kV 47.0 MVA transformer, four feeder breakers, 1000 ft. of reconductor to 3 – 795AAC, 2650 ft. of new 3 - 1000 Cu cable, 450 ft. of 8E6 duct bank, install two 600A ABS switches, and perform switching. The completion of this project will solve the loading problems on Bryan, East Network Overhead, and Lemmon Avenue Substations. | 2012: -9.30% 2013: 1.59% 2014: -3.05% 2015: 3.31% 2016: 0.39% | 2017: -4.47% 2018: 16.29% 2019: -1.61% 2020: -1.57% 2021: 0.28% | 15 MW | 2017: 21.8 MW 2018: 25.7 MW 2019: 25.6 MW 2020: 24.1 MW 2021: 27.5 MW | Industrial Residential | Not Applicable
49 | 17T62041 -- JOHN DAY SUB: ESTABLISH 138-25 KV | The 2017 projected summer load on Fossil Creek Substation Bank #2 is 47.9 which is 103% of the 46.7 MVA nameplate rating for this transformer. In addition, the 2017 projected summer load on Fossil Creek substation feeder 6732 is 30.9 which is 111% of the 27.8 MVA maximum continuous rating for this feeder. Also, the 2017 projected summer load on Wagley Robertson Substation Banks #1 and #2 is 73.7 MVA which is 126% of the 58.4 MVA rating for this substation. In order to correct these problems it is proposed to establish John Day Substation with one 47 MVA 138-25 kV transformer and two feeder breakers. In addition, it is proposed to install two feeders and transfer 17 MVA from Wagley Robertson substation feeder 8412 and transfer 6.0 MVA from Fossil Creek substation feeder 6732 to the new John Day Substation feeders. Completion to this project will correct the loading problems at Fossil Creek and Wagley Robertson Substations. | 2012: -2.66% 2013: -16.32% 2014: -4.29% 2015: 10.23% 2016: 9.11% | 2017: 1.38% 2018: 7.35% 2019: 5.14% 2020: 1.27% 2021: -6.42% | 23 MW | 2017: 0.3 MW 2018: 4.0 MW 2019: 24.4 MW 2020: 28.1 MW 2021: 26.4 MW | Commercial | Not Applicable
50 | 17T63013 -- DEEP CREEK SUB: ESTABLISH STATION AS PART OF RELOCATING DIST FROM SNYDER SUB | The 2017 summer projected load on Snyder Substation bank #2 is 22.2 MW which is 111% of this transformer’s 20 MVA nameplate rating. In addition, the projected load on Snyder Substation is 41.8 MW which is 167% of this station’s 25 MVA backstand rating. In order to correct these overloads, the original proposal was to install Bank #4 at Snyder Substation with one 138/12.5 kV 47 MVA transformer, two 12.5 kV feeder breakers, two 1000 Cu feeder exits, and remove the existing 69/12.5 kV 20 MVA transformer and associated bus work. The actual project constructed differed from the recommendation after detailed engineering analysis performed by Oncor’s Transmission Engineering group determined that construction of the project as recommended would be less economical and require mobile transformer installation. It was decided to instead, build Deep Creek substation on the adjacent property to avoid a total rebuild of the existing station. | 2012: 1.75% 2013: 1.15% 2014: -0.28% 2015: 2.27% 2016: -12.50% | 2017: 6.67% 2018: 10.09% 2019: 3.61% 2020: -1.88% 2021: -6.56% | 41.8 MW | 2017: 32.7 MW 2018: 36.0 MW 2019: 37.3 MW 2020: 36.6 MW 2021: 34.2 MW | Commercial Industrial Residential | Not Applicable
51 | 17T63070 -- PLOWBOY SUB: ESTABLISH STATION | The 2017 winter projected load on Roscoe Substation bank #1 is 11.6 MW which is 124% of this transformer’s 9.4 MVA nameplate rating. Minimum fault current on feeder 2921 is less than the reach of the breaker settings. In order to correct these overload and reach issue, it is proposed to establish Plowboy Substation with one 69/12.5 kV 28 MVA transformer and two 12.5 KV feeder breakers, install approximately 5500 ft. of 3-795 KCMIL, 150 ft. of 3-4/0 AL, reconductor approximately 8400 ft. of existing line with 3-795 KCMIL, install two air-break switches, remove spans across Broadway St. and re-feed from feeder that`s closer to the load, reconfigure feeders to feed from the new substation, and install a 3-phase Nova electronic recloser to address breaker reach. The completion of this work will correct the transformer nameplate overload at Roscoe Substation. | 2013: 19.44% 2014: 8.14% 2015: -12.90% 2016: 22.22% 2017: -8.08% | 2018: 4.40% 2019: -11.58% 2020: -2.38% 2021: 1.47% | 11.6 MW | 2018: 0.4 MW 2019: 8.4 MW 2020: 8.2 MW 2021: 8.3 MW | Commercial Industrial Residential | Not Applicable
52 | 17T64011 -- MCLENNAN CO EAST SUBSTATION: ESTABLISH TRANSFORMER #1 | The 2017 summer projected load on Bellmead Substation is 50.5 MW which is 144% of this stations 35 MVA backstand rating. In addition, the 2016 summer projected load on Bellmead Bank #1 is 29.0 MW which is 104% of the 28 MVA nameplate rating. The 2017/2018 winter projected load on Tradinghouse Substation is 10.3 MW which is 110 % of this stations 9.375 MVA nameplate rating. Additionally, two large industrial customers (Customer L and Customer M) sit at the end of two different feeders on Northcrest Substation with no backstand capabilities. In order to correct these overloads, it is proposed to establish a new substation on property already owned by Oncor under an existing 138 kV line which runs from Elm Mott to Lake Creek with one 138/12.5 kV 28 MVA transformer and two 12.5 kV feeder breakers. Additionally install approximately 16,000 ft. of new feeders; reconductor approx. 9,400 ft. of conductor to 3-795; install various switches, regulators, and reclosers; and perform switching to transfer 3.3 MW from THSES to new substation and approximately 8.8 MW from BLMED to neighboring substations and the new substation. The completion of this work will solve the overloads at Bellmead and Tradinghouse substations, provide backstand capability to Customer L and Customer M, and provide a future means to serve the load growth potential of the land owned by the Customer N near Customer L. | 2012: -3.63% 2013: -2.06% 2014: -1.40% 2015: 5.21% 2016: -3.37% | 2017: 0.23% 2018: 12.43% 2019: -5.48% 2020: -1.53% 2021: -4.51% | 16.8 MW | 2017: 2.4 MW 2018: 16.5 MW 2019: 15.7 MW 2020: 18.9 MW 2021: 18.5 MW | Industrial Residential | Customer L Customer M Customer N
53 | 17T65037 -- WESTRIDGE SUB: ESTABLISH STATION AS PART OF RELOCATING THE EXISTING COLLIN SUB | The 2017 projected load on Collin SES Substation Transformer #2 and Collin SES Substation is 36.1 MVA and 67.9 MVA respectively which is 129% and 194% of the 28 MVA nameplate rating and 35.0 MVA Backstand rating for this substation. In order to correct this problem, it is proposed to relocate the two transformers (at Westridge) (47 MVA & 28 MVA) and four feeder breakers at Collin SES Substation with 2-47 MVA 138-24.9 kV transformers and four feeder breakers. In addition, it is proposed to relocate the existing four feeder exits with underground 1000 Cu feeder exits. The completion of this project will correct the loading problems at Collin SES Substation. | 2012: 0.98% 2013: -4.60% 2014: 2.03% 2015: 13.43% 2016: 18.86% | 2017: -9.96% 2018: 37.50% 2019: -11.77% 2020: 8.28% 2021: -1.70% | 67.9 MW | 2017: 48.8 MW 2018: 67.1 MW 2019: 59.2 MW 2020: 64.1 MW 2021: 63.0 MW | Commercial Industrial Residential | Not Applicable
54 | 17T65062 -- FRISCO WEST SUB: EST SUB W/ 138-26.4 KV 47 MVA XFMR, TWO FDRS, BUS-TIE | The 2017 projected summer load on Rolater #1, #2, Rolater Substation, and Rolater 2921 is 42.3 MVA, 49.6 MVA, 91.9 MVA, and 29.5 MVA respectively which is 91%, 106%, 157%, and 110% of the 47 MVA nameplate rating, 58.4 MVA Backstand Rating, and 26.9 MVA maximum continuous rating for this substation and feeder. In addition, the 2017 projected summer load on McDermott #1, #2, #3, McDermott Substation, and McDermott 2554 is 35.5 MVA, 41.6 MVA, 41.2 MVA, 118.3 MVA, and 30.6 MVA respectively which is 76%, 89%, 88%, 101%, and 104% of the 47 MVA nameplate rating, 116.8 MVA Backstand Rating, and 29.4 MVA maximum continuous rating for this substation and feeder. In addition, the 2017 projected summer load on The Colony #1, #2, The Colony Substation, and The Colony 2405 is 41.2 MVA, 54.2 MVA, 95.4 MVA, and 29.7 MVA respectively which is 44%, 58%, 81%, and 110% of the 47 MVA nameplate rating, 117.5 MVA Backstand Rating, and 26.9 MVA maximum continuous rating for this substation and feeder. This area is seeing high profile growth related to developments such as the Dallas Cowboys facility, Frisco Station, Wade Park and others. In order to correct these problems, it is proposed to build the Frisco West Substation, install one 47.0 MVA, 138-24.9 kV transformer with two 24.9 kV circuit breakers, a 3-1000 Cu circuit in proposed 8E6 duct bank for an estimated 5,650 ft. (Feeder #1), and a 3-1000 Cu circuit for an estimated 4200 ft. (Feeder #2) and transfer load from existing circuits using existing switches. The completion of this work will resolve the issue(s) identified. | 2012: -7.42% 2013: -0.92% 2014: -5.97% 2015: 3.71% 2016: 6.03% | 2017: 2.09% 2018: 4.23% 2019: -4.54% 2020: 1.30% 2021: -4.76% | 38.5 MW | 2017: 31.5 MW 2018: 38.6 MW 2019: 41.4 MW 2020: 41.6 MW 2021: 40.7 MW | Commercial Industrial Residential | Not Applicable
55 | 17T65087 -- BUFFALO CREEK SUB: ESTABLISH 138-25 KV 47 MVA XFMR & 2 FDR BKRS | The 2017 projected summer load on Forney Switch 2025 is 29.4 MVA which is 109% of the feeder capacity of 26.9 MVA. In addition, the 2017 projected summer load on Forney Switch Substation is 89.5 MVA which is 153% of the substation rating of 58.4 MVA. Also, the winter projected load is 74.2 MVA which is 127% of the recommended backstand rating of 58.4 MVA. In order to correct this problem, it is proposed to establish Rockwall County Buffalo Creek Substation with 1-47 MVA, 138-25 kV, transformer and two 25 kV feeder breakers with 1000 kcmil Cu feeder exits. In addition, it is proposed to reconductor 15000 ft. of #4/0 and small wire to 3-795 kcmil AAC, install 4100 ft. of 3-795 kcmil AAC, remove and relocate 1200 ft. of 3-795 kcmil AAC double-circuit, and transfer load with existing and proposed devices. The completion of this project will correct the overload problems on Forney Switch 2025 and the backstand problems at Forney Switch Substation. | 2012: -2.74% 2013: 5.07% 2014: -0.54% 2015: 7.55% 2016: 0.13% | 2017: -0.25% 2018: 7.40% 2019: 1.05% 2020: 3.01% 2021: 0.36% | 13.7 MW | 2017: 14.0 MW 2018: 15.7 MW 2019: 15.6 MW 2020: 17.1 MW 2021: 15.8 MW | Commercial Industrial Residential | Not Applicable
56 | 18T63040 -- HIGH SKY SUBSTATION: ESTABLISH STATION W/ 47MVA TRANSFORMER | Customer B has requested 12.8 MW distribution one-span service by 2020 to an oil field near Midland NW Switch in Midland County. Customer B currently has 2 PMEs with a total load of approximately 7 MW that will be combined and 5.5 MW added for the total of 12.8 MW. The requested in-service date is June 1, 2018. The current distribution to this area is served from Mockingbird Feeders 5312 and 5321. Mockingbird 5312 is projected to have a 2018 summer load of 13.0 MW which 86 % of its’ 13.5 MVA maximum continuous rating, and Mockingbird 5321 is projected to have a 2018 summer load of 13.5 MW which is 112 % of its 12.1 MW maximum continuous rating. The distance to this new load, which is virtually all motor load, from Mockingbird Substation is 54,000 ft. or 10.2 miles. A study of the Distribution system has determined that an acceptable motor starting capacity cannot be provided at this requested point of service due to the distance. An acceptable voltage level cannot be maintained over this distance, and coordination is not possible due to extremely low available fault currents. In order to serve the Customer B load, it is proposed to install Hwy 158 Substation (now known as High Sky Sub) with 1-47.0 MVA 138-24.9 kV substation transformer and two 24.9 kV feeder breakers. The new station will be located west of the new Midland NW Switching Station approximately 1000 ft.. It is anticipated that Customer B will request a substation rate PME at the new substation, however Distribution Planning recommends that two of the new feeders be tied to existing distribution in the area by installing 4,200 ft. 3-795 KCMIL AAAC, reconductoring 8,600 ft. of 3-#1/0 ACSR with 3-795 KCMIL AAC, removing 6-328 amp voltage regulators, removing 3-219 amp voltage regulators, installing 6-900 amp ABSs, removing one recloser, transferring load from Mockingbird 5312 and 5321 to the new feeders. Completion of this work will provide service to the Customer B Oil Field, provide load relief for Mockingbird Substation feeders, and will improve reliability, voltage stability, motor starting capabilities, and coordination in this area. | 2013: 24.20% 2014: -0.64% 2015: -9.48% 2016: 30.00% 2017: -15.02% | 2018: -2.80% 2019: 37.25% 2020: -4.20% 2021: -9.16% | 21.2 MW | 2018: 1.8 MW 2019: 1.9 MW 2020: 2.5 MW 2021: 2.6 MW | Commercial Industrial Residential | Customer B
57 | 18T63045 -- GRAVEL PIT SUB: ESTABLISH STATION | T.I. Odessa Substation feeder 9611 has a 2018 summer projected load of 16.9 MW which is 120% of this feeder’s 14.1 MVA maximum continuous rating, Pegasus Substation feeder 2311 has a 2018 summer projected load of 12.4 which is 128% of this feeder’s 9.7 MVA maximum continuous rating, and Odessa Substation feeder 0212 has a 2018 summer projected load of 14.8 MW which is 102% of this feeder’s 14.5 MVA maximum continuous rating. In addition, T.I. Odessa Substation has a 2018 summer projected load of 37.9 MW which is 108% of this substation’s 35 MVA backstand rating. There is limited availability to serve added oil field load in southwest Midland County due to voltage flicker during motor starts, voltage stability during steady state conditions, and available fault currents for coordination due to the excessive distances from Odessa, TI Odessa, and Pegasus Substations. Customer C and Customer Y have a very heavy concentration of motor loads in this area. In order to correct these problems, it is proposed to install Midland Co. FM 1788 Rd S Substation (now known as Gravel Pit Sub) with 1-28 MVA 128-12.5 kV transformer and three 12.5 kV feeder breakers and exits. It is proposed to reconductor approximately 54,000 ft. of 3-#1/0 ACSR with 3-795 kcmil AAC, install 6000 ft. 3-795 kcmil AAC, install 9 air break switches, and transfer loads from TI Odessa feeders 9611 and 9621, Pegasus feeder 2311, and Odessa feeder 0212 to the three proposed feeders. It is proposed to remove 3-328 amp voltage regulators and install 1-140 amp W recloser. Completion of this project will correct feeder loading on TI Odessa 9611, Odessa 0212, and Pegasus 2311 and will provide motor starting support, voltage stability, and coordination in the southeast Midland county area. | 2013: -13.65% 2014: 16.72% 2015: 33.59% 2016: -17.74% 2017: 15.40% | 2018: 17.45% 2019: 5.59% 2020: -14.74% 2021: 12.65% | 19 MW | 2018: 3.0 MW 2019: 24.6 MW 2020: 17.4 MW 2021: 17.2 MW | Commercial Industrial Residential | Not Applicable
58 | 18T64038 -- GREYS LAKE: CONSTRUCT 47 MVA, 138-12.5 KV STATION | The projected 2018 summer load on Tyler Northeast 1624 is 13.7 MVA which is 116% of the 11.8 MVA maximum continuous rating. Also, the projected 2018 summer load on Tyler Northeast 1623 is 11.9 MW which is 101% of the 11.8 MVA maximum continuous rating. In addition, the projected 2018 summer load on Tyler Northeast Substation is 45.25 MVA, which is 131% of its 35 MVA backstand rating. The 7 MW offsite for a large commercial customer is dependent on this plan item. 3 MW load growth on Cherokee County Electric Co-op Owentown POI is also dependent on this plan item. In order to correct this issue, it is proposed to establish Greys Lake Substation with a 138-12.5 kV, 47 MVA transformer, four feeder breakers and four 3-1000 Cu feeder exits. In addition, it is proposed to install approximately 7900 ft. of 3-795 AAC, reconductor approximately 1800 ft. of 4/0 ACSR to 795 AAC, reconductor approximately 2900 ft. of #2 ACSR to 795 AAC, and reconductor approximately 4500 ft. of #4 ACSR to 795 AAC. Load will be transferred from Tyler Northeast 1605, 1613, 1623, and 1624 to the new Greys Lake feeders and transfer load using existing switches. In addition it is proposed to relocate 2 sets of regulators, remove 3 sets of regulators, relocate 2 reclosers, relocate 1 capacitor, and install 3 air switches. The completion of this project will correct the feeder overload of Tyler Northeast 1624, Tyler Northeast 1623, and the backstand issue of Tyler Northeast substation. | 2013: -1.17% 2014: -9.14% 2015: 6.82% 2016: 10.33% 2017: -4.41% | 2018: 6.92% 2019: 23.99% 2020: 1.52% 2021: 6.26% | 16.5 MW | 2018: 1.0 MW 2019: 8.6 MW 2020: 22.6 MW 2021: 22.5 MW | Commercial Industrial Residential | Not Applicable
59 | 18T65040 -- CREEKSIDE SUB: ESTABLISH STATION WITH 138-13.2 KV 47 MVA XFMR AND THREE FDRS | The 2018 projected Summer load on Dalrock substation transformer bank #1 is 51.5 MVA which is 110% of the 46.7 MVA transformer nameplate rating. In order to correct this problem, it is proposed to establish Creekside Sub substation with 1-46.7 MVA, 138-12.5 kV, transformer and three 12.5 kV feeder breakers with 1000 kcmil Cu feeder exits. In addition, it is proposed to install 12300 ft. of 3-795 kcmil AAC overhead conductor, reconductor 3500 ft. of 3-#4/0 AAC to 3-795 kcmil AAC overhead conductor, install five 900A air break switches, transfer 6.8 MW from Dalrock 1307 to Creekside Sub feeder 2, transfer 3.9 MW from Dalrock 1301 to Creekside Sub feeder 3, and transfer 3.7 MW from Dalrock 1301, 1.5 MW from Dalrock 1307, and 5.2 MW from Dalrock 1303 to Creekside Sub feeder 1. The completion of this project will correct the overload problems at Dalrock substation. | 2013: -2.58% 2014: -4.03% 2015: 10.89% 2016: 6.75% 2017: -13.97% | 2018: 7.73% 2019: -4.07% 2020: 5.99% 2021: -6.11% | 21.1 MW | 2018: 9.7 MW 2019: 13.5 MW 2020: 14.8 MW 2021: 15.8 MW | Commercial Residential | Not Applicable
60 | 0PT04147 -- RIVERVIEW SUB : ESTABLISH ONE 47 MVA 138-22 KV TRANSFORMER AND TWO 22 KV OH FEEDER BREAKERS | The 2021 Summer Projected load on Coyanosa Northwest Bank #1 is 30.3 MVA which is 108% of the 28 MVA rating. In addition, the 2021 Summer Projected load on Coyanosa Northwest Bank #2 is 32.9 MVA which is 118% of the 28 MVA rating. The 2021 Summer Projected load on Coyanosa Northwest Substation is 63.2 MVA which is 181% of its 35 MVA contingency rating. Finally, Coyanosa Northwest Feeder 8151 is on the SQR list. In order to correct these loading violations, it is proposed to establish Riverview Substation with 1-47 MVA 138-22 kV transformer and 2-22 kV OH feeder breakers. It is also recommended to construct various distribution facilities in order to transfer load to the new substation. The completion of this work will resolve the overloads that have been identified. | 2016: 16.25% 2017: 62.37% 2018: 45.7% 2019: 93.18% 2020: 14.82% | 2021: -51.8% | 37 MW | 2021: 0.3 MW | Commercial Industrial Residential | Not Applicable
61 | 0PT04289 -- WESTON SUBSTATION: ESTABLISH SUBSTATION WITH A 47 MVA 138-24.9 KV TRANSFORMER AND TWO FEEDER BREAKERS | The 2020 projected summer load on McKinney White Street #1 is 50.4 MVA, which is 108% of its 46.7 MVA nameplate rating and the 2020 projected summer load on McKinney White Street Substation is 73.4 MVA, which is 126% of its 58.4 MVA backstand rating. In addition, the 2020 projected summer load on McKinney #3 and McKinney #4 is 79.4 MV, which is 136% of the 58.4 MVA backstand rating of these two 24.9 kV transformers. In order to correct these problems, it is proposed to establish the Weston Substation and install a 47 MVA, 138-24.9 kV transformer and two 24.9 kV feeder breakers with 1000 Cu feeder exits, install 4000 ft. of 3-795 kcmil AAC, install 1500 ft. of 2-795 kcmil AAC, reconductor 3400 ft. of existing 3 phase to 3-795 kcmil AAC, install 3-900 Amp air break switches and transfer load from McKinney 1252, 1254 and McKinney White 3512 to the new Weston feeders. The completion of this project will correct the overloading problem on McKinney White Street #1 and the backstand issue on McKinney #3 & #4. | 2016: 1.07% 2017: 0.88% 2018: 7.5% 2019: -12.17% 2020: -12.47% | 2021: 11.99% | 37 MW | 2021: 11.4 MW | Commercial Industrial Residential | Not Applicable
62 | 0PT39201 -- WEST NETWORK SUB : REBUILD STATION ADJACENT TO THE EXISTING SUBSTATION | The 2020 projected summer load on the Dallas West Network Substation is 53.2MVA. There are three 138-13.2kV 60MVA substation transformers in parallel at this substation. The substation equipment (including three switchgear houses containing four feeder breakers each) is old and obsolete plus new replacement parts are rare. Due to this, the probability of a fault in the switchgear is greater than normal which can cause outages within the substation feeder breakers. In order to correct this problem, it is proposed to rebuild the substation adjacent to the existing substation on the same property. Twelve 1000Cu 13.2kV feeder exits in duct structure are to be installed between the proposed substation feeder breakers and the existing feeder exits. The completion of this project will improve reliability issues at Dallas West Network Substation | 2016: -1.64% 2017: -1.66% 2018: 3.38% 2019: -0.4% 2020: 0.71% | 2021: 0.22% | 53.2 MW | 2021: 46.6 MW | Commercial Industrial Residential | Not Applicable
63 | 0PT39282 -- POOLVILLE SUB : ESTABLISH SUBSTATION WITH A 28 MVA 138-12.5KV TRANSFORMER AND 2 FEEDER BREAKERS | The 2019/2020 projected winter load on Balsora Transformer #1 is 11.1 MVA which is 106% of its 10.5 MVA nameplate rating. Additionally, the 2019/2020 projected winter load on a 20,000 ft. section of 3-4/0ACSR on Balsora 1601 is 396 amps which is 118% of its 337 amp continuous rating. Also pertaining to Balsora 1601, there are 2 separate sections of 1-6STL along with several protective devices across the feeder that are all projected to be loaded to greater than 105% of their maximum continuous ratings by winter 2019/2020. Balsora 1601 has a very poor reliability history and has no 3-phase ties to any other substation transformer. To address these issues, it is proposed to establish Poolville Substation with a 28 MVA 138-12.5kV transformer and 2 feeder breakers. It is also proposed to reconductor approx. 39,800 ft. with 3-795AAC, reconductor approx. 11,000 ft. of 1-6STL with 1-2ACSR, install 2 air break switches, 1 set of voltage regulators, 2 NOVA reclosers, 4 TripSavers, and perform switching to transfer 7.1 MW from Balsora 1601 to Poolville Fdr. #1, 0.2 MW from Balsora 1601 to Poolville Fdr. #2, and 2.7 MW from Weatherford 2002 to Poolville Fdr. #2. The completion of this project will correct the loading issue on Balsora #1, correct the overloaded conductor and protective devices on Balsora 1601, and greatly improve the reliability of this feeder. | 2016: -8.13% 2017: 0.0% 2018: 17.69% 2019: -31.7% 2020: -12.44% | 2021: 25.68% | 10 MW | 2021: 4 MW | Commercial Industrial Residential | Not Applicable
64 | 0PT40937 -- BLAIR LAKE SUB : ESTABLISH STATION WITH 47 MVA, 138/69-21.6 KV TRANSFORMER AND INSTALL DISTRIBUTION AUTOMATION ON FEEDER 6321 | The 2021 projected winter load on Coyanosa Substation Transformer Bank #1 is 13.5 MVA which is 129% of the 10.5 MVA rating for this transformer bank. Coyanosa is a single transformer substation. In order to correct this problem, it is recommended to establish Blair Lake Substation with a 138/69-22kV 47MVA transformer and 2 feeder breakers with UG feeder exits. It is also recommended to construct various distribution facilities in order to transfer the load of Coyanosa Substation to the new Blair Lake Substation. The completion of this project will correct the overload at Coyanosa Substation. | 2016: -1.96% 2017: -24% 2018: 50% 2019: 33.33% 2020: 73.68% | 2021: -10.6% | 12.9 MW | 2021: 1.5 MW | Commercial Industrial | Not Applicable
65 | 0PT40959 -- REINDEER SUB : ESTABLISH REINDEER SUBSTATION WITH ONE 47 MVA 138-25 KV TRANSFORMERS AND TWO 25 KV UG FEEDER BREAKERS | The 2021 Summer projected load on Red Oak Bank #1 is 51.8 MVA which is 111% of the 46.7 MVA rating. In addition, the 2021 Summer Projected load on Red Oak Bank #2 is 48.3 MVA which is 103% of the 46.7 MVA rating. Furthermore, the 2021 Summer Projected load on Red Oak Substation is 100.1 MVA which is 164% of its 58.4 MVA contingency rating. In order to correct these loading violations, it is recommended to establish Reindeer Substation with 1-47 MVA 138-25 kV transformers and 2-25 kV UG feeder breakers. It is also recommended to construct various distribution facilities in order to transfer load to the new substation. The completion of this work will resolve the overloads that have been identified. | 2016: 13.18% 2017: -12.68% 2018: 9.78% 2019: 7.56% 2020: 1.38% | 2021: 13.27% | 37 MW | 2021: 1.5 MW | Commercial Industrial Residential | Not Applicable
66 | 0PT41754 -- OIL MILL LAKE SUB : REBUILD MARLIN SUB ON NEW SITE | Transmission Engineering has requested to remove the Distribution transformers from Marlin Substation. In order to accommodate this request, it is proposed to establish Oil Mill Lake Substation with (2) 28 MVA 138/12 kV Transformers and (4) 12 kV feeder breakers along with performing the necessary distribution work to transfer the 12 kV and 25 kV distribution load from Marlin Substation to Oil Mill Lake Substation. The completion of this work will allow the removal of the 12 kV and 25 kV transformer(s) at Marlin Substation. | 2016: 61.54% 2017: -21.09% 2018: -1.85% 2019: 29.73% 2020: 1.6% | 2021: -0.71% | 13.4 MW | 2021: 0.9 MW | Commercial Residential | Not Applicable
67 | 0PT42128 -- FLAT LAND (RED LAKE) SUB : ESTABLISH FLAT LAND SUB WITH TWO 47 MVA 138-25 KV TRANSFORMERS AND TWO 25 KV OH FEEDER BREAKERS. | The 2021 summer projected load on Brown Bank #1 is 61.2 MVA which is 109% of the 56 MVA rating. The 2021 Summer Projected load on Grady Substation is 84.7 MVA which is 121% of its 70 MVA contingency rating. In order to correct these loading violations, it is recommended to establish Flat Land Substation with 2-47 MVA 138-25 kV transformers and 2-25 kV OH feeder breakers. It is also recommended to construct various distribution facilities in order to transfer load to the new substation. The completion of this work will resolve the overloads that have been identified. | 2016: -35.28% 2017: 2% 2018: 127.45% 2019: 62.07% 2020: 18.35% | 2021: -46.34% | 19 MW | 2021: 5.7 MW | Commercial Industrial Residential | Not Applicable
68 | 0PT42129 -- MIDNIGHT SUB (ROUND ROCK NORTH): ESTABLISH TWO 47 MVA 138-25 KV TRANSFORMERS AND THREE 25 KV UG FEEDER BREAKERS | The 2021 summer projected load on Round Rock Northeast Feeder 2405 is 37.8 MVA which is 128% of the 29.5 MVA feeder rating. In addition, the 2021 summer projected load on Round Rock Westinghouse Feeder 1623 is 33 MVA which is 111% of the 29.5 MVA feeder rating. Furthermore, the 2021 Summer Projected load on Round Rock Northeast Bank #3 is 58.4 MVA which is 125% of the 46.7 MVA rating. Finally, the 2021 Summer Projected load on Round Rock Northeast Substation is 147.2 MVA which is 126% of its 116.8 MVA contingency rating. There are several feeders that have high customer counts (4,000) that will be affected by this plan item. In order to correct these loading violations, it is recommended to establish Midnight (Round Rock North Substation) with 2-47 MVA 138-25 kV transformers and 3-25 kV UG feeder breakers. It is also recommended to construct various distribution facilities in order to transfer load to the new substation. The completion of this work will resolve the overloads that have been identified. | 2016: 16.8% 2017: 5.89% 2018: 22.76% 2019: 6.59% 2020: 9.61% | 2021: -10.16% | 43.7 MW | 2021: 15.8 MW | Commercial Industrial Residential | Not Applicable
69 | 0PT42153 -- STAGECOACH SUB : ESTABLISH STATION WITH ONE 47 MVA 138/25 KV TRANSFORMER AND TWO 25 KV FEEDER BREAKERS | The 2021 winter projected load on Killeen South substation feeder 4504 is 38.2 MVA which is 119% of this feeders 32.2 MVA rating. The 2021 winter projected load on Killeen South Bank #2 is 53 MVA which is 113% of this transformers 46.7 MVA nameplate rating. The 2021 winter projected load on Killeen South Bank #1 is 51.7 MVA which is 111% of this transformers 46.7 MVA nameplate rating. The 2021 winter projected load on Harker Heights Substation Bank #2 is 50.1 MVA which is 107% of this transformers 46.7 MVA rating. In order to correct these overloads, it is proposed to Establish Killeen Stagecoach Substation with 1-47 MVA 138/25 kV transformer and 2-25 kV feeder breakers and perform the necessary distribution upgrades in order to transfer load to the new substation. The completion of this work will correct the overloads mentioned above. | 2016: 4.37% 2017: -0.98% 2018: 14.08% 2019: 18.81% 2020: 2.63% | 2021: 13.4% | 42.9 MW | 2021: 14.5 MW | Commercial Industrial Residential | Not Applicable
70 | 0PT42207 -- ALCATRAZ SUB : ESTABLISH SUBSTATION WITH TWO 47 MVA 138-22 KV TRANSFORMER AND FOUR 22 KV OH FEEDER BREAKERS | The 2021 Summer Projected load on Kyle Ranch Bank #1 is 49.9 MVA which is 107% of the 46.7 MVA rating. In addition, the 2021 Summer Projected load on Kyle Ranch Feeder 9011 is 27.9 MVA which is 103% of the 27.1 MVA feeder rating. Furthermore, the 2021 Summer Projected load on Kyle Ranch Feeder 9012 is 29.8 MVA which is 109% of the 27.1 MVA feeder rating. Finally, the 2021 Summer Projected load on Mason Substation is 45.0 MVA which is 128% of its 35.0 MVA contingency rating. In order to correct these problems, it is proposed to establish Alcatraz Substation with 2-47 MVA 138-22 kV transformer and 4-22 kV OH feeder breakers. It is also recommended to construct various distribution facilities in order to transfer load to the new substation. The completion of this work will resolve the overloads that have been identified. | 2016: 31.69% 2017: -10.37% 2018: 8.8% 2019: 22.13% 2020: 20.21% | 2021: 173.91% | 41 MW | 2021: 14.3 MW | Commercial Industrial | Not Applicable
71 | 0PT43010 -- GUNSOLUS CREEK SUB : ESTABLISH A NEW STATION WITH (2) 138/12.5 KV 47 MVA TRANSFORMERS AND (7) FEEDER BREAKERS ON A NEW SITE TO REPLACE BRECKENRIDGE SUB. | This is a CMPC Project due to operational issues with the existing 69 kV single-phase transformers, substation voltage regulators, and repeat flooding of the station relay house. In addition to these operational issues, Breckenridge Substation Banks #1 & #2 are loaded to 33.1 MVA which is 133% of their 25 MVA backstand rating. Banks #2 and #3 are loaded to 31.7 MVA which is 127% of their 25 MVA backstand rating. In order to resolve these loading concerns and operational issues, it is proposed to establish a new station out of the flood plane and energize with (2) 138/12.5 kV 47 MVA transformers and (7) feeder breakers on a new piece of land. This will require upgrading a re-routing a portion of the distribution system near the substation in order to re-route the feeders to the new station. It is recommended to decommission the distribution equipment at Breckenridge Substation upon completion of the work mentioned. The completion of this work will correct the issues identified above. | 2016: 7.18% 2017: 6.94% 2018: -6.49% 2019: 1.91% 2020: 1.17% | 2021: 15.6% | 23.1 MW | 2021: 10 MW | Commercial Industrial Residential | Not Applicable
72 | 0PT43602 -- PROSPER SUB : ESTABLISH SUBSTATION WITH 47 MVA 138/25 KV TRANSFORMER AND TWO FEEDER BREAKERS | The 2021 Summer Projected load on Westridge Feeder 3056 is 30.4 MVA which is 103% of the 29.4 MVA feeder rating. In addition, the 2021 Summer Projected load on Westridge Substation is 73.6 MVA which is 125% of its 58.8 MVA contingency rating. In order to correct these problems it is recommended to establish Prosper Substation with 1-47 MVA 138-25kV transformer and 2-25kV feeder breakers. It is also recommended to construct various distribution facilities in order to transfer load to the new substation. The completion of this work will resolve the overloads that have been identified. | 2016: 16.8% 2017: -9.75% 2018: 34.62% 2019: 13.06% 2020: 3.25% | 2021: -14.2% | 33.4 MW | 2021: 2.2 MW | Commercial Industrial Residential | Not Applicable
73 | 17T65080 -- DELTA SUB - ESTABLISH STATION | In the winter of 2017, Transmission Planning has identified load capacity problems in the Paris Plant – Commerce 69 kV line. Cooper substation consists of (2)69/12.5 kV 10.5 MVA transformers and (3)12.5/4.2 kV 833 kVA single phase transformers, and is fed from these transmission lines. In order to correct this problem, Transmission Planning proposes to convert the Paris Plant – Commerce 69 kV line to 138 kV operations. In order to do this conversion, the Cooper substation transformers will need to be replaced and the substation will be relocated. It is recommended to replace the existing transformer banks with (2)138-12.5 kV 10.5 MVA delta-wye transformers and two feeder breakers with 1000 kcmil Al feeder exits. In addition, it is proposed to reconductor 5300 ft. of various small wire to (3)795 kcmil AAC, install (2)12.5-4.2 kV 1500 kVA auto stepdown transformers, install two normally open air break switches, transfer 2.85 MW from Cooper 0402 and 1201 to the new Feeder 1, and transfer 5.6 MW from Cooper 0401 and 1202 to the new Feeder 2. The completion of this work will correct the load capacity problems on the 69 kV transmission lines. | 2012: 10.96% 2013: -9.88% 2014: -9.59% 2015: 0.00% 2016: 3.03% | 2017: 0.00% 2018: -5.88% 2019: -1.56% 2020: -1.59% 2021: -0.49% | 7 MW | 2017: 6.8 MW 2018: 6.4 MW 2019: 6.3 MW 2020: 6.2 MW 2021: 6.2 MW | Commercial Industrial Residential | Not Applicable
74 | 18T62058 -- BOURLAND SUB: ESTABLISH STATION | The Forest Hill to Cresson 69 kV transmission line is being converted to 138 kV. The 69 kV transmission line from Forest Hill to Crowley is scheduled to be completed in 2017. The remaining section of the transmission line from Crowley to Cresson is scheduled to be converted to 138 KV in 2018. Since the transformer at Cresson Substation is 69 kV, it is proposed to remove Cresson Substation and establish Bourland Substation just to the south of the existing Cresson substation with a single 23.3 MVA, 138-24.9 kV transformer, two feeder breakers (both with Distribution Automation) and 1000 Cu feeder exits, install 20,000 ft. of 3-4/0 AAC conductor, reconductor 7500 ft. of small wire with 3-4/0 AAC conductor, relocate one recloser and transfer load using new and existing facilities. Since this transmission line is currently radial, the existing Cresson Substation load will need to be transferred to Benbrook and Godley substations while the Transmission and Substation work is being done. The switching that is required to take the existing Cresson Substation out of service for this time period is shown in the following drawings. The completion of this project will complete the conversion of the Forest Hill to Cresson (Bourland) transmission line. | 2013: -13.10% 2014: 13.70% 2015: 1.20% 2016: -17.86% 2017: -2.90% | 2018: 11.94% 2019: 0.00% 2020: 3.03% 2021: 35.14% | 8.9 MW | 2018: 7.5 MW 2019: 6.6 MW 2020: 6.8 MW 2021: 9.2 MW | Commercial Industrial Residential | Not Applicable
75 | TPSU.12.005404 --2570 EAST STILES SUBSTATION | Refer to Section 3.4 of Exhibit JBN-3 | No load data prior to project | 2014: 35.6% 2015: 3.1% 2016: -16.4% 2017: -4.8% 2018: 15.1% 2019: 10.5% 2020: -10.3% | 5.2 MW | 2014: 9.3 MW 2015: 9.6 MW 2016: 8 MW 2017: 10.2 MW 2018: 10.9 MW 2019: 10.6 MW 2020: 8.5 MW | Industrial | Not Applicable
76 | TPSU.12.005426 --EILAND SUBSTATION | Refer to Section 3.5 of Exhibit JBN-3 | No load data prior to project | No load data prior to project | No load data prior to project | 2013: 6.8 MW 2014: 12.5 MW 2015: 14 MW 2016: 10.4 MW 2017: 15.7 MW 2018: 15.4 MW 2019: 18.7 MW 2020: 18.6 MW | Industrial | Not Applicable
77 | TPSU.13.005628 --CONSTRUCT REBEL SUBSTATION | Refer to Section 3.9 of Exhibit JBN-3 | No load data prior to project | 2014: 13.3% 2015: -0.1% 2016: -8.6% 2017: 26.4% 2018: 42.7% 2019: 6.6% 2020: 0% | 4.1 MW | 2014: 3.9 MW 2015: 7.1 MW 2016: 12.8 MW 2017: 15.7 MW 2018: 47.7 MW 2019: 45.9 MW 2020: 51.8 MW | Industrial | Not Applicable
78 | TPSU.13.005629 --CONSTRUCT AIRPORT ROAD SUBSTATION (CONSTRUCT LORAINE SUBSTATION) | Refer to Section 3.12 of Exhibit JBN-3 | No load data prior to project | 2014: 8.7% 2015: 60% 2016: -44.5% 2017: -1.8% 2018: 9.2% 2019: 14.3% 2020: 1.5% | 0.4 MW | 2015: 7.4 MW 2016: 3.1 MW 2017: 3.9 MW 2018: 4.7 MW 2019: 5.5 MW 2020: 6 MW | Commercial Residential | Not Applicable
79 | TPSU.13.005630 --CONSTRUCT LUTHER SUBSTATION | Refer to Section 3.11 of Exhibit JBN-3 | No load data prior to project | 2014: 14.2% 2015: 33.3% 2016: -2% 2017: 53.7% 2018: 100.7% 2019: 7.4% 2020: -13.3% | 5.0 MW | 2015: 3.2 MW 2016: 5.91 MW 2017: 16.7 MW 2018: 35.8 MW 2019: 43.4 MW 2020: 27.9 MW | Industrial | Not Applicable
80 | TPSU.14.005773 --SALE RANCH SUBSTATION | Refer to Section 3.19 of Exhibit JBN-3 | 2012: 18.1% 2013: 106.5% 2014: 72.9% | 2015: -15.9% 2016: -41.4% 2017: 19.7% 2018: 64% 2019: 40.9% 2020: -9.8% | 4.2 MW | 2015: 1.7 MW 2016: 1.5 MW 2017: 1.7 MW 2018: 3.5 MW 2019: 4.2 MW 2020: 8.6 MW | Industrial | Not Applicable
81 | TPSU.15.005867 --GRADY 138 KV SUBSTATION | Refer to Section 3.23 of Exhibit JBN-3 | 2014: 17% | 2015: 119% 2016: 34.2% 2017: 34.3% 2018: 38% 2019: 23.8% 2020: -4% | 22.6 MW | 2015: 26.4 MW 2016: 20.9 MW 2017: 15.8 MW 2018: 21.3 MW 2019: 26 MW 2020: 25.7 MW | Commercial Industrial | Not Applicable
1 The Study used to support the Legacy Sharyland projects can be found attached to Joseph B. Nichols testimony, Exhibit JBN-3.
2 Customer names have been removed, and a unique identifier have been assigned to each customer. A key that contains the unique identifier that corresponds to each customer name is provided as confidential. See Schedule VI-M-2.1.1 (NTU) or Schedule VI-M-2.1.1 (Oncor).