## Energy Loss Factor
WP/II-H-1.3/1
Page 1 of 3
2024 Test Year Data
Oncor Electric Delivery Company LLC
Unadjusted Test Year Load Data
For the Test Year Ended December 31, 2024
Sponsor: D. E. Nelson
System Line Loss Calculation (Test Year 2024)
Energy Loss Factor Calculation
Line
No.
(a) | (b) | (c) | (d)
1 | System Net Consumed, MWh (as Calculated page 3) |  | 191736910.1165
2
3 | Booked Sales and Energy Losses by Voltage Level, MWh
4 | (Booked Sales and Energy Losses Page 3):
5 |  | Energy | Booked
6 |  | Losses | Sales
7 | Substation | 788616.4528 | 6412195
8 | Primary | 1451858.0282 | 17209450
9 | Secondary | 3667714.9454 | 162207075.69
10 | Total | 5908189.4265 | 185828720.69
11
12 | Percent Losses Calculation Procedure
13 | Substation:
14 | Input to Distribution Substation Transformation System, MWh |  | 191736910.1165
15 | Substation Losses, MWh |  | 788616.4528
16 | Substation Sales, MWh |  | 6412195
17 | Remainder to Distribution Primary System, MWh |  | 184536098.6637
18 | Percent Losses (Line 15/Line14) |  | 0.4113%
19 | Primary:
20 | Input to Distribution Primary System, MWh |  | 184536098.6637
21 | Primary Losses, MWh |  | 1451858.0282
22 | Primary Sales, MWh |  | 17209450
23 | Remainder to Distribution Secondary System, MWh |  | 165874790.6354
24 | Percent Losses (Line 21/Line 20) |  | 0.7868%
25 | Secondary:
26 | Input to Distribution Secondary System, MWh |  | 165874790.6354
27 | Secondary Losses, MWh |  | 3667714.9454
28 | Secondary Sales, MWh |  | 162207075.69
29 | Percent Losses (Line 27/Line 26) |  | 2.211%
30
31 | Loss Factors
32 | Loss Element by Voltage Level (1 - (Percent Losses/100):
33 | Substation |  | 0.99589
34 | Primary |  | 0.99213
35 | Secondary |  | 0.97789
36
37 | Factor by Voltage Level :
38 | Substation (1.0/Line 33) |  | 1.0041
39 | Primary (Line 38/Line 34) |  | 1.0121
40 | Secondary (Line 39/Line 35) |  | 1.035

## Demand Loss Factor
WP/II-H-1.3/1
Page 2 of 3
2024 Test Year Data
Oncor Electric Delivery Company LLC
Unadjusted Test Year Load Data
For the Test Year Ended December 31, 2024
Sponsor: D. E. Nelson
System Line Loss Calculation (Test Year 2024)
Demand Loss Factor Calculation
Line
No.
(a) | (b) | (c) | (d)
1 | System Peak Demand, MW (as Calculated Page 3) |  | 312153.6196
2
3 | Coincident Demand and Demand Losses, MW
4 | (Coincident Demands and Demand Losses Page 3):
5 |  | Demand | Coincident
6 |  | Losses | Demand
7 | Substation | 654.1489 | 766.781
8 | Primary | 4462.3587 | 2197.9
9 | Secondary | 5979.951 | 298092.48
10 | Total | 11096.4586 | 301057.161
11
12 | Percent Losses Calculation Procedure
13 | Substation:
14 | Input to Distribution Substation System, MW |  | 312153.6196
15 | Substation Losses, MW |  | 654.1489
16 | Substation Demand, MW |  | 766.781
17 | Remainder to Distribution Primary System, MW |  | 310732.6897
18 | Percent Losses (Line 15/Line 14) |  | 0.2096%
19 | Primary:
20 | Input to Distribution Primary System, MW |  | 310732.6897
21 | Primary Losses, MW |  | 4462.3587
22 | Primary Demand, MW |  | 2197.9
23 | Remainder to Distribution Secondary System, MW |  | 304072.431
24 | Percent Losses (Line 21/Line 20) |  | 1.436%
25 | Secondary:
26 | Input to Distribution Secondary System, MW |  | 304072.431
27 | Secondary Losses, MW |  | 5979.951
28 | Secondary Demand, MW |  | 298092.48
29 | Percent Losses (Line 27/Line 26) |  | 1.967%
30
31 | Loss Factors
32 | Loss Element by Voltage Level (1 - (Percent Losses/100):
33 | Substation |  | 0.9979
34 | Primary |  | 0.98564
35 | Secondary |  | 0.98033
36
37 | Factor by Voltage Level :
38 | Substation (1.0/Line 33) |  | 1.0021
39 | Primary (Line 38/Line 34) |  | 1.0167
40 | Secondary (Line 39/Line 35) |  | 1.0371

## 2024 Stats
WP/II-H-1.3/1
Page 3 of 3
2024 Test Year Data
Oncor Electric Delivery Company LLC
Unadjusted Test Year Load Data
For the Test Year Ended December 31, 2024
Sponsor: D. E. Nelson
System Line Loss Calculation (Test Year 2024)
Calculated Losses Using 2015 Oncor Integrated Power System Loss Analysis
| MWh |  | MW
Retail Sales from Service Drop | 162207075.69 |  | 298092.48
Service Drop Factor * | 1.0037 |  | 1.0046
Output from Secondary | 162812351.3929 |  | 299463.7054
Secondary Conductor Loss Factor * | 1.0011 |  | 1.0023
Output from Line Transformers | 162993073.103 |  | 300149.4773
Line Transformer Loss Factor * | 1.0177 |  | 1.0131
Input to Line Transformers | 165874790.6354 |  | 304072.431
Sales from Primary | 17209450 |  | 2197.9
Output from Primary Lines | 183084240.6354 |  | 306270.331
Primary Line Loss Factor * | 1.0079 |  | 1.0146
Output from Distribution Substations | 184536098.6637 |  | 310732.6897
Sales from Substations | 6412195 |  | 766.781
Total Output from Distribution Substations | 190948293.6637 |  | 311499.4707
Distribution Substation Loss Factor * | 1.0041 |  | 1.0021
Input to Distribution Substations | 191736910.1165 |  | 312153.6196
Total System Losses | 5908189.4265 |  | 11096.4586
NOTE:
2024 Annual Energy from company records and Demand at ERCOT's 2024 annual peak
* For Loss Factors, refer to WP/II-H-1.3/2