## SCHEDULE VI-M-2.1
| Project Name | Portions of Planning Studies that Support Need for Project 1 | Load growth rate in area to be served by project during each of 5 calendar years immediately before project was energized | Load growth rate in area served by project during each calendar year starting with year project initially energized | Peak Load projected to be served by project as forecasted by applicant and consistent with planning study | Peak Load served by project during each year since project was initially energized | Identify types of load the project was planned to serve (Industrial, Commercial, Residential, others) | Identify Customers if project was planned to serve a limited number of Customers with relatively large loads 1
1 | 13T65029 -- LAWRENCE SUB : ESTABLISH WITH ONE 47 MVA 138-25 KV BANK AND TWO 25 KV FEEDER BREAKERS | The 2013 projected summer load on Terrell South Substation Transformer #1 will be loaded to 36.3 MVA which is 130 percent of the 28 MVA nameplate rating. In addition, the Terrell South Feeder 2503 will be loaded to 30.1 MVA which is 108 percent of the 28 MVA maximum continuous rating and Forney Switch Substation will be loaded to 74.1 MVA which is 127 percent of the 58.4 substation rating. In order to correct these problems, it is proposed to establish the Lawrence Substation by installing 1-23 MVA, 138-25 kV, transformer and two 25 kV feeder breakers with 1000 kcmil copper exits. | 2017: 17.38% 2018: -8.25% 2019: -3.95% 2020: -2.53% 2021: 33.94% | 2022: -6.44% 2023: 7.99% 2024: -2.68% | 9.5 MW | 2022: 1.5 MW 2023: 5.0 MW 2024: 3.0 MW | Residential Commercial Industrial | Not Applicable
2 | 0PT51845 -- AZALEA SUB : ESTABLISH SUBSTATION WITH THREE 47 MVA, 138-25 KV TRANSFORMERS AND FOUR FEEDER BREAKERS | With the added load of 55 MW by Customer A, the 2024 projected load on Buchanan Ranch Bank #1 is 82 MVA which is 174 percent of the 47 MVA nameplate rating for this transformer. In addition, Customer A is expected to continue adding load at this location in the near future. In order to correct this loading condition, it is recommended to establish a new substation called Azalea Substation with three 138-24.9 kV, 47 MVA transformers and four underground feeder breakers. It is also recommended to construct various distribution facilities in order to serve Customer A's load. The completion of this work will correct the transformer loading condition that has been identified due to the added load of Customer A. | 2019: 0.91% 2020: 20.75% 2021: 1.49% 2022: 131.11% 2023: 504.41% | 2024: 67.88% | 55.0 MW | 2024: 42.8 MW | Commercial | Customer A
3 | 0PT51217 -- RIDGEVIEW SUB: ESTABLISH STATION WITH THREE 47MVA 138/26.4KV TRANSFORMERS AND 6 FEEDERS | The 2024/25 winter projected load on McKinney South Substation Feeder 3614 is 121% of this feeder's 27 MVA maximum continuous rating. In addition, the 2024/25 winter projected load on McKinney South Substation is 78 MVA which is 133% of this two-transformer substation's 58.4 MVA backstand rating. Oncor has also received a signed FEA to provide 70 MW of service to Customer B near Allen North Substation. Allen North Substation is built out with (4) transformers and does not have capacity to serve this added load. This added load by the customer will result in the 2024 winter projected load on Allen North Bank #1 to be 125% of the 46.7 MVA nameplate rating for this transformer. In addition, the total 2024 winter projected load at Allen North Substation will be 117% of the 156 MVA backstand rating. In order to correct these loading conditions and provide the customer's requested service, it is proposed to establish Ridgeview substation with (3) 138/25 kV 47 MVA transformer with (6) feeder breakers and construct the necessary distribution in order to transfer load from McKinney South Substation and MKNSO3614, as well as connect to the customer load to the new substation. The completion of this work will correct the loading conditions identified above. | 2019: -3.95% 2020: -12.46% 2021: 5.74% 2022: 12.46% 2023: 40.57% | 2024: 29.20% | 110 MW | 2024: 19.6 MW | Residential Commercial | Customer B
4 | 0PT50975 -- TEN MILE SUB (FORMERLY GREENE SUB): ESTABLISH STATION WITH TWO TRANSFORMERS | The 2024/25 winter projected load on Reindeer Substation Feeder 2403 is 95% of the 29.5 MVA max continuous rating. In addition, the 2024 summer projected load on Millers Ferry Road Bank #3 is 96% of the 46.7 MVA nameplate rating. The 2024/25 winter projected load on Red Oak Substation is 129% of the 58.75 MVA substation backstand rating. In order to correct these conditions, it is proposed to establish Ten Mile Substation with two 138/25 kV 47 MVA transformers and four feeder breakers and construct the necessary distribution to transfer loads to these new transformers. The completion of this work will correct the loading conditions identified above. | 2019: 13.30% 2020: -13.99% 2021: 16.54% 2022: 2.39% 2023: 40.89% | 2024: 30.48% | 26.0 MW | 2024: 10.6 MW | Commercial Industrial | Not Applicable
5 | 0PT50973 -- GRAIN BELT (FKA MASCH BRANCH SUB): ESTABLISH STATION WITH ONE TRANSFORMER | The 2024/25 winter projected load on Krum Substation Feeder 1203 is 95% of the 13.5 MVA max continuous rating for this feeder. In addition, the 2024/25 winter projected load on Krum Substation is 129% of the 29.1 MVA backstand rating for this substation. In order to correct the loading conditions, it is proposed to establish Masch Branch Substation with (1) 47 MVA 138/12.5 kV transformer with (2) feeder breakers and construct the necessary distribution facilities to transfer load from Krum Feeder 1203 and Krum Substation to the new substation. The completion of this work will correct the loading conditions identified above. | 2019: -3.12% 2020: -10.84% 2021: 40.76% 2022: -10.33% 2023: 35.76% | 2024: 32.11% | 16.0 MW | 2024: 6.7 MW | Residential Commercial Industrial | Not Applicable
6 | 0PT50967 -- HOWE SUB (FORMERLY SHERMAN SOUTH SUB): ESTABLISH STATION WITH TWO TRANSFORMERS | The 2024 summer projected peak load on the Sherman South Substation Transformer #1 is 30.2MVA which is 121% of the 25.0 MVA nameplate rating for this transformer. In addition, the 2024 summer projected peak load on the Sherman South Substation is 58.3 MVA which is 187% of the 31.3 MVA backstand rating for this substation. In order to correct these loading conditions, it is proposed to replace/relocate the Sherman South Sub with (2) 46.7 MVA 138-12.5 kV transformers and (6) feeder breakers at the newly established Howe Sub.The completion of this work will correct the loading conditions identified. To meet reliability objectives and provide adequate transmission capacity for contingency conditions, the Howe Substation is planned to be complete by 2024. | 2019: -0.74% 2020: 7.01% 2021: 5.90% 2022: -5.76% 2023: 1.36% | 2024: -4.20% | 58.3 MW | 2024: 44.8 MW | Residential Commercial Industrial | Not Applicable
7 | 0PT50817 -- LAZY RANCH SUB (FKA MUSTANG SPRINGS SUB) : ESTABLISH STATION WITH TWO 138-25 KV TRANSFORMERS | With the added load of 20 MW by Customer A, the 2024 projected load on Glass Ranch Bank #1 is 67.4 MVA which is 120 percent of the 56 MVA nameplate rating for this transformer. In addition, the 2024 projected load on Glass Ranch Substation is 167 percent of the 70 MVA substation backstand rating. In order to correct this problem, it is recommended to establish Lazy Ranch Substation adjacent to Glass Ranch Substation with Bank #1 with a 138-25 kV, 47 MVA transformer and install two feeder breakers. It is also recommended to construct various distribution facilities in order to serve Customer A's load and balance substation loading.The completion of this work will correct the transformer and backstand overloads that have been identified due to the added load of Customer A. Additionally, the 2024 Summer projected load on Sale Ranch Bank #1 is 56.1 MVA which is 100% of the 56 MVA nameplate rating. In addition, the 2024 Summer projected load on Glass Ranch Substation is 89 MVA which is 127% of the 70 MVA backstand rating for the substation. In order to resolve this overload, it is proposed to install Lazy Ranch Bank #2, 138-24.9 kV, 47 MVA transformer and two 25 kV feeder breakers and transfer load from Sale Ranch 2104 and Glass Ranch 2107 to the new Lazy Ranch Feeders. The completion of this work will resolve the overload on Sale Ranch Bank #1 and the backstand overload at Glass Ranch Substation. | 2019: 54.25% 2020: 16.44% 2021: 4.63% 2022: 52.56% 2023: -26.91% | 2024: 25.97% | 20.0 MW | 2024: 3.7 MW | Commercial | Customer A
8 | 0PT50814 -- CALF TANK SUB: ESTABLISH STATION WITH TWO TRANSFORMERS | The 2024 summer peak load on Natural Dam Bank #1 is 52.1MVA which is 112 percent of the reduced 46.7MVA nameplate rating for this substation transformer. Natural Dam Substation is a Sharyland single transformer substation. In order to correct the condition above, it is proposed to establish a new substation, Calf Tank Substation, immediately to the west of Natural Dam substation in existing right of way and install two 46.7MVA, 138-24.9kV transformers with 3-24.9 kV underground feeder breakers (two breakers on Bank #1 and one breaker on Bank #2). It is also recommended to construct various distribution facilities in order to transfer load from Natural Dam to Calf Tank. The completion of this work will correct the loading condition that has been identified. | 2019: 52.03% 2020: 65.52% 2021: 70.45% 2022: 34.11% 2023: 6.75% | 2024: 84.07% | 38.6 MW | 2024: 24.8 MW | Commercial | Not Applicable
9 | 0PT49790 -- BRONZE AGE SUB : ESTABLISH SUBSTATION WITH (1) 138/69-12.5 KV TRANSFORMER AND (2) 12.5 KV FEEDER BREAKERS | The need to expand Oncor facilities in the Waco and Temple areas is driven by load growth and the need to rebuild aging facilities. The aging facilities in the area limit system capacity. Rebuilding the 6.7-mile Eddy - Troy 69 kV Line Section will allow for the conversion of the 31.4-mile Peppervine Switch - Temple Line from 69 kV to 138 kV operation. This conversion, along with other transmission projects in the area, will improve power flow and voltage in the Waco area and increase operational flexibility. To meet reliability objectives and provide adequate transmission capacity for future load growth in the area, the existing Troy Substation will be replaced by the new Bronze Age Substation to accommodate converting the Peppervine Switch - Temple 69 kV Line to 138 kV. | 2019: -16.49% 2020: 1.34% 2021: -9.10% 2022: 32.41% 2023: 21.71% | 2024: 48.78% | 12.9 MW | 2024: 9.3 MW | Residential Commercial | Not Applicable
10 | 0PT49746 -- STEER SUB: ESTABLISH 138-12.5 KV STATION WITH TWO TRANSFORMERS | The 2024 summer projected load on Big Spring West Substation is 103% of the 25 MVA backstand rating for this substation. In addition, the 2024 summer projected load on Bis Spring Switch Substation is 102% of the 25 MVA backstand rating for this substation. In addition, the 2024 summer projected load on Big Spring Airpark Substation is 127% of the 28 MVA backstand rating for this substation In order to correct these loading conditions, it is proposed to decommission Big Spring West Substation and establish Steer Substation with (2) 47 MVA 138/12.5 kV transformers with (6) feeder breakers (2 overhead and 4 underground) and construct the necessary distribution facilities to transfer all load from Big Spring West Substation and transfer additional load from Big Spring Switch and Big Spring Airpark Substations to the new substation. The completion of this work will correct the loading conditions identified above. | 2019: 5.79% 2020: -10.08% 2021: -29.35% 2022: 20.90% 2023: 1.51% | 2024: -24.50% | 9.5 MW | 2024: 19.2 MW | Residential Commercial | Not Applicable
11 | 0PT48489 -- FLOYD BRANCH SUB (FKA CEDARDALE SUB): ESTABLISH 138-12.5 KV STATION WITH ONE 47 MVA TRANSFORMER & THREE FEEDER BREAKERS | The 2023/24 Winter load on Witt Substation feeder 1701 is 107% of the 13.5 MVA Max Cont Rating for this feeder. In addition, Witt Substation feeder 1705 is projected to be at 100% of its 13.5 MVA Max Cont Rating. In addition, Witt Substation feeder is projected to reach 97% of this feeder's 12.2 MVA Max Cont rating. Hutchins Substation is projected to reach 114% of the 35 MVA substation rating at this sub for Summer 2023. In order to correct these loading problems, it is proposed to Establish Floyd Branch Substation (1) 47 MVA 138/12 kV transformer and (3) feeder breakers and construct the necessary distribution facilities to transfer load from Witt Substation and Hutchins Substation to the proposed Floyd Branch Substation. The completion of this work will correct the loading issues identified above. | 2019: 2.19% 2020: -15.69% 2021: 35.25% 2022: 8.26% 2023: 21.11% | 2024: 19.06% | 23.2 MW | 2024: 10.0 MW | Residential Commercial Industrial | Not Applicable
12 | 0PT48249 -- GOODNIGHT SUB (FKA PECOS TRAIL SUB): ESTABLISH 138/24.9 KV STATION WITH ONE TRANSFORMER AND TWO OH FEEDERS | The 2023 projected summer load on Lonesome Draw Feeder 6623 is 28.2 MVA which is 108% of the 26.0 MVA maximum continuous rating for this feeder. In addition, the 2023 projected summer load on Upton Substation Transformer #1 is 27.4 MVA which is 97% of the 28 MVA nameplate rating for this transformer. Upton Substation is a single transformer substation with limited backstand. In order to resolve these conditions, it is proposed to establish the new Goodnight Substation with a 138/25 kV 47 MVA transformer and 2 OH feeder breakers and decommission Upton Substation. It is also recommended to construct various distribution facilities in order to transfer load to the new substation and to provide strong distribution ties between Lonesome Draw Substation and the new Goodnight Substation for substation backstand. Ensure phasing match between Goodnight, Lonesome Draw and Canal Rd.The completion of this work will resolve the loading conditions identified. | 2018: 22.59% 2019: -3.26% 2020: -4.25% 2021: 88.35% 2022: -15.22% | 2023: 69.98% 2024: -6.56% | 36.5 MW | 2023: 7.8 MW 2024: 15.3 MW | Commercial | Customer A
13 | 0PT47786 -- HARRIS CREEK SUB : ESTABLISH ONE 47 MVA 138-25 KV SUBSTATION, REPLACES FAILED MCGREGOR SUB | The 2022 winter projected peak load on McGregor Substation is 7.2MVA. On February 02, 2022, this substation caught fire and it has been decommissioned. The town of Oglesby has a single feed without backstand and the distribution source Oglesby Substation is old and obsolete and it is causing low voltage issues due to the regulators inside the substation being inoperative.In order to serve the load of McGregor Substation, it is proposed to establish Harris Creek Substation with a 47MVA 138/69-25kV transformer and two UG feeder breakers. In addition, it is recommended to construct various distribution facilities in order to transfer the load of McGregor Substation to the new Harris Creek Substation, provide a second feed to the town of Oglesby, and replace the distribution source Oglesby Substation .The completion of this plan item will replace McGregor Substation, provide a second feed to the town of Oglesby, and replace the distribution source Oglesby Substation. | 2017: 36.49% 2018: -32.61 % 2019: 52.61% 2020: 6.87% 2021: -34.83% | 2022: 0.18% 2023: 12.21% 2024: 32.81% | 7.2 MW | 2022: 0.2 MW 2023: 8.1 MW 2024: 10.8 MW | Residential Commercial | Not Applicable
14 | 0PT47407 -- RENDON SUB: ESTABLISH STATION | The 2023 Winter projected load on Burleson Substation is 123% of the 58.4 MVA substation rating. In addition, Kennedale Bank #2 is loaded to 95% of the 46.7 MVA nameplate rating. Mansfield feeder 6282 has limited backstand capability in the event of a feeder outage. It is proposed to establish Rendon Substation with (2) 47 MVA transformers and (4) 25 kV feeder breakers and construct the necessary distribution facilities with DA to transfer load from Kennedale, Mansfield and Burleson Substations to the new substation. The completion of this work will resolve the conditions identified above. | 2019: 6.21% 2020: -10.99% 2021: 31.60% 2022: -9.92% 2023: 7.69% | 2024: 13.16% | 34.8 MW | 2024: 2.8MW | Residential Commercial Industrial | Not Applicable
15 | 0PT47405 -- CASTLEMAN SUB (FKA SOUTH HEWITT SUB): ESTABLISH STATION | The 2023 winter projected peak load on Waco Atco Feeder 2605 is 29.2 MVA which is 100% of the maximum continuous rating for this feeder. In addition, the 2023 winter projected peak load on Waco Atco Transformer #2 is 45.2 MVA which is 97% of the 46.7 MVA nameplate rating for this transformer. Also, the 2023 winter projected peak load on Waco Atco Substation is 72.4 MVA which is 124% of the 58.4 MVA rating for this substation. Robinson Northwest Feeder 1503 has limited backstand. In order to correct the loading conditions, it is proposed to establish Castleman Substation with a 46.7 MVA 138/69-24.9kV transformer and two underground feeder breakers. In addition, it is proposed to construct the necessary distribution in order to transfer loads to the new substation. The completion of this work will correct the loading concerns identified above. | 2019: -19.04% 2020: 2.71% 2021: 23.54% 2022: -4.04% 2023: 16.20% | 2024: -0.53% | 15.2 MW | 2024: 19.8 MW | Residential | Not Applicable
16 | 0PT47403 -- VANGUARD SUB (FORMERLY MESQUITE LUCAS SUB): ESTABLISH 138/12.5 KV STATION | The 2024/25 Winter projected load on Balch Springs Substation is 127% of the 35 MVA substation rating. At this loading, Balch Springs Bank #2 is projected to reach 99% of the 28 MVA nameplate rating. In addition to these loading conditions, Balch Springs Substation is fed by a radial 138 kV tap. This 138 kV configuration exposes both transformers to an outage in the event of a single transmission contingency, this would place the entire substation out until repairs are made. In order to address the loading conditions above and the single-contingency 138 kV issue, it is proposed to establish a new substation with (2) 138/12 kV 47 MVA transformers and (5) 12 kV feeders and construct the necessary distribution facilities to transfer load from Balch Springs Sub to the new Vanguard Substation. The completion of this work will correct the loading conditions on Balch Springs Substation as well as provide emergency switching to backstand the remaining load out of Balch Springs during a single-contingency event. | 2019: -14.00% 2020: -8.86% 2021: 6.09% 2022: 3.74% 2023: 34.87% | 2024: 1.16% | 34.6 MW | 2024: 5.5 MW | Residential Commercial | Not Applicable
17 | 0PT47361 -- TEMPLETON SUB: ESTABLISH SUBSTATION WITH ONE 28 MVA TRANSFORMER AND TWO FEEDER BREAKERS | The 2023/24 Winter projected load on Waxahachie Feeder 1202 is 102% of the 12.4 MVA max continuous rating. In addition, a radial section of feeder 1206 and feeder 1208 have no ties or backstand capability. In order to correct these loading conditions, it is proposed to establish Templeton Substation with (1) 28 MVA transformer and (2) 12 kV Feeders and construct the necessary distribution facilities to transfer load to the new station. The completion of this work will correct the loading and backstand conditions identified above. | 2018: 143.58% 2019: -10.86% 2020: -8.27% 2021: 24.66% 2022: 9.71% | 2023: 90.07% 2024: 18.83% | 10.5 MW | 2023: 11.2 MW 2024: 10.9 MW | Residential Commercial | Not Applicable
18 | 0PT47356 -- RUNAWAY BAY SUB: ESTABLISH WITH ONE 138-12.5 KV TRANSFORMER AND TWO FEEDER BREAKERS | The 2023 winter projected load on Balsora Substation Transformer #1 is 11.4 MVA which is 109% of the 10.5 nameplate rating for this transformer. Balsora Substation is a single transformer substation with limited backstand. In addition, the town of Runaway Bay (6.0MVA) has limited backstand. In order to correct these backstand conditions, it is proposed to establish Runaway Bay Substation with (1) 28.0MVA 138-12.5kV transformer and (2) UG feeder breakers and decommission Balsora Substatiion. It is also recommended to construct various distribution facilities in order to transfer load to the new substation. The completion of this work will resolve the loading conditions identified and provide backstand to the town of Runaway Bay. | 2019: 4.73% 2020: -4.62% 2021: 9.85% 2022: -34.80% 2023: 25.75% | 2024: 17.64% | 10.0 MW | 2024: 4.2 MW | Residential | Not Applicable
19 | 0PT47355 -- CIRCLE POINT SUB: ESTABLISH STATION | The 2024 summer projected peak load on Bellmead Substation is 38.0MVA which is 109% of the 35.0 MVA capacity rating for this substation. In addition, Bellmead Feeders 1617 and 1620 has limited backstand. Also China Spring Feeder 2412 has limited backstand.In order to correct these loading conditions, it is proposed to establish Circle Point Substation with a 28MVA 138-12.5kV transformer and two overhead feeder breakers. In addition, it is proposed to construct the necessary distribution in order to transfer loads to the new substation. The completion of this work will correct the loading concerns identified above. | 2019: 58.07% 2020: -27.64% 2021: 1.51% 2022: 3.46% 2023: 4.51% | 2024: 0.63% | 10.3 MW | 2024: 1.1 MW | Residential Commercial | Not Applicable
20 | 0PT47350 -- VINCENT SUB (FKA GETTY VEALMOOR SUB): ESTABLISH STATION WITH A 138-25 KV 46.4 MVA TRANSFORMER AND TWO FEEDER BREAKERS | The 2023 projected summer load on Getty Vealmoor Transformer #1 (single transformer sub) is 12.7 MVA which is 121% of the 10.5 MVA nameplate rating for this transformer. In addition, the 2023 projected summer load on Luther Feeder 2104 is 20.1 MVA which is 159% of the 12.65 MVA backstand rating for this feeder. In order to resolve these overload conditions, it is proposed to establish Vincent Substation with a 138-25kV 46.7 MVA transformer and two feeder breakers and decommission Getty Vealmoor Substation. It is also recommended to construct various distribution facilities in order to transfer load to the Vincent Substation. The completion of this work will resolve the loading conditions identified and will decommission Getty Vealmoor Substation. | 2018: 7.14% 2019: 214.71% 2020: 60.64% 2021: 18.02% 2022: -27.85% | 2023: 54.39% 2024: -17.21% | 16.5 MW | 2023: 2.8 MW 2024: 2.7 MW | Commercial | Not Applicable
21 | 0PT47255 -- STARR RANCH SUB (NORMAN CROSSING): ESTABLISH 138/24.9 KV STATION | The 2023 winter projected loads on Pflugerville Feeder 2003 and Round Rock SE Feeder 2601 are 30.2MVA and 26.6MVA which are 122% and 104% of the 24.8MVA maximum continuous rating, respectively. In addition, the 2023 winter projected loads on Pflugerville Transformer #1 and Round Rock Southeast Transformer #1 are 43.8MVA and 42.7MVA which are 94% and 91% of the 46.7MVA nameplate rating, respectively. In order to correct these load problems, it is proposed to establish Star Ranch Substation with a 46.7 MVA 138-24.9kV transformer and (2) UG feeder breakers. In addition, it is recommended to construct various distribution facilities in order to transfer loads to this new substation. The completion of this work will correct the overloads identified on the Pflugerville and Round Rock Southeast Substations. | 2018: 16.75% 2019: -10.33% 2020: -9.03% 2021: 52.17% 2022: -22.14% | 2023: 61.50% 2024: -15.88% | 34.1 MW | 2023: 29.8 MW 2024: 30.1 MW | Residential Commercial | Not Applicable
22 | 0PT47225 -- NEWTON BRANCH SUB: ESTABLISH STATION WITH A 47 MVA 138-13.2 KV TRANSFORMER AND TWO FEEDERS FOR TXI OPERATIONS DBA MARTIN MARIETTA | Oncor Electric Delivery and Customer C have signed a Facility Extension Agreement (FEA) in which Customer C has requested Oncor to provide two 13.2 kV PODs to serve their rock crushing facilities for approximately 11.55 MW. To accommodate the customer's request, it is proposed to establish the Newton Branch Substation in Ellis County, Texas on the Kemp Ranch Switch Sardis Switch (BEPC) 138 kV Line. | 2019: 49.12% 2020: 2.86% 2021: -2.83% 2022: -24.87% 2023: 37.14% | 2024: 24.18% | 22.0 MW | 2024: 12.6 MW | Industrial | Customer C
23 | 0PT47142 -- ROSENTHAL SUB: ESTABLISH 28 MVA 138X69-26.4X13.2 KV TRANSFORMER WITH TWO FEEDER BREAKERS AND ONE TIE BREAKER. | The need to expand Oncor facilities in Southeast Texas is driven by load growth and the need to rebuild aging facilities. The aging facilities in the area limit system capacity. Rebuilding the 6.7-mile Eddy - Troy 69 kV Line Section will allow for the conversion of the 31.4-mile Waco West Switch - Temple Line from 69 kV to 138 kV operation. This conversion, along with other transmission projects in the area, will improve power flow and voltage in the Waco area and increase operational flexibility. In order to operate at this new voltage, it is proposed to establish the Rosenthal Subwith a 28 MVA 138x69-26.4x13.2 kV transformer and two underground feeder breakers. This station will replace the Lorena Substation. In addition, it is proposed to construct the necessary distribution in order to transfer loads to the new substation. | 2019: 0.20% 2020: -9.90% 2021: 11.79% 2022: 3.43% 2023: 8.48% | 2024: -13.14% | 7.2 MW | 2024: 6.8 MW | Residential Commercial | Not Applicable
24 | 0PT46981 -- NAVIGATION SUB : ESTABLISH SUBSTATION WITH ONE 47 MVA TRANSFORMER AND TWO 25 KV FEEDER BREAKERS TARGA'S PS4 | Customer A has requested 13.5 MW service from Saltmine Substation. In order to satisfy this request, it is proposed to build Navigation Substation with a 138-21.6 kV, 47 MVA transformer and two 21.6 kV feeder breakers with 3-795 AAC feeder exits. It is also recommended to construct various distribution facilities in order to serve the 13.5 MW load. The completion of this work will resolve the customer's request. | 2019: -8.00 % 2020: 41.30% 2021: -10.46% 2022: -0.69% 2023: 745.18% | 2024: 56.35% | 13.0 MW | 2023: 8.8 MW 2024: 10.2 MW | Commercial | Customer A
25 | 0PT46414 -- ROSEDALE SUB : (FORMERLY KNOWN AS RANSOM TERRACE SUB) ESTABLISH SUBSTATION WITH TWO 138-12.5 KV 47 MVA TRANSFORMERS | This project is mostly driven by aged infrastructure which is no longer supported by the manufacturer and has reached the end of its serviceable life. To improve operational reliability and flexibility of the system there is an urgent need to replace this aging infrastructure. The replacement of the current 69 kV system with the 138 kV system would provide additional power flow capacity for the future, leading to more operational system flexibility and also increasing the reliability by installing modern equipment and updated design standards. This 69 kV to 138 kV conversion moves Oncor closer to modernizing and upgrading the system to 138 kV and completing the elimination of our aging 69 kV system. Handley Switch currently feeds this 69 kV line via a 138/69 kV Autotransformer. The removal of this autotransformer would remove a 12.5 kV tertiary load feeding the Exelon Generator #3 startup transformer. In order to meet the required loading criteria for this generator startup transformer, it is necessary to repurpose the Handley Transformer #3 and move the six existing Handley 12.5 kV feeders to the new Rosedale Substation. The new Rosedale Substation will be built in the footprint of the newly demolished Handley 69 kV Switch yard and will allow Oncor to fully complete the conversion of operating the Marrs Switch - Handley Switch line at 138 kV. Oncor has performed the appropriate analyses to evaluate the potential impacts to the ERCOT system as a result of the proposed project. | 2019: -14.38% 2020: -1.56% 2021: -3.30% 2022: 7.37% 2023: 1.07% | 2024: -18.91% | 60.2 MW | 2024: 21.2 MW | Residential Commercial Industrial | Not Applicable
26 | 0PT46413 -- MOUNTAIN BRANCH SUB : ESTABLISH (1) 47 MVA 138-12.5KV & (1) 28MVA 138-12.5KV TRANSFORMER AND THREE 12.5KV FEEDERS | Leon EBAA has a single 69-12.5 kV, 28 MVA transformer. It serves 4 MVA of local residential/commercial load and 15+ MVA arc furnace load. During arc furnace operating hours the voltage swings cause numerous LTC operations and undesirable power quality to both the arc furnace load and local residential/commercial load. The LTC on this station has failed in the past and requires additional maintenance in order to be kept in service. TD Planning would like to transfer the 15+ MVA arc furnace load at Leon EBAA to the 138kV system by connecting to the Leon Switch Putnam 138 kV Line. This will help by reducing load on the 69kV system and putting the arc furnace load on the stronger 138 kV source. It is proposed to install a 138-12.5kV, 47 MVA transformer with (2) breakers and a 138-12.5kV, 28 MVA transformer with (1) breaker and connect them to the 138 kV Line. Split the load such that the arc furnace load will be on the 47 MVA with the LTC parameters set to help minimize unnecessary operations, and the other Oncor load on the 28 MVA transformer. This will alleviate power quality issues, provide some back stand capabilities and reduce the loading on the 69kV system in the area. | 2018: 0.53% 2019: -1.00% 2020: -8.48% 2021: -2.41% 2022: 0.38% | 2023: -5.86% 2024: 2.72% | 22.4 MW | 2023: 18.5 MW 2024: 19.1 MW | Residential Commercial Industrial | Not Applicable
27 | 0PT46242 -- ESTABLISH DRY FORK SUB : ESTABLISH TWO 138-12.5 KV, 28 MVA TRANSFORMERS AND THREE FEEDER BREAKERS | The 2022 summer projected load on Henrietta is 11.0 MVA which is a single transformer substation with limited backstand. Transmission Engineering is converting the 69 kV line to 138 kV that serves Henrietta and Henrietta West Substations. In order to correct these backstand loading condition and allow the conversion of the 69 kV line to 138 kV, it is proposed to establish Dry Fork Substation with two (2) 138-12.5 kV 28.0 MVA transformers and three (3) UG feeder breakers (two (2) on bank #1 and one (1) on bank #2). In addition, it is proposed to decommission Henrietta and Henrietta West Substations. It is also recommended to construct various distribution facilities in order to transfer load to the new substation. The completion of this work will resolve the loading condition identified, decommission Henrietta and Henrietta West Substations, and allow the conversion of the 69 kV line to 138 kV. | 2019: -1.76% 2020: 5.59% 2021: -7.93% 2022: 2.80% 2023: 4.27% | 2024: -4.53% | 12.0 MW | 2024: 11.0 MW | Residential Commercial | Not Applicable
28 | 0PT45123 -- ROSEMONT SUB : ESTABLISH STATION WITH A DOUBLE TAP ARRANGEMENT WITH TWO 47 MVA TRANSFORMERS AND EIGHT LV CIRCUIT BREAKERS. | The Pafford Substation is being relocated to another location. Pafford Substation in surrounded by Railroad Tracks which makes it unable to bring in a mobile transformer for the loss of one of the transformers. In addition, the projected 2022 summer load on Pafford Substation is 66.3 MVA which is 114% of the 58.4 MVA backstand rating. It is proposed to install two 138-12.5 kV 46.7 MVA and eight new outdoor feeder breakers at the new location. The plan item also replaces nine old switchgear feeder breakers with eight new outdoor feeder breakers. In addition, it is recommended to construct various distribution facilities in order to transfer loads to the new substation. The completion of this plan item will allow for a mobile transformer to be installed for the loss of one of the transformers and resolve the backstand loading at Pafford Substation by balancing the load between the two new substation transformers. | 2018: -5.15% 2019: 8.79% 2020: 0.29% 2021: -6.83% 2022: 3.52% | 2023: 14.06% 2024: 8.66% | 58.8 MW | 2023: 21.3 MW 2024: 34.1 MW | Residential Commercial | Not Applicable
29 | 0PT42146 -- IVY LEAGUE SUB (PRINCETON EAST) : ESTABLISH WITH ONE 47 MVA 138-24.9 KV TRANSFORMER AND TWO 25 KV UG FEEDER BREAKERS | Due to the length and exposure associated with the existing feeders serving the Princeton Peninsula, reliability to the area south of Princeton has experienced an elevated number of distribution events. The 2024/25 winter projected load on MKNNY 1251 Feeder is 111% of this feeders 26.9 MVA max continuous rating. McKinney SW Substation Feeder 2601 is projected to have 136% of this feeders 27 MVA feeder rating. In order to correct these loading and exposure conditions, it is proposed to establish Ivy League Substation with 1-47 MVA 138-25 kV transformer and 2-25 kV UG feeder breakers. It is also recommended to construct various distribution facilities in order to transfer load to the new Ivy League Substation. The completion of this work will resolve the conditions identified above. | 2019: -10.55% 2020: -10.52% 2021: 7.13% 2022: 32.20% 2023: -6.73% | 2024: 22.49% | 30.8 MW | 2024: 23.8 MW | Residential Commercial | Not Applicable
30 | 0PT44443 -- BLAIN (FORMERLY KNOWN AS DEW) SUB : ESTABLISH SUBSTATION WITH ONE 47 MVA TRANSFORMER AND TWO 25 KV FEEDER BREAKERS | Teague Main Substation has received a 7.5 MW distribution service request from Customer A. The 2022 projected winter load at Teague Main Substation with this request is 29.9 MVA which is 107% of the transformer nameplate rating of 28 MVA. Teague Main Substation is a single transformer substation with limited backstand capability. It is expected that this 7.5 MW request will grow to 17.0 MW in the near future. In order to correct this problem it is proposed to establish Blain Substation with (1) 47 MVA 138-25 kV transformer, (2) 25 kV feeder breakers, and (2) overhead feeder exits. Customer A will receive (1) 25 kV feeder to their facility. The completion of this work will satisfy the customer's request for service and greatly improve reliability in the area. | 2017: -19.78% 2018: 8.90% 2019: -13.82% 2020: 20.80% 2021: 3.81% | 2022: 0.34% 2023: 50.77% 2024: 13.82% | 17.0 MW | 2022: 0.1 MW 2023: 5.9 MW 2024: 10.3 MW | Residential Commercial | Customer A
31 | 0PT44103 -- FLAT IRON (FORMERLY TARGA PARKS PLT) SUB : ESTABLISH THREE 138-25 KV 46.7 MVA TRANSFORMERS WITH SIX FEEDER BREAKERS FOR POD, TARGA PIPELINE MID-CONTINENT WESTTEX LLC | With the added load of 60 MW of Customer AM Plant, the 2022 projected load on Salt Flat Feeder 2103 is 78.2 MVA which is 309 percent of the 25.3 MVA maximum continuous rating for this feeder. In addition, the 2022 projected load on Salt Flat Substation Transformer #2 is 93.6 MVA which is 167 percent of the 56 MVA nameplate rating for this transformer. Also, the 2022 projected load on Salt Flat Substation is 110.7 MVA which is 190 percent of the backstand rating for this substation. Salt Flat Feeder 2102, Canal Rd Feeder 2101, and Canal Rd Feeder 2102 do not have adequate backstand during failures of these feeders.In order to correct this problem, it is recommended to establish West County Rd 320 Substation with three 138-24.9 kV 46.7 MVA transformers and six feeder breakers. It is also recommended to construct various distribution facilities in order to transfer loads to the new substation and to provide adequate backstand to Salt Flat Feeder 2102, Canal Rd Feeder 2101, and Canal Rd Feeder 2102.The completion of this work will correct the overloads that have been identified due to the added load of Customer AM Plant and will correct the feeder backstand problems that have been identified. | 2017: 30.06% 2018: -7.71% 2019: 60.39% 2020: 3.96% 2021: 34.39% | 2022: 25.55% 2023: 61.71% 2024: 1.20%` | 60.0 MW | 2022: 43.5 MW 2023: 95.00 MW 2024:112.0 MW | Commercial | Customer A
32 | 0PT44337 -- FROW SUB: ESTABLISH SUBSTATION WITH 1 – 28 MVA TRANSFORMER AND 2 – 12.5 KV FEEDER BREAKERS | The 69 kV transmission line that serves Waco Katy Substation is planned to be converted to 138 kV on a transmission RSCO project. In addition, the projected 2023 summer peak load on Bellmead Substation is 42.3 MVA which is 121% of the 35 MVA backstand rating for this substation. This project will be constructed in the fall of 2023. It is proposed to establish Frow Substation with a 138/69 - 12.5 kV 28 MVA transformer and 2 - UG 12.5 kV feeder breakers and decommission Waco Katy Substation. In addition, it is recommended to construct various distribution facilities in order to transfer loads from Waco East Substation, Bellmead Substation, and Waco Katy Substation to the new substation, respectively. The completion of this plan item will allow for the conversion of the 69 kV transmission line to 138 kV that serves Waco Katy and correct the backstand overload at Bellmead Substation. | 2019: 18.02% 2020: -12.98% 2021: 1.58% 2022: 10.83% 2023: 5.14% | 2024: 2.76% | 14.6 MW | 2024: 9.3 MW | Residential Commercial Industrial | Not Applicable
33 | 0PT44317 -- PECAN TREE SUB: ESTABLISH 138-13.2 KV SUBSTATION AND INSTALL ONE 138-13.2 KV TRANSFORMER WITH THREE 15 KV FEEDER BREAKERS | Transmission is de-energizing the 69kV line from Blackwell to Holliday due to its age and reliability issues in the Fall of 2022. Blackwell and Holliday Substations will need to be decommissioned. In order to do this, it is proposed to establish Pecan Tree Substation with (1) 138-12.5 kV 28MVA transformer and (3) UG feeder breakers. It is also recommended to construct various distribution facilities in order to transfer loads to the new substation. Once the new substation is installed with various distribution facilities, the existing Blackwell and Holliday Substations can be decommissioned. The completion of this work will allow for the 69kV transmission line from Holliday Substation to Blackwell Substation to be de-energize. | 2018: 6.60% 2019: -0.50% 2020: 2.38% 2021: -7.53% 2022: 13.59% | 2023: 15.75% 2024: 12.43% | 9.7 MW | 2023: 14.0 MW 2024: 15.7 MW | Residential Commercial | Not Applicable
34 | 0PT44313 -- SHORT GRASS (FORMERLY ARCHER CITY) SUB: ESTABLISH NEW 138-12.5 KV SUBSTATION | This project is driven by aged infrastructure as the Holliday - Navy Kickapoo Switch line equipment has reached the end of its serviceable life. To improve operational reliability and flexibility of the system there is a need to replace this aging infrastructure and will allow the de-energization of the Holliday - Navy Kickapoo 69 kV Line. The replacement of the current 69 kV system with the 138 kV system would provide additional power flow capacity for the future, leading to more operational system flexibility and also increasing the reliability by installing modern equipment and updated design standards. Establishing the Short Grass Substation on the Bowman Switch - Graham Switch 138 kV line moves Oncor closer to modernizing and upgrading the system to 138 kV and completing the elimination of the aging 69 kV system. Oncor has performed the appropriate analyses to evaluate the potential impacts to the ERCOT system as a result of the proposed project. | 2017: -5.45% 2018: 12.36% 2019: -14.24% 2020: -39.71% 2021: 54.19% | 2022: 37.63% 2023: -23.76% 2024: -13.19% | 5.6 MW | 2022: 1.0 MW 2023: 1.5 MW 2024: 4.6 MW | Residential Commercial | Not Applicable
35 | 0PT44276 -- PINKNEY SUB: ESTABLISH NEW 138/12.5 KV SUBSTATION | This project, along with the Proctor 69 kV Substation conversion to 138 kV, allows the de-energization of 47 miles of the Brownwood - Dublin 69 kV Line, which is #1 CU conductor on single wood-pole structures, and allows the removal of all 69 kV transmission equipment at Brownwood. The replacement of the current 69 kV system with the 138 kV system would provide additional power flow capacity for the future, leading to more operational system flexibility and also increasing the reliability by installing modern equipment and updated design standards. This 69 kV to 138 kV conversion moves Oncor closer to modernizing and upgrading the system to 138 kV and completing the elimination of our aging 69 kV system. Oncor has performed the appropriate analyses to evaluate the potential impacts to the ERCOT system as a result of the proposed project. | 2017: 12.23% 2018: -13.69% 2019: -8.27% 2020: 10.23% 2021: -15.40% | 2022: 12.76% 2023: 13.19% 2024: 0.74% | 1.2 MW | 2022: 0.1 MW 2023: 1.0 MW 2024: 1.1 MW | Residential Commercial | Not Applicable
36 | 0PT44264 -- BATTLEGROUND (FORMERLY KNOWN AS COUPLAND) SUB : ESTABLISH A 138 KV SUBSTATION WITH ONE 28 MVA, 138-13.2 KV TRANSFORMER | The existing Coupland substation is a wood structure, three single-phase transformers station. This project, along with the relocation of the Elgin Switch 138/69 kV Autotransformer to Taylor Switch and the upgrade of the Brushy Creek - Taylor Switch 138 kV Line (R6153), allows the de-energization of the 11-mile Elgin Switch - Taylor Switch 69 kV Line and the removal of all 69 kV transmission equipment at Elgin Switch. | 2017: 19.48% 2018: 11.74% 2019: 11.43% 2020: 21.11% 2021: 12.53% | 2022: 69.17% 2023: -66.09% 2024: 77.10% | 8.4 MW | 2022: 6.0 MW 2023: 2.9 MW 2024: 9.2 MW | Residential Commercial | Not Applicable
37 | 0PT44259 -- PADERA SUB : ESTABLISH WITH TWO 47 MVA TRANSFORMERS AND FOUR 12.5 KV BREAKERS | The 2022 summer projected load on Midlothian North Bank #2 is 27.6 MVA which is 99% of the 28 MVA nameplate rating for this station. Midlothian North Substation is a single transformer substation with a limited and no nearby back stand solution. In addition, the proximity of this station to a nearby industrial facility has caused operation and maintenance issues. It is proposed to replace the single bank 28 MVA transformer at Midlothian North Substation by establishing Padera Substationwith two 138/12.5 kV 47 MVA transformers and four 12.5 kV feeder breakers. The existing distribution facilities will be upgraded to transfer all load from Midlothian North Substation to the new Padera Substation. The completion of this work will correct the loading and operational concerns mentioned above. | 2018; 16.25% 2019: -2.02% 2020: 5.89% 2021: -20.91% 2022: 9.88% | 2023: 38.37% 2024: -0.12% | 27.6 MW | 2023: 7.4 MW 2024: 30.2 MW | Residential Commercial | Not Applicable
38 | 0PT44256 -- CHARCA SUB (FORMERLY NOLAN CREEK SUB) : ESTABLISH WITH ONE 47 MVA 138-25 KV TRANSFORMER, TWO FEEDER BREAKER AND RELAY UPGRADE ON FEEDER 5511 FOR DA | The 2023/24 projected winter load on Godley Substation is 10.8 MVA which is 103% of the 10.5 MVA nameplate rating for this substation transformer. Godley Substation is a single transformer substation with weak distribution ties that it cannot be picked up by other substations during failure. In order to resolve these conditions, it is proposed to establish the new Charca Substation with a 138/25 kV 47 MVA transformer with 2 UG feeder exits. It is also recommended to construct various distribution facilities with DA in order to transfer load to the new substation and to provide strong distribution ties between Godley Substation and the new Charca Substation for substation backstand. The completion of this work will resolve the loading conditions identified. | 2019: -27.99% 2020: -3.58% 2021: 15.77% 2022: -14.71% 2023: 18.95% | 2024: 14.53% | 15.5 MW | 2024: 4.6 MW | Residential Commercial | Not Applicable
39 | 0PT44255 -- WILSHIRE SUB (FORMERLY BURLESON SOUTHWEST SUB) : ESTABLISH WITH ONE 47 MVA 138/25 KV TRANSFORMER AND TWO FEEDER BREAKERS | The 2023/24 projected winter load on Crowley Substation Feeder 7012 is 25.4 MW which is 102 percent of the 24.8 MW maximum continuous rating for this feeder. The 2023/24 projected winter load on Crowley Substation Banks #1 and #2 is 71.7 MW which is 123 percent of the 58.4 MW substation rating for these transformers. The 2023/24 projected winter load on Burleson Substation Banks #1 and #2 is 69.2 MW which is 119 percent of the 58.4 MW substation rating for these transformers. The 2023/24 projected winter load on Joshua Substation Banks #1 and #2 is 13.9 MW which is 106 percent of the 13.1 MW substation rating for these transformers. In order to correct these conditions. It is proposed to establish Wilshire Sub with one 138-24.9 kV 47 MVA Transformer and two Feeder Breakers with 1000 CU feeder exits and build the necessary distribution facilities with DA to transfer load from all the substations listed above to the new substation. The completion of this work will correct the conditions listed above. | 2019: 0.34% 2020: -18.80% 2021: 67.84% 2022: -21.86% 2023: 24.90% | 2024: -4.53% | 26.9 MW | 2024: 28.6 MW | Residential Commercial | Not Applicable
40 | 0PT44245 -- HORSEMAN SUB (FORMERLY SAGINAW SE SUB) : ESTABLISH TWO 47 MVA TRANSFORMERS AND FOUR BREAKERS | The 2022 Summer Projected load on Blue Mound Sub Feeder 3213 is 101% of this feeder's 29.4 MVA max cont rating. In addition, the single 25 kV transformer at Blue Mound Sub is projected to be loaded to 97% of it's 46.7 MVA nameplate rating. In order to correct the loading out of Blue Mound and provide substation backstand to the 25 kV load out of Blue Mound, it is proposed to establish Horseman Sub with (2) 47 MVA transformers w/ (4) breakers, and perform distribution upgrades to transfer 100% of the load from Blue Mound Sub to the new substation. It is also proposed to decomission Blue Mound Substation Bank #3. The completion of this plan item will correct the overloads and operational limitations listed above. | 2018: 4.27% 2019: 8.25% 2020: 0.68% 2021: 0.95% 2022: 0.91% | 2023: 0.21% 2024: -15.85% | 56.0 MW | 2023: 5.2 MW 2024: 25.9 MW | Residential Commercial | Not Applicable
41 | 0PT44242 -- SABANA SUB : (FORMERLY KNOWN AS PROCTOR SUB) ESTABLISH STATION WITH A 138-12.5 KV 10.5 MVA TRANSFORMER WITH TWO FEEDER BREAKERS | The Proctor substation is being converted from 69 kV to 138 kV operation.In order to do this, it is proposed to establish a new substation near the Proctor substation with (1) 28 MVA 138 /12.5 kV transformer and (2) feeder breakers on the Stephenville - Comanche 138 kV Line. Once the new Sabana Substation is established, the existing Proctor Substation can be de-comissioned as well as 47 miles of the Brownwood - Dublin 69 kV transmission line. This allows for the removal of all 69 kV transmission equipment at Brownwood. | 2017: 3.53% 2018: 15.23% 2019: -21.10% 2020: -2.88% 2021: 18.15% | 2022: 8.93% 2023: 2.50% 2024: 12.20% | 2.0 MW | 2022: 2.0 MW 2023: 2.1 MW 2024: 2.3 MW | Residential Commercial | Not Applicable
42 | 0PT44232 -- APPLE SUB (FORMERLY PLEASANT FARMS SUB) : ESTABLISH STATION WITH ONE 47 MVA, 138/69 KV AND TWO FEEDER BREAKERS | The 2022 projected winter load on Edwards Feeder 5931 is 15.6 MVA which is 116% of the 13.4 MVA maximum continuous rating for this feeder. In addition, during backstand condition, the 2022 projected winter load on Pegasus South Feeder 7012 is 20.4 MVA which is 105% of the 19.4 MVA 24 hour emergency rating for this feeder. In order to resolve these problems, it is proposed to establish Apple Substation with a 138/69-12.5kV 47 MVA transformer with two OH feeder breakers. It is also recommended to construct various distribution facilities in order to transfer load to the new substation. The completion of this work will resolve the loading conditions identified. | 2017: 33.88% 2018: -10.87% 2019: 0.23% 2020: -13.07% 2021: 8.12% | 2022: -4.98% 2023: 52.32% 2024: -21.68% | 12.4 MW | 2022: 3.3 MW 2023: 11.4 MW 2024: 13.9 MW | Residential Commercial | Not Applicable
43 | 0PT44231 -- DOUBLE CREEK SUB (FORMERLY LOUIS HENNA SUB): ESTABLISH TWO 47 MVA 138-25 KV TRANSFORMERS AND FOUR 25 KV UG FEEDER BREAKERS | The 2023 projected summer load on Round Rock Southeast Feeders 2601, 2604, and 2607 are 31.9MVA, 26.9MVA, and 28.1MVA which are 118%, 100%, and 101% of the 27.0MVA, 27.0MVA, and 27.9MVA maximum continuous ratings for these feeders, respectively. In addition, the 2023 projected summer load on Round Rock Southeast Transformers #1, #2, and #3 are 47.4 MVA, 51.0MVA, and 45.6MVA which are 102%, 109%, and 98% of the 46.7 MVA nameplate ratings for these transformers, respectively. Also, the 2023 projected summer load on Round Rock Southeast Substation is 144.0MVA which is 123% of the backstand rating for this substation. In order to resolve these conditions, it is proposed to establish Double Creek Substation with two 138-24.9 kV 46.7 MVA transformers with four UG feeder breakers. It is also recommended to construct various distribution facilities with DA in order to transfer load to the new substation. The completion of this work will resolve the loading conditions identified. | 2018: 10.96% 2019: -9.67% 2020: 1.40% 2021: 1.25% 2022: 14.33% | 2023: 25.51% 2024: -19.56% | 50.2 MW | 2023: 42.8 MW 2024: 38.4 MW | Residential Commercial | Not Applicable
44 | 0PT44089 -- BEACON HILL SUB : ESTABLISH STATION WITH A 138/69-12.5KV 28MVA TRANSFORMER AND TWO FEEDER BREAKERS | With the added load of 10 MW of Customer D, the 2022 projected load on Flintkote Substation is 11.7 MW which is 468 percent of the 2.5 MVA nameplate rating of this transformer. In addition, the 2022 projected load on Eskota Switch Substation is 0.7 MW and this substation has a damage transformer and the load is being served by adjacent substation feeders in the area. In order to correct this problem, it is recommended to establish Beacon Hills Substation with (1) 138/69-12.5 kV 28 MVA transformer and two feeder breakers. In addition, it is recommended to decommission the distribution substation portion of Eskota Switch and Flintkote Substations. It is also recommended to construct various distribution facilities in order to transfer loads to the new feeder breakers. The completion of this work will correct the overload that have been identified due to the added load of Customer D and provide the decommissioning of the distribution substation portion of Estoka Switch and Flintkote Substations. | 2017: 2.39% 2018: 3.30% 2019: 0.08% 2020: 5.93% 2021: -13.08% | 2022: 10.34% 2023: 48.77% 2024: -4.23% | 13.0 MW | 2022: 0.3 MW 2023: 6.6 MW 2024: 6.9 MW | Residential Commercial Industrial | Customer D
45 | 0PT43970 -- LOY LAKE SUB : ESTABLISH WITH ONE 28 MVA 138-12.5 KV TRANSFORMER AND TWO UG FEEDER BREAKERS AND 3-18.4 MVAR 138 KV CAPACITORS | The 2022 projected summer load on Sherman Northwest Feeder 1612 is 15.5 MVA which is 115% of the 13.5 MVA maximum continuous rating for this feeder. In addition, the 2022 projected summer loads for Sherman Northwest and Denison Substations are 72.4 MVA and 38.8 MVA which are 124% and 111% of the 58.4 MVA and the 35.0 MVA backstand ratings, respectively for these substations. In order to resolve these conditions, it is proposed to establish Loy Lake Substation with a 138-12.5kV 28 MVA transformer with two feeder breakers. In addition, in 2022 the loss of Stone Creek Switch - Sherman Northwest 138 kV line section results in a voltage drop from 138 kV to 128 kV on the Stone Creek Switch - Valley Switch 138 kV line, which is outside the acceptable voltage limits. To meet reliability objectives and maintain voltage within acceptable operating limits under contingency, the installation of the 138 kV capacitor banks at Loy Lake Substation is planned to be complete by 2022. The completion of this work will resolve the loading and voltage conditions identified. | 2017: -8.32% 2018: 15.24% 2019: -6.18% 2020: 2.66% 2021: -2.37% | 2022: 10.73% 2023: -2.23% 2024: 3.00% | 10.8 MW | 2022: 1.5 MW 2023: 4.1 MW 2024: 8.0 MW | Residential Commercial | Not Applicable
46 | 0PT43226 -- TOWER ONE SUB: ESTABLISH NEW 138X69-12.5 KV SUBSTATION | Generation at the Jack County Generating Plant could vary from the base case. In 2022, after the loss of the Jack County Combined Cycle Train, the second contingency loss of the Wichita Falls South - Alvord 138 kV Line results in the Burnett Switch - Ringgold Magnolia Tap 69 kV Line loading to 103% of its emergency rating. To meet reliability objectives, relieve overloading and provide adequate transmission capacity for contingency conditions, the rebuild of the Burnett Switch - Ringgold Magnolia Tap 69 kV Line and establishing the new Tower One Sub is proposed. | 2018: 15.00% 2019: 17.39% 2020: -30.37% 2021: 103.76% 2022: 3.12% | 2023: -65.06% 2024: 44.93% | 0.4 MW | 2023: 0.1 MW 2024: 0.2 MW | Residential Commercial | Not Applicable
47 | 0PT42928 -- ANTLER HOLLOW SUB : ESTABLISH WITH TWO 47 MVA 138-12 KV TRANSFORMER AND THREE 12.5 KV BREAKERS | The 2022/23 winter projected load on Stephenville Substation Feeder 1203 is 13.7 MVA which is 102% of this feeder's 13.5MVA maximum continuous rating. The 2022/23 winter projected load on Stephenville Substation Feeder 1206 is 13.5 MVA which is 100% of this feeder's 13.5MVA maximum continuous rating. The 2022/23 winter projected load on Stephenville Substation Bank #3 is 28 MVA which is 100% of this transformer's 28MVA nameplate rating. This transformer has no backstand. Stephenville Substation is the only source to the town of Stephenville, Texas; of which serves as the home to Tarleton State University and the only hospital in Erath County. In order to resolve these overloads and diversify the sources into the town of Stephenville, it is proposed to establish Antler Hollow Substation with (2) 47 MVA 138/12 kV transformers and (3) 12.5 kV UG feeder breakers. In addition it is proposed to perform upgrades to the distribution system in order to transfer load from the existing Stephenville Substation to the new Antler Hollow Substation. The completion of this work will resolve the loading and operational issues mentioned above. | 2018: 9.56% 2019: -2.02% 2020: -9.12% 2021: 20.94% 2022: -3.91% | 2023: 23.48% 2024: -12.47% | 21.2 MW | 2023: 9.3 MW 2024: 9.9 MW | Residential Commercial | Not Applicable
48 | 0PT42594 -- INGLE SUB - ESTABLISH A NEW 138-25 KV SUBSTATION WITH TWO 28 MVA TRANSFORMERS TO REPLACE CADDO MILLS SUB | In 2021, the loss of the Royse Switch - Burrows POD 69 kV line section results in the Commerce - Royse Switch 69 kV Line loading to 103% of its emergency rating and a greater than 10% voltage drop on the Commerce - Royse Switch 69 kV Line. To meet reliability objectives, it is proposed to rebuild the 38.2-mile Royse Switch - Commerce 69 kV Line to 138 kV operation using a conductor rated 1649 A or greater. Establish the new Ingle Substation with two transformers. Upgrade Caddo Mills Explorer station to operate at 138 kV. Disconnect the existing capacitor bank from Caddo Mills Hwy 66. Relocate Caddo Mills substation feeders to Ingle substation. Disconnect Caddo Mills 69 kV Substation. Upgrade all line terminal and associated equipment to meet or exceed 2000 A. | 2018: -6.21% 2019: 23.62% 2020: -25.77% 2021: 8.05% 2022: -4.85% | 2023: 1.22% 2024: 6.77% | 13.6 MW | 2023: 0.2 MW 2024: 13.9 MW | Residential Commercial | Not Applicable
49 | 0PT42179 -- CAMPION (FORMERLY BLUEBONNET LAKES) SUB : ESTABLISH SUBSTATION WITH (1) 47 MVA 138/13.8KV AND (1) 28 MVA 138/12.5KV | The 2021 Summer Projected load on Calumet Feeder 0004 is 11.4 MVA which is 105% of the 13.7 MVA feeder rating. In addition, the 2021 Summer Projected load on Calumet Bank #1 is 20.9 MVA which is 105% of the 20 MVA rating. Furthermore, the 2021 Summer Projected load on Calumet Bank #2 is 23.3 MVA which is 100% of the 23.3 MVA rating. Finally, the 2021 Summer Projected load on Cockrell Hill Substation is 68.5 MVA which is 130% of its 52.5 MVA contingency rating. In order to correct these problems, it is recommended to establish Campion Substation with 1-47 MVA 138-13.2kV transformer and 2-feeder breakers with UG feeder exits. | 2018: 2.20% 2019: 0.59% 2020: -5.18% 2021: -0.88% 2022: -2.52% | 2023: 4.65% 2024: -7.17% | 32.7 MW | 2023: 17.7 MW 2024: 16.6 MW | Residential Commercial Industrial | Not Applicable
50 | 0PT42151 -- DESERT WIND (FKA GARDEN CITY WEST) SUB : ESTABLISH ONE 47 MVA 138/25 KV TRANSFORMER AND TWO 25 KV FEEDER BREAKERS | Garden City Substation is served by a 69 kV radial line and has limited access. Dewey Lake Substation Feeder 2105 is projected to be loaded to 146% of its maximum continuous rating. In order to correct the radially fed substation, it is proposed to establish Desert Wind Substation with 1-47 MVA 138/25 kV transformer and 2-25 kV feeder breakers. The first breaker will be used to tie into St. Lawrence load which will then pick up the old Garden City Substation load. The second breaker will be used to offload the overloaded Dewey Lake 2105 feeder. The completion of this work will allow the decommissioning of Garden City Substation and also correct the overload on Dewey Lake Substation Feeder 2105. | 2017: -16.18% 2018: 55.91% 2019: 29.48% 2020: 19.22% 2021: -19.01% | 2022: 25.67% 2023: 33.18% 2024: 15.87% | 14.3 MW | 2022: 0.6 MW 2023: 6.0 MW 2024: 13.9 MW | Commercial | Not Applicable
51 | 0PT41229 -- BELL MOUNTAIN (FORMERLY HUDSON OAKS) SUB : ESTABLISH SUBSTATION WITH ONE 138-25 KV, 47 MVA TRANSFORMER AND TWO FEEDER BREAKERS | The 2020 projected winter load on Weatherford East Transformer #1 is 8.3 MVA which is 111 percent of the 7.5 MVA nameplate rating for this transformer. Additionally, under backstand conditions, the load on Laguna Vista 8521 is 22.2 MW which is 105 percent of the 21.1 MW rating. In order to correct this problem, it is proposed to establish Bell Mountain Substation with one 28 MVA, 138-12.5 kV substation transformer and two 12.5 kV feeder breakers. | 2018: 6.97% 2019: -18.05% 2020: -9.93% 2021: 42.10% 2022: -17.15% | 2023: 23.83% 2024: -2.11% | 17.8 MW | 2023: 1.3 MW 2024: 3.0 MW | Residential Commercial | Not Applicable
52 | 0PT41016 -- DUVAL SUB: REMOVE 69 KV STATION AND ESTABLISH 138-12.5 KV STATION | The purpose and necessity of this project is mostly driven by aged infrastructure. Duval Substation has been in service nearly 66 years old, while Bryan Avenue also has infrastructure nearing 70 years of age. The equipment at both sites is no longer supported by the manufacturer and has reached the end of its serviceable life. To improve operational reliability and flexibility of the system there is an urgent need to replace this aging infrastructure. The replacement of the current 69 kV system with the 138 kV system would provide additional power flow capacity for the future, leading to more operational system flexibility and also increasing the reliability by installing modern equipment and updated design standards. This 69 kV to 138 kV conversion moves Oncor closer to modernizing and upgrading the system to 138 kV and completing the elimination of our aging 69 kV system. In 2014 Oncor began the Handley - Duval upgrade to upgrade the line to 138 kV capability and continued to operate it at 69 kV. The subject project will allow Oncor to fully complete the conversion of operating at 138 kV level from Marrs Switch - Handley Switch. There are currently no planning criteria violations contributing to the need of this project. While there are no planning criteria violations, Oncor has performed the appropriate analyses to evaluate the potential impacts to the ERCOT system as a result of the proposed project. | 2017: -6.73% 2018: 11.01% 2019: 2.56% 2020: -1.00% 2021: -1.19% | 2022: 18.72% 2023: 0.14% 2024: -5.76% | 63.8 MW | 2022: 16.8 MW 2023: 69.8 MW 2024: 65.8 MW | Residential Commercial | Not Applicable
53 | 0PT47352 -- DONAHOE SUB: ESTABLISH STATION | The rebuild of the Taylor Switch - Holland 69 kV Line Section will upgrade the aging line infrastructure and improve customers' reliability from the connected stations. The upgrade will also enable the line to be converted to 138 kV operation in the future, increasing capacity in one of the main power transfer paths.The establishment of the new Donahoe Substation with one 138/69kV 24.9 kV, 46.7 MVA transformer and two feeder breakers is required to pick up the load for existing Bartlett and Granger 69 kV substations. | 2019: -7.23% 2020: 28.68% 2021: 24.77% 2022: -25.40% 2023: 19.18% | 2024: 14.66% | 5.4 MW | 2024: 1.4 MW | Residential Commercial | Not Applicable
54 | 0PT50807 -- EBERHARDT SUB (FORMERLY INDUSTRIAL SUB): ESTABLISH STATION WITH ONE TRANSFORMER | The 2024/25 winter peak load on Lake Belton Feeder 2101 is 16.0MVA which is 103% of the 15.6MVA maximum continuous rating for this feeder. In addition, the 2024/25 winter peak load on Lake Belton Substation is 72.4 MVA which is 124% of the 58.4MVA capacity rating for this substation. Also, the 2024/25 projected winter peak loads on Temple North Feeders 1606 and 1607 are 14.0MVA and 16.6MVA which are 104% and 123% of the 13.5MVA maximum continuous ratings for these feeders, respectively. With the added load of 12MW for Customer AD, the 2024/25 projected winter peak load on Moorse Mills Feeder 3912 is 20.5MVA which is 132% of the 15.5MVA maximum continuous rating for this feeder. In order to resolve these loading conditions, it is proposed to establish Eberhardt Substation with a 138-12.5kV 46.7MVA transformer and four 12.5kV UG feeder breakers. It is also recommended to construct various distribution facilities to transfer load to the new substation . The completion of this work will correct the loading conditions identified above. | 2019: -8.85% 2020: 7.87% 2021: 2.40% 2022: 51.16% 2023: -10.19% | 2024: -5.03% | 22.7 MW | 2024: 0.7 MW | Residential Commercial Industrial | Not Applicable
55 | 0PT50812 -- FOUNDERS TRAIL SUB: ESTABLISH STATION WITH TWO TRANSFORMERS | The 2024/25 projected winter load on Killeen South Transformer #1 and Killeen Transformer #1 are 52.3.7MVA and 29.4 which are 112% and 105% of the 46.7MVA nameplate rating and the 28MVA nameplate rating for these substation transformers, respectively. In addition, the 2024/25 winter load on Killeen South Substation, Killeen Substation, and Killeen Clear Creek are 88.2MVA., 46.3MVA, and 72.0MVA which are 153%, 132%, and 123% of the 58.4MVA capacity rating, 35.0MVA capacity rating, and 58.4MVA capacity rating for these substations, respectively.In order to resolve these loading conditions, it is proposed to establish Founders Trail Substation with two 138-24.9kV 46.7MVA transformers and three UG feeder breakers. It is also recommended to construct various distribution facilities to transfer load to the new substation.The completion of this work will resolve the loading conditions identified. | 2019: -13.04% 2020: -4.07% 2021: -6.95% 2022: 38.37% 2023: 10.89% | 2024: 1.84% | 57.3 MW | 2024: 4.7 MW | Residential Commercial | Not Applicable