## Index
RTP Scope Section Number | Input Assumption | Status | Date
Transmission Topology
3.1.1 | Start Cases | Final | 2025-08-05
3.1.2 | RPG Projects Backed Out For Lack of Approval or Moved Due to ISD Change | Final | 2025-12-18
3.1.2 | Recently Approved RPG Projects | Final | 2025-12-03
3.1.2 | Model Updates & Corrections | Final | 2025-12-18
3.1.3 | Transmission & Generation Outages | Final | 2025-12-19
3.1.5 | Temperatures Used in Dynamic Rating Calculation | Final | 2025-08-05
Generation
3.2.1 | Generation Additions, Retirements and Mothballs | Final | 2025-12-19
3.2.2 | Renewable Generation Dispatch | Final | 2025-08-05
3.2.3 | Switchable Generation | Final | 2025-08-05
3.2.4 | DC Tie Modeling and Dispatch | Final | 2025-08-05
3.2.5 | Reserve Requirement | Final | 2025-08-05
3.2.6 | Fuel Price Assumptions | Final | 2025-08-05
Demand
3.3 | SSWG Forecast 90/10 Forecast RTP Summer Peak Case Forecast RTP Min Load Case Forecast | Final | 2025-08-05
Other Studies
4.2.2 | Sensitivity Analysis | Final | 2025-12-22

## Start Cases
Date Last Updated: | 2025-08-05 | Back
Status: | Final
SSWG Case Version: | 24SSWG Update 1 Final - October 14, 2022
On Peak Cases:
24SSWG_2027_SUM1_U1_Final_10142024.raw
24SSWG_2028_SUM1_U1_Final_10142024.raw
24SSWG_2030_SUM1_U1_Final_10142024.raw
24SSWG_2031_SUM1_U1_Final_10142024.raw
Off Peak Case:
24SSWG_2028_MIN_U1_Final_10142024.raw

## RPG Projects Removed or Moved
Date Last Updated: | 2025-12-18 | Back
Status: | Final
Based on TPIT dated: | 2024-10-01
RPG Projects Removed from the RTP Cases
ERCOT Project Number | Project Title | Project Description | "from" Location | "to" Location | Associated Projects | Transmission Owner | TSP Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Service Level kV | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Phase Number | MOD Project Number
70710 | Eden to Yellowjacket: Rebuild 69 kV Line | Rehab the Eden to Yellowjacket 69kV line. | Eden | Yellowjacket |  | AEP TCC | Damian Raab twang1@aep.com 918-599-2635 | TA2021119 | 2027-11-30 | 69 | Tier 3 | Not Submitted | NA | NA | 6363, 6372 | Y | 70711 | 70710
67915 | Asherton to West Batesville: Rebuild 138 kV Line | Rehab Asherton to West Batesville 138 kV line. | Asherton | West Batesville |  | AEP TCC/ETT | John Solis jsolis@aep.com 361-881-5574 |  | 2028-12-30 | 138 | Tier 3 | NA | NA | NA | 8236, 8283, 8285 | Y | 67916 | 67915
78473A | Odin (ODI) 138kV CEHE Substation | Loop new CEHE 138kV substation Odin (ODI) into Ckt. 36 to create new Ckt. 36 COPPER to Odin to Booster tap to Jones Creek. | Odin | Brazosport/Booster |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-01-31 | 138 | Tier 3 | NA | NA | NA | 42199, 42215, 42280 | Y | 87133 | 78473
78473B | Odin (ODI) 138kV CEHE Substation | Install one generator lead from CEHE 138kV substation Odin (ODI) to VALHAL (VAL) / Valhalla Solar (26INR0042) | Odin | VALHAL |  | CNP | Wesley Woitt wesley.woitt@centerpointenergy.com 713-207-2760 |  | 2026-01-31 | 138 | Tier 3 | NA | NA | NA | 42280, 113811 | Y | 87134 | 78473
76654 | Establish Voss Lake 345/138 kV Switch | Establish Voss Lake 345/138 kV Switch | Voss Lake | Voss Lake |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R6278 | 2026-12-15 | 345 | Tier 3 | 2025-02-27 |  |  | 3675, 3678, 3687, 3717, 3740, 3750, 3751, 3752, 3761, 13429, 13430 | Y | 76655 | 76654
76728 | Skyview 345/138 kV Switch | Establish Skyview 345/138 kV Switch | Skyview |  |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | M4350 | 2027-05-15 | 138 | Tier 3 | Not Submitted | NA | NA | 1922, 1924, 1927, 2119, 2120, 2123, 2124, 2125, 2127, 2128, 2129, 2130, 2131, 2132, 2134, 2231, 2243, 2244, 11938 | Y | 76831 | 76728
71910 | Rebuild the Hillsboro - Elm Mott 69 kV Line | Rebuild the Hillsboro - Elm Mott 68 kV Line | Hillsboro | Elm Mott |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R6221 | 2028-12-15 | 69 | Tier 3 | Not Submitted | NA | NA | 3408, 3523, 3524, 3525, 3526, 3527, 3528, 3529, 13525 | Y | 71911 | 71910
6287 | Sherry Sw. - Webb/Kennedale 345 kV DCKT Line | Upgrade existing 345 kV Line | Sherry | Webb/Kennedale |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | M4252 |  | 345 | Tier 3 | Not Submitted | NA | NA | 1911, 1918, 1929, 1930, 1932, 1934 | Y | 14016 | 6287
76669 | Rebuild Elbow to Redberry to Bulldog 138 kV Line | Rebuild Elbow to Redberry to Bulldog 138 kV Line | Elbow | Bulldog |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R8666 | 2026-12-15 | 138 | Tier 3 | Not Submitted | NA | NA | 10080, 23833, 23834 | Y | 77043 | 76669
76696 | Construct a new Border – Shifting Sands 138 kV Line | Construct a new Border – Shifting Sands 138 kV Line | Atchison | Shifting Sands |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R8628 | 2026-12-15 | 138 | Tier 3 | Permian Basin Reliability Plan (common local transmission upgrade L1C) |  |  | 11089, 11189, 11392, 18672, 18705 | Y | 87872 | 76696
76712 | Bluff Creek to China Grove Line Rebuild | Rebuild existing 138 kV Line | Bluff Creek 138 kV Switch | China Grove Switch |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R8655 | 2026-12-15 | 138 | Tier 3 | Not Submitted |  |  | 1309, 1318 | Y | 87645 | 76712
81034 | Lamesa - Willow Valley 138 kV Line | Rebuild Lamesa to Willow Valley 138 kV line. | Lamesa Switch | Willow Valley Switch |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R8654 | 2026-12-30 | 138 | Tier 3 | Not Submitted |  |  | 1163, 1301, 1307, 1308 | Y | 81035 | 81034
81152 | China Grove to Tributary Line Rebuild | China Grove to Tributary Line Rebuild | China Grove | Tributary Switch |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R8656 | 2026-12-15 | 138 | Tier 3 | Not Submitted |  |  | 1318, 1394 | Y | 87650 | 81152
81175 | Salt Flat Road 138 kV Switch and Salt Flat Road - Barr Ranch - Reiter 138 kV Second Circuit | Add Salt Flat Road 138 kV Switch and Salt Flat Road - Barr Ranch - Reiter 138 kV Second Circuit | Reiter | Salt Flat Road |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R8704 | 2025-12-15 | 138 | Tier 3 | 2025-02-28 |  |  | 1027, 1111, 1193, 1234, 1276, 11111, 11217, 11235, 11344, 18545, 18701, 23859 | Y | 87224 | 81175
81418 | Reiter to Yarbrough 138 kV Line Rebuild | 138 kV existing line rebuild. | Reiter | Yarbrough |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R8527 | 2026-12-16 | 138 | Tier 3 | 2025-02-28 |  |  | 11111, 18545 | Y | 81419 | 81418
87653 | Bluff Creek to Scurry Chevron Line Rebuild | Rebuild Bluff Creek to Scurry Chevron | Bluff Creek | Scurry Chevron |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R9002 | 2026-12-15 | 138 | Tier 3 | Not Submitted |  |  | 1309, 1310, 1312 | Y | 87654 | 5526
81305 | Oncor_FW_Expanse - Tredway 138 kV Line | Rebuild the existing Expanse – Vealmoor 138 kV Line with both circuits in place. | Expanse | Tredway |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R8681 | 2026-05-15 | 345 | Tier 3 | 2023-09-29 |  |  | 1355, 10032, 10090, 10097, 10098, 10110, 10112, 10113, 11006, 11338, 11348, 11349, 11368, 11383, 23829, 23835, 23838, 23849, 23880 | Y | 87873 | 81305
73436 | Rockhound - Connell 345 kV Double-Circuit Line | Construct a new 345 kV Double-Circuit Line and establish a 345/138 kV Switch | Rockhound | Connell |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R8718, R8807 | 2026-12-16 | 345 | Tier 2 | 2024-06-18 |  |  | 10033, 10036, 10062, 10085, 10086, 10087, 10088, 10089, 11371, 23840, 23841, 23855 | Y | 81403 | 73436
81440 | Wolf to Monahan to Pecos / Odessa EHV to Reiter138 kV Line Rebuild | 138 kV existing line rebuild. | Wolf/Odessa EHV | Pecos/Reiter |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R8527, R8629 | 2027-12-16 | 138 | Tier 3 | 2025-02-28 |  |  | 1013, 1027, 1107, 11117, 18545 | Y | 81441 | 81440
72457 | AddKiowaToQuinlanLine | Add 138kV line from Kiowa to Quinlan | Kiowa | Quinlan |  | RCEC | Scott Donhamsdonham@rayburnelectric.com 469-402-2024 |  | 2028-01-01 | 138 | Tier 2 | Not Submitted | NA | NA | 6796, 6884 | Y | 72458 | 72457
RPG Projects With ISD Changes
ERCOT Project Number | Project Title | Project Description | "from" Location | "to" Location | Associated Projects | Transmission Owner | TSP Contact | Transmission Owner Project Number (Optional) | Original Projected In-Service Date (Month/Yr) | New Projected In-Service Date (Month/Yr) | Service Level kV | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Phase Number | MOD Project Number
17TPIT0031 | Elkton 345/138 kV Autotransformer | Replace existing autotransformer | Elkton | Elkton |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R6023-E |  | 2030-05-15 | 345 | Tier 3 | Not Submitted |  |  | 3105, 3106, 29150 | Y | 10501 | 3155
5981 | Shamburger North 345/138 kV Switching Station | Establish Shamburger North 345/138 kV Switching Station | Shamburger North | Shamburger North |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R6083 |  | 2030-05-15 | 345 | Tier 3 | Not Submitted |  |  | 2485, 3103, 3201, 3206, 3217, 3223, 3226 | Y | 13696 | 5981
6304 | Shamburger North - Shamburger 345 kV Line | Upgrade existing 345 kV Line | Shamburger North | Shamburger |  | ONCOR | Jared Gurley jared.gurley@oncor.com 817-215-6079 | R6085 |  | 2030-05-15 | 345 | Tier 3 | Not Submitted |  |  | 3103, 3223 | Y | 14033 | 6304

## Recently Approved RPG Projects
Date Last Updated: | 2025-12-03 | Back
Status: | Final
RPG Project ID | RPG Project Name | TDSP | Approve Date
24RPG001 | Temple Area Project | ONCOR | 2024
24RPG002 | Rockhound 345/138-kV Switch and Grey Well Draw to Buffalo 2nd 138-kV Circuit Project | ONCOR | 2024
24RPG003 | Eastside 345/138-kV Switching Station Project | CPS | 2024
24RPG004 | Omicron Reliability Project | CPS | 2024
24RPG005 | Montfort Switch to Shankle Switch 138-kV Line Project | ONCOR | 2024
24RPG006 | Prairieland 345/138-kV Switch and Prairieland Switch to Quartz Sand Switch/Hog Mountain Pod 138-kV Line Project | ONCOR | 2024
24RPG008 | Brownsville Area Improvements Transmission Project | AEP | 2024
24RPG010 | Delaware Basin Stage 3 and 4 Project | ONCOR | 2024
24RPG014 | Sim Gideon to Cedar Hill Transmission Line Upgrade Project | LCRA | 2024
24RPG015 | Delaware Basin Stage 5 Project | ONCOR | 2025
24RPG017 | Venus Switch to Sam Switch 345-kV Line Project | ONCOR | 2024
24RPG018 | Salado Switch to Hutto Switch 138-kV Line Project | ONCOR | 2024
24RPG020 | Connell 345/138-kV Switch and Connell to Rockhound 345-kV Double-Circuit Line Project | ONCOR | 2025
24RPG021 | Forney 345/138-kV Switch Rebuild Project | ONCOR | 2025
24RPG022 | Wilmer 345/138-kV Switch Project | ONCOR | 2025
24RPG024 | Hartring to Upland 138-kV Line and Benedum Autotransformer Addition Project | ONCOR/LCRA | 2025
24RPG025 | Gunter 345/138-kV Switch Project | ONCOR | 2024
24RPG026 | Jordan/Mont Belvieu Area Improvement Project | CNP | 2024
24RPG028 | CNP Baytown Area Load Addition Project | CNP | 2025
24RPG029 | Oncor Tredway 138kV Switch and Expanse to Tredway 138kV 2nd Circuit Project | ONCOR | 2025
24RPG034 | Redwood to San Marcos Transmission Line Upgrade Project | LCRA | 2025
24RPG035 | Aransas Pass to Rincon 69-kV Line Rebuild Project | AEP | 2025
24RPG037 | Partial Rebuild of 138-kV Ckt.63 West Galveston to Moody Project | CNP | Reclassified as Tier 4
24RPG038 | Bergheim Substation Upgrade Project | LCRA/PEC | 2025
24RPG040 | Roscoe Area Upgrades Project | ONCOR | 2025
24RPG041 | Buck Canyon and Binturong 345-kV Synchronous Condenser Stations Project | WETT | 2025
25RPG001 | Texas A&M University System RELLIS Campus Reliability Project | BTU | 2025
25RPG002 | East Munday 138-kV Station Rebuild Project | AEP | Reclassified as Tier 4
25RPG003 | Hamilton County Conversion Project | BEC | 2025
25RPG005 | Pitchfork 345-kV Substation Addition Project | WETT | 2025
25RPG006 | Salado Switch to Hutto Switch 138-kV Line Project | ONCOR | 2025
25RPG007 | Salt Flat Road to Barr Ranch to Reiter 138-kV Second Circuit Project | ONCOR | 2025
25RPG008 | Wolf Switch to Reiter Switch 138-kV Line Project | ONCOR | 2025
25RPG010 | 138-kV Flewellen to Fort Bend Upgrades Project | CNP | 2025
25RPG011 | 138-kV West Columbia to Needville Upgrades | CNP | 2025
25RPG014 | Cedar Bayou Autotransformer Upgrades Project | CNP | 2025
25RPG019 | Lamesa Switch to Willow Valley Switch 138-kV Line Rebuild Project | ONCOR | 2025
25RPG021 | AEPSC Victoria to Warburton 138-kV Line Rebuild Project | AEP | 2025
25RPG022 | Oncor and AEPSC Drill Hole to Sand Lake to Solstice 765-kV Line Project | AEPSC/ONCOR | 2025
25RPG025 | AEP Texas, CPS Energy, Oncor, and CNP Texas 765-kV-STEP Eastern Backbone Project | AEP Texas/CPS/Oncor/CNP | 2025
25RPG027 | Royse Switch to Edgewood 69-kV Line Conversion to 138-kV Project | ONCOR | Reclassified as Tier 4
25RPG029 | Hillsboro Switch to Elm Mott Switch 69-kV Line Rebuild Project | ONCOR | Reclassified as Tier 4
25RPG030 | Bonham Switch to Toco Switch 69-kV Line Rebuild Project | ONCOR | Reclassified as Tier 4
25RPG031 | Sam Switch Resiliency Project | LST | 2025
25RPG032 | Fort Stockton Plant 138-kV Transmission Station Rebuild Project | AEP | 2025

## Model Updates & Corrections
Date Last Updated: | 2025-12-18 | Back
Status: | Final
Model Corrections/Updates Made to the 2025 RTP Cases
Transmission Changes | TO | [5 empty] | Comments
|  | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM
Applied model update to update ratings, impedances, and line lengths on lines connected to Progress Park 138-kV Switch | ONCOR | X | X | X | X | X | MOD 90069 - SSWG Incremental Update
Added the LCRATSC Bastrop West Bluebonnet Transmission Line Upgrade MOD project to upgrade ratings on Bastrop West to Bluebonnet | LCRA TSC |  |  | X | X | X | MOD 92602
Added the LCRATSC Bluebonnet Wyldwood Transmission Line Overhaul MOD project to upgrade ratings on Wyldwood to Bluebonnet | LCRA TSC | X | X | X | X | X | MOD 92598
Added the LCRATSC Colton Elroy Transmission Line Overhaul MOD project to upgrade ratings on Colton to Elroy | LCRA TSC | X | X | X | X | X | MOD 92561
Added the LCRATSC Colton Mendoza Transmission Line Upgrade MOD project to upgrade ratings on Colton to Mendoza | LCRA TSC | X | X | X | X | X | MOD 92627
Added the LCRATSC Elroy Wolf Lane Transmission Line Overhaul MOD project to upgrade ratings on Elroy to County Line to Wolf Lane | LCRA TSC | X | X | X | X | X | MOD 92622
Added the LCRATSC Lockhart Mendoza Transmission Line Overhaul MOD project to upgrade ratings on Lockhart to Mendoza | LCRA TSC |  |  | X | X | X | MOD 92572
Added the LCRATSC Wolf Lane Wyldwood Transmission Line Overhaul MOD project to upgrade ratings on Wolf Lane to County Line to Wyldwood | LCRA TSC | X | X | X | X | X | MOD 91397
Added the ONCOR Watermill Reindeer Line Upgrade MOD project to upgrade ratings on the Watermill to Reindeer Line | ONCOR | X | X | X | X | X | MOD 92845
Applied topology update to the 138-kV path from TNMP Amoco to MPL Tank Farm to be Amoco to Spoonbill to MPL Tank Farm. | TNMP | X | X | X | X | X | Confirmed by TNMP
Added the ONCOR Tonkawa to Ranger Camp 345-kV Line Rebuild MOD project since the in-service MOD date has been updated | ONCOR | X |  |  |  |  | MOD 72011
Updated load interconnection topology which included relocating load from bus 8759 to bus 8318. | AEPSC | X | X | X | X | X | Provided by AEPSC
Updated load interconnection topology which included relocating load from bus 40170 to bus 940000. | CNP |  |  |  | X | X | Provided by CNP
Updated load interconnection topology which included relocating load from bus 40700 to bus 940450. | CNP |  |  |  |  | X | Provided by CNP
Applied topology update to remove the Haber substation. | AEPSC | X | X |  |  |  | Confirmed by AEPSC
Added the LCRATSC Canyon to San Marcos Transmission Line Upgrade MOD project to upgrade ratings on Canyon to San Marcos | LCRA TSC | X | X | X | X | X | MOD 92575
Added the LCRATSC Gabriel to Rivery MLSE Upgrade MOD project to upgrade ratings on Gabriel to Rivery | LCRA TSC | X | X | X | X | X | MOD 92629
Added the LCRATSC Howard Lane to Wells Branch Transmission Line Upgrade MOD project to upgrade ratings on Howard Lane to Wells Branch | LCRA TSC | X | X | X | X | X | MOD 91404
Added the LCRATSC Lytton Springs to Mendoza Transmission Line Upgrade MOD project to upgrade ratings on Lytton Springs to Mendoza | LCRA TSC | X | X | X | X | X | MOD 100184
Added the LCRATSC Georgetown to Rivery Transmission Line Upgrade MOD project to upgrade ratings on Georgetown to Rivery | LCRA TSC | X | X | X | X | X | MOD 85973
Holly (8486) bus tie breaker ratings upgrade. | AEPSC | X | X | X | X | X | Updated ratings based on current operations model.
Transformer Changes | TO/GO | [5 empty] | Comments
|  | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM
Removed the branch connecting the Jordan transformer to Philip transformer. | CNP | X |  |  |  |  | The connecting branch caused an violation on the Philip transformer (modeling error).
Updated the voltage limits on the Cedar Bayou ckt. A3 transformer | CNP | X | X | X | X | X | Confirmed by CNP
Turned on North Edinburg transformer #2 | AEPSC | X | X | X | X | X | SSWG modeling error
Opened Kendal (7046) 345/138-kV AT#3 (N.O. in operations) | LCRA TSC | X | X | X | X | X | Node breaker to bus branch modeling error; confirmed by LCRA TSC
Generation Changes | TO/GO | [5 empty] | Comments
|  | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM
Removed Garcitas Solar Unit on bus 113051 | AEP | X | X | X | X | X | AEP confirmed that this solar site project has been cancelled
Load Changes | TO | [5 empty] | Comments
|  | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM
Moved/Adjusted Network-served and Self-Serve Loads at all buses within the DOWGEN PUN facility | CNP | X | X | X | X | X | This self-serve adjustment was to account for the mothballing of DOWGEN units G66 and ST64.
Bus Voltage Changes | TO | [5 empty] | Comments
|  | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM
Reactive Device Changes | TO | [5 empty] | Comments
|  | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM
Phase Shifters Changes | TO | [5 empty] | Comments
|  | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM
Synchronous Condensers Changes | TO | [5 empty] | Comments
|  | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM
FACTS Device Changes | TO | [5 empty] | Comments
|  | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM

## Transmission & Gen Outages
Date Last Updated: | 2025-12-19 | Back
Status: | Final
Case
Outaged Elements | Outage Description | Associated TO/RE | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM | Notes
Known outages collected by ERCOT from TSPs and Resource Entities were incorporated based on the TSP and ERCOT technical rationale into the known outages impact studies.

## Temp. for Dynamic Ratings
Date Last Updated: | 2025-08-05 | Back
Status: | Final
Weather Zone | 90th Percentile Temperature (degree F)
Coast | 105
East | 110
Far West | 115
North Central | 110
North | 110
South Central | 110
South | 105
West | 110

## Gen Add. Ret. and Mothball
Date Last Updated: | 2025-12-19 | Back
Status: | Final
New generators that met PG Section 6.9 requirements (1)(b) through (1)(d) by 5/31/2025 in FULL LOAD CASES. New generators that met PG Section 6.9 requirements (1)(b) through (1)(d) by 9/30/2025 in SENSITIVITY CASES.
GINR Reference Number | Project Name | County | Projected COD | Fuel | MW For Grid | Meets Section 6.9 Requirements (1)(b) through (1)(d) | 2027 SUM | 2027 SUM SENS | 2028 MIN | 2028 MIN SENS | 2028 SUM | 2030 SUM | 2030 SUM SENS | 2031 SUM | Comments
22INR0540 | Walstrom BESS | Austin | 2025-06-19 | Battery | 205.31 | Y | Y | Y | Y | Y | Y | Y | Y | Y
22INR0517 | Lane City Wind | Wharton | 2025-06-30 | Wind | 199.5 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0079 | Chillingham Storage | Bell | 2025-07-15 | Battery | 153.93 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0456 | FRIENDSWOOD ENERGY GENCO | Harris | 2025-07-18 | Gas | 143.7 | Y | Y | Y | Y | Y | Y | Y | Y | Y
21INR0517 | Tidwell Prairie Storage 1 | Robertson | 2025-07-31 | Battery | 204 | Y | Y | Y | Y | Y | Y | Y | Y | Y
22INR0525 | St. Gall II Energy Storage | Pecos | 2025-07-31 | Battery | 100.24 | Y | Y | Y | Y | Y | Y | Y | Y | Y
19INR0054 | Monte Cristo 1 Wind | Hidalgo | 2025-08-20 | Wind | 234.5 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0467 | Bocanova Power | Brazoria | 2025-08-26 | Battery | 150.46 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0389 | Stoneridge BESS | Milam | 2025-09-01 | Battery | 101.9 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0166 | Stillhouse Solar | Bell | 2025-09-02 | Solar | 210.8 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0364 | Tierra Seca BESS | Val Verde | 2025-09-03 | Battery | 102.7 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0672 | Fagus Solar Park 2 SLF | Childress | 2025-09-26 | Solar | 166.57 | Y | Y | Y | Y | Y | Y | Y | Y | Y | Split INR fix for Fagus Solar Park 1
26INR0669 | Greyhound Solar - Phase E | Ector | 2025-09-26 | Solar | 150.71 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0494 | Cartwheel BESS 1 | Hopkins | 2025-09-30 | Battery | 154.2 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0302 | Pintail Pass BESS | San Patricio | 2025-09-30 | Battery | 207.25 | Y | Y | Y | Y | Y | Y | Y | Y | Y
16INR0104 | Big Sampson Wind | Crockett | 2025-10-04 | Wind | 265.4 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0116 | Hart Wind | Castro | 2025-10-31 | Wind | 163.4 | Y | Y | Y | Y | Y | Y | Y | Y | Y
26INR0670 | Greyhound Solar - Phase F | Ector | 2025-10-31 | Solar | 101.6 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0181 | Bynum Solar Project | Coryell | 2025-12-01 | Solar | 56 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0351 | Seven Flags BESS | Webb | 2025-12-12 | Battery | 102.7 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0578 | Forest Creek Wind Repower | Glasscock | 2025-12-15 | Wind | 125.1 | Y | Y | Y | Y | Y | Y | Y | Y | Y | Repower
23INR0501 | Soda Lake BESS 1 | Crane | 2025-12-17 | Battery | 203.87 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0344 | Hermes Solar | Bell | 2025-12-30 | Solar | 100.36 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0365 | Hermes Storage | Bell | 2025-12-30 | Battery | 100.42 | Y | Y | Y | Y | Y | Y | Y | Y | Y
20INR0242 | Anson Solar 2 | Jones | 2025-12-31 | Solar | 200.9 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0150 | Cradle Solar | Brazoria | 2025-12-31 | Solar | 200.85 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0249 | Limewood Solar | Bell | 2025-12-31 | Solar | 204.6 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0358 | Castor BESS | Brazoria | 2025-12-31 | Battery | 205.39 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0538 | Roadrunner Crossing BESS SLF | Eastland | 2025-12-31 | Battery | 150.4 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0472 | Amador Storage | Van Zandt | 2025-12-31 | Battery | 102.41 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0286 | Dry Creek Solar I | Rusk | 2026-01-01 | Solar | 201.06 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0453 | Longfellow BESS I | Pecos | 2026-01-31 | Battery | 54.99 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0455 | Longfellow BESS II | Pecos | 2026-01-31 | Battery | 105.75 | Y | Y | Y | Y | Y | Y | Y | Y | Y
26INR0333 | VERTUS ENERGY STORAGE | Galveston | 2026-02-01 | Battery | 207.3 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0364 | Pitts Dudik II | Hill | 2026-02-04 | Solar | 30.23 | Y | Y | Y | Y | Y | Y | Y | Y | Y
26INR0296 | Sherbino II BESS SLF | Pecos | 2026-02-08 | Battery | 77.37 | Y | Y | Y | Y | Y | Y | Y | Y | Y
21INR0359 | Hickerson Solar | Bosque | 2026-03-01 | Solar | 311.1 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0477 | Barrett Solar | Rains | 2026-03-01 | Solar | 125.81 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0294 | Citrus Flatts BESS | Cameron | 2026-03-11 | Battery | 101.2 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0329 | Project Lynx BESS | Nueces | 2026-03-14 | Battery | 125.36 | Y | Y | Y | Y | Y | Y | Y | Y | Y
21INR0268 | Greyhound Solar | Ector | 2026-03-31 | Solar | 335.45 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0128 | Desna BESS | Brazoria | 2026-03-31 | Battery | 205.46 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0493 | Crowned Heron BESS 2 | Fort Bend | 2026-03-31 | Battery | 154.2 | Y | Y | Y | Y | Y | Y | Y | Y | Y
19INR0042 | Long Point Solar | Brazoria | 2026-04-01 | Solar | 120.7 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0044 | Millers Branch Solar II | Haskell | 2026-04-01 | Solar | 178 | Y | Y | Y | Y | Y | Y | Y | Y | Y | Split INR fix for Millers Branch Solar 1
26INR0524 | Fagus Solar Park 3 SLF | Childress | 2026-04-01 | Solar | 186.83 | Y | Y | Y | Y | Y | Y | Y | Y | Y | Split INR fix for Fagus Solar Park 1
23INR0361 | Third Coast BESS | Jackson | 2026-04-04 | Battery | 102.82 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0503 | Uhland Maxwell Expansion | Caldwell | 2026-04-07 | Gas | 188.4 | Y | Y | Y | Y | Y | Y | Y | Y | Y
22INR0274 | Crowded Star Solar II | Jones | 2026-04-16 | Solar | 190.18 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0078 | Shaw Solar | Bandera | 2026-04-29 | Solar | 124.65 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0482 | NRG THW GT 345 (TEF -Due Diligence) | Harris | 2026-05-01 | Gas | 422 | Y | Y | Y | Y | Y | Y | Y | Y | Y
26INR0049 | Pin Peaking Energy Center 1 (TEF- Due Diligence) | Freestone | 2026-05-01 | Gas | 214.8 | Y | Y | Y | Y | Y | Y | Y | Y | Y
26INR0109 | Pin Peaking Energy Center 2 (TEF- Due Diligence) | Freestone | 2026-05-01 | Gas | 214.8 | Y | Y | Y | Y | Y | Y | Y | Y | Y
26INR0226 | First Capitol BESS | Brazoria | 2026-05-01 | Battery | 257.48 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0225 | MRG GOODY SOLAR | Lamar | 2026-05-02 | Solar | 170.82 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0305 | MRG Goody Storage | Lamar | 2026-05-02 | Battery | 52.29 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0528 | Blanquilla BESS | Nueces | 2026-05-15 | Battery | 200.78 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0290 | Zeya BESS | Galveston | 2026-06-01 | Battery | 255.33 | Y | Y | Y | Y | Y | Y | Y | Y | Y
26INR0405 | Buffalo Creek BESS | Fort Bend | 2026-06-01 | Battery | 251.4 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0584 | Houston IV BESS | Harris | 2026-06-03 | Battery | 164.6 | Y | Y | Y | Y | Y | Y | Y | Y | Y
21INR0334 | Nightfall Solar SLF | Uvalde | 2026-06-30 | Solar | 180.87 | Y | Y | Y | Y | Y | Y | Y | Y | Y
22INR0559 | Honeycomb Solar SLF | Bee | 2026-06-30 | Solar | 61.1 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0392 | Honeycomb Storage SLF | Bee | 2026-06-30 | Battery | 61.47 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0399 | Buzios Solar | Motley | 2026-06-30 | Solar | 252 | Y | Y | Y | Y | Y | Y | Y | Y | Y
22INR0558 | Callisto II Energy Center | Harris | 2026-07-01 | Battery | 203.2 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0492 | Blue Summit Energy Storage | Wilbarger | 2026-07-01 | Battery | 100 | Y | Y | Y | Y | Y | Y | Y | Y | Y
26INR0023 | Leon Solar Park | Leon | 2026-07-01 | Solar | 210.11 | Y | Y | Y | Y | Y | Y | Y | Y | Y
22INR0457 | Anson BAT | Jones | 2026-08-01 | Battery | 150.6 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0354 | Bordertown BESS | Starr | 2026-08-15 | Battery | 100 | Y | Y | Y | Y | Y | Y | Y | Y | Y
21INR0031 | Indigo Solar | Fisher | 2026-08-17 | Solar | 150 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0533 | Padua Grid BESS Unit 2 | Bexar | 2026-08-31 | Battery | 150.94 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0199 | Bonham Solar 1 | Limestone | 2026-08-31 | Solar | 138.4 | Y | Y | Y | Y | Y | Y | Y | Y | Y
26INR0521 | Millers Branch Solar III | Haskell | 2026-10-01 | Solar | 133 | Y | Y | Y | Y | Y | Y | Y | Y | Y | Split INR fix for Millers Branch Solar 1
23INR0056 | Caliche Mound Solar | Deaf Smith | 2026-10-10 | Solar | 408.21 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0235 | Hoyte Solar | Milam | 2026-12-15 | Solar | 206.75 | Y | Y | Y | Y | Y | Y | Y | Y | Y
26INR0447 | Honey Mesquite Wind Farm | Glasscock | 2026-12-15 | Wind | 180.48 | Y | Y | Y | Y | Y | Y | Y | Y | Y
21INR0421 | Armadillo Solar | Navarro | 2026-12-31 | Solar | 200.09 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0084 | Lavaca Bay Solar | Matagorda | 2026-12-31 | Solar | 243.46 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0188 | Tehuacana Creek Solar SLF | Navarro | 2027-03-10 | Solar | 505.5 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0189 | Tehuacana Creek BESS SLF | Navarro | 2027-03-10 | Battery | 419 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0206 | Glasgow Solar | Navarro | 2027-03-16 | Solar | 203.5 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0207 | Glasgow Storage | Navarro | 2027-03-16 | Battery | 101 | Y | Y | Y | Y | Y | Y | Y | Y | Y
22INR0437 | TORMES SOLAR | Navarro | 2027-03-31 | Solar | 382.12 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0355 | Anatole Renewable Energy Storage | Henderson | 2027-03-31 | Battery | 207.82 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0018 | Yellow Cat Wind | Navarro | 2027-04-01 | Wind | 262 | Y | Y | Y | Y | Y | Y | Y | Y | Y
26INR0034 | Bracero Pecan Storage | Reeves | 2027-04-01 | Battery | 232 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0425 | Two Brothers ESS | Victoria | 2027-04-07 | Battery | 152 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0086 | Hanson Solar | Coleman | 2027-04-17 | Solar | 398.83 | Y | Y | Y | Y | Y | Y | Y | Y | Y
24INR0298 | Leighton Solar SLF | Limestone | 2027-04-30 | Solar | 183 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0093 | Alila Solar | San Patricio | 2027-05-08 | Solar | 256.5 | Y | Y | Y | Y | Y | Y | Y | Y | Y
23INR0181 | Starling Storage | Gonzales | 2027-05-15 | Battery | 63.6 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0391 | Purple Sage BESS 1 | Collin | 2027-05-30 | Battery | 156 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0392 | Purple Sage BESS 2 | Collin | 2027-05-30 | Battery | 156 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0060 | Argenta Solar | Bee | 2027-07-01 | Solar | 310 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0061 | Argenta Storage | Bee | 2027-07-01 | Battery | 192 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0262 | Shepard Energy Storage | Galveston | 2027-07-01 | Battery | 256.37 | Y | Y | Y | Y | Y | Y | Y | Y | Y
25INR0208 | Iron Belt Energy Storage | Borden | 2026-07-31 | Battery | 401.9 | Y | Y | N | Y | Y | Y | Y | Y | Y
22INR0342 | Matagorda Solar | Matagorda | 2026-08-24 | Solar | 101 | Y | Y | N | Y | Y | Y | Y | Y | Y
23INR0061 | Noria Solar DCC | Nueces | 2026-10-13 | Solar | 145 | Y | Y | N | Y | Y | Y | Y | Y | Y
26INR0543 | Three Canes Solar SLF | Navarro | 2027-03-10 | Solar | 333 | Y | Y | N | Y | Y | Y | Y | Y | Y
24INR0291 | Rubicon Alpha Wind | Haskell | 2027-07-01 | Wind | 225.6 | Y | Y | N | Y | Y | Y | Y | Y | Y
23INR0089 | Donegal Solar | Dickens | 2027-03-01 | Solar | 201.68 | Y | Y | N | Y | N | Y | Y | Y | Y
26INR0189 | Skipjack Energy Storage | Brazoria | 2027-04-05 | Battery | 150.6 | Y | Y | N | Y | N | Y | Y | Y | Y
23INR0035 | Starling Solar | Gonzales | 2027-05-15 | Solar | 123 | Y | Y | N | Y | N | Y | Y | Y | Y
23INR0202 | Erath County Solar | Erath | 2026-08-27 | Solar | 207.4 | Y | Y | N | Y | N | Y | Y | Y | Y
19INR0023 | Monte Alto 2 Wind | Willacy | 2027-06-01 | Wind | 307.9 | Y | N | Y | Y | Y | Y | Y | Y | Y
22INR0239 | Rockefeller Storage | Schleicher | 2027-06-01 | Battery | 206.8 | Y | N | Y | Y | Y | Y | Y | Y | Y
25INR0102 | Austin Bayou Solar | Brazoria | 2027-06-01 | Solar | 502.48 | Y | N | Y | Y | Y | Y | Y | Y | Y
23INR0244 | Tiger Solar | Jones | 2027-06-30 | Solar | 255 | Y | N | Y | Y | Y | Y | Y | Y | Y
24INR0386 | Black & Gold Energy Storage | Menard | 2027-06-30 | Battery | 254.58 | Y | N | Y | Y | Y | Y | Y | Y | Y
25INR0131 | SOSA Storage | Madison | 2027-09-30 | Battery | 157.36 | Y | N | Y | Y | Y | Y | Y | Y | Y
25INR0081 | SanPat Solar I | San Patricio | 2027-06-01 | Solar | 308.88 | Y | N | N | Y | Y | Y | Y | Y | Y
26INR0269 | Moccasin Solar | Stonewall | 2027-06-01 | Solar | 806.8 | Y | N | N | Y | Y | Y | Y | Y | Y
25INR0319 | Northington Solar | Wharton | 2027-07-15 | Solar | 129.81 | Y | N | N | Y | Y | Y | Y | Y | Y
22INR0209 | Felix North Solar | Wilbarger | 2027-07-31 | Solar | 100.54 | Y | N | N | Y | Y | Y | Y | Y | Y
27INR0004 | Dundee North Wind | Wilbarger | 2027-07-31 | Wind | 307.72 | Y | N | N | Y | Y | Y | Y | Y | Y
27INR0005 | Dundee South A Wind | Baylor | 2027-07-31 | Wind | 307.23 | Y | N | N | Y | Y | Y | Y | Y | Y
27INR0007 | Felix East Solar | Wilbarger | 2027-07-31 | Solar | 301.44 | Y | N | N | Y | Y | Y | Y | Y | Y
27INR0011 | Dundee South B Wind | Baylor | 2027-07-31 | Wind | 300.27 | Y | N | N | Y | Y | Y | Y | Y | Y
27INR0012 | Felix West Solar | Wilbarger | 2027-07-31 | Solar | 200.95 | Y | N | N | Y | Y | Y | Y | Y | Y
25INR0103 | Elio BESS | Brazoria | 2027-08-05 | Battery | 317.2 | Y | N | N | Y | Y | Y | Y | Y | Y
22INR0220 | Lamkin Solar | Comanche | 2027-08-08 | Solar | 101.5 | Y | N | N | Y | Y | Y | Y | Y | Y
24INR0498 | Fort Watt Storage | Tarrant | 2027-08-30 | Battery | 205.4 | Y | N | N | Y | Y | Y | Y | Y | Y
24INR0059 | Cuchillas Solar | Webb | 2027-09-01 | Solar | 305.6 | Y | N | N | Y | Y | Y | Y | Y | Y
25INR0052 | SanPat Solar II | San Patricio | 2027-09-01 | Solar | 256.23 | Y | N | N | Y | Y | Y | Y | Y | Y
23INR0059 | Briggs Solar | Haskell | 2027-09-15 | Solar | 323.7 | Y | N | N | Y | Y | Y | Y | Y | Y
24INR0058 | Briggs Storage | Haskell | 2027-09-15 | Battery | 70.39 | Y | N | N | Y | Y | Y | Y | Y | Y
21INR0326 | Dove Run Solar | Duval | 2027-10-15 | Solar | 120.86 | Y | N | N | Y | Y | Y | Y | Y | Y
25INR0109 | Sun Cactus Solar | Duval | 2027-10-15 | Solar | 120.63 | Y | N | N | Y | Y | Y | Y | Y | Y
25INR0425 | Aldrin 345 BESS | Brazoria | 2027-12-01 | Battery | 362 | Y | N | N | Y | Y | Y | Y | Y | Y
23INR0029 | Cedar Bayou 5 (TEF - Due Diligence) | Chambers | 2027-12-15 | Gas | 674 | Y | N | N | Y | Y | Y | Y | Y | Y
20INR0162 | Diamondback solar | Starr | 2027-12-31 | Solar | 203.8 | Y | N | N | Y | Y | Y | Y | Y | Y
25INR0046 | Blue Skies BESS | Hill | 2027-12-31 | Battery | 306.26 | Y | N | N | Y | Y | Y | Y | Y | Y
25INR0282 | Hornet Solar II SLF | Swisher | 2027-06-01 | Solar | 208.95 | Y | N | N | Y | N | Y | Y | Y | Y
25INR0283 | Hornet Storage II SLF | Swisher | 2027-06-01 | Battery | 207.96 | Y | N | N | Y | N | Y | Y | Y | Y
19INR0022 | Monte Alto I | Willacy | 2027-12-31 | Wind | 141.5 | Y | N | N | Y | N | Y | Y | Y | Y
26INR0452 | Cannibal Draw Solar | Glasscock | 2028-04-10 | Solar | 149.5 | Y | N | N | N | N | Y | Y | Y | Y
26INR0453 | Cannibal Draw Storage | Glasscock | 2028-04-10 | Battery | 98.6 | Y | N | N | N | N | Y | Y | Y | Y
24INR0124 | High Noon Solar | Hill | 2028-05-09 | Solar | 182 | Y | N | N | N | N | Y | Y | Y | Y
24INR0126 | High Noon Storage | Hill | 2028-05-09 | Battery | 94 | Y | N | N | N | N | Y | Y | Y | Y
23INR0116 | Cantaloupe Solar | Reeves | 2028-07-01 | Solar | 307 | Y | N | N | N | N | Y | Y | Y | Y
24INR0201 | Short Creek Solar | Wichita | 2029-03-02 | Solar | 625 | Y | N | N | N | Y | N | Y | Y | Y
25INR0068 | High Chap Solar | Brazoria | 2028-06-26 | Solar | 152.25 | Y | N | N | N | N | N | Y | Y | Y
24INR0258 | Zeissel Solar | Knox | 2028-06-30 | Solar | 457.5 | Y | N | N | N | N | N | Y | Y | Y
23INR0248 | Limewood Storage | Bell | 2028-12-29 | Battery | 50 | Y | N | N | N | N | N | Y | Y | Y
22INR0401 | Eval Storage | Cameron | 2028-12-31 | Battery | 251.85 | Y | N | N | N | N | N | Y | Y | Y
27INR0127 | Bigway Solar I | King | 2028-12-31 | Solar | 203 | Y | N | N | N | N | N | Y | Y | Y
27INR0128 | Bigway Solar II | King | 2028-12-31 | Solar | 203 | Y | N | N | N | N | N | Y | Y | Y
21INR0207 | Quantum Solar | Haskell | 2026-03-31 | Solar | 321.66 | Y | N | Y | N | Y | N | N | Y | N
25INR0101 | Mallard BESS | Collin | 2026-04-02 | Battery | 257.3 | Y | N | Y | N | Y | N | N | Y | N
26INR0310 | Quantum Storage | Haskell | 2026-06-30 | Battery | 321.75 | Y | N | Y | N | Y | N | N | Y | N
21INR0265 | Sisters Solar | Ector | 2027-05-31 | Solar | 301.6 | Y | N | Y | N | Y | N | N | Y | N
21INR0428 | Pecan Prairie North | Leon | 2027-05-01 | Solar | 321.27 | Y | N | Y | N | Y | N | N | Y | N
22INR0262 | Sequoia II Solar | Callahan | 2026-11-21 | Solar | 417.47 | Y | N | Y | N | Y | N | N | Y | N
22INR0499 | Aquilla Lake 3 Wind | Hill | 2027-03-01 | Wind | 297.4 | Y | N | Y | N | Y | N | N | Y | N
22INR0503 | Tidwell Prairie II Batt | Robertson | 2026-03-01 | Battery | 203.62 | Y | N | Y | N | Y | N | N | Y | N
22INR0504 | Barton Branch IA | Robertson | 2026-03-01 | Battery | 203.62 | Y | N | Y | N | Y | N | N | Y | N
23INR0231 | Rocinante Solar | Gonzales | 2026-11-01 | Solar | 95.29 | Y | N | Y | N | Y | N | N | Y | N
23INR0266 | Langer Storage | Bosque | 2027-03-01 | Battery | 61.53 | Y | N | Y | N | Y | N | N | Y | N
23INR0300 | Greater Bryant G Solar | Midland | 2026-09-16 | Solar | 17.7 | Y | N | Y | N | Y | N | N | Y | N
24INR0042 | Yaupon Solar SLF | Milam | 2027-07-01 | Solar | 200.78 | Y | N | Y | N | Y | N | N | Y | N
24INR0186 | Rowdy Creek Solar | Lamar | 2027-04-01 | Solar | 351.78 | Y | N | Y | N | Y | N | N | Y | N
24INR0187 | Rowdy Creek BESS | Lamar | 2027-04-01 | Battery | 175.89 | Y | N | Y | N | Y | N | N | Y | N
24INR0303 | Erika Solar | Kaufman | 2027-06-30 | Solar | 200.5 | Y | N | Y | N | Y | N | N | Y | N
24INR0331 | Chisme Storage | Brown | 2027-04-13 | Battery | 146 | Y | N | Y | N | Y | N | N | Y | N
24INR0333 | Chisme Solar | Brown | 2027-04-13 | Solar | 147 | Y | N | Y | N | Y | N | N | Y | N
24INR0476 | DOS RIOS ENERGY STORAGE SLF | Milam | 2027-03-15 | Battery | 164.5 | Y | N | Y | N | Y | N | N | Y | N
24INR0485 | Rutile BESS | Runnels | 2026-06-30 | Battery | 100.65 | Y | N | Y | N | Y | N | N | Y | N
24INR0490 | Lupinus Storage 3 | Franklin | 2026-09-21 | Battery | 50.9 | Y | N | Y | N | Y | N | N | Y | N
24INR0543 | Thomas Cameron BESS | Lampasas | 2027-05-03 | Battery | 201.52 | Y | N | Y | N | Y | N | N | Y | N
25INR0055 | Three W Solar | Hill | 2026-06-01 | Solar | 110.89 | Y | N | Y | N | Y | N | N | Y | N
25INR0166 | Padrino Solar | Hill | 2026-07-30 | Solar | 201.4 | Y | N | Y | N | Y | N | N | Y | N
25INR0168 | Piedra Solar | Freestone | 2026-12-22 | Solar | 281.7 | Y | N | Y | N | Y | N | N | Y | N
25INR0169 | Piedra BESS | Freestone | 2026-12-22 | Battery | 103.65 | Y | N | Y | N | Y | N | N | Y | N
25INR0215 | Middlebrook BESS | Nacogdoches | 2027-06-30 | Battery | 158.63 | Y | N | Y | N | Y | N | N | Y | N
25INR0368 | Echols Creek Solar | Lamar | 2027-04-03 | Solar | 201.15 | Y | N | Y | N | Y | N | N | Y | N
25INR0432 | Brotherton Storage | Anderson | 2026-12-31 | Battery | 176.13 | Y | N | Y | N | Y | N | N | Y | N
25INR0557 | McCamey's Castle Battery | Upton | 2025-12-15 | Battery | 409.6 | Y | N | Y | N | Y | N | N | Y | N
25INR0706 | Bocanova Power II | Brazoria | 2026-05-01 | Battery | 150.46 | Y | N | Y | N | Y | N | N | Y | N
26INR0021 | Crossroads Wind | Victoria | 2027-06-30 | Wind | 276.7 | Y | N | Y | N | Y | N | N | Y | N
26INR0250 | Duffy BESS | Matagorda | 2026-12-31 | Battery | 235.9 | Y | N | Y | N | Y | N | N | Y | N
26INR0309 | Solace Storage | Haskell | 2026-03-31 | Battery | 321.79 | Y | N | Y | N | Y | N | N | Y | N
27INR0056 | Laurel Wind Energy Center | Pecos | 2027-03-28 | Wind | 306.6 | Y | N | Y | N | Y | N | N | Y | N
27INR0080 | Laurel Storage Energy Center | Pecos | 2027-03-28 | Battery | 200.8 | Y | N | Y | N | Y | N | N | Y | N
29INR0015 | Funston Solar | Jones | 2027-07-01 | Solar | 351.4 | Y | N | Y | N | Y | N | N | Y | N
28INR0024 | Padua Grid BESS Unit 3 | Bexar | 2026-05-15 | Battery | 201.35 | Y | N | Y | N | Y | N | N | Y | N
22INR0605 | Camino Santiago Solar | Milam | 2027-02-18 | Solar | 196.3 | Y | N | Y | N | Y | N | N | Y | N
25INR0229 | OCI Cobb Creek Solar | Hill | 2026-12-01 | Solar | 203.1 | Y | N | Y | N | Y | N | N | Y | N
25INR0233 | OCI Cobb Creek ESS | Hill | 2026-12-01 | Battery | 201.6 | Y | N | Y | N | Y | N | N | Y | N
27INR0297 | Tolivar Power Plant (TEF- Due Diligence) | Reeves | 2027-05-06 | Gas | 224.5 | Y | N | Y | N | Y | N | N | Y | N
27INR0321 | Rock Island Generating (TEF -Due Diligence) | Colorado | 2027-06-01 | Gas | 121.8 | Y | N | Y | N | Y | N | N | Y | N
23INR0561 | Cascabel Wind 2 | Zapata | 2027-12-01 | Wind | 197.75 | Y | N | N | N | Y | N | N | Y | N
24INR0150 | Lupinus Solar 1 | Franklin | 2027-09-13 | Solar | 164.86 | Y | N | N | N | Y | N | N | Y | N
24INR0153 | Lupinus Storage 1 | Franklin | 2027-09-13 | Battery | 82.97 | Y | N | N | N | Y | N | N | Y | N
24INR0418 | Middlebrook Solar Limited Liability Company | Nacogdoches | 2027-08-13 | Solar | 316.19 | Y | N | N | N | Y | N | N | Y | N
24INR0422 | Hollow Branch Creek Solar | Leon | 2027-12-31 | Solar | 460 | Y | N | N | N | Y | N | N | Y | N
24INR0424 | Cascabel Wind 1 | Zapata | 2027-12-01 | Wind | 197.75 | Y | N | N | N | Y | N | N | Y | N
25INR0122 | Vial BESS | Hill | 2027-09-15 | Battery | 135.18 | Y | N | N | N | Y | N | N | Y | N
25INR0281 | Cosper Solar | Bell | 2027-11-12 | Solar | 148.16 | Y | N | N | N | Y | N | N | Y | N
25INR0370 | Willis Storage | Rains | 2027-08-13 | Battery | 176.13 | Y | N | N | N | Y | N | N | Y | N
25INR0441 | Dios BESS | Jackson | 2027-12-31 | Battery | 201.08 | Y | N | N | N | Y | N | N | Y | N
26INR0241 | Sol Marina Energy Center | Ellis | 2027-10-29 | Solar | 175.3 | Y | N | N | N | Y | N | N | Y | N
26INR0242 | Sol Marina Energy Center BESS | Ellis | 2027-10-29 | Battery | 57.15 | Y | N | N | N | Y | N | N | Y | N
26INR0380 | Pepper Solar Farm | McLennan | 2027-09-20 | Solar | 120.69 | Y | N | N | N | Y | N | N | Y | N
27INR0399 | Resaca Oasis Storage | Cameron | 2027-09-20 | Battery | 200.7 | Y | N | N | N | Y | N | N | Y | N
20INR0086 | Arroyo Solar | Cameron | 2028-02-22 | Solar | 100 | Y | N | N | N | N | N | N | Y | N
23INR0137 | BRP Diran BESS | Wharton | 2028-01-31 | Battery | 100.63 | Y | N | N | N | N | N | N | Y | N
24INR0442 | Midnight Sun Energy Storage | Crockett | 2028-06-29 | Battery | 510 | Y | N | N | N | N | N | N | Y | N
25INR0112 | August Draw Energy | Reeves | 2028-06-27 | Solar | 250 | Y | N | N | N | N | N | N | Y | N
26INR0255 | Operation Sunshine | Concho | 2028-03-12 | Solar | 603.2 | Y | N | N | N | N | N | N | Y | N
26INR0357 | Operation Sunshine Storage | Concho | 2028-03-12 | Battery | 409.8 | Y | N | N | N | N | N | N | Y | N
26INR0407 | Rock Creek BESS | Kendall | 2028-03-29 | Battery | 251.05 | Y | N | N | N | N | N | N | Y | N
27INR0076 | Bob Creek Wind | Sterling | 2028-07-01 | Wind | 240 | Y | N | N | N | N | N | N | Y | N
27INR0243 | Brookview Road BESS | Harris | 2028-05-02 | Battery | 203.2 | Y | N | N | N | N | N | N | Y | N
23INR0479 | Taormina Storage | Bexar | 2029-05-26 | Battery | 231.86 | Y | N | N | N | N | N | N | Y | N
25INR0008 | BasRanch (TEF - Due Diligence) | Ward | 2028-12-01 | Gas | 1350 | Y | N | N | N | N | N | N | Y | N
27INR0047 | Sunscape Renewable Energy Solar SLF | Nueces | 2029-01-26 | Solar | 522.75 | Y | N | N | N | N | N | N | Y | N
27INR0048 | Sunscape Renewable Energy Storage SLF | Nueces | 2029-01-26 | Battery | 522.75 | Y | N | N | N | N | N | N | Y | N
27INR0118 | Grapefruit Solar | Hidalgo | 2028-12-31 | Solar | 291.4 | Y | N | N | N | N | N | N | Y | N
27INR0126 | Corvus Solar | Webb | 2028-11-12 | Solar | 201.5 | Y | N | N | N | N | N | N | Y | N
27INR0224 | Leopard BESS | Victoria | 2028-07-09 | Battery | 264.24 | Y | N | N | N | N | N | N | Y | N
28INR0127 | Half Moon Solar | Starr | 2029-07-01 | Solar | 512.5 | Y | N | N | N | N | N | N | Y | N
New generators that have a signed IA in 2028MIN and 2028-2031SUM ONLY.
GINR Reference Number | Project Name | County | Projected COD | Fuel | MW For Grid | IA Signed | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM | Comments
18INR0073 | Sweetwater 1 repower | Nolan | 2024-11-30 | Wind | 3 | Y | N | Y | Y | Y | Y | Repower
16INR0112 | Loma Pinta Wind | La Salle | 2025-09-01 | Wind | 197.01 | Y | N | Y | Y | Y | Y
25INR0557 | McCamey's Castle Battery | Upton | 2025-12-15 | Battery | 409.6 | Y | N | Y | Y | Y | Y
25INR0688 | Giga Texas Data Center | Travis | 2025-12-15 | Battery | 133 | Y | N | Y | Y | Y | Y
21INR0207 | Quantum Solar | Haskell | 2026-03-31 | Solar | 320.8 | Y | N | Y | Y | Y | Y
24INR0313 | Backbone Creek BESS | Burnet | 2026-04-21 | Battery | 121 | Y | N | Y | Y | Y | Y
21INR0256 | Amsterdam Solar | Brazoria | 2026-05-01 | Solar | 509.88 | Y | N | Y | Y | Y | Y
22INR0417 | Amsterdam Storage | Brazoria | 2026-05-01 | Battery | 201.13 | Y | N | Y | Y | Y | Y
25INR0166 | Padrino Solar | Hill | 2026-05-01 | Solar | 201.4 | Y | N | Y | Y | Y | Y
24INR0514 | Rogers Draw BESS | Gillespie | 2026-05-10 | Battery | 145.55 | Y | N | Y | Y | Y | Y
26INR0417 | GAMAY ENERGY STORAGE | Brazoria | 2026-05-15 | Battery | 418.6 | Y | N | Y | Y | Y | Y
25INR0480 | Bell Creek BESS | Brazoria | 2026-05-15 | Battery | 200.9 | Y | N | Y | Y | Y | Y
28INR0024 | Padua Grid BESS Unit 3 | Bexar | 2026-05-15 | Battery | 201.35 | Y | N | Y | Y | Y | Y
24INR0471 | McGee Storage | Henderson | 2026-05-29 | Battery | 151.39 | Y | N | Y | Y | Y | Y
25INR0055 | Three W Solar | Hill | 2026-06-01 | Solar | 110.5 | Y | N | Y | Y | Y | Y
24INR0042 | Yaupon Solar SLF | Milam | 2026-06-15 | Solar | 204.08 | Y | N | Y | Y | Y | Y
23INR0300 | Greater Bryant G Solar | Midland | 2026-06-22 | Solar | 17.7 | Y | N | Y | Y | Y | Y
23INR0502 | Adelite Storage | Milam | 2026-06-30 | Battery | 231.88 | Y | N | Y | Y | Y | Y
25INR0202 | East West BESS | Kerr | 2026-06-30 | Battery | 122.6 | Y | N | Y | Y | Y | Y
26INR0310 | Quantum Storage | Haskell | 2026-06-30 | Battery | 320.6 | Y | N | Y | Y | Y | Y
22INR0301 | Fortuna Wind | Jack | 2026-07-01 | Wind | 295.3 | Y | N | Y | Y | Y | Y
24INR0274 | Bufflehead BESS | Collin | 2026-07-06 | Battery | 153.3 | Y | N | Y | Y | Y | Y
26INR0309 | Solace Storage | Haskell | 2026-07-23 | Battery | 321.02 | Y | N | Y | Y | Y | Y
22INR0262 | Sequoia II Solar | Callahan | 2026-07-31 | Solar | 417.47 | Y | N | Y | Y | Y | Y
25INR0382 | HappyDogSolar | Milam | 2026-09-14 | Solar | 85.54 | Y | N | Y | Y | Y | Y
25INR0442 | Happy Dog Storage | Milam | 2026-09-14 | Battery | 104.47 | Y | N | Y | Y | Y | Y
21INR0362 | Oystercatcher Solar | Ellis | 2026-09-17 | Solar | 218.1 | Y | N | Y | Y | Y | Y
24INR0484 | Lupinus Solar 3 | Franklin | 2026-09-21 | Solar | 100.8 | Y | N | Y | Y | Y | Y
24INR0490 | Lupinus Storage 3 | Franklin | 2026-09-21 | Battery | 50.9 | Y | N | Y | Y | Y | Y
25INR0168 | Piedra Solar | Freestone | 2026-09-30 | Solar | 282 | Y | N | Y | Y | Y | Y
25INR0169 | Piedra BESS | Freestone | 2026-09-30 | Battery | 103.8 | Y | N | Y | Y | Y | Y
21INR0391 | Grandslam Solar | Atascosa | 2026-11-28 | Solar | 121.89 | Y | N | Y | Y | Y | Y
24INR0452 | Longfellow Solar I | Pecos | 2026-12-01 | Solar | 178.2 | Y | N | Y | Y | Y | Y
24INR0454 | Longfellow Solar II | Pecos | 2026-12-01 | Solar | 207.36 | Y | N | Y | Y | Y | Y
25INR0229 | OCI Cobb Creek Solar | Hill | 2026-12-01 | Solar | 203.1 | Y | N | Y | Y | Y | Y
25INR0233 | OCI Cobb Creek ESS | Hill | 2026-12-01 | Battery | 201.6 | Y | N | Y | Y | Y | Y
26INR0375 | Avalon BESS | Fort Bend | 2026-12-01 | Battery | 522.12 | Y | N | Y | Y | Y | Y
26INR0474 | Sorghum BESS | Wharton | 2026-12-01 | Battery | 208.9 | Y | N | Y | Y | Y | Y
24INR0275 | Picadillo BESS | Martin | 2026-12-15 | Battery | 100.83 | Y | N | Y | Y | Y | Y
26INR0201 | Rock Rose Energy BESS | Fort Bend | 2026-12-15 | Battery | 211.5 | Y | N | Y | Y | Y | Y
25INR0230 | Great Rock BESS | Leon | 2026-12-20 | Battery | 300.9 | Y | N | Y | Y | Y | Y
21INR0444 | Long Point Storage | Brazoria | 2026-12-30 | Battery | 100.62 | Y | N | Y | Y | Y | Y
22INR0307 | Desert Vine Solar | Zapata | 2026-12-30 | Solar | 121.29 | Y | N | Y | Y | Y | Y
24INR0401 | Portside Energy Center (Solar) SLF | Victoria | 2026-12-31 | Solar | 41.11 | Y | N | Y | Y | Y | Y
24INR0403 | Portside Energy Center (BESS) SLF | Victoria | 2026-12-31 | Battery | 41.11 | Y | N | Y | Y | Y | Y
26INR0290 | Cold Creek Solar 2 | Schleicher | 2026-12-31 | Solar | 445.41 | Y | N | Y | Y | Y | Y
26INR0291 | Cold Creek Storage 2 | Schleicher | 2026-12-31 | Battery | 174.24 | Y | N | Y | Y | Y | Y
25INR0170 | Pinewood Solar | Brazoria | 2027-01-09 | Solar | 150.68 | Y | N | Y | Y | Y | Y
26INR0340 | SOUTHERN SELECT ENERGY STORAGE | Galveston | 2027-01-15 | Battery | 404.3 | Y | N | Y | Y | Y | Y
25INR0253 | Whiskey BESS | Van Zandt | 2027-01-30 | Battery | 153.72 | Y | N | Y | Y | Y | Y
22INR0605 | Camino Santiago Solar | Milam | 2027-02-18 | Solar | 196.3 | Y | N | Y | Y | Y | Y
23INR0266 | Langer Storage | Bosque | 2027-03-01 | Battery | 61.53 | Y | N | Y | Y | Y | Y
22INR0499 | Aquilla Lake 3 Wind | Hill | 2027-03-01 | Wind | 304.6 | Y | N | Y | Y | Y | Y
24INR0476 | DOS RIOS ENERGY STORAGE SLF | Milam | 2027-03-15 | Battery | 164.5 | Y | N | Y | Y | Y | Y
27INR0056 | Laurel Wind Energy Center | Pecos | 2027-03-28 | Wind | 501.76 | Y | N | Y | Y | Y | Y
27INR0080 | Laurel Storage Energy Center | Pecos | 2027-03-28 | Battery | 200.8 | Y | N | Y | Y | Y | Y
24INR0186 | Rowdy Creek Solar | Lamar | 2027-04-01 | Solar | 351.78 | Y | N | Y | Y | Y | Y
24INR0187 | Rowdy Creek BESS | Lamar | 2027-04-01 | Battery | 175.89 | Y | N | Y | Y | Y | Y
25INR0554 | Dan Kearney BESS | Brazoria | 2027-04-01 | Battery | 200.78 | Y | N | Y | Y | Y | Y
25INR0334 | Star Dairy Storage | Lamar | 2027-04-03 | Battery | 204.93 | Y | N | Y | Y | Y | Y
24INR0154 | Lupinus Solar 2 | Franklin | 2027-04-03 | Solar | 244.24 | Y | N | Y | Y | Y | Y
24INR0155 | Lupinus Storage 2 | Franklin | 2027-04-03 | Battery | 122.92 | Y | N | Y | Y | Y | Y
25INR0164 | Star Dairy Solar | Lamar | 2027-04-03 | Solar | 125.61 | Y | N | Y | Y | Y | Y
24INR0304 | Jack Barton BESS | Jack | 2027-04-13 | Battery | 47.34 | Y | N | Y | Y | Y | Y
27INR0297 | Tolivar Power Plant (TEF- Due Diligence) | Reeves | 2027-04-15 | Gas | 224.5 | Y | N | Y | Y | Y | Y
26INR0241 | Sol Marina Energy Center | Ellis | 2027-04-17 | Solar | 175.3 | Y | N | Y | Y | Y | Y
26INR0242 | Sol Marina Energy Center BESS | Ellis | 2027-04-17 | Battery | 57.15 | Y | N | Y | Y | Y | Y
23INR0207 | El Patrimonio Solar | Bexar | 2027-04-29 | Solar | 152.32 | Y | N | Y | Y | Y | Y
26INR0314 | Brazos River BESS | Brazoria | 2027-04-30 | Battery | 180.36 | Y | N | Y | Y | Y | Y
22INR0281 | Pink Solar | Hunt | 2027-04-30 | Solar | 151.9 | Y | N | Y | Y | Y | Y
21INR0428 | Nabatoto Solar North | Leon | 2027-05-01 | Solar | 321.27 | Y | N | Y | Y | Y | Y
24INR0285 | APV Plumwood Storage | Chambers | 2027-05-01 | Battery | 200.82 | Y | N | Y | Y | Y | Y
25INR0384 | Zorro BESS | Van Zandt | 2027-05-01 | Battery | 153.69 | Y | N | Y | Y | Y | Y
24INR0543 | Thomas Cameron BESS | Lampasas | 2027-05-03 | Battery | 201.52 | Y | N | Y | Y | Y | Y
23INR0340 | Larkspur Energy Storage | Upton | 2027-05-05 | Battery | 307.46 | Y | N | Y | Y | Y | Y
23INR0289 | Skull Creek Solar | Anderson | 2027-05-16 | Solar | 137.26 | Y | N | Y | Y | Y | Y
27INR0243 | Brookview Road BESS | Harris | 2027-05-31 | Battery | 203.2 | Y | N | Y | Y | Y | Y
25INR0293 | TOCE BESS 1 | Wharton | 2027-06-01 | Battery | 205.2 | Y | N | Y | Y | Y | Y
25INR0236 | Austin Bayou Storage II | Brazoria | 2027-06-01 | Battery | 156.6 | Y | N | Y | Y | Y | Y
25INR0237 | Austin Bayou Storage III | Brazoria | 2027-06-01 | Battery | 156.6 | Y | N | Y | Y | Y | Y
21INR0022 | Red Holly Solar | Dawson | 2027-06-01 | Solar | 260 | Y | N | Y | Y | Y | Y
25INR0100 | Goldeneye BESS | Bell | 2027-06-01 | Battery | 201.6 | Y | N | Y | Y | Y | Y
25INR0235 | Austin Bayou Storage I | Brazoria | 2027-06-01 | Battery | 150.68 | Y | N | Y | Y | Y | Y
27INR0321 | Rock Island Generating (TEF -Due Diligence) | Colorado | 2027-06-01 | Gas | 121.8 | Y | N | Y | Y | Y | Y
24INR0303 | Erika Solar | Kaufman | 2027-06-30 | Solar | 204.08 | Y | N | Y | Y | Y | Y
24INR0356 | Cibeles Solar | McLennan | 2027-06-30 | Solar | 251 | Y | N | Y | Y | Y | Y
25INR0225 | Lucy Solar | Concho | 2027-06-30 | Solar | 351.3 | Y | N | Y | Y | Y | Y
26INR0021 | Crossroads Wind | Victoria | 2027-06-30 | Wind | 253.29 | Y | N | Y | Y | Y | Y
24INR0326 | Blarney Solar | Hopkins | 2027-07-01 | Solar | 81 | Y | N | Y | Y | Y | Y
26INR0431 | Big Rooter West Solar SLF | Robertson | 2027-07-01 | Solar | 403.42 | Y | N | Y | Y | Y | Y
29INR0015 | Funston Solar | Jones | 2027-07-01 | Solar | 351.4 | Y | N | Y | Y | Y | Y
21INR0520 | Yellow Viking Solar | Somervell | 2027-07-13 | Solar | 170.86 | Y | N | Y | Y | Y | Y
26INR0155 | Ross Solar | Refugio | 2027-07-31 | Solar | 1025.57 | Y | N | Y | Y | Y | Y
26INR0156 | Ross Storage | Refugio | 2027-07-31 | Battery | 510.99 | Y | N | Y | Y | Y | Y
23INR0200 | Paradiso BESS | Atascosa | 2027-08-01 | Battery | 100.92 | Y | N | Y | Y | Y | Y
23INR0441 | Bug Tussle Wind Project | Lamar | 2027-08-23 | Wind | 396.8 | Y | N | Y | Y | Y | Y
24INR0106 | Payne Battlecreek | Hill | 2027-08-25 | Solar | 84.99 | Y | N | Y | Y | Y | Y
23INR0040 | Dori BQ Solar | Harris | 2027-08-30 | Solar | 50.42 | Y | N | Y | Y | Y | Y
24INR0196 | Dori BQ BESS | Harris | 2027-08-30 | Battery | 154 | Y | N | Y | Y | Y | Y
21INR0210 | Adamstown Solar | Wichita | 2027-08-31 | Solar | 250.88 | Y | N | Y | Y | Y | Y
25INR0460 | Acker BESS | Castro | 2027-09-14 | Battery | 301.04 | Y | N | Y | Y | Y | Y
25INR0172 | Wolf Spring Solar | Dickens | 2027-09-16 | Solar | 195.7 | Y | N | Y | Y | Y | Y
25INR0173 | Wolf Spring Storage | Dickens | 2027-09-16 | Battery | 202.7 | Y | N | Y | Y | Y | Y
21INR0263 | Monarch Creek Wind | Throckmorton | 2027-09-17 | Wind | 284.3 | Y | N | Y | Y | Y | Y
22INR0426 | LUBIO SOLAR | Kaufman | 2027-09-17 | Solar | 54.47 | Y | N | Y | Y | Y | Y
27INR0399 | Resaca Oasis Storage | Cameron | 2027-09-20 | Battery | 200.7 | Y | N | Y | Y | Y | Y
26INR0180 | Cape Rich BESS | Navarro | 2027-09-23 | Battery | 150.52 | Y | N | Y | Y | Y | Y
23INR0261 | Dodd Solar I | Henderson | 2027-09-30 | Solar | 201.8 | Y | N | Y | Y | Y | Y
23INR0082 | Bottom Grass Solar | Colorado | 2027-10-01 | Solar | 508.61 | Y | N | Y | Y | Y | Y
23INR0083 | Bottom Grass BESS | Colorado | 2027-10-01 | Battery | 202.21 | Y | N | Y | Y | Y | Y
20INR0050 | Castro Solar | Castro | 2027-10-11 | Solar | 222.95 | Y | N | Y | Y | Y | Y
25INR0174 | Concho Pearl Solar | Concho | 2027-10-14 | Solar | 171.9 | Y | N | Y | Y | Y | Y
25INR0175 | Concho Pearl Storage | Concho | 2027-10-14 | Battery | 162.4 | Y | N | Y | Y | Y | Y
23INR0058 | Erin Solar | Wharton | 2027-11-30 | Solar | 202.5 | Y | N | Y | Y | Y | Y
23INR0080 | Soda Lake Solar 2 SLF | Crane | 2027-12-01 | Solar | 201.74 | Y | N | Y | Y | Y | Y
23INR0561 | Cascabel Wind 2 | Zapata | 2027-12-01 | Wind | 197.75 | Y | N | Y | Y | Y | Y
24INR0424 | Cascabel Wind 1 | Zapata | 2027-12-01 | Wind | 197.75 | Y | N | Y | Y | Y | Y
23INR0140 | Seine BESS | Foard | 2027-12-01 | Battery | 301.19 | Y | N | Y | Y | Y | Y
23INR0342 | Brizo BESS | Victoria | 2027-12-01 | Battery | 140.76 | Y | N | Y | Y | Y | Y
25INR0422 | Waterloo Solar 1 | Bastrop | 2027-12-01 | Solar | 200.64 | Y | N | Y | Y | Y | Y
25INR0447 | Waterloo BESS 1 | Bastrop | 2027-12-01 | Battery | 105.64 | Y | N | Y | Y | Y | Y
24INR0161 | Miranda Solar Project | McMullen | 2027-12-06 | Solar | 261.42 | Y | N | Y | Y | Y | Y
20INR0247 | Water Valley Wind Energy | Tom Green | 2027-12-15 | Wind | 180 | Y | N | Y | Y | Y | Y
25INR0080 | Meitner Solar | Gray | 2027-12-20 | Solar | 702.64 | Y | N | Y | Y | Y | Y
26INR0113 | Meitner Wind | Gray | 2027-12-20 | Wind | 709 | Y | N | Y | Y | Y | Y
24INR0269 | Bar Candela Solar SLF | Freestone | 2027-12-31 | Solar | 200.3 | Y | N | Y | Y | Y | Y
24INR0271 | Bar Candela Storage SLF | Freestone | 2027-12-31 | Battery | 199.6 | Y | N | Y | Y | Y | Y
24INR0422 | Hollow Branch Creek Solar | Leon | 2027-12-31 | Solar | 460 | Y | N | Y | Y | Y | Y
25INR0441 | Dios BESS | Jackson | 2028-01-31 | Battery | 201.08 | Y | N | N | Y | Y | Y
23INR0137 | BRP Diran BESS | Wharton | 2028-01-31 | Battery | 100.63 | Y | N | N | Y | Y | Y
25INR0097 | Soleil Solar | Clay | 2028-02-01 | Solar | 728.72 | Y | N | N | Y | Y | Y
20INR0086 | Arroyo Solar | Cameron | 2028-02-22 | Solar | 100 | Y | N | N | Y | Y | Y
24INR0065 | Keys Hollow Solar Phase II SLF | Goliad | 2028-03-10 | Solar | 204.08 | Y | N | N | Y | Y | Y
24INR0066 | Keys Hollow Storage Phase II SLF | Goliad | 2028-03-10 | Battery | 102.04 | Y | N | N | Y | Y | Y
24INR0067 | KEYS HOLLOW SOLAR SLF | Goliad | 2028-03-10 | Solar | 204.08 | Y | N | N | Y | Y | Y
24INR0068 | KEYS HOLLOW STORAGE SLF | Goliad | 2028-03-10 | Battery | 102.04 | Y | N | N | Y | Y | Y
23INR0324 | Lumberjack Storage | Cherokee | 2028-03-31 | Battery | 51.3 | Y | N | N | Y | Y | Y
24INR0382 | Remy Jade III Power Station | Harris | 2028-05-01 | Gas | 102 | Y | N | N | Y | Y | Y
24INR0410 | NRG Greens Bayou 6 (TEF-Due Diligence) | Harris | 2028-05-01 | Gas | 442 | Y | N | N | Y | Y | Y
25INR0313 | Staked Plains BESS | Lubbock | 2028-05-10 | Battery | 254.8 | Y | N | N | Y | Y | Y
21INR0029 | Red Holly Storage 1 | Dawson | 2028-05-30 | Battery | 50 | Y | N | N | Y | Y | Y
21INR0033 | Red Holly Storage | Dawson | 2028-05-30 | Battery | 50 | Y | N | N | Y | Y | Y
22INR0279 | Clutch City Solar Phase I | Brazoria | 2028-07-01 | Solar | 200.75 | Y | N | N | Y | Y | Y
25INR0330 | Clutch City Solar Phase II | Brazoria | 2028-07-01 | Solar | 251.27 | Y | N | N | Y | Y | Y
22INR0257 | Corazon Solar Phase II | Webb | 2028-06-01 | Solar | 203.9 | Y | N | N | N | Y | Y
26INR0074 | Anila Solar | Wilson | 2028-06-30 | Solar | 200.8 | Y | N | N | N | Y | Y
26INR0077 | Anila BESS | Wilson | 2028-06-30 | Battery | 209 | Y | N | N | N | Y | Y
23INR0345 | Elmax Power Station | Harris | 2028-07-05 | Gas | 518.83 | Y | N | N | N | Y | Y
26INR0359 | Uva Creek Solar | Borden | 2028-08-25 | Solar | 302.16 | Y | N | N | N | Y | Y
23INR0385 | Camp Creek Solar SLF | Robertson | 2028-09-15 | Solar | 110 | Y | N | N | N | Y | Y
23INR0423 | Camp Creek Storage SLF | Robertson | 2028-09-15 | Battery | 82.08 | Y | N | N | N | Y | Y
24INR0330 | TRAVIS KIMBRO BESS | Travis | 2028-09-18 | Battery | 36.84 | Y | N | N | N | Y | Y
27INR0047 | Sunscape Renewable Energy Solar SLF | Nueces | 2028-10-28 | Solar | 522.75 | Y | N | N | N | Y | Y
27INR0048 | Sunscape Renewable Energy Storage SLF | Nueces | 2028-10-28 | Battery | 522.75 | Y | N | N | N | Y | Y
20INR0143 | Tri-X Solar 1 SLF | Crane | 2028-12-01 | Solar | 201.5 | Y | N | N | N | Y | Y
27INR0118 | Grapefruit Solar | Hidalgo | 2028-12-31 | Solar | 301.2 | Y | N | N | N | Y | Y
24INR0108 | Louisa Energy Storage | Bexar | 2029-03-12 | Battery | 102.77 | Y | N | N | N | Y | Y
23INR0479 | Taormina Storage | Bexar | 2029-05-26 | Battery | 231.86 | Y | N | N | N | Y | Y
23INR0088 | Nockenut Springs Solar 1 | Guadalupe | 2029-06-05 | Solar | 203.17 | Y | N | N | N | Y | Y
24INR0156 | Moonstone Solar Project | Wilson | 2030-03-24 | Solar | 145.81 | Y | N | N | N | Y | Y
New generators that have a completed FIS in 2030 and 2031 ONLY.
GINR Reference Number | Project Name | County | Projected COD | Fuel | MW For Grid | FIS Completed | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM | Comments
24INR0567 | Wolf Hollow III | Hood | 2026-05-31 | Gas | 306.32 | Y | N | N | N | Y | Y
26INR0408 | Liatris Flexible Gas | Brazoria | 2026-12-31 | Gas | 204.71 | Y | N | N | N | Y | Y
26INR0519 | Sky Global West Houston | Austin | 2027-06-01 | Gas | 324.58 | Y | N | N | N | Y | Y
23INR0422 | Masroor Storage | Fannin | 2025-06-26 | Battery | 203 | Y | N | N | N | Y | Y
22INR0444 | Liberty Senate Solar 1 | Jack | 2025-10-27 | Solar | 202 | Y | N | N | N | Y | Y
23INR0101 | Atria Solar | Chambers | 2025-12-30 | Solar | 112.4 | Y | N | N | N | Y | Y
23INR0474 | AP Greenport | Travis | 2026-02-18 | Battery | 100.45 | Y | N | N | N | Y | Y
24INR0369 | Glory Bee Storage | Erath | 2026-04-14 | Battery | 101 | Y | N | N | N | Y | Y
24INR0368 | Glory Bee Solar | Erath | 2026-04-14 | Solar | 305 | Y | N | N | N | Y | Y
24INR0011 | Pinnington Storage | Jack | 2026-04-30 | Battery | 508.7 | Y | N | N | N | Y | Y
23INR0439 | Smokey Willie Solar SLF | Anderson | 2026-04-30 | Solar | 200.92 | Y | N | N | N | Y | Y
25INR0706 | Bocanova Power II | Brazoria | 2026-04-30 | Battery | 150.46 | Y | N | N | N | Y | Y
25INR0487 | Marick Rose BESS | Fort Bend | 2026-05-01 | Battery | 50.18 | Y | N | N | N | Y | Y
25INR0167 | Padrino BESS | Hill | 2026-05-23 | Battery | 100.77 | Y | N | N | N | Y | Y
25INR0466 | Yooperlite Storage | Wise | 2026-05-29 | Battery | 175.65 | Y | N | N | N | Y | Y
21INR0320 | Ion Solar | Ellis | 2026-05-29 | Solar | 384 | Y | N | N | N | Y | Y
23INR0495 | Cartwheel BESS 2 | Hopkins | 2026-06-15 | Battery | 156.91 | Y | N | N | N | Y | Y
24INR0569 | Hadrian Energy Storage | Wharton | 2026-06-15 | Battery | 101.2 | Y | N | N | N | Y | Y
25INR0420 | Houston BESS | Harris | 2026-06-15 | Battery | 227.9 | Y | N | N | N | Y | Y
27INR0096 | Rubicon Power BESS | Brazoria | 2026-06-30 | Battery | 301.38 | Y | N | N | N | Y | Y
24INR0570 | Marcus Energy Storage | Brazoria | 2026-09-01 | Battery | 201.04 | Y | N | N | N | Y | Y
25INR0371 | McMurtre Storage | Hunt | 2026-09-07 | Battery | 176.13 | Y | N | N | N | Y | Y
24INR0110 | Kildare | Jackson | 2026-09-30 | Solar | 70 | Y | N | N | N | Y | Y
25INR0133 | Rose Quartz BESS | Dimmit | 2026-12-01 | Battery | 101.41 | Y | N | N | N | Y | Y
24INR0450 | Smokey Willie BESS SLF | Anderson | 2026-12-15 | Battery | 100.2 | Y | N | N | N | Y | Y
23INR0318 | Marcelina Storage | Wilson | 2026-12-18 | Battery | 203.21 | Y | N | N | N | Y | Y
24INR0255 | Mitchell Plant Road Storage | Pecos | 2026-12-30 | Battery | 201.6 | Y | N | N | N | Y | Y
24INR0177 | Mitchell Plant Road Solar | Pecos | 2026-12-30 | Solar | 201.5 | Y | N | N | N | Y | Y
25INR0482 | Vault Solar | Palo Pinto | 2026-12-31 | Solar | 108.5 | Y | N | N | N | Y | Y
26INR0139 | Weathervane Storage SLF | Montague | 2026-12-31 | Battery | 32.47 | Y | N | N | N | Y | Y
26INR0138 | Weathervane Solar SLF | Montague | 2026-12-31 | Solar | 160.49 | Y | N | N | N | Y | Y
26INR0551 | Hastings Park BESS | Brazoria | 2026-12-31 | Battery | 256.34 | Y | N | N | N | Y | Y
26INR0321 | Windmill Ridge Storage | Brazoria | 2026-12-31 | Battery | 151.4 | Y | N | N | N | Y | Y
25INR0372 | Elan BESS | Fort Bend | 2026-12-31 | Battery | 202.65 | Y | N | N | N | Y | Y
27INR0068 | Jerboa BESS | Hidalgo | 2027-02-28 | Battery | 201.08 | Y | N | N | N | Y | Y
27INR0085 | Eagle Claw Energy Center | Grimes | 2027-03-15 | Battery | 200.84 | Y | N | N | N | Y | Y
25INR0301 | Van Zandt Energy Storage | Ector | 2027-04-13 | Battery | 256.58 | Y | N | N | N | Y | Y
24INR0331 | Chisme Storage | Brown | 2027-04-13 | Battery | 146 | Y | N | N | N | Y | Y
24INR0333 | Chisme Solar | Brown | 2027-04-13 | Solar | 147 | Y | N | N | N | Y | Y
27INR0102 | Cottonseed Energy Storage | Wharton | 2027-04-20 | Battery | 207.6 | Y | N | N | N | Y | Y
24INR0099 | Two Rivers Solar | Milam | 2027-05-10 | Solar | 208.7 | Y | N | N | N | Y | Y
27INR0235 | Ochoa Energy Storage II | Waller | 2027-06-03 | Battery | 516.56 | Y | N | N | N | Y | Y
25INR0138 | Champaign BESS | Glasscock | 2027-06-28 | Battery | 201.13 | Y | N | N | N | Y | Y
26INR0231 | Energy City BESS | Midland | 2027-06-30 | Battery | 204.9 | Y | N | N | N | Y | Y
25INR0363 | Emerald Hill Energy Storage | Dallas | 2027-06-30 | Battery | 261.02 | Y | N | N | N | Y | Y
25INR0471 | Tyler BESS | Smith | 2027-06-30 | Battery | 305.3 | Y | N | N | N | Y | Y
27INR0209 | Goby Energy Center | Brazoria | 2027-06-30 | Battery | 200.65 | Y | N | N | N | Y | Y
25INR0222 | Olympic BESS | Nueces | 2027-07-01 | Battery | 222.81 | Y | N | N | N | Y | Y
25INR0139 | Dolce BESS | Mitchell | 2027-07-01 | Battery | 100.65 | Y | N | N | N | Y | Y
26INR0432 | Big Rooter West Storage SLF | Robertson | 2027-07-01 | Battery | 402.44 | Y | N | N | N | Y | Y
26INR0411 | Tex-Bar ESS | Madison | 2027-07-01 | Battery | 201.5 | Y | N | N | N | Y | Y
24INR0167 | OCI SunRoper | Wharton | 2027-07-12 | Solar | 265.1 | Y | N | N | N | Y | Y
26INR0280 | Pethrus BESS | Wichita | 2027-07-27 | Battery | 174.08 | Y | N | N | N | Y | Y
25INR0370 | Willis Storage | Rains | 2027-08-13 | Battery | 176.13 | Y | N | N | N | Y | Y
24INR0340 | Mystic Springs Renewable Energy Storage SLF | Kaufman | 2027-08-31 | Battery | 258.83 | Y | N | N | N | Y | Y
24INR0339 | Mystic Springs Renewable Energy Solar SLF | Kaufman | 2027-08-31 | Solar | 258.83 | Y | N | N | N | Y | Y
25INR0396 | Stewart Grady BESS | Martin | 2027-09-01 | Battery | 150.5 | Y | N | N | N | Y | Y
24INR0153 | Lupinus Storage 1 | Franklin | 2027-09-13 | Battery | 82.97 | Y | N | N | N | Y | Y
24INR0150 | Lupinus Solar 1 | Franklin | 2027-09-13 | Solar | 164.86 | Y | N | N | N | Y | Y
25INR0122 | Vial BESS | Hill | 2027-09-15 | Battery | 135.18 | Y | N | N | N | Y | Y
27INR0234 | Maddox Solar | Grayson | 2027-09-17 | Solar | 101.3 | Y | N | N | N | Y | Y
25INR0431 | Millennium Energy Storage | Martin | 2027-09-17 | Battery | 102.59 | Y | N | N | N | Y | Y
26INR0184 | Arc Energy Storage | Lamar | 2027-09-21 | Battery | 204.5 | Y | N | N | N | Y | Y
26INR0472 | Bologna BESS | Wichita | 2027-09-23 | Battery | 202.56 | Y | N | N | N | Y | Y
26INR0253 | Goldfinch Solar | Van Zandt | 2027-09-23 | Solar | 150.54 | Y | N | N | N | Y | Y
25INR0657 | O'Bannion Energy Storage | Jack | 2027-09-25 | Battery | 306.4 | Y | N | N | N | Y | Y
26INR0355 | Pleiades Storage | Glasscock | 2027-09-29 | Battery | 205.5 | Y | N | N | N | Y | Y
25INR0374 | Meridian BESS | Bosque | 2027-10-01 | Battery | 31.23 | Y | N | N | N | Y | Y
25INR0494 | Willow Beach Wind | Brazoria | 2027-10-01 | Wind | 202.33 | Y | N | N | N | Y | Y
26INR0215 | JackGard BESS | Jack | 2027-10-10 | Battery | 200.59 | Y | N | N | N | Y | Y
25INR0369 | Echols Creek Storage | Lamar | 2027-10-13 | Battery | 100.57 | Y | N | N | N | Y | Y
24INR0375 | Possum Kingdom BESS | Jack | 2027-10-29 | Battery | 200.86 | Y | N | N | N | Y | Y
24INR0118 | Possum Kingdom Solar | Jack | 2027-10-29 | Solar | 262.22 | Y | N | N | N | Y | Y
25INR0281 | Cosper Solar | Bell | 2027-11-12 | Solar | 148.16 | Y | N | N | N | Y | Y
25INR0142 | Sagewood BESS | Glasscock | 2027-11-13 | Battery | 100.57 | Y | N | N | N | Y | Y
23INR0335 | BRP Bachman BESS | Wharton | 2027-12-01 | Battery | 411.04 | Y | N | N | N | Y | Y
23INR0360 | BRP Charon BESS | Fort Bend | 2027-12-01 | Battery | 410.81 | Y | N | N | N | Y | Y
24INR0461 | Augie BESS | Waller | 2027-12-17 | Battery | 200.81 | Y | N | N | N | Y | Y
27INR0218 | Themisto Solar | Nolan | 2027-12-30 | Solar | 301.2 | Y | N | N | N | Y | Y
22INR0443 | Bowstring BESS | San Patricio | 2027-12-30 | Battery | 155 | Y | N | N | N | Y | Y
24INR0423 | Hollow Branch Creek Storage | Leon | 2027-12-31 | Battery | 460 | Y | N | N | N | Y | Y
25INR0311 | RIVERBEND STORAGE SLF | Falls | 2027-12-31 | Battery | 150 | Y | N | N | N | Y | Y
24INR0178 | Cumulus Grid BESS | Ellis | 2028-01-01 | Battery | 210.74 | Y | N | N | N | Y | Y
20INR0244 | Montezuma Storage | Colorado | 2028-02-29 | Battery | 50.6 | Y | N | N | N | Y | Y
26INR0235 | Noor Solar | Liberty | 2028-03-01 | Solar | 188.2 | Y | N | N | N | Y | Y
25INR0440 | Bronc Rodeo Solar Project | Falls | 2028-03-17 | Solar | 121.63 | Y | N | N | N | Y | Y
25INR0405 | Pledgor BESS | Matagorda | 2028-04-06 | Battery | 100.33 | Y | N | N | N | Y | Y
25INR0184 | Legato BESS | Wise | 2028-04-24 | Battery | 202.65 | Y | N | N | N | Y | Y
25INR0190 | Fortissimo BESS | Montague | 2028-04-24 | Battery | 202.65 | Y | N | N | N | Y | Y
23INR0174 | Campsey Wind | Jack | 2028-06-01 | Wind | 238.3 | Y | N | N | N | Y | Y
26INR0294 | Longleaf Power Station | Angelina | 2028-06-01 | Gas | 600 | Y | N | N | N | Y | Y
26INR0285 | Hill Valley BESS | Grimes | 2028-07-15 | Battery | 245.8 | Y | N | N | N | Y | Y
26INR0324 | Misty Hollow BESS | Grimes | 2028-07-15 | Battery | 245.8 | Y | N | N | N | Y | Y
26INR0349 | ARTIO ENERGY STORAGE | Collin | 2028-10-01 | Battery | 205.94 | Y | N | N | N | Y | Y
27INR0190 | Millsing BESS | Grimes | 2028-10-15 | Battery | 501.6 | Y | N | N | N | Y | Y
25INR0008 | BasRanch (TEF - Due Diligence) | Ward | 2028-12-01 | Gas | 1300 | Y | N | N | N | Y | Y
29INR0018 | Big Rooter East Storage SLF | Robertson | 2029-04-01 | Battery | 553.65 | Y | N | N | N | Y | Y
29INR0017 | Big Rooter East Solar SLF | Robertson | 2029-04-01 | Solar | 554.94 | Y | N | N | N | Y | Y
26INR0183 | TRIFECTA Gas | Midland | 2029-10-31 | Gas | 453 | Y | N | N | N | Y | Y
New generators that have a started FIS in 2031 ONLY.
GINR Reference Number | Project Name | County | Projected COD | Fuel | MW For Grid | FIS Started | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM | Comments
27INR0272 | EMPower Odessa (TEF - Due Diligence) | Ector | 2027-07-07 | Gas | 123.4 | Y | N | N | N | N | Y
26INR0261 | Bastrop Peaking Generators (TEF-Due Diligence) | Bastrop | 2026-05-31 | Gas | 1104 | Y | N | N | N | N | Y
28INR0105 | Vast Sands Power I (TEF -Due Diligence) | Ward | 2027-12-01 | Gas | 440 | Y | N | N | N | N | Y
27INR0095 | Bulldog Power (TEF - Due Diligence) | Brazoria | 2027-12-18 | Gas | 311 | Y | N | N | N | N | Y
24INR0576 | Boling Generation (TEF-Due Diligience) | Wharton | 2027-10-29 | Gas | 390 | Y | N | N | N | N | Y
28INR0109 | Vast Sands Power II (TEF-Due Diligence) | Ward | 2028-02-01 | Gas | 440 | Y | N | N | N | N | Y
28INR0108 | RAYBURN ENERGY STATION II Gas (TEF-Due Diligence) | Grayson | 2028-02-26 | Gas | 570 | Y | N | N | N | N | Y
29INR0041 | Homestead Power (TEF-Due Diligence) | Austin | 2029-12-15 | Gas | 260.3 | Y | N | N | N | N | Y
28INR0087 | North Royal Thermal (TEF- Due Diligence) | Lamar | 2030-08-01 | Gas | 452 | Y | N | N | N | N | Y
28INR0086 | West Royal Natural Gas (TEF-Due Diligence) | Upton | 2029-05-01 | Gas | 816 | Y | N | N | N | N | Y
26INR0351 | Jack County III – 345 kV (TEF -Due Diligence) | Jack | 2027-07-01 | Gas | 660 | Y | N | N | N | N | Y
26INR0396 | Kodiak AGR1 (TEF- Due Diligence) | Reeves | 2027-06-15 | Fuel Oil | 132 | Y | N | N | N | N | Y
Retired Units
Unit Name | MW For Grid | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM | Comments
CALAVERS_JTD1 | 420 | X | X | X | X | X | Notification of Change of Generation Resource Designation (NCGRD)
CALAVERS_JTD2 | 420 | X | X | X | X | X | NCGRD
TOSBATT_UNIT1 | 2 | X | X | X | X | X | NCGRD
OCI_ALM1_ASTRO1 | 1 | X | X | X | X | X | Notice of Suspension of Operations (NSO)
DOWGEN_DOW_G37 | 61 | X | X | X | X | X | NSO
DECKER_DPG2 | 420 | X | X | X | X | X | NSO
Generation Resources Unavailable in Planning Studies Prior to NSO
Unit Name | MW For Grid | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM | Comments
BRAUNIG_VHB1 | 217 | X | X | X | X | X | https://www.ercot.com/mp/data-products/data-product-details?id=PG3-1411-M
BRAUNIG_VHB2 | 230 | X | X | X | X | X
BRAUNIG_VHB3 | 412 | X | X | X | X | X
CALAVER_OWS1 | 420 | X | X | X | X | X
CALAVER_OWS2 | 410 |  |  |  | X | X
CALAVER_JKS1 | 560 |  |  |  | X | X
Generation Resources Unavailable in Planning Studies Prior to NSO - Now Available
Unit Name | MW For Grid | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM | Comments
COL_COLETOG1 | 655 |  | X | X | X | X | May 2025 Capacity, Demand, and Reserves Report (CDR) (Unconfirmed Planned Fuel Conversion for an Operating Unit)
Mothballed Units
Unit Name | MW For Grid | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM | Comments
AMOC_AMOCO_5 | 32 | X | X | X | X | X | Notice of probability
BRANDON_UNIT1 | 20 | X | X | X | X | X | CDR, NSO
DOWGEN_DOW_G66 | 95.62 | X | X | X | X | X | NSO
DOWGEN_DOW_ST64 | 50 | X | X | X | X | X | NSO
FLCNS_UNIT3 | 62 | X | X | X | X | X | CDR, NSO
MASSENGL_G6 | 18 | X | X | X | X | X | CDR, NSO
MASSENGL_G7 | 18 | X | X | X | X | X | CDR, NSO
MASSENGL_G8 | 38 | X | X | X | X | X | CDR, NSO
OLINGR_OLING_1 | 78 | X | X | X | X | X | CDR, NSO
SGMTN_SIGNALM2 | 2.73 | X | X | X | X | X | CDR, NSO
TY_COOKE_GT2 | 14 | X | X | X | X | X | CDR, NSO
TY_COOKE_GT3 | 17 | X | X | X | X | X | CDR, NSO
WFCOGEN_UNIT4 | 16 | X | X | X | X | X | CDR, NSO
BYU_BYU_G8 | 4 | X | X | X | X | X | NSO
Seasonal Mothballed Units (Offline in the 2028 Min case only)
Unit Name | MW For Grid | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM | Comments
STEAM1A_STEAM_1 | 17.5 |  | X |  |  |  | CDR, NSO
SPNCER_SPNCE_4 | 57 |  | X |  |  |  | CDR, NSO
SPNCER_SPNCE_5 | 61 |  | X |  |  |  | CDR, NSO
CHISMGRD_BES1 | 100 | X | X | X |  |  | NSO, temporary MB ends 1/1/2029
Retirement Units back in service
Unit Name | MW For Grid | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM | Comments
B_DAVIS_B_DAVIG1 | 292 | X | X | X | X | X | Withdrawal of NSO
MCSES_UNIT8 | 568 | X | X | X | X | X | NCGRD
PNPI_GT2 | 71 | X | X | X | X | X | NCGRD
LGE_LGE_GT1 | 145 | X | X | X | X | X | NCGRD
LGE_LGE_GT2 | 145 | X | X | X | X | X | NCGRD
LGE_LGE_STG | 75 | X | X | X | X | X | NCGRD
Planned Units Removed Due to Project Cancellation
Unit Name | MW For Grid | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM | Comments
MIRAGE_G1 | 11 | X | X | X | X | X | CDR
VALHALLA_S1 | 306.8 | X | X | X | X | X | February Generation Interconnection Status (GIS)
BERKMAN_B1 | 150.86 | X | X | X | X | X | March GIS
NEPTUNE_S1 | 200 | X | X | X | X | X | September GIS
Units Removed Due to Confirmed Extended Outage
Unit Name | MW For Grid | 2027 SUM | 2028 MIN | 2028 SUM | 2030 SUM | 2031 SUM | Comments
MIL_MILLERG1 | 70 | X | X | X | X | X | Monthly Outlook for Resource Adequacy (MORA) - February 2026

## Renewable Generation Dispatch
Date Last Updated: | 2025-08-05 | Back
Status: | Final
Solar
Solar maximum capacity percentage based on historical Settlements HSL dispatch levels during the top 20 load hours of the last five years for summer peak conditions. Note: All solar units are offline in the MIN case.
Summer Peak, Solar | 73%
Wind
Wind region maximum capacity percentages based on historical Settlements HSL dispatch levels during the top 20 load hours of the last ten years for summer peak conditions and three years for minimum load conditions. Each wind region was then scaled up 4% in the minimum load case to allow Quick Start units to be turned off.
Summer Peak, Coastal | Summer Peak, Panhandle | Summer Peak, Other
55% | 28% | 21%
Min Case, Coastal | Min Case, Panhandle | Min Case, Other
36% | 54% | 48%
Hydro
Unit specific generation MW dispatch modeled based on historical Settlements HSL dispatch levels during the top 20 load hours of the last three years. Note: All Hydro units are offline in the MIN case.
AMI_AMISTAG1 (H1) | 15.9667
AMI_AMISTAG2 (H2) | 16.1417
AUS_AUSTING1 (H2) | 8.0972
AUS_AUSTING1 (H1) | 8
BUC_BUCHANG1 (H1) | 15.2258
BUC_BUCHANG2 (H2) | 15.192
BUC_BUCHANG3 (H3) | 16.1438
CAN_CANYHYG1 (H1) | 0
CAN_CANYHYG1 (H2) | 0
DND_DENISOG1 (H1) | 44.6667
DND_DENISOG2 (H2) | 40.1667
EA_EAGLE_HY1 (H3) | 0
EA_EAGLE_HY1 (H2) | 0
EA_EAGLE_HY1 (H1) | 0
FAL_FALCONG1 (H1) | 7.0333
FAL_FALCONG2 (H2) | 7.3333
FAL_FALCONG3 (H3) | 6.8333
INKS_INKS_G1 (H1) | 13.3457
MAR_MARBFAG1 (H1) | 20.5017
MAR_MARBFAG2 (H2) | 20
MAR_MARSFOG1 (H1) | 28.3697
MAR_MARSFOG2 (H2) | 29.506
MAR_MARSFOG3 (H3) | 28.664
WIR_WIRTZ_G1 (H1) | 28.62
WIR_WIRTZ_G2 (H2) | 28.9567
WND_WHITNEY1 (H1) | 19.7933
WND_WHITNEY2 (H2) | 19.7933

## Switchable Generation
Date Last Updated: | 2025-08-05 | Back
Status: | Final
Operational Resources Unavailable to ERCOT (Switchable) | [5 empty] | Summer | Winter | Summer | Summer | Summer
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | 2027 | 2027/2028 | 2028 | 2030 | 2031
ANTELOPE IC 1 | AEEC_ANTLP_1_UNAVAIL | HALE | GAS | PANHANDLE | 2016 | -54 | -56 | -54 | -54 | -54
ANTELOPE IC 2 | AEEC_ANTLP_2_UNAVAIL | HALE | GAS | PANHANDLE | 2016 | -54 | 0 | -54 | -54 | -54
ANTELOPE IC 3 | AEEC_ANTLP_3_UNAVAIL | HALE | GAS | PANHANDLE | 2016 | -54 | 0 | -54 | -54 | -54
ELK STATION CTG 1 | AEEC_ELK_1_UNAVAIL | HALE | GAS | PANHANDLE | 2016 | -190 | -200 | -190 | -190 | -190
ELK STATION CTG 2 | AEEC_ELK_2_UNAVAIL | HALE | GAS | PANHANDLE | 2016 | -190 | -200 | -190 | -190 | -190
ELK STATION CTG 3 | AEEC_ELK_3_UNAVAIL | HALE | GAS | PANHANDLE | 2001 | -190 | 0 | -190 | -190 | -190
TENASKA GATEWAY STATION CTG 1 | TGCCS_CT1_UNAVAIL | RUSK | GAS | NORTH | 2001 | -156 | -162 | -156 | 0 | 0
TENASKA GATEWAY STATION CTG 2 | TGCCS_CT2_UNAVAIL | RUSK | GAS | NORTH | 2001 | -135 | -179 | -135 | -135 | -135
TENASKA GATEWAY STATION CTG 3 | TGCCS_CT3_UNAVAIL | RUSK | GAS | NORTH | 2001 | -153 | -178 | -153 | 0 | -153
TENASKA GATEWAY STATION STG 4 | TGCCS_UNIT4_UNAVAIL | RUSK | GAS | NORTH | 2001 | -400 | -389 | -400 | -400 | 0
TENASKA KIAMICHI STATION 2CT101 | KMCHI_2CT101_UNAVAIL | FANNIN | GAS | NORTH | 2003 | -150 | 0 | -150 | -150 | 0
TENASKA KIAMICHI STATION 2CT201 | KMCHI_2CT201_UNAVAIL | FANNIN | GAS | NORTH | 2003 | -152 | 0 | 0 | 0 | 0
TENASKA KIAMICHI STATION 2ST | KMCHI_2ST_UNAVAIL | FANNIN | GAS | NORTH | 2003 | -311 | 0 | 0 | 0 | 0
Switchable Capacity Unavailable to ERCOT Total | [5 empty] | -2189 | -1364 | -1726 | -1417 | -1020

## DC Tie Modeling & Dispatch
Date Last Updated: | 2025-08-05 | Back
Status: | Final
Reliability Analysis
DC Tie Dispatch - Summer Peak Conditions (MW)
DC_E | 600 | Import
DC_N | 220 | Import
DC_L | 0
DC_R | 0
DC Tie Dispatch - Minimum Load Conditions (MW)
DC_E | 0
DC_N | 0
DC_L | 0
DC_R | 0

## Reserve Requirement
Date Last Updated: | 2025-08-05 | Back
Status: | Final
Reliability Cases | 3,000 MW
The reserve requirements used in the reliability models account for the outage of ERCOT's two largest units as well as the increased losses observed during such an G-1 & N-1 outage. The reserves target is an approximation and will fluctuate with losses in the cases.

## Fuel Price Assumptions
Date Last Updated: | 2025-08-05 | Back
Status: | Final
Source: | Annual Energy Outlook 2025 was incorporated into a longer-term historical analysis of natural gas prices
https://www.eia.gov/outlooks/aeo/
Natural Gas Price Forecast ($/MMBtu)
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Average
2025 | 3.12 | 2.91 | 2.72 | 2.79 | 2.89 | 2.95 | 2.87 | 2.9 | 2.91 | 3.02 | 3 | 3.17 | 2.9375
2026 | 3.02 | 2.81 | 2.63 | 2.7 | 2.79 | 2.86 | 2.77 | 2.81 | 2.82 | 2.92 | 2.9 | 3.06 | 2.8408
2027 | 2.94 | 2.73 | 2.56 | 2.62 | 2.71 | 2.78 | 2.69 | 2.73 | 2.74 | 2.84 | 2.82 | 2.98 | 2.7617
2028 | 3.12 | 2.9 | 2.71 | 2.79 | 2.88 | 2.95 | 2.86 | 2.9 | 2.91 | 3.01 | 3 | 3.16 | 2.9325
2029 | 3.37 | 3.13 | 2.93 | 3.01 | 3.11 | 3.18 | 3.09 | 3.13 | 3.14 | 3.25 | 3.23 | 3.41 | 3.165
2030 | 3.65 | 3.4 | 3.18 | 3.26 | 3.37 | 3.45 | 3.35 | 3.39 | 3.4 | 3.53 | 3.51 | 3.7 | 3.4325
2031 | 3.9 | 3.63 | 3.39 | 3.49 | 3.61 | 3.69 | 3.58 | 3.62 | 3.64 | 3.77 | 3.75 | 3.96 | 3.6692

## Reliability Case-Load Forecast
Date Last Updated: | 2025-08-05 | Back
Status: | Final
SSWG load based on 24 SSWG cases posted on 10/14/2024 less self-served load and losses (MW)
Year | Coast | East | Far West | North | North Central | South Central | South | West | NCP Total
2027 | 27267.43 | 4134.24 | 16443.58 | 6982.63 | 36710.49 | 20420.4 | 10445.95 | 5319.66 | 127724.38
2028 | 29416.83 | 4213.67 | 16874.29 | 7072.26 | 38024.5 | 21259.51 | 11570 | 5459.22 | 133890.28
2030 | 29825.1 | 4343.36 | 17283.28 | 7442.79 | 39843.96 | 22112.19 | 11782.62 | 5922.12 | 138555.42
2031 | 30032.33 | 4428.7 | 17493.73 | 7482.23 | 40474.49 | 22481 | 11849.33 | 5970.21 | 140212.02
ERCOT 90th percentile coincident peak load forecast less self-served and losses (MW)
Year | Coast | East | Far West | North | North Central | South Central | South | West | CP Total
2027 | 23425.166 | 2910.0746 | 6958.808 | 1953.632 | 27794.2922 | 15092.2183 | 6444.8791 | 1998.3519 | 86577.4221
2028 | 23440.0369 | 2939.4465 | 7203.9919 | 1996.9663 | 28032.9623 | 15287.4913 | 6638.1939 | 2113.4374 | 87652.5266
2030 | 24096.8045 | 2998.9795 | 7688.6187 | 2089.2479 | 28459.5239 | 15641.0738 | 6650.8034 | 2140.9541 | 89766.0057
2031 | 24297.1103 | 3026.0566 | 7922.5139 | 2159.7223 | 27813.9028 | 15457.8028 | 6501.497 | 2179.0934 | 89357.6992
2025 RTP load level with self-served load and less losses (MW) - based on ERCOT large load incorporation of the PUC-approved Good Cause Exception, the incorporation of the S&P Global Permian Basin load forecast, EV load adoption, and rooftop PV growth forecast contribution
Year | Coast | East | Far West | North | North Central | South Central | South | West | Total
2027 | 28437.82 | 3267.07 | 15273.67 | 10554.36 | 32574.55 | 21902.55 | 9107.15 | 4744.98 | 125862.15
2028 | 32385.8 | 3338.45 | 16743.87 | 12158.85 | 35486.03 | 24869.71 | 13259.08 | 7022.98 | 145264.77
2030 | 35004.82 | 3430.61 | 18915.93 | 12480.07 | 38184.96 | 28515.12 | 14972.22 | 7575.09 | 159078.82
2031 | 36160.15 | 3501.33 | 19921.75 | 12529.83 | 39822.59 | 29324.92 | 15346.38 | 7900.56 | 164507.51
2025 RTP load level with self-served load and less losses for Off-Peak Case (MW) - based on 2026 SSWG Min Case, ERCOT large load incorporation of the PUC-approved Good Cause Exception, the incorporation of the S&P Global Permian Basin load forecast, and EV load adoption
Year | Coast | East | Far West | North | North Central | South Central | South | West | Total
2028 | 18692.03 | 1655.02 | 12512.73 | 10653.44 | 17226.91 | 14385.59 | 10086.88 | 5707.36 | 90919.96

## Sensitivity Analysis
Date Last Updated: | 2025-12-22 | Back
Status: | Final
Sensitivity 1 and Sensitivity 2 were used to meet NERC TPL sensitivity requirements, while Sensitivity 3(a) was developed as the basis for Sensitivity 3(b), which was used for Minimum Deliverability analysis.
Sensitivity 1: | The summer peak load cases were modeled with load substantiated by TSP officer letters reduced to zero and included only generators compliant with ERCOT Planning Guide 6.9(1) requirements.
Year | ERCOT Load (MW) | DC Tie Export* (MW) | Wind Output (MW) |  |  |  | Solar Output (MW) | Total Renewable Output (MW)
|  |  | South Wind (Coastal) | South Wind (Non-Coastal) | Panhandle | Other
2030 | 129170.34 | -820 | 3302.86 | 884.56 | 1471.03 | 7066.13 | 47662.6 | 59503
2027 | 111120.89 | -820 | 3225.04 | 801.5 | 1471.03 | 6702.01 | 39948.19 | 51346
Sensitivity 2: | The minimum load case was modeled with load substantiated by TSP officer letters reduced to zero and included only generators compliant with ERCOT Planning Guide 6.9(1) requirements.
Year | ERCOT Load (MW) | DC Tie Export* (MW) | Wind Output (MW) |  |  |  | Solar Output (MW) | Total Renewable Output (MW)
|  |  | South Wind (Coastal) | South Wind (Non-Coastal) | Panhandle | Other
2028MIN | 71735.57 | 0 | 1055.49 | 1019.58 | 1576.13 | 8026.52 | 0 | 10658
Sensitivity 3(a): | The peak net load case was modeled with generation dispatch and load updated to represent "sunset" conditions typically observed during the 7–8 PM time period. Load substantiated by TSP officer letters was reduced to zero, and only generators compliant with ERCOT Planning Guide 6.9(1) requirements were included.
Year | ERCOT Load (MW) | DC Tie Export* (MW) | Wind Output (MW) |  |  |  | Solar Output (MW) | Total Renewable Output (MW)
|  |  | South Wind (Coastal) | South Wind (Non-Coastal) | Panhandle | Other
2027 | 106261.22 | -820 | 3711.74 | 2706.05 | 630.46 | 12146.73 | 7278.28 | 23767
Sensitivity 3(b): | The peak net load ("sunset") case was modeled with generation dispatch updated to reflect the Minimum Deliverability Criteria outlined in Planning Guide Section 4.1.1.7. Load substantiated by TSP officer letters was reduced to zero, and only generators compliant with ERCOT Planning Guide 6.9(1) requirements were included.
Year | ERCOT Load (MW) | DC Tie Export* (MW) | Wind Output (MW) |  |  |  | Solar Output (MW) | Total Renewable Output (MW)
|  |  | South Wind (Coastal) | South Wind (Non-Coastal) | Panhandle | Other
2027 | 106261.22 | -820 | 3711.74 | 2706.05 | 630.46 | 12146.72 | 7278.28 | 23767
* negative sign indicating DC tie import.