## Index
RTP Scope Section Number | Input Assumption | Status | Date
Transmission Topology
4.3 | Start Cases | Final | 2025-02-23
4.3 | Recently Approved RPG Projects | Final | 2025-11-12
4.3 | Model Updates/Corrections | Final | 2025-10-11
3.1.3 | Transmission & Generation Outages | Final | 2025-05-27
Generation
3.2.1 | Generation Additions, Retirements and Mothballs | Final | 2025-08-31
3.2.2 | Renewable Generation Dispatch | Final | 2025-02-23
3.2.3 | Switchable Generation | Final | 2025-05-23
3.2.4 | DC Tie Modeling and Dispatch | Final | 2025-02-23
3.2.5 | Reserve Requirements | Final | 2025-03-05
3.2.6 | Fuel Price Assumptions | Final | 2025-07-21
3.2.6 | Emission Cost Assumptions | Final | 2025-07-01
Demand
3.3 | Load Forecast Weather Year | Final | 2025-07-01

## Start Cases
Date Last Updated: | 2025-02-23 | Back
Status | Final
Based on 2024 RTP final summer peak reliability cases for years 2027 and 2030*
*765-kV case for 2030

## Recently Approved RPG Projects
| Date Last Updated: | 2025-11-12 | Back
| Status | Final
RPG Project ID | Project Name | TDSP | Approve Date | 2027 | 2030
23RPG032 | San Antonio South Reliability II Project * | BEC | 2024 | X
24RPG010 | Delaware Basin Stages 3 and 4 Project | Oncor | 2024 | X | X
24RPG015 | Delaware Basin Stage 5 Project | Oncor | 2025 |  | X
24RPG008 | Brownsville Area Improvements Transmission Project | AEPSC | 2024 | X | X
24RPG038 | Bergheim Substation Upgrade Project | LCRA TSC, PEC | 2025 |  | X
24RPG017 | Venus Switch to Sam Switch 345-kV Line Project | Oncor | 2024 | X | X
24RPG007 | P.H. Robinson to WA Parish 345-kV Hardening Project | CNP | 2025 |  | X
Notes: | *Part of the San Antonio South Reliability II Project is accelerated to be in service by 2027. The project is already in 2030 RTP case.

## Model Updates & Corrections
Date Last Updated: | 2025-10-11 | Back
Status | Final
Model Corrections/Updates Made to the 2024 RTP Cases
Transmission Changes | TO | 2027 | 2030 | Comments
Updated line ratings for Navarro (68091) - Big Brown (3380 & 3381) 345-kV lines | LSTR/ONCOR | X | X | Based on NMMS ratings
Updated line ratings for Weatherford Switch (1592) - Flat Rock Tap (15015) 138-kV line | ONCOR | X | X | Based on NMMS ratings
Updated line ratings for Fisher Road Switch (1425) - Riley (6101) 345-kV line | ONCOR/AEP | X | X | Based on NMMS ratings
Updated line ratings for Westside (8485) - Mckenzie (8858) 138-kV line | AEP | X | X | MOD Project 86882 (Tier 4)
Updated line ratings for Wharton (43570) - Caney (44132) 138-kV line | CNP | X | X | Based on NMMS ratings
Updated line ratings for Bell County (132) - Fryers Creek (Boggy) (3493) 138-kV line based on the latest submission in MOD (MOD Project 87675) | ONCOR | X |  | Updated to reflect the most current information related to the Temple Area Project (24RPG001)
Updated line ratings for Bell County (132) - Salado (3640) 138-kV line based on the latest submission in MOD (MOD Project 87673) | ONCOR | X
Updated line ratings for Temple Switch (3415) - Fryers Creek (Boggy) (3493) 138-kV line based on the latest submission in MOD (MOD Project 87677) | ONCOR | X | X
Updated line ratings for South Texas Project (5915) - WA Parish (44000) 345-kV line | CNP | X | X | Based on NMMS ratings
Updated line ratings for Georgetown (7343) - Rivery (7347) 138-kV line | LCRA | X | X | MOD Project 85973 (Tier 4)
Updated line ratings for Reiter (18545) - Yarbrough Sub (11111) 138-kV line based on the latest submission in MOD (MOD Project 81418) | ONCOR | X | X | Updated to reflect the most current information related to the Wolf Switch to Reiter Switch 138-kV Line Project (25RPG008)
Updated line ratings for Cedar Crest (2486) - Buntin Drive (2985) 138-kV line | ONCOR | X | X | MOD 98739 (NOMCR)
Updated line ratings for Angstrom (8249) - Static (8676) - Haber (81003) 345-kV lines | AEP | X | X | MOD Project 80630 (Tier 4)
Updated line ratings for Lon Hill (8452) - Saxet (78568) 138-kV line | LCRA |  | X | MOD Project 86043 (Tier 4)
Updated line ratings for Abilene Mulberry Creek (6235) - Bluff Creek (60040) 345-kV line | AEP | X |  | MOD Project 48816 (Tier 4)
Bypassed Edison series capacitors | AEP |  | X | ERCOT Permian Basin Reliability Plan Study (Project ID: Import A1)
Generation Changes | TO | 2027 | 2030 | Comments
Changed POI for ElDora Solar (24INR0337) and BESS (24INR0338) to HICKL_RD (9063) | Austin Energy | X | X | Based on latest information in RIOO as of 8/1/2025
Phase Shifters | TO | 2027 | 2030 | Comments

## Transmission & Gen Outages
Date Last Updated: | 2025-05-27 | Back
Status | Final
Outaged Element | Associated TO/RE | 2027 | 2030 | Notes
Spencer Unit 4 | City of Garland | X | X | (AS OF 10/24/2022, AVAILABLE 3/1 THROUGH 11/30)
Spencer Unit 5 | City of Garland | X | X | (AS OF 10/24/2022, AVAILABLE 3/1 THROUGH 11/30)
R W MILLER STG 1 | BEPC | X | X | EXT-OUT
Powerlane Plant STG 1 | GEUS | X | X | (AS OF 10/1/2022, AVAILABLE 5/1 THROUGH 9/30)
CHISHOLM GRID BAT | Chisholm Grid, LLC/Able Grid | X |  | NSO posted (EXT-OUT)
Automated maintenance schedules modeled by UPLAN

## Renewable Generation Dispatch
Date Last Updated: | 2025-02-23 | Back
Status | Final
Solar
http://www.ercot.com/gridinfo/resource
Weather years used for analysis:
Base/Sensitivity | 2013
Wind
http://www.ercot.com/gridinfo/resource
Weather years used for analysis:
Base/Sensitivity | 2013
Hydro
Unit specific monthly capacity factors modeled based on historical dispatch levels during the last three years.

## Gen Add, Ret. and Mothball
Date Last Updated: | 2025-08-31 | Back
Status | Final
6.9(1) conditions met as of: | 2025-05-30
New generators that met PG 6.9(1) requirements
GINR Reference Number | Project Name | County | Projected Date | Fuel | MW For Grid | Changes From Last Report | Meets Section 6.9 Requirements (1)(b) through (1)(d) | 2027 | 2027 Sensitivity | 2030 | 2030 Sensitivity | Comments
23INR0372 | Cross Trails Storage | Scurry | 2025-05-30 | Battery Storage | 58.29 |  | 2024-07-26 | X | X | X | X
25INR0231 | Apache Hill BESS | Hood | 2026-11-15 | Battery Storage | 201.15 |  | 2024-07-17 | X | X | X | X
22INR0525 | St. Gall II Energy Storage | Pecos | 2025-07-31 | Battery Storage | 100.24 |  | 2024-11-01 | X | X | X | X
24INR0493 | Crowned Heron BESS 2 | Fort Bend | 2026-03-31 | Battery Storage | 154.2 |  | 2024-10-10 | X | X | X | X
24INR0631 | Radian Storage SLF | Brown | 2025-07-14 | Battery Storage | 160.25 |  | 2024-07-24 | X | X | X | X
23INR0539 | Gregory BESS | San Patricio | 2024-11-11 | Battery Storage | 9.9 |  | 2024-03-01 | X | X | X | X
24INR0610 | Century BESS | Tarrant | 2024-12-27 | Battery Storage | 9.88 |  | 2024-04-03 | X | X | X | X
23INR0807 | Mayberry II BESS | Hidalgo | 2025-01-20 | Battery Storage | 9.95 |  | 2024-04-29 | X | X | X | X
22INR0602 | Regis Palacios BESS | Matagorda | 2024-11-22 | Battery Storage | 9.9 |  | 2024-03-01 | X | X | X | X
24INR0586 | Judkins BESS | Ector | 2024-02-29 | Battery Storage | 9.95 |  | 2023-11-01 | X | X | X | X
24INR0614 | Russek Street BESS | Reagan | 2024-12-20 | Battery Storage | 9.9 |  | 2024-01-04 | X | X | X | X
24INR0624 | Mainland BESS | Galveston | 2024-06-21 | Battery Storage | 9.9 |  | 2024-01-04 | X | X | X | X
24INR0660 | Liggett Switch BESS | Dallas | 2024-12-27 | Battery Storage | 9.88 |  | 2024-05-22 | X | X | X | X
24INR0688 | SANDLAKE BESS | Reeves | 2024-10-01 | Battery Storage | 9.99 |  | 2024-04-17 | X | X | X | X
20INR0162 | Diamondback solar | Starr | 2027-12-31 | Solar | 203.8 |  | 2025-02-12 | X | X | X | X
22INR0239 | Rockefeller Storage | Schleicher | 2027-06-01 | Battery Storage | 206.8 |  | 2025-02-12 | X | X | X | X
22INR0437 | TORMES SOLAR | Navarro | 2027-03-31 | Solar | 382.12 |  | 2025-02-13 | X | X | X | X
22INR0457 | Anson BAT | Jones | 2026-08-01 | Battery Storage | 150.6 |  | 2025-02-12 | X | X | X | X
23INR0181 | Starling Storage | Gonzales | 2027-05-15 | Battery Storage | 63.6 |  | 2025-02-12 | X | X | X | X
23INR0244 | Tiger Solar | Jones | 2027-06-30 | Solar | 255 |  | 2025-02-12 | X | X | X | X
24INR0126 | High Noon Storage | Hill | 2028-05-09 | Battery Storage | 94 |  | 2025-02-12 |  |  | X | X
24INR0201 | Short Creek Solar | Wichita | 2029-03-02 | Solar | 625 |  | 2025-02-12 |  |  | X | X
24INR0305 | MRG Goody Storage | Lamar | 2026-05-02 | Battery Storage | 52.29 |  | 2025-02-12 | X | X | X | X
24INR0355 | Anatole Renewable Energy Storage | Henderson | 2027-03-31 | Battery Storage | 207.82 |  | 2025-02-12 | X | X | X | X
24INR0364 | Pitts Dudik II | Hill | 2026-02-04 | Solar | 30.23 |  | 2025-02-12 | X | X | X | X
24INR0386 | Black & Gold Energy Storage | Menard | 2027-06-30 | Battery Storage | 254.58 |  | 2025-02-13 | X | X | X | X
24INR0498 | Fort Watt Storage | Tarrant | 2027-08-30 | Battery Storage | 205.4 |  | 2025-02-12 | X | X | X | X
24INR0528 | Blanquilla BESS | Nueces | 2026-05-15 | Battery Storage | 200.78 |  | 2025-02-13 | X | X | X | X
24INR0584 | Houston IV BESS | Harris | 2026-06-03 | Battery Storage | 164.6 |  | 2025-02-12 | X | X | X | X
25INR0018 | Yellow Cat Wind | Navarro | 2027-04-01 | Wind | 262 |  | 2025-02-12 | X | X | X | X
25INR0046 | Blue Skies BESS | Hill | 2027-12-31 | Battery Storage | 306.26 |  | 2025-02-12 | X | X | X | X
25INR0103 | Elio BESS | Brazoria | 2027-08-05 | Battery Storage | 317.2 |  | 2025-02-12 | X | X | X | X
25INR0282 | Hornet Solar II SLF | Swisher | 2027-06-01 | Solar | 208.95 |  | 2025-02-12 | X | X | X | X
25INR0283 | Hornet Storage II SLF | Swisher | 2027-06-01 | Battery Storage | 207.96 |  | 2025-02-12 | X | X | X | X
25INR0319 | Northington Solar | Wharton | 2027-07-15 | Solar | 129.81 |  | 2025-02-12 | X | X | X | X
25INR0391 | Purple Sage BESS 1 | Collin | 2027-05-30 | Battery Storage | 156 |  | 2025-02-13 | X | X | X | X
25INR0392 | Purple Sage BESS 2 | Collin | 2027-05-30 | Battery Storage | 156 |  | 2025-02-13 | X | X | X | X
25INR0425 | Aldrin 345 BESS | Brazoria | 2027-12-01 | Battery Storage | 362 |  | 2025-02-12 | X | X | X | X
25INR0492 | Blue Summit Energy Storage | Wilbarger | 2026-07-01 | Battery Storage | 154 |  | 2025-02-13 | X | X | X | X
26INR0034 | Bracero Pecan Storage | Reeves | 2027-04-01 | Battery Storage | 232 |  | 2025-02-12 | X | X | X | X
26INR0226 | First Capitol BESS | Brazoria | 2026-05-01 | Battery Storage | 257.48 |  | 2025-02-12 | X | X | X | X
26INR0269 | Moccasin Solar | Stonewall | 2027-06-01 | Solar | 806.8 |  | 2025-02-12 | X | X | X | X
26INR0296 | Sherbino II BESS SLF | Pecos | 2026-02-08 | Battery Storage | 77.37 |  | 2025-02-12 | X | X | X | X
26INR0333 | VERTUS ENERGY STORAGE | Galveston | 2026-02-01 | Battery Storage | 207.3 |  | 2025-02-14 | X | X | X | X
26INR0447 | Honey Mesquite Wind Farm | Glasscock | 2026-12-15 | Wind | 180.48 |  | 2025-02-12 | X | X | X | X
26INR0452 | Cannibal Draw Solar | Glasscock | 2028-04-10 | Solar | 149.5 |  | 2025-02-12 |  |  | X | X
26INR0453 | Cannibal Draw Storage | Glasscock | 2028-04-10 | Battery Storage | 98.6 |  | 2025-02-12 |  |  | X | X
26INR0543 | Three Canes Solar SLF | Navarro | 2027-03-10 | Solar | 333 |  | 2025-02-12 | X | X | X | X
24INR0188 | Tehuacana Creek Solar SLF | Navarro | 2027-03-10 | Solar | 505.5 |  | 2025-02-12 | X | X | X | X
24INR0189 | Tehuacana Creek BESS SLF | Navarro | 2027-03-10 | Battery Storage | 419 |  | 2025-02-12 | X | X | X | X
23INR0618 | Farmersville West BESS 2 | Collin | 2024-11-30 | Battery Storage | 9.9 |  | 2024-03-20 | X | X | X | X
26INR0189 | Skipjack Energy Storage | Brazoria | 2027-04-05 | Battery Storage | 154 |  | 2025-02-24 | X | X | X | X
23INR0059 | Briggs Solar | Haskell | 2027-09-15 | Solar | 309.6 |  | 2025-03-24 | X | X | X | X
23INR0078 | Shaw Solar | Bandera | 2026-04-29 | Solar | 124.65 |  | 2025-03-26 | X | X | X | X
24INR0044 | Millers Branch Solar II | Haskell | 2026-04-01 | Solar | 178 |  | 2025-03-18 | X | X | X | X
24INR0058 | Briggs Storage | Haskell | 2027-09-15 | Battery Storage | 70.39 |  | 2025-03-24 | X | X | X | X
24INR0578 | Panther Creek 1 Repower | Glasscock | 2025-09-01 | Wind | 149.16 |  | 2024-06-21 | X | X | X | X
24INR0582 | Panther Creek 2 Repower | Glasscock | 2025-09-01 | Wind | 123.42 |  | 2024-06-21 | X | X | X | X
25INR0578 | Forest Creek Wind Repower | Glasscock | 2025-12-15 | Wind | 125.1 |  | 2025-01-24 | X | X | X | X
25INR0672 | Fagus Solar Park 2 SLF | Childress | 2025-09-26 | Solar | 166.57 |  | 2024-12-19 | X | X | X | X
26INR0524 | Fagus Solar Park 3 SLF | Childress | 2026-04-01 | Solar | 186.83 |  | 2024-12-19 | X | X | X | X
21INR0359 | Hickerson Solar | Bosque | 2026-03-01 | Solar | 311.1 |  | 2025-01-30 | X | X | X | X
23INR0021 | Hornet Solar | Swisher | 2025-06-13 | Solar | 602.37 |  | 2021-12-22 | X | X | X | X
24INR0630 | Andromeda Storage SLF | Scurry | 2025-07-12 | Battery Storage | 160.35 |  | 2024-04-29 | X | X | X | X
24INR0629 | Jade Storage SLF | Scurry | 2026-06-08 | Battery Storage | 160.8 |  | 2024-04-03 | X | X | X | X
22INR0546 | Enchanted Rock NEWPP | Harris | 2025-06-06 | Gas | 30 |  | 2024-05-01 | X | X | X | X
24INR0405 | Crowned Heron BESS | Fort Bend | 2025-09-30 | Battery Storage | 154.2 |  | 2024-05-01 | X | X | X | X
22INR0356 | Jungmann Solar | Milam | 2025-06-30 | Solar | 40.21 |  | 2024-05-06 | X | X | X | X
22INR0511 | Gransolar Texas One | Milam | 2025-06-30 | Solar | 50.8 |  | 2024-05-03 | X | X | X | X
22INR0468 | Lower Rio BESS | Hidalgo | 2025-07-09 | Battery Storage | 60.37 |  | 2024-04-30 | X | X | X | X
23INR0103 | Burksol BESS | Dickens | 2025-03-31 | Battery Storage | 103.27 |  | 2024-04-03 | X | X | X | X
23INR0195 | Desert Willow BESS | Ellis | 2025-04-28 | Battery Storage | 154.4 |  | 2024-05-01 | X | X | X | X
23INR0299 | Anole BESS | Dallas | 2025-06-30 | Battery Storage | 247.1 |  | 2024-04-30 | X | X | X | X
24INR0421 | Swift Air Solar | Ector | 2025-03-19 | Solar | 146.5 |  | 2024-05-01 | X | X | X | X
19INR0110 | Azalea Springs Solar | Angelina | 2025-06-27 | Solar | 181 |  | 2024-05-01 | X | X | X | X
23INR0425 | Coneflower Storage Project | Chambers | 2027-02-03 | Battery Storage | 170.85 |  | 2024-04-11 | X | X | X | X
23INR0401 | Headcamp Energy Storage Plant | Pecos | 2025-11-26 | Battery Storage | 152.88 |  | 2024-04-11 | X | X | X | X
24INR0568 | Shamrock Energy Storage (SLF) | Crockett | 2025-06-30 | Battery Storage | 99.33 |  | 2024-05-06 | X | X | X | X
21INR0443 | Cottonwood Bayou Storage | Brazoria | 2025-12-03 | Battery Storage | 153.03 |  | 2024-04-29 | X | X | X | X
25INR0421 | Aldrin 138 BESS | Brazoria | 2027-07-01 | Battery Storage | 207 |  | 2024-05-06 | X | X | X | X
20INR0255 | Renegade Project | Deaf Smith | 2026-03-12 | Solar | 515.66 |  | 2024-04-30 | X | X | X | X
20INR0222 | Tyson Nick Solar | Lamar | 2025-08-08 | Solar | 90.5 |  | 2024-04-19 | X | X | X | X
24INR0315 | Black Springs BESS | Palo Pinto | 2025-10-15 | Battery Storage | 120.68 |  | 2024-04-19 | X | X | X | X
22INR0526 | Pine Forest BESS | Hopkins | 2025-10-29 | Battery Storage | 200.74 |  | 2024-05-23 | X | X | X | X
23INR0469 | Big Elm Storage | Bell | 2026-08-15 | Battery Storage | 100.8 |  | 2024-05-15 | X | X | X | X
24INR0491 | Gunnar BESS | Hidalgo | 2026-08-31 | Battery Storage | 150 |  | 2024-05-06 | X | X | X | X
20INR0203 | Pine Forest Solar | Hopkins | 2025-12-01 | Solar | 301.51 |  | 2024-05-22 | X | X | X | X
16INR0049 | Nazareth Solar | Castro | 2026-12-31 | Solar | 203 |  | 2024-03-22 | X | X | X | X
25INR0271 | City Breeze BESS | Matagorda | 2026-07-15 | Battery Storage | 143.1 |  | 2024-05-25 | X | X | X | X
24INR0198 | Two Forks BESS | Cooke | 2027-06-30 | Battery Storage | 309.8 |  | 2024-05-06 | X | X | X | X
24INR0298 | Leighton Solar SLF | Limestone | 2027-04-30 | Solar | 183 |  | 2025-02-13 | X | X | X | X
22INR0554 | Platinum Storage | Fannin | 2025-09-02 | Battery Storage | 309.53 |  | 2024-07-31 | X | X | X | X
23INR0225 | MRG GOODY SOLAR | Lamar | 2026-05-02 | Solar | 170.82 |  | 2025-02-12 | X | X | X | X
26INR0049 | Pin Peaking Energy Center 1 (TEF- Due Diligence) | Freestone | 2026-05-01 | Gas | 229.5 |  | 2025-02-12 | X | X | X | X
26INR0109 | Pin Peaking Energy Center 2 (TEF- Due Diligence) | Freestone | 2026-05-01 | Gas | 229.5 |  | 2025-02-12 | X | X | X | X
23INR0119 | Blevins Storage | Falls | 2025-07-28 | Battery Storage | 181.33 |  | 2024-07-31 | X | X | X | X
23INR0118 | Blevins Solar | Falls | 2025-10-30 | Solar | 271.58 |  | 2024-07-31 | X | X | X | X
24INR0166 | Stillhouse Solar | Bell | 2025-09-02 | Solar | 210.8 |  | 2024-10-31 | X | X | X | X
23INR0249 | Limewood Solar | Bell | 2025-12-31 | Solar | 204.6 |  | 2025-02-13 | X | X | X | X
21INR0421 | Armadillo Solar | Navarro | 2026-12-31 | Solar | 200.09 |  | 2025-02-12 | X | X | X | X
23INR0079 | Chillingham Storage | Bell | 2025-07-15 | Battery Storage | 153.93 |  | 2024-11-04 | X | X | X | X
24INR0365 | Hermes Storage | Bell | 2025-12-30 | Battery Storage | 100.42 |  | 2025-01-31 | X | X | X | X
23INR0344 | Hermes Solar | Bell | 2025-12-30 | Solar | 100.36 |  | 2025-01-31 | X | X | X | X
23INR0235 | Hoyte Solar | Milam | 2026-12-15 | Solar | 206.75 |  | 2025-02-13 | X | X | X | X
25INR0389 | Stoneridge BESS | Milam | 2025-09-01 | Battery Storage | 101.9 |  | 2025-01-28 | X | X | X | X
24INR0031 | Stoneridge Solar | Milam | 2025-09-04 | Solar | 201.6 |  | 2024-07-18 | X | X | X | X
24INR0093 | Oriana Solar | Victoria | 2025-09-18 | Solar | 181 |  | 2024-07-25 | X | X | X | X
22INR0342 | Matagorda Solar | Matagorda | 2026-08-24 | Solar | 101 |  | 2025-02-12 | X | X | X | X
21INR0393 | Orange Grove Solar | Jim Wells | 2025-06-25 | Solar | 130.6 |  | 2024-07-30 | X | X | X | X
22INR0467 | Bird Dog BESS | Live Oak | 2026-03-30 | Battery Storage | 60.4 |  | 2024-02-16 | X | X | X | X
24INR0472 | Amador Storage | Van Zandt | 2025-12-31 | Battery Storage | 102.58 |  | 2025-02-03 | X | X | X | X
23INR0035 | Starling Solar | Gonzales | 2027-05-15 | Solar | 123 |  | 2025-02-12 | X | X | X | X
22INR0388 | Cachi BESS | Guadalupe | 2025-07-13 | Battery Storage | 205.46 |  | 2024-07-30 | X | X | X | X
25INR0329 | Project Lynx BESS | Nueces | 2026-03-14 | Battery Storage | 125.36 |  | 2025-02-12 | X | X | X | X
23INR0392 | Honeycomb Storage SLF | Bee | 2026-06-30 | Battery Storage | 61.47 |  | 2025-02-14 | X | X | X | X
22INR0559 | Honeycomb Solar SLF | Bee | 2026-06-30 | Solar | 61.1 |  | 2025-02-14 | X | X | X | X
23INR0361 | Third Coast BESS | Jackson | 2026-04-04 | Battery Storage | 102.82 |  | 2025-01-29 | X | X | X | X
24INR0302 | Pintail Pass BESS | San Patricio | 2025-09-30 | Battery Storage | 207.25 |  | 2024-11-01 | X | X | X | X
23INR0093 | Alila Solar | San Patricio | 2027-05-08 | Solar | 256.5 |  | 2025-02-12 | X | X | X | X
23INR0364 | Tierra Seca BESS | Val Verde | 2025-09-03 | Battery Storage | 102.7 |  | 2024-10-30 | X | X | X | X
23INR0351 | Seven Flags BESS | Webb | 2025-12-12 | Battery Storage | 102.7 |  | 2025-01-15 | X | X | X | X
19INR0023 | Monte Alto 2 Wind | Willacy | 2027-06-01 | Wind | 307.9 |  | 2025-02-12 | X | X | X | X
19INR0022 | Monte Alto I | Willacy | 2027-12-31 | Wind | 141.5 |  | 2025-02-12 | X | X | X | X
24INR0306 | Arroyo Storage | Cameron | 2025-12-26 | Battery Storage | 183.76 |  | 2024-06-24 | X | X | X | X
23INR0354 | Bordertown BESS | Starr | 2026-08-15 | Battery Storage | 100 |  | 2025-02-13 | X | X | X | X
24INR0425 | Two Brothers ESS | Victoria | 2027-04-07 | Battery Storage | 152 |  | 2025-02-13 | X | X | X | X
21INR0268 | Greyhound Solar | Ector | 2026-03-31 | Solar | 587.76 |  | 2024-11-04 | X | X | X | X
23INR0056 | Caliche Mound Solar | Deaf Smith | 2026-10-10 | Solar | 408.21 |  | 2025-02-12 | X | X | X | X
23INR0287 | Avila BESS | Pecos | 2025-09-11 | Battery Storage | 164.28 |  | 2024-07-31 | X | X | X | X
23INR0290 | Zeya BESS | Galveston | 2026-06-01 | Battery Storage | 255.33 |  | 2025-02-12 | X | X | X | X
24INR0460 | Evelyn Battery Energy Storage System | Galveston | 2025-08-21 | Battery Storage | 221.3 |  | 2024-07-03 | X | X | X | X
25INR0262 | Shepard Energy Storage | Galveston | 2027-07-01 | Battery Storage | 256.37 |  | 2025-02-12 | X | X | X | X
25INR0300 | Wizard BESS | Galveston | 2025-10-21 | Battery Storage | 150.82 |  | 2024-07-30 | X | X | X | X
25INR0467 | Bocanova Power | Brazoria | 2025-08-26 | Battery Storage | 150.46 |  | 2024-11-02 | X | X | X | X
23INR0358 | Castor BESS | Brazoria | 2025-12-31 | Battery Storage | 205.39 |  | 2024-10-22 | X | X | X | X
24INR0128 | Desna BESS | Brazoria | 2026-03-31 | Battery Storage | 205.46 |  | 2024-10-30 | X | X | X | X
23INR0029 | Cedar Bayou 5 (TEF - Due Diligence) | Chambers | 2027-12-15 | Gas | 721 |  | 2025-02-12 | X | X | X | X
20INR0155 | Peyton Creek Wind II | Matagorda | 2025-07-15 | Wind | 241.2 |  | 2024-06-25 | X | X | X | X
23INR0084 | Lavaca Bay Solar | Matagorda | 2026-12-31 | Solar | 243.46 |  | 2025-02-17 | X | X | X | X
23INR0150 | Cradle Solar | Brazoria | 2025-12-31 | Solar | 200.85 |  | 2025-02-12 | X | X | X | X
25INR0102 | Austin Bayou Solar | Brazoria | 2027-06-01 | Solar | 753.4 |  | 2025-02-12 | X | X | X | X
23INR0057 | Duffy Solar | Matagorda | 2027-12-31 | Solar | 502.46 |  | 2023-05-24 |  |  | X | X
22INR0517 | Lane City Wind | Wharton | 2025-06-30 | Wind | 199.5 |  | 2024-08-01 | X | X | X | X
24INR0482 | NRG THW GT 345 (TEF -Due Diligence) | Harris | 2026-05-01 | Gas | 456 |  | 2025-02-12 | X | X | X | X
22INR0540 | Walstrom BESS | Austin | 2025-06-19 | Battery Storage | 205.31 |  | 2024-08-01 | X | X | X | X
22INR0558 | Callisto II Energy Center | Harris | 2026-07-01 | Battery Storage | 406.06 |  | 2025-02-12 | X | X | X | X
24INR0456 | FRIENDSWOOD ENERGY GENCO | Harris | 2025-07-18 | Gas | 143.7 |  | 2024-10-28 | X | X | X | X
24INR0258 | Zeissel Solar | Knox | 2028-06-30 | Solar | 457.5 |  | 2025-02-12 |  |  | X | X
20INR0242 | Anson Solar 2 | Jones | 2025-12-31 | Solar | 200.8 |  | 2025-02-12 | X | X | X | X
22INR0274 | Crowded Star Solar II | Jones | 2026-04-16 | Solar | 190.18 |  | 2025-02-12 | X | X | X | X
23INR0202 | Erath County Solar | Erath | 2026-08-27 | Solar | 207.4 |  | 2025-02-12 | X | X | X | X
23INR0501 | Soda Lake BESS 1 | Crane | 2025-12-17 | Battery Storage | 203.87 |  | 2024-11-01 | X | X | X | X
23INR0350 | Fort Duncan BESS | Maverick | 2025-06-07 | Battery Storage | 101.52 |  | 2024-07-31 | X | X | X | X
24INR0294 | Citrus Flatts BESS | Cameron | 2026-03-11 | Battery Storage | 101.2 |  | 2025-02-13 | X | X | X | X
25INR0081 | SanPat Solar I | San Patricio | 2027-06-01 | Solar | 308.88 |  | 2025-02-13 | X | X | X | X
25INR0052 | SanPat Solar II | San Patricio | 2027-09-01 | Solar | 256.23 |  | 2025-02-13 | X | X | X | X
24INR0059 | Cuchillas Solar | Webb | 2027-09-01 | Solar | 305.6 |  | 2025-02-13 | X | X | X | X
22INR0401 | Eval Storage | Cameron | 2028-12-31 | Battery Storage | 255 |  | 2025-02-14 |  |  | X | X
23INR0061 | Noria Solar DCC | Nueces | 2026-10-13 | Solar | 145 |  | 2025-02-12 | X | X | X | X
24INR0627 | Champion Wind Repower | Nolan | 2025-05-09 | Wind | 124.6 |  | 2024-07-29 | X | X | X | X
25INR0208 | Iron Belt Energy Storage | Borden | 2026-07-31 | Battery Storage | 401.9 |  | 2025-02-13 | X | X | X | X
25INR0131 | SOSA Storage | Madison | 2027-09-30 | Battery Storage | 157.36 |  | 2025-02-13 | X | X | X | X
23INR0286 | Dry Creek Solar I | Rusk | 2026-01-01 | Solar | 201.06 |  | 2024-10-29 | X | X | X | X
21INR0517 | Tidwell Prairie Storage 1 | Robertson | 2025-07-31 | Battery Storage | 204 |  | 2024-11-04 | X | X | X | X
23INR0494 | Cartwheel BESS 1 | Hopkins | 2025-09-30 | Battery Storage | 154.2 |  | 2024-11-04 | X | X | X | X
24INR0477 | Barrett Solar | Rains | 2026-03-01 | Solar | 125.81 |  | 2025-04-10 | X | X | X | X
19INR0042 | Long Point Solar | Brazoria | 2026-04-01 | Solar | 120.7 |  | 2025-02-12 | X | X | X | X
16INR0104 | Big Sampson Wind | Crockett | 2025-10-04 | Wind | 265.4 |  | 2024-10-31 | X | X | X | X
25INR0061 | Argenta Storage | Bee | 2027-07-01 | Battery Storage | 192 |  | 2025-02-12 | X | X | X | X
25INR0060 | Argenta Solar | Bee | 2027-07-01 | Solar | 310 |  | 2025-02-12 | X | X | X | X
24INR0124 | High Noon Solar | Hill | 2028-05-09 | Solar | 182 |  | 2025-02-12 |  |  | X | X
24INR0291 | Rubicon Alpha Wind | Haskell | 2027-07-01 | Wind | 225.6 |  | 2025-02-13 | X | X | X | X
26INR0023 | Leon Solar Park | Leon | 2026-07-01 | Solar | 210.11 |  | 2025-02-12 | X | X | X | X
25INR0400 | Maldives Solar | Scurry | 2027-07-01 | Solar | 184 |  | 2024-07-17 | X | X | X | X
23INR0086 | Hanson Solar | Coleman | 2027-04-17 | Solar | 400.58 |  | 2025-02-12 | X | X | X | X
21INR0031 | Indigo Solar | Fisher | 2026-08-17 | Solar | 150 |  | 2025-02-12 | X | X | X | X
25INR0109 | Sun Cactus Solar | Duval | 2027-10-15 | Solar | 120.63 |  | 2025-02-12 | X | X | X | X
21INR0326 | Dove Run Solar | Duval | 2027-10-15 | Solar | 120.86 |  | 2025-02-12 | X | X | X | X
24INR0207 | Glasgow Storage | Navarro | 2027-03-16 | Battery Storage | 101 |  | 2025-02-12 | X | X | X | X
24INR0206 | Glasgow Solar | Navarro | 2027-03-16 | Solar | 203.5 |  | 2025-02-12 | X | X | X | X
23INR0031 | Solace Solar | Haskell | 2026-03-31 | Solar | 374.4 |  | 2024-06-07 | X | X | X | X
24INR0399 | Buzios Solar | Motley | 2026-06-30 | Solar | 252 |  | 2025-02-11 | X | X | X | X
24INR0116 | Hart Wind | Castro | 2025-10-31 | Wind | 163.4 |  | 2024-10-31 | X | X | X | X
22INR0220 | Lamkin Solar | Comanche | 2027-08-08 | Solar | 101.5 |  | 2025-04-23 | X | X | X | X
24INR0533 | Padua Grid BESS Unit 2 | Bexar | 2026-08-31 | Battery Storage | 150.94 |  | 2025-04-24 | X | X | X | X
22INR0209 | Felix North Solar | Wilbarger | 2027-07-31 | Solar | 100.54 |  | 2025-04-03 | X | X | X | X
27INR0004 | Dundee North Wind | Wilbarger | 2027-07-31 | Wind | 307.72 |  | 2025-04-03 | X | X | X | X
27INR0005 | Dundee South A Wind | Baylor | 2027-07-31 | Wind | 307.23 |  | 2025-04-03 | X | X | X | X
27INR0007 | Felix East Solar | Wilbarger | 2027-07-31 | Solar | 301.44 |  | 2025-04-03 | X | X | X | X
27INR0011 | Dundee South B Wind | Baylor | 2027-07-31 | Wind | 300.27 |  | 2025-04-03 | X | X | X | X
27INR0012 | Felix West Solar | Wilbarger | 2027-07-31 | Solar | 200.95 |  | 2025-04-03 | X | X | X | X
24INR0181 | Bynum Solar Project | Coryell | 2025-12-01 | Solar | 56 |  | 2025-04-28 | X | X | X | X
27INR0127 | Bigway Solar I | King | 2028-12-31 | Solar | 203 |  | 2025-03-19 |  |  | X | X
27INR0128 | Bigway Solar II | King | 2028-12-31 | Solar | 203 |  | 2025-03-19 |  |  | X | X
26INR0405 | Buffalo Creek BESS | Fort Bend | 2026-06-01 | Battery Storage | 251.4 |  | 2025-05-01 | X | X | X | X
27INR0005 | Dundee South A Wind | Baylor | 2027-07-31 | Wind | 307.23 |  | 2025-04-03 | X | X | X | X
22INR0209 | Felix North Solar | Wilbarger | 2027-07-31 | Solar | 100.54 |  | 2025-04-03 | X | X | X | X
27INR0004 | Dundee North Wind | Wilbarger | 2027-07-31 | Wind | 307.72 |  | 2025-04-03 | X | X | X | X
22INR0220 | Lamkin Solar | Comanche | 2027-08-08 | Solar | 101.5 |  | 2025-04-23 | X | X | X | X
27INR0012 | Felix West Solar | Wilbarger | 2027-07-31 | Solar | 200.95 |  | 2025-04-03 | X | X | X | X
25INR0199 | Bonham Solar 1 | Limestone | 2026-08-31 | Solar | 138.4 |  | 2025-05-09 | X | X | X | X
27INR0127 | Bigway Solar I | King | 2028-12-31 | Solar | 203 |  | 2025-03-19 |  |  | X | X
27INR0011 | Dundee South B Wind | Baylor | 2027-07-31 | Wind | 300.27 |  | 2025-04-03 | X | X | X | X
27INR0128 | Bigway Solar II | King | 2028-12-31 | Solar | 203 |  | 2025-03-19 |  |  | X | X
27INR0007 | Felix East Solar | Wilbarger | 2027-07-31 | Solar | 301.44 |  | 2025-04-03 | X | X | X | X
24INR0181 | Bynum Solar Project | Coryell | 2025-12-01 | Solar | 56 |  | 2025-04-28 | X | X | X | X
26INR0521 | Millers Branch Solar III | Haskell | 2026-10-01 | Solar | 133 |  | 2025-05-14 | X | X | X | X
21INR0334 | Nightfall Solar SLF | Uvalde | 2026-06-30 | Solar | 180.87 |  | 2025-05-14 | X | X | X | X
23INR0089 | Donegal Solar | Dickens | 2027-03-01 | Solar | 201.68 |  | 2025-05-14 | X | X | X | X
24INR0453 | Longfellow BESS I | Pecos | 2026-01-31 | Battery Storage | 54.99 |  | 2025-04-29 | X | X | X | X
24INR0455 | Longfellow BESS II | Pecos | 2026-01-31 | Battery Storage | 105.75 |  | 2025-04-29 | X | X | X | X
23INR0248 | Limewood Storage | Bell | 2028-12-29 | Battery Storage | 50 |  | 2025-05-22 |  |  | X | X
25INR0068 | High Chap Solar | Brazoria | 2028-06-26 | Solar | 152.25 |  | 2025-05-28 |  |  | X | X
23INR0116 | Cantaloupe Solar | Reeves | 2028-07-01 | Solar | 307 |  | 2025-05-28 |  |  | X | X
23INR0538 | Roadrunner Crossing BESS SLF | Eastland | 2025-12-31 | Battery Storage | 151.4 |  | 2025-04-28 | X | X | X | X
26INR0669 | Greyhound Solar - Phase E | Ector | 2025-09-26 | Solar | 150.71 |  | 2024-11-04 | X | X | X | X
23INR0538 | Roadrunner Crossing BESS SLF | Eastland | 2025-12-31 | Battery Storage | 151.4 |  | 2025-04-28 | X | X | X | X
New generators that have a signed IA
GINR Reference Number | Project Name | County | Projected COD | Fuel | MW For Grid | Changes From Last Report | IA Signed | 2027 | 2027 Sensitivity | 2030 | 2030 Sensitivity | Comments
23INR0502 | Adelite Storage | Milam | 2026-06-30 | Battery Storage | 231.88 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0066 | Keys Hollow Storage Phase II SLF | Goliad | 2028-03-10 | Battery Storage | 102.04 |  | SS Completed, FIS Started, IA |  |  | X | X
24INR0068 | KEYS HOLLOW STORAGE SLF | Goliad | 2028-03-10 | Battery Storage | 102.04 |  | SS Completed, FIS Started, IA |  |  | X | X
24INR0285 | APV Plumwood Storage | Chambers | 2027-05-01 | Battery Storage | 200.82 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0330 | TRAVIS KIMBRO BESS | Travis | 2028-09-18 | Battery Storage | 36.84 |  | SS Completed, FIS Started, IA |  |  | X | X
25INR0169 | Piedra BESS | Freestone | 2026-09-30 | Battery Storage | 100.4 |  | SS Completed, FIS Completed, IA | X | X | X | X
25INR0173 | Wolf Spring Storage | Dickens | 2027-09-16 | Battery Storage | 202.7 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0175 | Concho Pearl Storage | Concho | 2027-10-14 | Battery Storage | 162.4 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0230 | Great Rock BESS | Leon | 2026-12-20 | Battery Storage | 300.9 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0233 | OCI Cobb Creek ESS | Hill | 2026-12-01 | Battery Storage | 201.6 |  | SS Completed, FIS Completed, IA | X | X | X | X
25INR0293 | TOCE BESS 1 | Wharton | 2027-06-01 | Battery Storage | 205.2 |  | SS Completed, FIS Completed, IA | X | X | X | X
25INR0313 | Staked Plains BESS | Lubbock | 2028-05-10 | Battery Storage | 254.8 |  | SS Completed, FIS Completed, IA |  |  | X | X
25INR0442 | Happy Dog Storage | Milam | 2026-09-14 | Battery Storage | 104.47 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0480 | Bell Creek BESS | Brazoria | 2026-05-15 | Battery Storage | 200.9 |  | SS Completed, FIS Completed, IA | X | X | X | X
25INR0554 | Dan Kearney BESS | Brazoria | 2027-04-01 | Battery Storage | 200.78 |  | SS Completed, FIS Completed, IA | X | X | X | X
26INR0156 | Ross Storage | Refugio | 2027-07-31 | Battery Storage | 510.99 |  | SS Completed, FIS Started, IA | X | X | X | X
26INR0310 | Quantum Storage | Haskell | 2026-06-30 | Battery Storage | 321.06 |  | SS Completed, FIS Completed, IA | X | X | X | X
26INR0375 | Avalon BESS | Fort Bend | 2026-12-01 | Battery Storage | 522.12 |  | SS Completed, FIS Completed, IA | X | X | X | X
26INR0474 | Sorghum BESS | Wharton | 2026-12-01 | Battery Storage | 208.9 |  | SS Completed, FIS Completed, IA | X | X | X | X
27INR0048 | Sunscape Renewable Energy Storage SLF | Nueces | 2028-10-28 | Battery Storage | 522.75 |  | SS Completed, FIS Started, IA |  |  | X | X
27INR0297 | Tolivar Power Plant (TEF- Due Diligence) | Reeves | 2027-04-15 | Gas | 224.5 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0154 | Lupinus Solar 2 | Franklin | 2027-04-03 | Solar | 244.24 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0156 | Moonstone Solar Project | Wilson | 2030-03-24 | Solar | 145.81 |  | SS Completed, FIS Completed, IA |  |  | X | X
24INR0161 | Miranda Solar Project | McMullen | 2027-12-06 | Solar | 261.42 |  | SS Completed, FIS Completed, IA | X | X | X | X
22INR0605 | Camino Santiago Solar | Milam | 2027-02-18 | Solar | 196.3 |  | SS Completed, FIS Completed, IA | X | X | X | X
27INR0243 | Brookview Road BESS | Harris | 2027-05-31 | Battery Storage | 203.2 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0174 | Concho Pearl Solar | Concho | 2027-10-14 | Solar | 171.9 |  | SS Completed, FIS Started, IA | X | X | X | X
26INR0431 | Big Rooter West Solar SLF | Robertson | 2027-07-01 | Solar | 403.42 |  | SS Completed, FIS Completed, IA | X | X | X | X
25INR0168 | Piedra Solar | Freestone | 2026-09-30 | Solar | 300.93 |  | SS Completed, FIS Completed, IA | X | X | X | X
26INR0155 | Ross Solar | Refugio | 2027-07-31 | Solar | 1025.57 |  | SS Completed, FIS Started, IA | X | X | X | X
28INR0024 | Padua Grid BESS Unit 3 | Bexar | 2026-05-15 | Battery Storage | 201.35 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0229 | OCI Cobb Creek Solar | Hill | 2026-12-01 | Solar | 203.1 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0065 | Keys Hollow Solar Phase II SLF | Goliad | 2028-03-10 | Solar | 204.08 |  | SS Completed, FIS Started, IA |  |  | X | X
25INR0164 | Star Dairy Solar | Lamar | 2027-04-03 | Solar | 125.61 |  | SS Completed, FIS Completed, IA | X | X | X | X
22INR0301 | Fortuna Wind | Jack | 2026-07-01 | Wind | 295.3 |  | SS Completed, FIS Completed, IA | X | X | X | X
25INR0382 | HappyDogSolar | Milam | 2026-09-14 | Solar | 85.54 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0067 | KEYS HOLLOW SOLAR SLF | Goliad | 2028-03-10 | Solar | 204.08 |  | SS Completed, FIS Started, IA |  |  | X | X
26INR0021 | Crossroads Wind | Victoria | 2027-06-30 | Wind | 253.29 |  | SS Completed, FIS Started, IA | X | X | X | X
27INR0047 | Sunscape Renewable Energy Solar SLF | Nueces | 2028-10-28 | Solar | 522.75 |  | SS Completed, FIS Started, IA |  |  | X | X
22INR0426 | LUBIO SOLAR | Kaufman | 2027-09-17 | Solar | 54.47 |  | SS Completed, FIS Completed, IA | X | X | X | X
25INR0172 | Wolf Spring Solar | Dickens | 2027-09-16 | Solar | 195.7 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0330 | Clutch City Solar Phase II | Brazoria | 2028-07-01 | Solar | 251.27 |  | SS Completed, FIS Started, IA |  |  | X | X
23INR0261 | Dodd Solar I | Henderson | 2027-09-30 | Solar | 201.8 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0356 | Cibeles Solar | McLennan | 2027-06-30 | Solar | 251 |  | SS Completed, FIS Completed, IA | X | X | X | X
23INR0441 | Bug Tussle Wind Project | Lamar | 2027-08-23 | Wind | 396.8 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0166 | Padrino Solar | Hill | 2026-05-01 | Solar | 201.4 |  | SS Completed, FIS Started, IA | X | X | X | X
26INR0074 | Anila Solar | Wilson | 2028-06-30 | Solar | 200.8 |  | SS Completed, FIS Completed, IA |  |  | X | X
24INR0484 | Lupinus Solar 3 | Franklin | 2026-09-21 | Solar | 100.8 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0155 | Lupinus Storage 2 | Franklin | 2027-04-03 | Battery Storage | 122.92 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0490 | Lupinus Storage 3 | Franklin | 2026-09-21 | Battery Storage | 50.9 |  | SS Completed, FIS Completed, IA | X | X | X | X
26INR0180 | Cape Rich BESS | Navarro | 2027-09-23 | Battery Storage | 150.52 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0543 | Thomas Cameron BESS | Lampasas | 2027-05-03 | Battery Storage | 201.52 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0108 | Louisa Energy Storage | Bexar | 2029-03-12 | Battery Storage | 102.77 |  | SS Completed, FIS Started, IA |  |  | X | X
25INR0235 | Austin Bayou Storage I | Brazoria | 2027-06-01 | Battery Storage | 150.68 |  | SS Completed, FIS Completed, IA | X | X | X | X
25INR0236 | Austin Bayou Storage II | Brazoria | 2027-06-01 | Battery Storage | 150.68 |  | SS Completed, FIS Completed, IA | X | X | X | X
25INR0237 | Austin Bayou Storage III | Brazoria | 2027-06-01 | Battery Storage | 150.68 |  | SS Completed, FIS Completed, IA | X | X | X | X
29INR0015 | Funston Solar | Jones | 2027-07-01 | Solar | 351.4 |  | SS Completed, FIS Started, IA | X | X | X | X
20INR0086 | Arroyo Solar | Cameron | 2028-02-22 | Solar | 100 |  | SS Completed, FIS Started, IA |  |  | X | X
23INR0137 | BRP Diran BESS | Wharton | 2028-01-31 | Battery Storage | 100.63 |  | SS Completed, FIS Started, IA |  |  | X | X
23INR0487 | Brightside Solar Alt POI | Live Oak | 2025-08-14 | Solar | 50 |  | SS Completed, FIS Not Started, IA | X | X | X | X
26INR0201 | Rock Rose Energy BESS | Fort Bend | 2026-12-15 | Battery Storage | 211.5 |  | SS Completed, FIS Completed, IA | X | X | X | X
20INR0247 | Water Valley Wind Energy | Tom Green | 2027-12-15 | Wind | 180 |  | SS Completed, FIS Started, IA | X | X | X | X
23INR0140 | Seine BESS | Foard | 2027-12-01 | Battery Storage | 301.19 |  | SS Completed, FIS Started, IA | X | X | X | X
24INR0304 | Jack Barton BESS | Jack | 2027-04-13 | Battery Storage | 47.34 |  | SS Completed, FIS Completed, IA | X | X | X | X
25INR0202 | East West BESS | Kerr | 2026-06-30 | Battery Storage | 123.5 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0225 | Lucy Solar | Concho | 2027-06-30 | Solar | 351.3 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0422 | Waterloo Solar 1 | Bastrop | 2027-12-01 | Solar | 200.64 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0447 | Waterloo BESS 1 | Bastrop | 2027-12-01 | Battery Storage | 105.64 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0557 | McCamey's Castle Battery | Upton | 2025-12-15 | Battery Storage | 409.6 |  | SS Completed, FIS Started, IA | X | X | X | X
26INR0309 | Solace Storage | Haskell | 2026-07-23 | Battery Storage | 321.02 |  | SS Completed, FIS Started, IA | X | X | X | X
27INR0056 | Laurel Wind Energy Center | Pecos | 2027-03-28 | Wind | 501.76 |  | SS Completed, FIS Started, IA | X | X | X | X
27INR0080 | Laurel Storage Energy Center | Pecos | 2027-03-28 | Battery Storage | 200.8 |  | SS Completed, FIS Started, IA | X | X | X | X
23INR0088 | Nockenut Springs Solar 1 | Guadalupe | 2029-06-05 | Solar | 203.17 |  | SS Completed, FIS Started, IA |  |  | X | X
26INR0359 | Uva Creek Solar | Borden | 2028-08-25 | Solar | 302.16 |  | SS Completed, FIS Started, IA |  |  | X | X
22INR0281 | Pink Solar | Hunt | 2027-04-30 | Solar | 151.9 |  | SS Completed, FIS Started, IA | X | X | X | X
24INR0274 | Bufflehead BESS | Collin | 2026-07-06 | Battery Storage | 153.3 |  | SS Completed, FIS Completed, IA | X | X | X | X
25INR0100 | Goldeneye BESS | Bell | 2027-06-01 | Battery Storage | 201.6 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0042 | Yaupon Solar SLF | Milam | 2026-06-15 | Solar | 204.08 |  | SS Completed, FIS Started, IA | X | X | X | X
21INR0391 | Grandslam Solar | Atascosa | 2026-11-28 | Solar | 121.89 |  | SS Completed, FIS Started, IA | X | X | X | X
16INR0112 | Loma Pinta Wind | La Salle | 2025-09-01 | Wind | 197.01 |  | SS Completed, FIS Started, IA | X | X | X | X
21INR0210 | Adamstown Solar | Wichita | 2027-08-31 | Solar | 251.28 |  | SS Completed, FIS Started, IA | X | X | X | X
24INR0313 | Backbone Creek BESS | Burnet | 2026-04-21 | Battery Storage | 121 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0514 | Rogers Draw BESS | Gillespie | 2026-05-10 | Battery Storage | 145.55 |  | SS Completed, FIS Started, IA | X | X | X | X
22INR0307 | Desert Vine Solar | Zapata | 2026-12-30 | Solar | 121.29 |  | SS Completed, FIS Started, IA | X | X | X | X
23INR0300 | Greater Bryant G Solar | Midland | 2026-06-22 | Solar | 17.7 |  | SS Completed, FIS Completed, IA | X | X | X | X
21INR0263 | Monarch Creek Wind | Throckmorton | 2027-09-17 | Wind | 287 |  | SS Completed, FIS Started, IA | X | X | X | X
24INR0275 | Picadillo BESS | Martin | 2026-12-15 | Battery Storage | 100.83 |  | SS Completed, FIS Completed, IA | X | X | X | X
20INR0050 | Castro Solar | Castro | 2027-10-11 | Solar | 222.95 |  | SS Completed, FIS Started, IA | X | X | X | X
24INR0410 | NRG Greens Bayou 6 (TEF-Due Diligence) | Harris | 2028-05-01 | Gas | 455 |  | SS Completed, FIS Started, IA |  |  | X | X
24INR0382 | Remy Jade III Power Station | Harris | 2028-05-01 | Gas | 102 |  | SS Completed, FIS Completed, IA |  |  | X | X
24INR0196 | Dori BQ BESS | Harris | 2027-08-30 | Battery Storage | 154 |  | SS Completed, FIS Started, IA | X | X | X | X
23INR0040 | Dori BQ Solar | Harris | 2027-08-30 | Solar | 50.42 |  | SS Completed, FIS Started, IA | X | X | X | X
22INR0417 | Amsterdam Storage | Brazoria | 2026-05-01 | Battery Storage | 201.13 |  | SS Completed, FIS Started, IA | X | X | X | X
21INR0256 | Amsterdam Solar | Brazoria | 2026-05-01 | Solar | 509.88 |  | SS Completed, FIS Started, IA | X | X | X | X
23INR0058 | Erin Solar | Wharton | 2027-11-30 | Solar | 202.5 |  | SS Completed, FIS Completed, IA | X | X | X | X
23INR0423 | Camp Creek Storage SLF | Robertson | 2028-09-15 | Battery Storage | 82.08 |  | SS Completed, FIS Completed, IA |  |  | X | X
23INR0385 | Camp Creek Solar SLF | Robertson | 2028-09-15 | Solar | 110 |  | SS Completed, FIS Completed, IA |  |  | X | X
22INR0499 | Aquilla Lake 3 Wind | Hill | 2027-03-01 | Wind | 304.6 |  | SS Completed, FIS Started, IA | X | X | X | X
22INR0262 | Sequoia II Solar | Callahan | 2026-07-31 | Solar | 425.02 |  | SS Completed, FIS Started, IA | X | X | X | X
23INR0340 | Larkspur Energy Storage | Upton | 2027-05-05 | Battery Storage | 307.46 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0080 | Meitner Solar | Gray | 2027-12-20 | Solar | 702.64 |  | SS Completed, FIS Started, IA | X | X | X | X
26INR0113 | Meitner Wind | Gray | 2027-12-20 | Wind | 709 |  | SS Completed, FIS Started, IA | X | X | X | X
21INR0428 | Nabatoto Solar North | Leon | 2027-05-01 | Solar | 451.35 |  | SS Completed, FIS Started, IA | X | X | X | X
24INR0403 | Portside Energy Center (BESS) SLF | Victoria | 2026-12-31 | Battery Storage | 41.11 |  | SS Completed, FIS Started, IA | X | X | X | X
24INR0401 | Portside Energy Center (Solar) SLF | Victoria | 2026-12-31 | Solar | 41.11 |  | SS Completed, FIS Started, IA | X | X | X | X
22INR0257 | Corazon Solar Phase II | Webb | 2028-06-01 | Solar | 203.9 |  | SS Completed, FIS Started, IA |  |  | X | X
18INR0073 | Sweetwater 1 repower | Nolan | 2024-11-30 | Wind | 41 |  | SS Completed, FIS Completed, IA | X | X | X | X
23INR0289 | Skull Creek Solar | Anderson | 2027-05-16 | Solar | 137.26 |  | SS Completed, FIS Started, IA | X | X | X | X
23INR0345 | Elmax Power Station | Harris | 2028-07-05 | Gas | 518.83 |  | SS Completed, FIS Started, IA |  |  | X | X
22INR0279 | Clutch City Solar Phase I | Brazoria | 2028-07-01 | Solar | 200.75 |  | SS Completed, FIS Started, IA |  |  | X | X
21INR0444 | Long Point Storage | Brazoria | 2026-12-30 | Battery Storage | 100.62 |  | SS Completed, FIS Started, IA | X | X | X | X
23INR0324 | Lumberjack Storage | Cherokee | 2028-03-31 | Battery Storage | 51.3 |  | SS Completed, FIS Started, IA |  |  | X | X
21INR0029 | Red Holly Storage 1 | Dawson | 2028-05-30 | Battery Storage | 50 |  | SS Completed, FIS Started, IA |  |  | X | X
21INR0033 | Red Holly Storage | Dawson | 2028-05-30 | Battery Storage | 50 |  | SS Completed, FIS Started, IA |  |  | X | X
21INR0022 | Red Holly Solar | Dawson | 2027-06-01 | Solar | 260 |  | SS Completed, FIS Started, IA | X | X | X | X
21INR0362 | Oystercatcher Solar | Ellis | 2026-09-17 | Solar | 218.1 |  | SS Completed, FIS Started, IA | X | X | X | X
23INR0083 | Bottom Grass BESS | Colorado | 2027-10-01 | Battery Storage | 202.21 |  | SS Completed, FIS Started, IA | X | X | X | X
23INR0082 | Bottom Grass Solar | Colorado | 2027-10-01 | Solar | 508.61 |  | SS Completed, FIS Started, IA | X | X | X | X
23INR0207 | El Patrimonio Solar | Bexar | 2027-04-29 | Solar | 152.32 |  | SS Completed, FIS Completed, IA | X | X | X | X
21INR0520 | Yellow Viking Solar | Somervell | 2027-07-13 | Solar | 288.99 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0055 | Three W Solar | Hill | 2026-06-01 | Solar | 110.5 |  | SS Completed, FIS Started, IA | X | X | X | X
24INR0106 | Payne Battlecreek | Hill | 2027-08-25 | Solar | 84.99 |  | SS Completed, FIS Started, IA | X | X | X | X
24INR0303 | Erika Solar | Kaufman | 2027-06-30 | Solar | 204.08 |  | SS Completed, FIS Started, IA | X | X | X | X
21INR0207 | Quantum Solar | Haskell | 2026-03-31 | Solar | 374.4 |  | SS Completed, FIS Completed, IA | X | X | X | X
23INR0200 | Paradiso BESS | Atascosa | 2027-08-01 | Battery Storage | 100.92 |  | SS Completed, FIS Started, IA | X | X | X | X
23INR0342 | Brizo BESS | Victoria | 2027-12-01 | Battery Storage | 140.76 |  | SS Completed, FIS Started, IA | X | X | X | X
23INR0479 | Taormina Storage | Bexar | 2029-05-26 | Battery Storage | 231.86 |  | SS Completed, FIS Started, IA |  |  | X | X
24INR0422 | Hollow Branch Creek Solar | Leon | 2027-12-31 | Solar | 460 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0452 | Longfellow Solar I | Pecos | 2026-12-01 | Solar | 178.2 |  | SS Completed, FIS Started, IA | X | X | X | X
24INR0454 | Longfellow Solar II | Pecos | 2026-12-01 | Solar | 207.36 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0441 | Dios BESS | Jackson | 2028-01-31 | Battery Storage | 201.08 |  | SS Completed, FIS Started, IA |  |  | X | X
26INR0290 | Cold Creek Solar 2 | Schleicher | 2026-12-31 | Solar | 445.41 |  | SS Completed, FIS Started, IA | X | X | X | X
26INR0291 | Cold Creek Storage 2 | Schleicher | 2026-12-31 | Battery Storage | 174.24 |  | SS Completed, FIS Started, IA | X | X | X | X
25INR0253 | Whiskey BESS | Van Zandt | 2027-01-30 | Battery Storage | 153.72 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0471 | McGee Storage | Henderson | 2026-05-29 | Battery Storage | 151.39 |  | SS Completed, FIS Completed, IA | X | X | X | X
25INR0384 | Zorro BESS | Van Zandt | 2027-05-01 | Battery Storage | 153.69 |  | SS Completed, FIS Completed, IA | X | X | X | X
26INR0077 | Anila BESS | Wilson | 2028-06-30 | Battery Storage | 209 |  | SS Completed, FIS Completed, IA |  |  | X | X
24INR0326 | Blarney Solar | Hopkins | 2027-07-01 | Solar | 81 |  | SS Completed, FIS Completed, IA | X | X | X | X
26INR0241 | Sol Marina Energy Center | Ellis | 2027-04-17 | Solar | 175.3 |  | SS Completed, FIS Completed, IA | X | X | X | X
25INR0460 | Acker BESS | Castro | 2027-09-14 | Battery Storage | 301.04 |  | SS Completed, FIS Completed, IA | X | X | X | X
25INR0688 | Giga Texas Data Center | Travis | 2025-12-15 | Battery Storage | 133 |  | SS Completed, FIS Completed, IA | X | X | X | X
26INR0242 | Sol Marina Energy Center BESS | Ellis | 2027-04-17 | Battery Storage | 57.15 |  | SS Completed, FIS Completed, IA | X | X | X | X
26INR0340 | SOUTHERN SELECT ENERGY STORAGE | Galveston | 2027-01-15 | Battery Storage | 404.3 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0476 | DOS RIOS ENERGY STORAGE SLF | Milam | 2027-03-15 | Battery Storage | 164.5 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0271 | Bar Candela Storage SLF | Freestone | 2027-12-31 | Battery Storage | 199.6 |  | SS Completed, FIS Completed, IA | X | X | X | X
26INR0314 | Brazos River BESS | Brazoria | 2027-04-30 | Battery Storage | 180.36 |  | SS Completed, FIS Completed, IA | X | X | X | X
26INR0417 | GAMAY ENERGY STORAGE | Brazoria | 2026-05-15 | Battery Storage | 418.6 |  | SS Completed, FIS Completed, IA | X | X | X | X
24INR0269 | Bar Candela Solar SLF | Freestone | 2027-12-31 | Solar | 200.3 |  | SS Completed, FIS Completed, IA | X | X | X | X
27INR0321 | Rock Island Generating (TEF -Due Diligence) | Colorado | 2027-06-01 | Gas | 121.8 |  | SS Completed, FIS Completed, IA | X | X | X | X
27INR0118 | Grapefruit Solar | Hidalgo | 2028-12-31 | Solar | 301.2 |  | SS Completed, FIS Started, IA |  |  | X | X
New generators that have completed FIS
GINR Reference Number | Project Name | County | Projected COD | Fuel | MW For Grid | Changes From Last Report | FIS Started/Completed | 2027 | 2027 Sensitivity | 2030 | 2030 Sensitivity | Comments
25INR0374 | Meridian BESS | Bosque | 2027-10-01 | Battery Storage | 31.23 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0190 | Fortissimo BESS | Montague | 2028-04-24 | Battery Storage | 202.65 |  | SS Completed, FIS Completed, No IA |  |  | X
25INR0301 | Van Zandt Energy Storage | Ector | 2027-04-13 | Battery Storage | 256.58 |  | SS Completed, FIS Completed, No IA | X |  | X
26INR0215 | JackGard BESS | Jack | 2027-10-10 | Battery Storage | 200.59 |  | SS Completed, FIS Completed, No IA | X |  | X
23INR0422 | Masroor Storage | Fannin | 2025-06-26 | Battery Storage | 203 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0178 | Cumulus Grid BESS | Ellis | 2028-01-01 | Battery Storage | 210.74 |  | SS Completed, FIS Completed, No IA |  |  | X
23INR0495 | Cartwheel BESS 2 | Hopkins | 2026-06-15 | Battery Storage | 156.91 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0450 | Smokey Willie BESS SLF | Anderson | 2026-12-15 | Battery Storage | 100.2 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0167 | Padrino BESS | Hill | 2026-05-23 | Battery Storage | 100.77 |  | SS Completed, FIS Completed, No IA | X |  | X
20INR0244 | Montezuma Storage | Colorado | 2028-02-29 | Battery Storage | 50.6 |  | SS Completed, FIS Completed, No IA |  |  | X
25INR0222 | Olympic BESS | Nueces | 2027-07-01 | Battery Storage | 222.81 |  | SS Completed, FIS Completed, No IA | X |  | X
22INR0443 | Bowstring BESS | San Patricio | 2027-12-30 | Battery Storage | 155 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0431 | Millennium Energy Storage | Martin | 2027-09-17 | Battery Storage | 102.59 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0396 | Stewart Grady BESS | Martin | 2027-09-01 | Battery Storage | 150.5 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0570 | Marcus Energy Storage | Brazoria | 2026-09-01 | Battery Storage | 201.04 |  | SS Completed, FIS Completed, No IA | X |  | X
27INR0096 | Rubicon Power BESS | Brazoria | 2026-06-30 | Battery Storage | 301.38 |  | SS Completed, FIS Completed, No IA | X |  | X
26INR0432 | Big Rooter West Storage SLF | Robertson | 2027-07-01 | Battery Storage | 402.44 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0372 | Elan BESS | Fort Bend | 2026-12-31 | Battery Storage | 202.65 |  | SS Completed, FIS Completed, No IA | X |  | X
27INR0102 | Cottonseed Energy Storage | Wharton | 2027-04-20 | Battery Storage | 207.6 |  | SS Completed, FIS Completed, No IA | X |  | X
23INR0335 | BRP Bachman BESS | Wharton | 2027-12-01 | Battery Storage | 411.04 |  | SS Completed, FIS Completed, No IA | X |  | X
26INR0285 | Hill Valley BESS | Grimes | 2028-07-15 | Battery Storage | 245.8 |  | SS Completed, FIS Completed, No IA |  |  | X
27INR0190 | Millsing BESS | Grimes | 2028-10-15 | Battery Storage | 501.6 |  | SS Completed, FIS Completed, No IA |  |  | X
24INR0461 | Augie BESS | Waller | 2027-12-17 | Battery Storage | 200.81 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0011 | Pinnington Storage | Jack | 2026-04-30 | Battery Storage | 508.7 |  | SS Completed, FIS Completed, No IA | X |  | X
27INR0085 | Eagle Claw Energy Center | Grimes | 2027-03-15 | Battery Storage | 200.84 |  | SS Completed, FIS Completed, No IA | X |  | X
26INR0411 | Tex-Bar ESS | Madison | 2027-07-01 | Battery Storage | 201.5 |  | SS Completed, FIS Completed, No IA | X |  | X
23INR0360 | BRP Charon BESS | Fort Bend | 2027-12-01 | Battery Storage | 410.81 |  | SS Completed, FIS Completed, No IA | X |  | X
26INR0355 | Pleiades Storage | Glasscock | 2027-09-29 | Battery Storage | 205.5 |  | SS Completed, FIS Completed, No IA | X |  | X
23INR0318 | Marcelina Storage | Wilson | 2026-12-18 | Battery Storage | 203.21 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0487 | Marick Rose BESS | Fort Bend | 2026-05-01 | Battery Storage | 50.18 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0420 | Houston BESS | Harris | 2026-06-15 | Battery Storage | 227.9 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0405 | Pledgor BESS | Matagorda | 2028-04-06 | Battery Storage | 100.33 |  | SS Completed, FIS Completed, No IA |  |  | X
25INR0371 | McMurtre Storage | Hunt | 2026-09-07 | Battery Storage | 176.13 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0370 | Willis Storage | Rains | 2027-08-13 | Battery Storage | 176.13 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0369 | Echols Creek Storage | Lamar | 2027-10-13 | Battery Storage | 100.57 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0363 | Emerald Hill Energy Storage | Dallas | 2027-06-30 | Battery Storage | 261.02 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0311 | RIVERBEND STORAGE SLF | Falls | 2027-12-31 | Battery Storage | 150 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0184 | Legato BESS | Wise | 2028-04-24 | Battery Storage | 202.65 |  | SS Completed, FIS Completed, No IA |  |  | X
25INR0142 | Sagewood BESS | Glasscock | 2027-11-13 | Battery Storage | 100.57 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0139 | Dolce BESS | Mitchell | 2027-07-01 | Battery Storage | 100.65 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0138 | Champaign BESS | Glasscock | 2027-06-28 | Battery Storage | 201.13 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0369 | Glory Bee Storage | Erath | 2026-04-14 | Battery Storage | 101 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0331 | Chisme Storage | Brown | 2027-04-13 | Battery Storage | 146 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0153 | Lupinus Storage 1 | Franklin | 2027-09-13 | Battery Storage | 82.97 |  | SS Completed, FIS Completed, No IA | X |  | X
23INR0474 | AP Greenport | Travis | 2026-02-18 | Battery Storage | 100.45 |  | SS Completed, FIS Completed, No IA | X |  | X
26INR0321 | Windmill Ridge Storage | Brazoria | 2026-12-31 | Battery Storage | 151.4 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0110 | Kildare | Jackson | 2026-09-30 | Solar | 70 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0167 | OCI SunRoper | Wharton | 2027-07-12 | Solar | 265.1 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0482 | Vault Solar | Palo Pinto | 2026-12-31 | Solar | 108.5 |  | SS Completed, FIS Completed, No IA | X |  | X
22INR0444 | Liberty Senate Solar 1 | Jack | 2025-10-27 | Solar | 202 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0281 | Cosper Solar | Bell | 2027-11-12 | Solar | 148.16 |  | SS Completed, FIS Completed, No IA | X |  | X
23INR0101 | Atria Solar | Chambers | 2025-12-30 | Solar | 112.4 |  | SS Completed, FIS Completed, No IA | X |  | X
23INR0439 | Smokey Willie Solar SLF | Anderson | 2026-04-30 | Solar | 200.92 |  | SS Completed, FIS Completed, No IA | X |  | X
26INR0235 | Noor Solar | Liberty | 2028-03-01 | Solar | 188.2 |  | SS Completed, FIS Completed, No IA |  |  | X
26INR0253 | Goldfinch Solar | Van Zandt | 2027-09-23 | Solar | 150.54 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0099 | Two Rivers Solar | Milam | 2027-05-10 | Solar | 219.35 |  | SS Completed, FIS Completed, No IA | X |  | X
21INR0320 | Ion Solar | Ellis | 2026-05-29 | Solar | 384 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0494 | Willow Beach Wind | Brazoria | 2027-10-01 | Wind | 202.33 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0150 | Lupinus Solar 1 | Franklin | 2027-09-13 | Solar | 164.86 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0333 | Chisme Solar | Brown | 2027-04-13 | Solar | 147 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0368 | Glory Bee Solar | Erath | 2026-04-14 | Solar | 305 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0569 | Hadrian Energy Storage | Wharton | 2026-06-15 | Battery Storage | 101.2 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0118 | Possum Kingdom Solar | Jack | 2027-10-29 | Solar | 262.22 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0177 | Mitchell Plant Road Solar | Pecos | 2026-12-30 | Solar | 201.5 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0255 | Mitchell Plant Road Storage | Pecos | 2026-12-30 | Battery Storage | 201.6 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0375 | Possum Kingdom BESS | Jack | 2027-10-29 | Battery Storage | 200.86 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0440 | Bronc Rodeo Solar Project | Falls | 2028-03-17 | Solar | 121.63 |  | SS Completed, FIS Completed, No IA |  |  | X
25INR0706 | Bocanova Power II | Brazoria | 2026-04-30 | Battery Storage | 150.46 |  | SS Completed, FIS Completed, No IA | X |  | X
26INR0138 | Weathervane Solar SLF | Montague | 2026-12-31 | Solar | 160.49 |  | SS Completed, FIS Completed, No IA | X |  | X
26INR0139 | Weathervane Storage SLF | Montague | 2026-12-31 | Battery Storage | 122.69 |  | SS Completed, FIS Completed, No IA | X |  | X
26INR0231 | Energy City BESS | Midland | 2027-06-30 | Battery Storage | 204.9 |  | SS Completed, FIS Completed, No IA | X |  | X
26INR0280 | Pethrus BESS | Wichita | 2027-07-27 | Battery Storage | 174.08 |  | SS Completed, FIS Completed, No IA | X |  | X
26INR0324 | Misty Hollow BESS | Grimes | 2028-07-15 | Battery Storage | 245.8 |  | SS Completed, FIS Completed, No IA |  |  | X
26INR0349 | ARTIO ENERGY STORAGE | Collin | 2028-10-01 | Battery Storage | 205.94 |  | SS Completed, FIS Completed, No IA |  |  | X
26INR0472 | Bologna BESS | Wichita | 2027-09-23 | Battery Storage | 202.56 |  | SS Completed, FIS Completed, No IA | X |  | X
26INR0551 | Hastings Park BESS | Brazoria | 2026-12-31 | Battery Storage | 256.34 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0471 | Tyler BESS | Smith | 2027-06-30 | Battery Storage | 305.3 |  | SS Completed, FIS Completed, No IA | X |  | X
26INR0519 | Sky Global West Houston | Austin | 2027-06-01 | Gas | 324.58 |  | SS Completed, FIS Completed, No IA | X | X | X | X
24INR0567 | Wolf Hollow III | Hood | 2026-05-31 | Gas | 306.32 |  | SS Completed, FIS Completed, No IA | X | X | X | X
26INR0294 | Longleaf Power Station | Angelina | 2028-06-01 | Gas | 600 |  | SS Completed, FIS Completed, No IA |  |  | X | X
25INR0008 | BasRanch (TEF - Due Diligence) | Ward | 2028-12-01 | Gas | 1390 |  | SS Completed, FIS Completed, No IA |  |  | X | X
26INR0408 | Liatris Flexible Gas | Brazoria | 2026-12-31 | Gas | 204.71 |  | SS Completed, FIS Completed, No IA | X | X | X | X
26INR0183 | TRIFECTA Gas | Midland | 2029-10-31 | Gas | 453 |  | SS Completed, FIS Completed, No IA |  |  | X | X
27INR0209 | Goby Energy Center | Brazoria | 2027-06-30 | Battery Storage | 200.65 |  | SS Completed, FIS Completed, No IA | X |  | X
25INR0133 | Rose Quartz BESS | Dimmit | 2026-12-01 | Battery Storage | 101.41 |  | SS Completed, FIS Completed, No IA | X |  | X
27INR0234 | Maddox Solar | Grayson | 2027-09-17 | Solar | 101.3 |  | SS Completed, FIS Completed, No IA | X |  | X
27INR0218 | Themisto Solar | Nolan | 2027-12-30 | Solar | 301.2 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0423 | Hollow Branch Creek Storage | Leon | 2027-12-31 | Battery Storage | 460 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0340 | Mystic Springs Renewable Energy Storage SLF | Kaufman | 2027-08-31 | Battery Storage | 258.83 |  | SS Completed, FIS Completed, No IA | X |  | X
24INR0339 | Mystic Springs Renewable Energy Solar SLF | Kaufman | 2027-08-31 | Solar | 258.83 |  | SS Completed, FIS Completed, No IA | X |  | X
New generators that have started FIS
GINR Reference Number | Project Name | County | Projected COD | Fuel | MW For Grid | Changes From Last Report | FIS Started/Completed | 2027 | 2027 Sensitivity | 2030 | 2030 Sensitivity | Comments
27INR0324 | LONE STAR INDUSTRIAL PARK GAS POWER PROJECT | Morris | 2028-05-11 | Gas | 166 |  | SS Completed, FIS Started, No IA |  |  | X
29INR0041 | Homestead Power (TEF-Due Diligence) | Austin | 2029-12-15 | Gas | 260.3 |  | SS Completed, FIS Started, No IA |  |  | X
26INR0529 | Electric E - West Texas Generation | Loving | 2028-04-09 | Gas | 44.4 |  | SS Completed, FIS Started, No IA |  |  | X
27INR0071 | Sandow Lakes Energy Station | Milam | 2028-04-01 | Gas | 1291.6 |  | SS Completed, FIS Started, No IA |  |  | X
26INR0597 | Electric E - West Texas Generation 2 | Midland | 2028-09-19 | Gas | 44.4 |  | SS Completed, FIS Started, No IA |  |  | X
29INR0083 | Denver City - Mustang - Gas | Yoakum | 2029-10-27 | Gas | 472.1 |  | SS Completed, FIS Started, No IA |  |  | X
26INR0537 | Comanche Creek generating station | Pecos | 2026-09-30 | Gas | 107 |  | SS Completed, FIS Started, No IA | X |  | X
29INR0048 | Rippling Curve Peaking Power | Harris | 2029-01-01 | Gas | 208 |  | SS Completed, FIS Started, No IA |  |  | X
26INR0345 | NET Power Demonstration plant | Harris | 2027-07-05 | Gas | 25.5 |  | SS Completed, FIS Started, No IA | X |  | X
28INR0086 | West Royal Natural Gas (TEF-Due Diligence) | Upton | 2029-05-01 | Gas | 889.6 |  | SS Completed, FIS Started, No IA |  |  | X
27INR0084 | Aegle Power | Cameron | 2027-07-30 | Gas | 1536.4 |  | SS Completed, FIS Started, No IA | X |  | X
28INR0108 | RAYBURN ENERGY STATION II Gas (TEF-Due Diligence) | Grayson | 2028-02-26 | Gas | 570 |  | SS Completed, FIS Started, No IA |  |  | X
28INR0105 | Vast Sands Power I (TEF -Due Diligence) | Ward | 2027-12-01 | Gas | 440 |  | SS Completed, FIS Started, No IA | X |  | X
28INR0109 | Vast Sands Power II (TEF-Due Diligence) | Ward | 2028-02-01 | Gas | 440 |  | SS Completed, FIS Started, No IA |  |  | X
28INR0090 | EmberGreen | Wharton | 2028-01-01 | Gas | 900 |  | SS Completed, FIS Started, No IA |  |  | X
28INR0089 | EmberYork | Austin | 2028-01-01 | Gas | 900 |  | SS Completed, FIS Started, No IA |  |  | X
27INR0272 | EMPower Odessa (TEF - Due Diligence) | Ector | 2027-07-07 | Gas | 123.4 |  | SS Completed, FIS Started, No IA | X |  | X
18INR0009 | Eagle Pines Gas | Cherokee | 2028-10-30 | Gas | 1174 |  | SS Completed, FIS Started, No IA |  |  | X
28INR0087 | North Royal Thermal (TEF- Due Diligence) | Lamar | 2029-05-01 | Gas | 479 |  | SS Completed, FIS Started, No IA |  |  | X
26INR0396 | Kodiak AGR1 (TEF- Due Diligence) | Reeves | 2027-06-15 | Fuel Oil | 132 |  | SS Completed, FIS Started, No IA | X |  | X
22INR0497 | TEXPO | Wilbarger | 2027-10-31 | Gas | 680 |  | SS Completed, FIS Started, No IA | X |  | X
26INR0351 | Jack County III – 345 kV (TEF -Due Diligence) | Jack | 2027-07-01 | Gas | 660 |  | SS Completed, FIS Started, No IA | X |  | X
26INR0350 | Jack County III – 138 kV | Jack | 2026-05-01 | Gas | 660 |  | SS Completed, FIS Started, No IA | X |  | X
24INR0145 | Calpine Guadalupe Peakers | Guadalupe | 2027-05-23 | Gas | 459 |  | SS Completed, FIS Started, No IA | X |  | X
26INR0261 | Bastrop Peaking Generators (TEF-Due Diligence) | Bastrop | 2026-05-31 | Gas | 1104 |  | SS Completed, FIS Started, No IA | X |  | X
27INR0095 | Bulldog Power (TEF - Due Diligence) | Brazoria | 2027-12-18 | Gas | 300.75 |  | SS Completed, FIS Started, No IA | X |  | X
24INR0576 | Boling Generation (TEF-Due Diligience) | Wharton | 2027-10-29 | Gas | 400 |  | SS Completed, FIS Started, No IA | X |  | X
24INR0479 | NRG THW GT 138 | Harris | 2026-06-05 | Gas | 466 |  | SS Completed, FIS Started, No IA | X |  | X
23INR0486 | Lamar Unit 1 Repower | Lamar | 2027-12-18 | Gas | 634 |  | SS Completed, FIS Started, No IA | X |  | X
27INR0181 | Elk Unit 4 | Hale | 2027-02-28 | Gas | 210 |  | SS Completed, FIS Started, No IA | X |  | X
21INR0534 | Midlothian Unit 2 repower | Ellis | 2026-03-03 | Gas | 274 |  | SS Completed, FIS Started, No IA | X |  | X
22INR0543 | Midlothian Unit 3 repower | Ellis | 2026-03-03 | Gas | 273 |  | SS Completed, FIS Started, No IA | X |  | X
22INR0523 | Midlothian 4 repower | Ellis | 2026-03-03 | Gas | 276 |  | SS Completed, FIS Started, No IA | X |  | X
22INR0586 | Hays Energy Unit 2 Repower | Hays | 2026-03-03 | Gas | 258 |  | SS Completed, FIS Started, No IA | X |  | X
21INR0527 | Hays Energy Unit 3 Repower | Hays | 2026-03-03 | Gas | 260 |  | SS Completed, FIS Started, No IA | X |  | X
26INR0111 | Graphic Packaging Gas | McLennan | 2026-04-07 | Gas | 43.36 |  | SS Completed, FIS Started, No IA | X |  | X
29INR0068 | Gregory Power Development | San Patricio | 2028-12-19 | Gas | 1100 |  | SS Completed, FIS Started, No IA |  |  | X
27INR0497 | Black Mountain Somervell Gas Combined | Somervell | 2027-06-30 | Gas | 495.3 |  | SS Started, FIS Started, No IA | X |  | X
26INR0560 | Fort Worth Power Core Bastrop Gas Plant | Bastrop | 2029-09-28 | Gas | 506.38 |  | SS Started, FIS Started, No IA |  |  | X
27INR0320 | Perseus Gas | Nueces | 2028-12-31 | Gas | 1056.8 |  | SS Completed, FIS Started, No IA |  |  | X
27INR0337 | Jalisco Cogen | Nueces | 2029-05-31 | Gas | 167.8 |  | SS Completed, FIS Started, No IA |  |  | X
27INR0489 | Power Lane II Gas | Hunt | 2027-06-01 | Gas | 105 |  | SS Started, FIS Started, No IA | X |  | X
28INR0121 | Jalisco Peaker | Nueces | 2029-05-31 | Gas | 183.6 |  | SS Completed, FIS Started, No IA |  |  | X
28INR0413 | Tolivar Power Plant Phase 2 | Reeves | 2027-07-30 | Gas | 224.5 |  | SS Started, FIS Started, No IA | X |  | X
29INR0166 | LOST PINES GAS RECIP | Bastrop | 2029-08-02 | Gas | 113.02 |  | SS Completed, FIS Started, No IA |  |  | X
29INR0176 | SCHNEIDER GAS RICE | Caldwell | 2029-08-02 | Gas | 113.02 |  | SS Started, FIS Started, No IA |  |  | X
PG 6.9(1) Inactive Projects
INR | Project Name | Fuel | County | MW
24INR0169 | Yaupon Storage SLF | Battery Storage | Milam | 102.04
23INR0232 | Rocinante BESS | Battery Storage | Gonzales | 33.17
23INR0231 | Rocinante Solar | Solar | Gonzales | 95.29
21INR0274 | Carol Solar | Solar | Potter | 223.2
24INR0259 | Zeissel Storage SLF | Battery Storage | Knox | 207.94
23INR0117 | Cantaloupe Storage | Battery Storage | Reeves | 251.05
24INR0605 | TEXAS GULF SULPHUR REPOWER | Gas | Wharton | 94
23INR0156 | Umbra (Stockyard) BESS | Battery Storage | Franklin | 72.98
23INR0155 | Umbra (Stockyard) Solar | Solar | Franklin | 207.84
24INR0075 | Blue Bird Solar | Solar | Johnson | 1004
PG 6.9(1) Cancelled Projects
INR | Project Name | Fuel | County | MW
21INR0344 | Lunis Creek Solar SLF | Solar | Jackson | 617.12
22INR0307 | Desert Vine Solar | Solar | Zapata | 121.29
24INR0411 | NRG Greens Bayou 9 345 | Gas | Harris | 455
21INR0256 | Amsterdam Solar | Solar | Brazoria | 509.88
22INR0417 | Amsterdam Storage | Battery Storage | Brazoria | 201.13
24INR0403 | Portside Energy Center (BESS) SLF | Battery Storage | Victoria | 41.11
24INR0401 | Portside Energy Center (Solar) SLF | Solar | Victoria | 41.11
21INR0017 | Danish Fields III Solar | Solar | Wharton | 201
21INR0016 | Danish Fields II Solar | Solar | Wharton | 201
18INR0058 | Texana Solar | Solar | Wharton | 152.34
26INR0042 | Valhalla Solar | Solar | Brazoria | 306.8
18INR0068 | Loraine Windpark Phase III | Wind | Mitchell | 100
22INR0211 | Schoolhouse Solar | Solar | Lee | 150.84
25INR0160 | Canvasback BESS | Battery Storage | Calhoun | 150.5
22INR0361 | Sibyl Power Station | Gas | Fort Bend | 312
21INR0226 | Equinox Solar 1 | Solar | Starr | 200
24INR0395 | Berkman Storage | Battery Storage | Galveston | 150.86
20INR0035 | Angus Solar | Solar | Bosque | 112
21INR0021 | Green Holly Solar | Solar | Dawson | 413.6
24INR0057 | Hanson Storage | Battery Storage | Coleman | 101.39
21INR0500 | SkySealy | Gas | Austin | 149.4
23INR0411 | SkySealy2 | Gas | Austin | 150
23INR0144 | Galactic Solar | Solar | Grayson | 205.2
17INR0022 | MIRAGE | Gas | Harris | 11
Retired Units
Unit Name | MW For Grid | 2027 | 2030 | Comments
CALENERGY-FALCON SEABOARD STG 3 (FLCNS_UNIT3) | 62 | X | X | 2025-01-08
TOS BATTERY STORAGE (DGR) | 2 | X | X | 2024-11-01
DOW G37 | 61 | X | X | 2023-07-04
J T DEELY U1 | 420 | X | X | 2023-07-07
J T DEELY U2 | 420 | X | X | 2023-07-07
OCI_ALM1_ASTRO1 | 1 | X | X
Generation Resources Unavailable in Planning Studies Prior to NSO
Unit Name | MW For Grid | 2027 | 2030 | Comments
Sommers Unit #1 | 420 | X | X | https://www.ercot.com/mp/data-products/data-product-details?id=PG3-1411-M
Sommers Unit #2 | 410 |  | X
Spruce Unit #1 | 560 |  | X
Spruce Unit #2 | 922 | X | X
Mothballed Units
Unit Name | MW For Grid | 2027 | 2030 | Comments
BRANDON (LP&L) (DGR) | 25 | X | X | NSO Posted (INDEFINITE MOTHBALL AS OF 10/2/2023)
R MASSENGALE CTG 1 (LP&L) | 20 | X | X | NSO Posted (INDEFINITE MOTHBALL AS OF 10/2/2023)
R MASSENGALE CTG 2 (LP&L) | 20 | X | X | NSO Posted (INDEFINITE MOTHBALL AS OF 10/2/2023)
R MASSENGALE STG (LP&L) | 59 | X | X | NSO Posted (INDEFINITE MOTHBALL AS OF 10/2/2023)
RAY OLINGER STG 1 | 78 | X | X | NSO Posted (INDEFINITE MOTHBALL AS OF 4/5/22)
TEXAS BIG SPRING WIND B | 7 | X | X | NSO Posted (INDEFINITE MOTHBALL STATUS AS ON 1/1/24)
TY COOKE CTG 1 (LP&L) | 19 | X | X | NSO Posted (INDEFINITE MOTHBALL AS OF 10/2/2023)
TY COOKE CTG 2 (LP&L) | 27 | X | X | NSO Posted (INDEFINITE MOTHBALL AS OF 10/2/2023)
WICHITA FALLS STG 4 | 20 | X | X | NSO Posted (INDEFINITE MOTHBALL STATUS AS ON 11/1/23)
AMOC_AMOCO_5 | 32 | X | X | Notice of probability to return
V H BRAUNIG STG 1 | 225 | X | X | 2024 RTP listed under 'Prior to NSO' (INDEFINITE MOTHBALL AS OF 3/31/2025)
V H BRAUNIG STG 2 | 240 | X | X | 2024 RTP listed under 'Prior to NSO' (INDEFINITE MOTHBALL AS OF 3/31/2025)
V H BRAUNIG STG 3 | 420 |  | X | 2024 RTP listed under 'Prior to NSO' (RMR FROM 3/1/25 TO 3/1/27)
DOWGEN_DOW_G66 | 105 | X | X | NSO Posted
Bayou Cogen | 4 | X | X | NSO Posted
DOW ST64 | 50 | X | X | NSO Posted
Retirement Units back in service
Unit Name | MW For Grid | 2027 | 2030 | Comments
BARNEY M DAVIS STG 1 | 292 | X | X | Withdrawal of NSO
MOUNTAIN CREEK STG 8 | 568 | X | X | NCGRD posted
PETRA NOVA | 71 | X | X | NCGRD posted
GREGORY POWER PARTNERS GT1 | 145 | X | X | NCGRD posted
GREGORY POWER PARTNERS GT2 | 145 | X | X | NCGRD posted
GREGORY POWER PARTNERS STG | 75 | X | X | NCGRD posted
Fuel Change - Coal to Gas
Unit Name | MW For Grid | 2027 | 2030 | Comments
Luminant’s Coleto Creek | 655 | X | X | 26INR0664

## Switchable Generation
Date Last Updated: | 2025-05-23 | Back
Status | Final
Operational Resources (Switchable)
Unavailable to ERCOT during summer 6/1-9/30
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | 2027 | 2030
ANTELOPE IC 1 | ANTLP_G1 | HALE | GAS | WEST | 2016 | 54 | 54
ANTELOPE IC 2 | ANTLP_G2 | HALE | GAS | WEST | 2016 | 54 | 54
ANTELOPE IC 3 | ANTLP_G3 | HALE | GAS | WEST | 2016 | 54 | 54
ELK STATION CTG 1 | AEEC_ELK_1 | HALE | GAS | WEST | 2016 | 190 | 190
ELK STATION CTG 2 | AEEC_ELK_2 | HALE | GAS | WEST | 2016 | 190 | 190
ELK STATION CTG 3 | AEEC_ELK_3 | HALE | GAS | WEST | 2016 | 190 | 190
TENASKA GATEWAY STATION CTG 1 | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | 156 | -
TENASKA GATEWAY STATION CTG 2 | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 135 | 135
TENASKA GATEWAY STATION CTG 3 | TGCCS_CT3 | RUSK | GAS-CC | NORTH | 2001 | 153 | -
TENASKA GATEWAY STATION STG 4 | TGCCS_UNIT4 | RUSK | GAS-CC | NORTH | 2001 | 400 | 400
TENASKA KIAMICHI STATION 2CT101 | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 150 | 150
TENASKA KIAMICHI STATION 2CT201 | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | 152 | 152
TENASKA KIAMICHI STATION 2ST | KMCHI_2ST | FANNIN | GAS-CC | NORTH | 2003 | 311 | 311
Switchable Capacity Unavailable to ERCOT | SWITCH_UNAVAIL |  | GAS |  |  | 2189 | 1880
Unavailable to ERCOT during winter 12/1-2/28
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | 2026/2027 | 2027/2028 | 2029/2030 | 2030/2031
ANTELOPE IC 1 | ANTLP_G1 | HALE | GAS | WEST | 2016 | 56 | 56 | 56 | 56
ANTELOPE IC 2 | ANTLP_G2 | HALE | GAS | WEST | 2016 | - | - | 56 | 56
ELK STATION CTG 1 | AEEC_ELK_1 | HALE | GAS | WEST | 2016 | 200 | 200 | 200 | 200
ELK STATION CTG 2 | AEEC_ELK_2 | HALE | GAS | WEST | 2016 | 200 | 200 | 200 | 200
TENASKA GATEWAY STATION CTG 1 | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | - | 162 | 162 | -
TENASKA GATEWAY STATION CTG 2 | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 179 | 179 | 179 | 179
TENASKA GATEWAY STATION CTG 3 | TGCCS_CT3 | RUSK | GAS-CC | NORTH | 2001 | - | - | 178 | -
TENASKA GATEWAY STATION STG 4 | TGCCS_UNIT4 | RUSK | GAS-CC | NORTH | 2001 | 389 | 389 | 389 | 389
TENASKA KIAMICHI STATION 2CT101 | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 185 | 185 | 185
TENASKA KIAMICHI STATION 2CT201 | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | - | - | 152 | 152
TENASKA KIAMICHI STATION 2ST | KMCHI_2ST | FANNIN | GAS-CC | NORTH | 2003 | - | - | 311 | 311
Switchable Capacity Unavailable to ERCOT | SWITCH_UNAVAIL |  | GAS |  |  | 1209 | 1371 | 1605 | 1265
Unavailable to ERCOT during Spring 3/1-5/30
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | 2027 | 2030
ANTELOPE IC 1 | ANTLP_G1 | HALE | GAS | WEST | 2016 | 56 | 56
ANTELOPE IC 2 | ANTLP_G2 | HALE | GAS | WEST | 2016 | - | 56
ELK STATION CTG 1 | AEEC_ELK_1 | HALE | GAS | WEST | 2016 | 195 | 195
ELK STATION CTG 2 | AEEC_ELK_2 | HALE | GAS | WEST | 2016 | 195 | 195
TENASKA GATEWAY STATION CTG 1 | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | - | 162
TENASKA GATEWAY STATION CTG 2 | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 179 | 179
TENASKA GATEWAY STATION CTG 3 | TGCCS_CT3 | RUSK | GAS-CC | NORTH | 2001 | 179 | 179
TENASKA GATEWAY STATION STG 4 | TGCCS_UNIT4 | RUSK | GAS-CC | NORTH | 2001 | 400 | 400
TENASKA KIAMICHI STATION 2CT101 | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 159 | 159
TENASKA KIAMICHI STATION 2CT201 | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | - | 152
Switchable Capacity Unavailable to ERCOT | SWITCH_UNAVAIL |  | GAS |  |  | 1363 | 1733 | *unavailable for March
Unavailable to ERCOT during Fall 10/1-11/30
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | 2027 | 2030
ANTELOPE IC 1 | ANTLP_G1 | HALE | GAS | WEST | 2016 | 56 | 56
ANTELOPE IC 2 | ANTLP_G2 | HALE | GAS | WEST | 2016 | 56 | 56
ANTELOPE IC 3 | ANTLP_G3 | HALE | GAS | WEST | 2016 | 54 | 54
ELK STATION CTG 1 | AEEC_ELK_1 | HALE | GAS | WEST | 2016 | 190 | 190
ELK STATION CTG 2 | AEEC_ELK_2 | HALE | GAS | WEST | 2016 | 190 | 190
ELK STATION CTG 3 | AEEC_ELK_3 | HALE | GAS | WEST | 2016 | 190 | 190
TENASKA GATEWAY STATION CTG 1 | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | 162 | -
TENASKA GATEWAY STATION CTG 2 | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | - | 135
TENASKA KIAMICHI STATION 2CT101 | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 149 | 149
TENASKA KIAMICHI STATION 2CT201 | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | - | 152
Switchable Capacity Unavailable to ERCOT | SWITCH_UNAVAIL |  | GAS |  |  | 1047 | 1172

## DC Tie Modeling & Dispatch
Date Last Updated: | 2025-02-23 | Back
Status | Final
Economic Analysis
DC Tie Dispatch - 8760-hour Assumptions
DC_E | Import + Export | Mapped to hourly generation and demand profiles based on historical operational data.
DC_N | Import + Export | Mapped to hourly generation and demand profiles based on historical operational data.
DC_L | Import + Export | Mapped to hourly generation and demand profiles based on historical operational data.
DC_R | Import + Export | Mapped to hourly generation and demand profiles based on historical operational data.

## Reserve Requirement
Date Last Updated: | 2025-03-05 | Back
Status | Final
Economic Analysis | 1801
The reserve requirement used in the economic models are based on a review of ERCOT’s 2025 Responsive Reserve and Regulation Up requirements. Note that the MW contribution of load resources is not an input into the economic model.

## Fuel Price Assumptions
Date Last Updated: | 2025-07-21 | Back
Status | Final
Source | EIA 2025 AEO Reference Case
Natural Gas Price Forecast ($/MMBtu)
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Average
2025 | 3.1246 | 2.9083 | 2.7184 | 2.7922 | 2.8875 | 2.9541 | 2.8657 | 2.9021 | 2.9143 | 3.019 | 3.0034 | 3.1703 | 2.9383
2026 | 3.0207 | 2.8116 | 2.628 | 2.6993 | 2.7914 | 2.8558 | 2.7704 | 2.8056 | 2.8174 | 2.9186 | 2.9035 | 3.0648 | 2.8406
2027 | 2.9374 | 2.7341 | 2.5556 | 2.6249 | 2.7145 | 2.7771 | 2.6941 | 2.7283 | 2.7398 | 2.8382 | 2.8235 | 2.9804 | 2.7623
2028 | 3.1185 | 2.9026 | 2.7131 | 2.7867 | 2.8818 | 2.9483 | 2.8601 | 2.8965 | 2.9087 | 3.0131 | 2.9975 | 3.1641 | 2.9326
2029 | 3.3651 | 3.1322 | 2.9277 | 3.0071 | 3.1097 | 3.1815 | 3.0863 | 3.1255 | 3.1387 | 3.2514 | 3.2346 | 3.4143 | 3.1645
2030 | 3.6498 | 3.3972 | 3.1754 | 3.2615 | 3.3728 | 3.4507 | 3.3474 | 3.39 | 3.4042 | 3.5265 | 3.5082 | 3.7032 | 3.4322
2031 | 3.902 | 3.6319 | 3.3948 | 3.4869 | 3.6059 | 3.6891 | 3.5787 | 3.6242 | 3.6395 | 3.7701 | 3.7507 | 3.959 | 3.6694
2032 | 4.5736 | 4.257 | 3.9791 | 4.087 | 4.2265 | 4.324 | 4.1946 | 4.248 | 4.2658 | 4.419 | 4.3962 | 4.6404 | 4.3009

## Emission Cost Assumptions
Date Last Updated: | 2025-07-01 | Back
Status | Final
Source | EIA AEO
Emission | $/ton
Nox (Seasonal) | 166
SO2 | 0
CO2 | 0

## Load Forecast Weather Year
Date Last Updated: | 2025-07-01 | Back
Status | Final
Load forecast
Weather year assumption | Base: 2013
The peak and hourly profile information is included in Appendix D along with the case information
Note that the 2013 weather scenario is the base weather scenario used as the starting point in the economic analysis.