## Project Legend
MTEP Database Export October 5, 2020
Project Table Field Legend
Appendix A contains projects which are being or have been approved by MISO Board of Directors.
Transmission Owners are obligated to make a good faith effort to construct projects in Appendix A.
Appendix B projects have been reviewed by MISO staff for need and effectivenes.
Project table has blue highlighted header. A project may have multiple facilties.
Facility table has beige highlighted header. A project's facilities may have different in service dates.
Project Table Field Legend
Field | Description
Target Appendix | Target appendix for the MTEPyy planning cycle. Example: "A in MTEP15" projects were reviewed in MTEP15. .
Region | MISO Planning Region: Central, East, West or South
Geographic Location by TO Member System | Project geographic location by Transmission Owner member systems
PrjID | Project ID: MISO project identifier
Project Name | Project name (short name)
Project Description | A description of the project's components
State 1 | State project is located or first state if in multiple states
State 2 | If applicable, the second state the project is located
Allocation Type per FF | Project Type per Attachment FF of Tariff. BaseRel is Baseline Reliability, GIP is Generator Interconnection Project, TDSP is Transmission Delivery Service Project, MEP is Market Efficiency Project, MVP is Multi Value Project, Other is none of the above. Preliminary project allocation types may be designated for projects in Appendix B
Share Status | Cost allocation status for projects in Appendix A or moving to Appendix A in current planning cycle. Projects are Shared, Not Shared or Excluded. Preliminary sharing designations may be input for Appendix B projects
Other Type | Indicates the project driver behind Other type projects.
Estimated Cost | Total estimated project cost from Facility table
Expected ISD (Min/Max) | Dates when project is expected to be in service. Min and Max dates. Expected ISD are in Facility table.
Max kV | Maximum facility voltage in project. Summary information from Facility table
Min kV | Minimum facility voltage in project. Summary information form Facility table
Transmission Project Type | Bottom-Up, Top-Down or Externally Driven per BPM-020 r12 section 2.3

## MTEP20 A Projects
Appendix | Planning Region | Geographic Location by TO Member System | Project ID | Project Name | Project Description | State | Need Date | Allocation Type per FF | Other Type | Expected ISD (Min) | Max kV | Min kV | Estimated Cost
A in MTEP20 | Central | AmerenIL | 11925 | New Massac Substation - Convert Joppa 230 kV substation to 345 kV substation | Install 2-345/161 kV, 560 MVA transformers, remove 230/161 kV equipment. Rebuild Joppa-West Frankfort 230 kV for 345 kV use (Massac-Jordan). | IL | 2023-12-01 | Other | Reliability | 2023-06-01 | 345 | 161 | 112400000
A in MTEP20 | West | ITCM | 18847 | Big Cedar Load Interconnection | A new load will be added at the Big Cedar Industrial Park in Cedar Rapids, IA and ITC will construct a new Big Cedar Substation to connect this new load. The new sub will tap the Beverly – Morgan Valley 345 kV line and create a Morgan Valley – Big Cedar #1 345 kV line and a Big Cedar – Beverly 345 kV line. New line taps should utilize bundled T2-795 ACSR conductor and have OPGW. ITC will also need to add a second 345 kV circuit on the existing Beverly – Morgan Valley 345 kV line to add a 3rd 345 kV feed into the new Big Cedar substation. The new 345 kV line should utilize bundled T2-795 ACSR conductor. The new Big Cedar substation will include a new 3 position 345 kV breaker and half substation with 3 – 345 kV lines and 2 – 345/161 kV transformers (450 MVA nameplate) and all 345 kV substation equipment should be rated 3000 amps summer normal rating. The 161 kV portion of the substation will be folded breaker and ½, with each transformer connected to a dedicated position (double breaker double bus), and the new 161 kV underground feeds to the customer will be connected on breaker and a half positions. All new 161 kV substation equipment should be rated 2000 amps minimum summer normal rating. All new underground 161 kV lines from Big Cedar to the customer substations should be rated 900 amps minimum summer normal rating. ITC will install new 161 kV ring bus substations at each of the new customer substations. All substation equipment should be rated 2000 amps minimum summer normal rating. ITC will build out the Morgan Valley substation to full 4 position breaker and ½ with the addition of this load and the additional line into Morgan Valley. IPL has also requested that the existing 69 kV double circuit line be relocated as part of this project. The Beverly – Fairfax #2 and Fairfax – Oakridge 69 kV line will be moved to follow the railroad tracks up to Edgewood Rd, then follow Edgewood Rd to meet up with the existing line route. | IA | 2021-12-31 | Other | Load Growth | 2021-12-31 | 345 | 69 | 104627788.2
A in MTEP20 | Central | AmerenIL | 18249 | New LaSalle Area 138 kV Statcom (100 MVAR) | Install a 100 MVAR Statcom. | IL | 2023-12-01 | BRP |  | 2023-12-01 | 138 | 0 | 91400000
A in MTEP20 | Central | AmerenIL | 18250 | New Robinson 138 kV Statcom (70 Mvar) | Install an 70 Mvar Statcom.a new substation just south of Robinson Marathon. Re locate the Robinson – Newton 138 kV line and the Robinson – Lawrenceville 138 kV line in and out of the new substation. | IL | 2023-06-01 | BRP |  | 2023-06-01 | 138 | 0 | 78000000
A in MTEP20 | Central | AmerenIL | 17910 | Rebuild Grand Tower-Carbondale NW 138 kV line | Rebuild ~36 miles of the Grand Tower-Carbondale NW-W. Frankfort 138 kV line as double circuit 345/138 kV. | IL | 2024-12-01 | Other | Age and Condition | 2024-12-01 | 345 | 138 | 75600000
A in MTEP20 | Central | AmerenIL | 13797 | Rebuild Albion South-Norris City North 138 kV to double circuit | Rebuild the existing 138 kV circuit to 2000A. Double circuit the line for new 3000A 345 kV circuit. | IL | 2022-06-01 | Other | Age and Condition | 2022-12-01 | 345 | 138 | 74000000
A in MTEP20 | Central | AEP | 17684 | Upgrade Greentown 765 kV substation | Rehabilitation and reconfiguration of the 765kV Greentown yard. | IN |  | Other | Age and Condition | 2023-02-15 | 765 | 138 | 70000000
A in MTEP20 | South | Entergy-TX | 18248 | Millbend 138 kV: New Distribution Station | Build ~ 7miles of new transmission line to cut the new Millbend 138 kV station into the existing New Caney to Parkway 138 kV line. | TX | 2024-06-01 | Other | Load Growth | 2024-06-01 | 138 | 0 | 65400000
A in MTEP20 | South | Entergy-LA | 13925 | Choudrant: New distribution substation | Construct a 230 kV distribution substation named Choudrant in southern Lincoln parish near the town of Choudrant and construct a 230 kV transmission line from the new substation that terminates into the existing Mt Olive substation. | LA | 2023-06-01 | Other | Load Growth | 2023-06-01 | 230 | 0 | 56225000
A in MTEP20 | Central | AmerenIL | 11926 | New Jordan Substation - Convert West Frankfort 230 kV substation to 345 kV substation | Install 345/138 kV, 560 MVA transformer. Rebuild/reinsulate 19.9 miles of existing 230 kV line between West Frankfort and St. Johns for use at 345 kV. | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 345 | 138 | 56100000
A in MTEP20 | South | Entergy-TX | 15648 | Castle 230 kV: New Distribution Station | Cut the Castle 230 kV station in and out on the Ponderosa to Grimes 230 kV line. 230 kV breakers will be installed at Castle. | TX | 2024-06-01 | Other | Load Growth | 2024-06-01 | 230 | 0 | 50510000
A in MTEP20 | Central | AmerenMO | 17908 | Rebuild Bland-Franks 345 kV line | Rebuild approximately 44 miles 345kV line to 3000A. | MO | 2024-12-01 | Other | Age and Condition | 2024-12-01 | 345 | 0 | 48400000
A in MTEP20 | East | NIPS | 18986 | Rebuild NIPSCo BES for Reinforcements | Strengthen the NIPSCo transmission system ahead of the anticipated suspension of the [NIPS] Schahfer units 14, 15, 17 and 18. | IN | 2023-05-01 | BRP |  | 2023-05-01 | 138 | 0 | 48100000
A in MTEP20 | Central | AmerenIL, AmerenMO | 16984 | Rebuild Sioux-Meppen North 138 kV line (4) | Rebuild existing river crossing (structures 173-179). | IL,MO | 2021-12-01 | Other | Age and Condition | 2021-12-01 | 138 | 0 | 45700000
A in MTEP20 | East | METC | 15896 | Battle Creek - Morrow (Jaguar) #1 138 kV Rebuild | The proposed solution is to rebuild 19.38 miles from Str #008E57412E to Str #008E8623 of the Battle Creek – Morrow #1 138kV circuit using 954 ACSR conductor with future double-circuit steel structures and leave adjacent side vacant for future circuit and also rebuild 3.3 miles from Str #008E8623 to Morrow station of 477 ACSR conductor to 954 ACSR conductor with double circuit steel structures. | MI | 2024-12-31 | BRP |  | 2024-12-31 | 138 | 0 | 41000000
A in MTEP20 | West | ATC | 16486 | Arcadian SS - Power Transformer and Control House Replacement and Asset Renewal | -Vacate and demolish existing control house buildings and procure new level-8 control house and contents (relay, RTU, etc.) -Remove both Westinghouse LTC transformers (T2 & T3) and replace with one 345/138kV 500MVA transformer -T1 wil be retained and relocated onto proper oil containment -Remove all 3 345kV live tan breakers and associated free standing CTs -Remove all 4 138kV Allis Chalmers BZO oil circuit breakers -Remove both 345kV circuit switchers -Spare 230kV transformer and towers will remain | WI | 2023-12-01 | Other | Age and Condition | 2023-12-31 | 345 | 138 | 40000000
A in MTEP20 | South | Entergy-LA | 18233 | Start 115 kV: Construct New Substation | Build new 115 kV substation named Start along with 2 miles of in-and-out 115 kV line from Alto to new substation site. | LA | 2025-06-01 | Other | Load Growth | 2025-06-01 | 115 | 0 | 39505305
A in MTEP20 | South | Entergy-LA | 18227 | Norris Road 138 kV: New Distribution Station | New distribution station to be cut into the CLECO Youngsville to Segura 138 kV line. | LA | 2026-06-01 | Other | Load Growth | 2026-06-01 | 138 | 0 | 39200000
A in MTEP20 | Central | AmerenMO | 18267 | New Wright City 345 kV substation | Joint project between Ameren Missouri and AECI. Tap the Ameren Missouri Labadie-Montgomery 345kV line via a new 3-breaker, 345kV ring bus near the intersection of the line and the AECI (Central Electric Power Coop) 161kV line west of Charrette. Rebuild the existing 161kV line between the tap point and the AECI Wright City Substation as double-circuit 345/161kV. Install new 345/161kV step down transformer at Wright City. | MO | 2023-12-01 | BRP |  | 2023-12-01 | 345 | 161 | 39100000
A in MTEP20 | West | ATC | 14909 | Small Capital Project and Asset Renewal Program 2021 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2021. | WI,MI |  | Other | Age and Condition | 2024-06-30 | 345 | 69 | 38913412
A in MTEP20 | Central | AmerenMO, WVPA | 17845 | New Wittenberg-Trail of Tears 138 kV line | Wabash Valley- Install new Wittenberg ring bus switching station on the Grand Tower-Perryville line. Reconfigure Trail of Tears substation to BAAH. Install new 161 kV line from Trail of Tears to Charmin Bulk Substation. Install 2 breakers at Charmin Bulk Substation. Ameren - Install 12 miles of new 138 kV line from Wittenberg Substation to Trail of Tears Substation. Install new 161-138 kV transformer at Trail of Tears Substation. | MO | 2023-12-01 | Other | Reliability | 2023-12-01 | 161 | 138 | 38500000
A in MTEP20 | South | Entergy-AR | 19767 | Heth 500kV: New Substation (J1060) | The Heth 500kV substation is to cut in the J1060 450 MW solar facility. This includes a 500kV cut in to the exiting West Memphis - Keo 500kV line. A new 500kV interconnection substation will be installed. Remote end upgrades at KEO and West Memphis include removing line traps, line tuners, existing relays, and replacing them with new relay panels. | AR | 2023-05-01 | GIP |  | 2023-05-01 | 500 | 0 | 38044000
A in MTEP20 | West | ITCM | 17740 | ITCM Asset Blanket for 2023 | Replace equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance have increased potential for misoperations and higher maintenance costs associated with their ongoing use. | IA,MN,IL | 2023-12-31 | Other | Age and Condition | 2023-12-31 | 345 | 69 | 37080000
A in MTEP20 | Central | AmerenIL | 17904 | New Highland-Aviston 138 kV line | Install new Highland area ring bus. Re-configure Aviston Substation to a ring bus. Install new 16.5 mile 138 kV line between Highland and Aviston. | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 138 | 0 | 35700000
A in MTEP20 | East | METC | 17844 | Summerton - Bullock cut in to Salt River 138 kV | Extend the Summerton - Bullock 138 kV circuit by extending ~15 miles of double circuit 138 kV construction into Salt River 138 kV station. | MI | 2022-10-28 | GIP |  | 2022-10-28 | 138 | 0 | 35493000
A in MTEP20 | West | XEL | 18345 | Scott County - Helena Line Upgrade | Upgrade Helena - Scott County 345kV line to accommodate additional flow from J587 Blazing Star 2 generation interconnection | MN | 2022-09-15 | GIP |  | 2022-09-15 | 345 | 0 | 34000000
A in MTEP20 | South | Entergy-TX | 19665 | Deer to Indian 138 kV line | Build ~16-19 miles of new 138 kV transmission line from Deer substation to Indian substation. The project will consist of a 795 ACSR Drake single circuit transmission line from Deer substation to Indian Substation, or a 795 ACSR Drake single circuit transmission line from Deer Substation to a new 3 breaker ring bus switching station (cut into existing Indian to Gulf Livingston transmission line) approximately 1 mile to the west of Indian substation. This is contingent on the ability to acquire ROW for the transmission project. | TX |  | BRP |  | 2025-06-01 | 138 | 0 | 33340000
A in MTEP20 | Central | AmerenMO | 17804 | Rebuild Lutesville-St. Francois 345 kV line | Rebuild 63 miles of 345kV wood H-frame circuit. | MO | 2023-12-01 | Other | Age and Condition | 2023-12-01 | 345 | 0 | 32800000
A in MTEP20 | Central | AmerenIL | 18275 | New Holland NW-Neoga South 345 kV line (4509) | Construct a 345 kV double circuit on the existing Holland Northwest-Neoga South-4509 line R.O.W. replacing structures. Target rating: 3000 A summer emergency. | IL | 2023-12-01 | BRP |  | 2023-12-01 | 345 | 0 | 32000000
A in MTEP20 | West | MEC | 18176 | Circuit Breaker Additions and Replacements 2020-2022 | Blanket project to add and replace new 345 kV circuit breakers to expand to ring bus which will reduce misoperations, increase reliability and operating flexibility. | IA | 2022-12-01 | Other | Reliability | 2022-12-01 | 345 | 0 | 31000000
A in MTEP20 | Central | AmerenIL, AmerenMO | 17905 | New Hull 161/138 kV transformer | Install new 161 kV Finn ring bus (Hannibal area). Convert the Spalding Substation to a ring bus configuration adding a positon for a line to the Hannibal area Substation. Double circuit the PENO-SPLD-2 line from Spalding to the Marion tap and rebuild the Marion Tap 161 kV section of the PENO-SPLD-2 line to the Mississippi River, through the new Hannibal area Substation and the existing Marion Substation. Install new 161 kV bus-tie breaker at Marion Substation. Install new 161-138 kV transformer at Hull substation. Operate the HULL-MRN-1690 line at 161kV. | MO | 2022-06-01 | Other | Reliability | 2022-06-01 | 161 | 138 | 30300000
A in MTEP20 | Central | AmerenIL | 17974 | New Crab Orchard 345/138 kV transformer | Tap the Shawnee-West Frankfort east-4564 line and install 345kV ring bus to make a connection for the installation of a new 345-138 kV transformer. | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 138 | 0 | 28000000
A in MTEP20 | Central | AmerenMO | 16555 | Relocate Page 138 kV substation to new Bugle 138 kV Substation | Relocate the existing 138 kV Page substation to the new Bugle site. 138 kV to be built as breaker and a half arrangement. | MO | 2023-06-01 | Other | Reliability | 2024-06-01 | 345 | 138 | 27500000
A in MTEP20 | Central | AmerenMO | 9721 | Reconductor Bland-Tegeler 138 kV line | Reconductor line to 1200 A summer emergency capability | MO | 2022-12-01 | BRP |  | 2022-12-01 | 138 | 138 | 27200000
A in MTEP20 | Central | AmerenMO | 16986 | Rebuild Page-Sioux 138 kV line (4) | Rebuild existing Missouri River crossing (Str. 112-117) | MO | 2023-12-01 | Other | Age and Condition | 2023-12-02 | 138 | 0 | 26657745
A in MTEP20 | West | ATC | 18985 | J850/J878 MPFCA East Paris New SS | The purpose of the project is to construct a 345-138 kV substation to the east of the 138kV Paris substation. | WI | 2022-12-23 | GIP |  | 2022-12-23 | 345 | 138 | 25525101
A in MTEP20 | Central | AmerenIL | 18269 | New LaSalle–North Utica 138 kV line | New 138 kV ring bus breaking the North LaSalle–Fox River 138 kV line. Construct a new line between LaSalle 138 kV substation and new ring bus. Add two line breakers at the LaSalle 138 kV substation. | IL | 2025-06-01 | BRP |  | 2025-06-01 | 138 | 0 | 25400000
A in MTEP20 | Central | AmerenIL | 16944 | New Louisville South 345/138 kV Transformer | Install new 345 kV ring bus at the Louisville South Substation location tapping the Newton-Xenia-1 line. Install 560 MVA 345-138 kV transformer and connect to the Louisville South 138 kV bus. | IL | 2022-12-01 | Other | Reliability | 2022-12-01 | 345 | 138 | 25200000
A in MTEP20 | West | ATC | 18568 | Howards Grove SS - Erdman SS 138 kV, new line | Construct approximately 7 miles of new 138 kV line from Howards Grove to Erdman. | WI | 2023-11-30 | BRP |  | 2023-11-30 | 138 | 0 | 25000000
A in MTEP20 | Central | AmerenIL | 16988 | New Fogarty-Limit 138 kV Line | Install new 138 kV line from Fogarty Substation to limit. Install new ring bus at Limit to make the connection | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 138 | 0 | 24600000
A in MTEP20 | West | ATC | 18017 | Petenwell-Badger-West-Saratoga, (X-43) 138kV, Line Rebuild | 138 kV Line X-43 is 22.7 miles long with pole vintages from the 1940s, 1950s and 1960s The limitations of the system result in voltage collapse for forced outages during planned maintenance The Council Creek SPS no longer fully mitigates market congestion issues due to increased system flows X-43 will be rebuilt with an a maximum rating of 1030 Amps for all seasons. This will resolve system reliability, market congestion and pending asset renewal issues | WI | 2022-12-31 | BRP |  | 2022-12-31 | 138 | 0 | 24500000
A in MTEP20 | West | MDU | 17466 | Heskett Substation Retirement | The Heskett substation will be retired due to age and condition concerns. The existing Mandan substation will be expanded to accommodate the 230 kV and 115 kV facilities currently connected to Heskett. A new Mandan 38th St substation will be constructed to accommodate the 69 and 41.6 kV facilities. | ND | 2022-09-30 | Other | Age and Condition | 2020-11-30 | 230 | 41.6 | 24000000
A in MTEP20 | Central | AmerenIL | 18311 | New Maple Flats Solar (J813) interconnection | Re-configure Louisville South 138 kV substation to BAAH bus. Add terminal facilities for J813 connection. | IL | 2021-10-29 | GIP |  | 2021-10-29 | 138 | 0 | 24000000
A in MTEP20 | East | METC | 18147 | Rebuild Bard Road – Warren 138 kV | Rebuild 16.4 miles of the Bard Road – Clare Junction section of the Bard Road – Warren 138kV circuit and to rebuild 3.3 miles of the Clare Junction – Warren section of the Bard Road – Warren 138kV circuit with 954 ACSR utilizing future 230 kV double circuit construction initially operated as 138 kV single circuit with adjacent side left vacant for future use. | MI | 2022-05-01 | GIP |  | 2022-05-01 | 138 | 0 | 23918246
A in MTEP20 | Central | AmerenIL | 17976 | New Redhawk 345/138 kV transformer | Tap the Coffeen-Roxford-4551 line and install 345kV ring bus to make the connection for a new 345-138 kV transformer at Redhawk Substation. | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 345 | 138 | 22400000
A in MTEP20 | West | ITCM | 17729 | Savanna-Argo Fay-York Area Rebuilds | ITC will build a new 69kV line approximately 6 miles from the York Substation to the Argo Fay Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. ITC will build a new 69kV line approximately 6.5 miles from the Clay Substation to the Chadwick Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. ITC will rebuild approximately 6.5 miles of the Argo Fay Substation to the Chadwick Substation 34.5kV line to 69kV Standards. The overhead conductor will have an ampacity of 600A or higher. ITC will retire approximately 6 miles of 34.5kV line between Argo Fay and the Clay substation. ITC will retire approximately 6 miles of 34.5kV line between Argo Fay and the Savanna substation. | IL | 2025-12-30 | Other | Age and Condition | 2025-12-30 | 69 | 34 | 22350000
A in MTEP20 | Central | AmerenIL | 13709 | New Putnam breaker-and-a-half 138 kV substation | Build new 138 kV BAAH substation on new site near Hennepin. | IL | 2022-12-01 | Other | Age and Condition | 2022-12-01 | 138 | 0 | 22300000
A in MTEP20 | East | METC | 18238 | Morrow (Jaguar) 138 kV Station Rebuild | Rebuild Morrow 138 kV station at a new site approximately 1.55 miles to the north utilizing new equipment in a five-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called Jaguar. • Acquire new property as necessary and install (15) 138 kV, 3000 A breakers with at least 40 kA interrupting capability in a five-row, breaker-and-a-half scheme configuration for this new station. • Redirect all circuits currently at the Morrow 138 kV station into the new Jaguar 138 kV station and connect CE’s new replacement step-down transformers, and Kalamazoo River Generation Station via radial feeds into the new Jaguar station. • Reconductor Morrow - Jaguar 795 ACSR section of the Morrow – Bradley (V22) 138kV line using 1431 ACSR conductor and utilizing this circuit to create Cork Street – Jaguar 138kV line. | MI | 2024-12-31 | Other | Age and Condition | 2024-12-31 | 138 | 0 | 22300000
A in MTEP20 | West | ATC | 17525 | J870/J871 MPFCA Highland Generator Network Upgrades | A 300 MW solar farm in Grant and Iowa County, Wisconsin. Customer has requested a Point of Interconnection (POI) at Highland Substation that taps the existing X-17 line between Eden and Wyoming Valley Substations. | WI | 2020-08-01 | GIP |  | 2020-08-01 | 138 | 69 | 22180519
A in MTEP20 | South | Entergy-TX | 13943 | Southern Point 138 kV: New Substation | Construct a new 138 kV substation that replaces the existing Speedway 138 kV substation. | TX | 2024-06-01 | Other | Load Growth | 2024-06-01 | 138 | 0 | 22000000
A in MTEP20 | East | METC | 18190 | Dort 138 kV Station Rebuild | Rebuild Dort 138 kV station with a new control house at a new site approximately 0.5 miles to the south utilizing new equipment in a four-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called Calvary. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance to be performed again in a safe and efficient manner. | MI | 2024-06-01 | Other | Age and Condition | 2024-06-01 | 138 | 0 | 21325000
A in MTEP20 | West | ATC | 19729 | J732 Superior SS Network Upgrades and Interconnection Facilities | Interconnection of about 560 MW the facility composed of one (1) steam turbine unit and one (1) natural gas unit in a 1x1 combined cycle facility interconnecting at the new Superior Substation. | WI | 2023-11-30 | GIP |  | 2023-11-30 | 345 | 230 | 21245605
A in MTEP20 | West | ATC | 14907 | Load Interconnection Program 2021 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2021. | WI,MI |  | Other | Load Growth | 2024-06-30 | 138 | 69 | 20124594
A in MTEP20 | Central | AmerenIL | 12176 | New West Frankfort East & Norris City 345 kV reactors | Reconfigure West Frankfort East to BAAH and install 345 kV, 50 Mvar shunt reactor. | IL | 2024-12-01 | BRP |  | 2023-12-01 | 345 | 0 | 19700000
A in MTEP20 | Central | DEI | 18284 | J754 Gen. Interconnect | J754 Wind Farm - Gen. Interconnect: 34501 ckt. - 300MW Wind farm; 3-breaker ring bus switching station | IN |  | GIP |  | 2021-03-15 | 345 | 0 | 19655000
A in MTEP20 | Central | AmerenIL | 18263 | New Fargo–Hines 138 kV line | New line between the Fargo 138 kV substation and the Hines 138 kV substation. | IL | 2025-06-01 | BRP |  | 2025-06-01 | 138 | 0 | 18720000
A in MTEP20 | East | ITCT | 17998 | Build Stone Pool - Temple 120 kV | The proposed solution is to build a new circuit (approximately 1.25 miles) from the Stone Pool 120 kV Station to the Temple 120 kV station utilizing 3200 Kcmil underground cable. | MI | 2024-06-01 | Other | Other Local Needs | 2024-06-01 | 120 | 0 | 18670000
A in MTEP20 | West | GRE | 14366 | Svea Tap - Litchfield Tap Line Rebuild Project | Rebuild GRE’s existing 69 kV transmission line from Willmar to Litchfield Muni Tap with a larger conductor. | MN | 2022-06-01 | Other | Age and Condition | 2024-06-14 | 69 | 0 | 18350000
A in MTEP20 | East | NIPS | 18276 | Rebuild Maple-LNG 138kV Line | Rebuild Maple to LNG 138kV Line | IN | 2023-05-01 | BRP |  | 2023-05-01 | 138 | 0 | 18000000
A in MTEP20 | West | ATC | 14915 | Physical Security Program 2021 | Physical Security projects typically have shorter project life cycles. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2021. | WI,MI |  | Other | Other Local Needs | 2024-06-30 | 345 | 69 | 17908909
A in MTEP20 | Central | AmerenMO | 16491 | Rebuild Sioux-Meppen-4, Page-Sioux-4, Sioux-Huster-1 138 kV lines | Sioux-Huster-1/Sioux-Meppen North-4: Rebuild ~9 miles of triple circuit 138 kV lattice tower line to double-circuit steel poles. | MO,IL | 2021-12-01 | Other | Age and Condition | 2021-12-01 | 138 | 0 | 17100000
A in MTEP20 | West | MEC | 18117 | Washburn-Hazleton 161 kV Reconductor | Reconductor Washburn-Hazleton 161 kV line. Upgrade Washburn substation terminal equipment. | IA | 2020-10-31 | GIP |  | 2020-10-31 | 161 | 0 | 16700000
A in MTEP20 | West | OTP | 18947 | OTP Ellendale-Oakes-Forman-Hankinson 230 kV Upgrades J302/J503 | This project consists of upgrades to Otter Tail Power Company’s substations and transmission lines to accommodate the interconnection of a wind generators, J302/J503. Four Facility upgrades are needed: • Ellendale to Oakes 230 kV Line Reconductor • Oakes to Forman 230 kV Reconductor • Forman to Hankinson 230 kV Structure Replacements • Forman 230 kV Switch Replacement | ND | 2021-03-01 | GIP |  | 2021-03-01 | 230 | 0 | 16500000
A in MTEP20 | South | Entergy-AR | 18097 | Pleasant Hill 500kV: Add 2 Reactors | Add 2 100 MVAR reactors at Pleasant Hill 500 kV bus | AR | 2020-12-01 | BRP |  | 2023-06-01 | 500 | 0 | 16333119
A in MTEP20 | East | NIPS | 18685 | J883 GIA Network Upgrades | Generator Interconnection. The existing East Winimac – Monticello line will be cut into at the site of the new substation. | IN | 2023-05-01 | GIP |  | 2023-04-15 | 138 | 0 | 15990564
A in MTEP20 | East | WPSC | 18011 | Rebuild Atlanta to Airport 138kV | Rebuild and upgrade 31.5 miles of 138 kV with double circuit steel poles, 795ACSS conductor, and OPGW. | MI | 2023-12-31 | Other | Age and Condition | 2023-12-31 | 138 | 0 | 15500000
A in MTEP20 | South | Entergy-AR | 18103 | Screeton 115kV: Construct new substation | Build a new 115kV substation with a single 40 MVA 115/13.8kV LTC transformer between Hazen and Carlisle 115kV substations near the town of Screeton. | AR | 2022-06-01 | Other | Load Growth | 2024-06-01 | 115 | 13.8 | 15132530
A in MTEP20 | West | XEL | 18505 | Jim Falls - Holcombe Rebuild | Rebuild Jim Falls - Holcombe 115kV line to remove overload under contingency | WI | 2023-03-01 | Other | Reliability | 2023-03-01 | 115 | 0 | 15000000
A in MTEP20 | Central | DEI | 18331 | Whitesville to Advance 69kV Rebuild | 69154 rebuild from Whitesville to Advance with 477ACSR and light-duty steel poles | IN |  | Other | Reliability | 2021-12-31 | 69 | 0 | 14410000
A in MTEP20 | Central | AmerenIL | 17627 | Rebuild Fogarty-Kickapoo 138 kV line (1672) | Rebuild 138 kV line to 2000A | IL | 2022-12-01 | Other | Age and Condition | 2022-12-01 | 138 | 0 | 14400000
A in MTEP20 | South | Entergy-TX | 18255 | Fort Worth to Kolbs 69 kV Rebuild | Rebuild the 69 kV line between Fort Worth and Kolbs stations. | TX |  | Other | Age and Condition | 2023-06-01 | 69 | 0 | 14100000
A in MTEP20 | East | NIPS | 18278 | Rebuild LNG-Stillwell 138kV Line | Rebuild LNG to Stillwell 138kV line | IN | 2023-05-01 | BRP |  | 2023-05-01 | 138 | 0 | 14000000
A in MTEP20 | West | ATC | 4727 | Winona - Atlantic (Winona69) 69kV, reconductor | System Reliability ($11.9M) i. The Winona - Atlantic (Winona69) 69kV circuit is 22 miles long, uses wood H Frame structures and 1/0 Copper conductor ii. This circuit can be a limiter for the import of energy to Houghton and Keweenaw Counties, MI iii. This project will re-conductor this circuit with 477 kcmil ACSR iv. Add ATC owned and operated OPGW to this circuit providing a redundant path for communication in the region Asset Renewal Component ($2M) i. The condition and performance of the existing line infrastructure requires replacement of the existing insulators and select structures ii. There are resource and cost efficiencies in doing the reliability project work in combination with the needed asset renewal work Non-Transmission Alternative (NTA) i. Mitigation of the reliability project, via and NTA, does not remove the need for necessary condition and performance work nor will it provide the reliability benefit of the communication circuit on this line | MI | 2024-12-31 | Other | Reliability | 2024-12-31 | 69 | 0 | 13900000
A in MTEP20 | Central | AmerenMO | 17624 | Rebuild Pike 161 kV Substation | Rebuild the Pike 161 kV substation to a Ring bus configuration. | MO | 2023-12-01 | Other | Reliability | 2023-12-01 | 161 | 0 | 13400000
A in MTEP20 | Central | DEI | 18290 | Purdue University CHP Generation | Purdue University CHP Generation - 15.5MW gas turbines with HRSG unit - non-MISO queue; non-BES | IN |  | Other | Reliability | 2021-07-16 | 138 | 12 | 13310000
A in MTEP20 | West | GRE | 17944 | Heron Lake - Round Lake (FE-RH) 69 kV Line Rebuild | Rebuild entire FE-RH line (from Heron Lake substation to Round Lake substation) | MN | 2021-09-30 | Other | Age and Condition | 2021-09-30 | 69 | 0 | 13232725
A in MTEP20 | West | GRE, MP | 17664 | Portage Lake 115/69 kV Project | GRE will interconnect to Minnesota Power’s (MP) 13 Line (Riverton – Cromwell 115 kV) with a 4 position, 115 kV ring bus, to be called Portage Lake, at or near the existing Mille Lacs Electric Cooperative (MLEC) Kimberly substation. The new 115 kV Portage Lake ring bus will have four positions; 115 kV line to Riverton (13 Line), 115 kV line to Cromwell (26 Line), 115/69 kV transformer with a 9.5 mile line to Palisade. AKA Kimberly. | MN | 2023-11-01 | Other | Reliability | 2023-09-30 | 115 | 69 | 13201117
A in MTEP20 | Central | AmerenIL | 16704 | Rebuild Salem West-Mt Vernon West 138 kV line (1332) | Rebuild line to 2000A. Upgrade terminal equipment at Salem West to 2000A including 1272 ACSR bus conductor and switch 1330. | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 138 | 0 | 13200000
A in MTEP20 | South | Entergy-AR | 18726 | Locust Creek 161kV: Construct Switching Station (J919) | Construct a new 3 breaker switching station 2.62 miles north east of the Newport Air Base substation on the L962 161kV Newport Air Base - Cash 161kV transmission line section. This will be used as the point of interconnection for the 180 MW solar photovoltaic generator project J919. | AR | 2023-02-01 | GIP |  | 2023-02-01 | 161 | 0 | 13077000
A in MTEP20 | Central | AmerenIL | 17285 | New Quiver 138 kV Substation | Install new ring bus installation at the intersection of Mason City West – Fogarty -1346 and San Jose Rail – Interstate – 1318 138 kV line. | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 138 | 0 | 13000000
A in MTEP20 | West | MEC | 18129 | 25th Street NW 161 KV Substation | Construct a new 161 kV substation and associated 161 kV line work to source customer-owned transformation and new load. | IA |  | Other | Load Growth | 2022-07-01 | 161 | 0 | 12935000
A in MTEP20 | West | ATC | 19146 | J850 North Creek SS, Generator Interconnection Facilities and Network Upgrades | Interconnection of a 250 MW solar farm located in Walworth County, Wisconsin. | WI | 2022-09-30 | GIP |  | 2022-09-30 | 138 | 0 | 12573372
A in MTEP20 | Central | AmerenIL | 15265 | Reconfigure Carbondale NE 138 kV substation to ring bus | Install initial 3-position ring bus at Carbondale NE Substation | IL | 2023-06-01 | Other | Reliability | 2023-06-01 | 138 | 0 | 12500000
A in MTEP20 | West | ATC | 18052 | Barneveld SS, DIC, new substation | ATC will: -Construct an underbuilt 69 kV (138kV capable) circuit from Hooterville to Wally Road onto the ordered route of the Cardinal - Hickory Creek 345kV project -Connect the new WPL Barneveld substation with a loop through straight bus configuration with 2 line breakers -Connect the new MHU Military Ridge substation with a radial tap with line switches -Reitre the existing Y-128 section from Mt. Horeb to Wally Road | WI | 2023-12-31 | Other | Load Growth | 2023-12-31 | 69 | 0 | 12300000
A in MTEP20 | West | GRE | 17964 | Blue Earth - East Chain - Wilbert Tap (FE-WB) 69 kV Line Rebuild | Rebuild entire FE-WB line (Blue Earth to East Chain to Wilbert Tap) | MN | 2022-12-31 | Other | Reliability | 2022-12-31 | 69 | 0 | 12273125
A in MTEP20 | Central | AmerenIL | 17565 | New Oreana-Decatur N 27th Street 138 kV line | Install new 138 kV line between Oreana and Decatur N 27th Street. | IL | 2025-06-01 | BRP |  | 2025-06-01 | 138 | 69 | 12200000
A in MTEP20 | Central | AmerenIL | 17982 | New Maroa 345 kV substation | Install new Maroa 345 kV ring bus substation. | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 345 | 0 | 12000000
A in MTEP20 | West | MEC | 18137 | South Waukee 161-13.2 kV Substation | Construct a new 161-13.2 kV distribution substation and associated 161 kV line work to accommodate area growth. | IA | 2022-06-01 | Other | Load Growth | 2022-06-01 | 161 | 13.2 | 11988000
A in MTEP20 | Central | PPI | 18162 | New Kington-Ellisville 69 kV Line | New 18-mile 69 kV line tying McDonough Power Cooperative to Spoon River Electric Cooperative | IL | 2023-12-31 | Other | Reliability | 2023-12-31 | 69 | 69 | 11925000
A in MTEP20 | Central | AmerenIL | 15504 | New Dempsey (Blue Mound) 138 kV ring bus addition | Install new ring bus at the tap to Blue Mound on the Pana-Route 51 Decatur-1462 line. | IL | 2022-06-01 | Other | Reliability | 2022-06-01 | 138 | 0 | 11700000
A in MTEP20 | East | METC | 15809 | Four Mile (Northridge) - North Belding 138 kV Rebuild | The proposed solution is to rebuild 8.38 miles Alpine Jct. – Rogue River Jct. and Rogue River Jct. – Cannon Jct. sections of the Four Mile – North Belding 138kV line using 954 ACSR conductor. | MI | 2024-12-31 | BRP |  | 2024-12-31 | 138 | 0 | 11700000
A in MTEP20 | Central | AmerenIL | 13793 | New El Paso 138 kV substation ring bus | Install initial 4-postion ring bus at El Paso Substation for in/out supply. | IL | 2022-12-01 | Other | Reliability | 2022-12-01 | 138 | 0 | 11400000
A in MTEP20 | South | Entergy-MS | 19286 | Cotton Blossom 230 kV: Construct switching station (J830) | This project will construct a new 230 kV switching station cut into the Canton South - Yandell Road line. | MS | 2022-03-01 | GIP |  | 2022-03-01 | 230 | 0 | 11367000
A in MTEP20 | South | Entergy-LA | 18787 | J697 Interconnection: Expand Oak Ridge 115 kV Substation | This project shall consist of transforming the existing 115 kV yard from single bus to dual bus, expanding the existing substation site, installing a new control house, and installing shielding and light fixtures to accommodate the connection of the Interconnection Customer’s transmission line. | LA | 2022-12-31 | GIP |  | 2022-10-15 | 115 | 0 | 11314000
A in MTEP20 | Central | AmerenMO | 17605 | Reconductor Page-Berkeley 138 kV lines 1/2 | Reconductor the Page-Berkeley-1&2 circuits with ACCR conductor | MO | 2022-12-01 | Other | Age and Condition | 2022-12-01 | 138 | 0 | 11300000
A in MTEP20 | South | Entergy-AR | 18946 | Kuhn Road 161kV: Expand Station and Line Rebuild (J934) | The Kuhn Road 161kV bus will be expanded to provide a point of interconnection for J934 solar generating facility. Upgrades will include two 161kV dead end structures, two 161kV 3000 A vertical break disconnects switches, one 161kV 3000 A gas circuit breaker, three 161kV rated surge arresters, three metering accuracy coupling capacitor voltage transformers, revenue accuracy meter, relaying panel and revenue metering panel. Three surge arresters on the incoming line L940 will be installed. Relay settings updates are required for the 161kV bus differential relay, and the Kuhn Road - Parkin and Kuhn Road - Ebony 161kV transmission lines. The existing Ebony - Kuhn Road 161kV transmission line will be rebuilt to support 666.6 kcmil ACSR Flamingo conductor at a minimum rating of 229 MVA. | AR | 2022-06-01 | GIP |  | 2022-06-01 | 161 | 0 | 11160000
A in MTEP20 | East | ITCT | 15890 | Pontiac - Walton 120 kV Rebuild | Rebuild approximately 4.8 miles of 477 ACSR X2 and 1431 ACSR conductors from Pontiac to Giddings 2 Tap to Walton using 2156 ACSR. Also, upgrade station equipment at Pontiac 120kV and Walton 120 kV. | MI | 2025-12-31 | BRP |  | 2025-12-31 | 120 | 0 | 11027000
A in MTEP20 | West | ITCM | 16864 | J475 Generator Interconnection | The Poweshiek to Irvine 161 kV line is to be rebuilt on existing ROW with a conductor having a minimum summer rating of 1,595A. Upgrades at the Poweshiek 161 kV substation will also be required. | IA | 2020-10-01 | GIP |  | 2020-10-01 | 161 | 161 | 11000000
A in MTEP20 | Central | AmerenIL | 17975 | New Rising 345/138 kV transformer No. 2 | Install 2nd 345-138 kV transformer at Rising Substation | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 345 | 138 | 11000000
A in MTEP20 | West | ATC | 14911 | Communication Reliability Program 2021 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2021. | WI,MI |  | Other | Other Local Needs | 2024-06-30 | 345 | 69 | 10927208
A in MTEP20 | South | Entergy-AR | 18101 | Hot Springs Plemmons 115kV: Construct new substation | Build a new 115kV substation with a single 40 MVA 115/13.8 kV LTC transformer. | AR | 2024-06-01 | Other | Load Growth | 2024-06-01 | 115 | 13.8 | 10904173
A in MTEP20 | West | ITCM | 17728 | Savanna-Metform-York 34kV to 69kV Rebuild | ITC will rebuild approximately 6 miles of the Savanna – Metform – York 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 1200A or higher. ITC will need to investigate the Danisco to York 34.5kV to determine if the insulators are capable of 69kV operation. If not, ITC will reinsulate the Danisco to York 34.5kV line with 69kV insulators. The existing conductor is 954 ACSR and does not need to be replaced due to ampacity needs. The static is 3/8 steel. | IL | 2020-12-30 | Other | Age and Condition | 2020-12-30 | 69 | 69 | 10749600
A in MTEP20 | West | ITCM | 16844 | J495 Generator Interconnection | ITCM and EDF have entered into an engineering and procurement agreement for the acquisition of materials and design of a 3-terminal, 3 breaker, 345 kV switching station to be constructed roughly 7 miles east of the Ledyard 345 kV station and connected to the Ledyard to Colby 345 kV line. The E&P agreement will cover the design and material acquisition for the 345 kV station, and construction work will occur under the GIA. | IA | 2019-10-18 | GIP |  | 2019-10-18 | 345 | 345 | 10662026
A in MTEP20 | South | Entergy-LA | 15645 | Nelson 138 kV: Install transmission breakers | Nelson – Lake Charles Bulk 138 kV L-654 should be re-terminated at the open bay east of Nelson to Deridder bay and L-698 should be moved to the bay L-654 currently occupies. Breaker 7920 and one new IPO breaker (3000A continuous rating, 80 kA interrupting rating) would be needed to re-terminate L-654 in double-bus-double-breaker scheme. | LA | 2021-06-01 | BRP |  | 2022-06-01 | 230 | 0 | 10600000
A in MTEP20 | Central | AmerenIL | 9723 | New Fishhook 138 kV substation | Construct 138 kV breaker station in East Quincy-Meredosia-2 138 kV line. | IL | 2019-06-01 | Other | Reliability | 2019-06-01 | 138 | 138 | 10500000
A in MTEP20 | West | ITCM | 17731 | Savanna City Loop 34kV to 69kV Rebuild | ITC will rebuild approximately 1.66 miles of the Savanna – Eaton 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. ITC will rebuild approximately 0.85 miles of the Bowen – Eaton 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. ITC will rebuild approximately 3.80 miles of the Bowen – Savanna 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. | IL | 2025-12-30 | Other | Age and Condition | 2025-12-30 | 69 | 69 | 10478146
A in MTEP20 | East | METC | 18728 | Cobb (Chopin) - Sternberg 138kV Line Rebuild | The proposed solution is to rebuild approximately 8 miles of the Cobb - Sternberg 138kV circuit using 954 ACSR conductor with single circuit steel structures. | MI | 2024-12-31 | BRP |  | 2024-12-31 | 138 | 0 | 10450000
A in MTEP20 | West | GRE | 17970 | Howard Lake - Highland - Maple Lake Line Rebuild | Rebuild the 69 kV transmission line from Howard Lake to Highland to Maple Lake. | MN | 2023-12-29 | Other | Age and Condition | 2023-12-29 | 69 | 0 | 10402000
A in MTEP20 | West | XEL | 18029 | West St Cloud - Millwood 69kV Rebuild | Rebuild 24 miles of 69kV line from West St. Cloud - Millwood to remediate aging condition issues | MN | 2021-06-01 | Other | Reliability | 2021-06-01 | 69 | 0 | 10400000
A in MTEP20 | South | Entergy-TX | 18251 | Alligator Bayou to Fort Worth 69 kV Rebuild | Rebuild and reconductor the Alligator Bayou to Fort Worth 69 kV line. | TX |  | Other | Age and Condition | 2022-03-01 | 69 | 0 | 10400000
A in MTEP20 | Central | AmerenIL | 19045 | New Rivian Load Interconnection | Provide 2 separate 138kV lines from West Washington St 138kV BAAH Expansion to serve all load at Diamond Star. | IL | 2021-02-01 | Other | Load Growth | 2021-02-01 | 138 | 0 | 10100000
A in MTEP20 | West | XEL | 15877 | East Metro Area Upgrades | To remediate overloads and voltage concerns in the East metro, line connections will be reconfigured at Red Rock, 115kV line from Baytown - Long Lake will be upgraded. | MN | 2022-06-15 | BRP |  | 2022-06-15 | 115 | 0 | 10000000
A in MTEP20 | West | XEL | 18007 | Prentice - Phillips 115kV Rebuild | Complete wreck out and rebuild of 14.8 miles of 115kV line from Prentice to Phillips Tap to remediate aging condition issues. | WI | 2023-01-31 | Other | Reliability | 2023-01-31 | 115 | 0 | 10000000
A in MTEP20 | Central | AmerenIL | 17324 | New Mason 138 kV Ring bus (J1055) Glacier Sands interconnection | Interconnection for new 144 MW wind farm at Mason (IL) substation. Tap existing bus at Mason to provide connection. | IL | 2020-10-15 | GIP |  | 2020-10-15 | 138 | 0 | 10000000
A in MTEP20 | Central | AmerenIL | 17978 | Rebuild Belleville 17th Street 138 kV substation | Rebuild the Belleville 17th street 138 kV substation to a ring bus configuration. | IL | 2022-12-01 | Other | Reliability | 2022-12-01 | 138 | 0 | 10000000
A in MTEP20 | South | Entergy-TX | 18259 | Lacon 138 kV: Breaker and feeders | Install a 138 kV breaker at Lacon in the bay looking toward the LNG tap. Also included in this project are distribution feeder additions. | TX |  | Other | Reliability | 2023-06-01 | 138 | 0 | 10000000
A in MTEP20 | South | Entergy-MS | 17086 | Brandon Area Loop Project | Tap L540A (East Whitfield to South Brandon) with a 115kV GOAB and build a new 115kV transmission line from the South Brandon tap to East Brandon delivery point GOAB. | MS | 2022-12-01 | Other | Load Growth | 2022-12-01 | 115 | 0 | 9952989
A in MTEP20 | West | ITCM | 17727 | York Substation 69kV Expansion | ITC will be expanding the York Substation to include a 161/69kV 150MVA transformer. All new 69kV equipment will be capable of 2000A. A tie switch will be added to the 161kV. All new 161kV equipment will be capable of 2000A or greater. See page 2 for the electrical layout of the York Substation. ITC will be retiring the 34.5kV out of the York Substation. No additional 161kV equipment will be needed to accommodate this work. All new 69kV equipment will be capable of 1200A or greater. | IL | 2021-12-30 | Other | Age and Condition | 2021-12-31 | 161 | 69 | 9776400
A in MTEP20 | West | ITCM | 18061 | Mason City Industrial 161kV Substation Interconnection | ITCM will interconnect Alliant Energy’s Mason City Industrial 161/24.9kV distribution substation with in/out taps to the Emery-Lime Creek 161kV line and install four (4) 161kV breakers in a ring bus configuration at the 161kV distribution substation. IPL will install a single distribution transformer initially to serve a load of ~18MW. IPL will install a second distribution transformer in the future to accommodate load growth and load moved from 69kV distribution substations. | IA | 2022-05-30 | Other | Load Growth | 2022-05-30 | 161 | 24.9 | 9747847
A in MTEP20 | East | ITCT | 17364 | J793 Generator Interconnection | ITCT will install a new 345 kV station with 3-345 kV breakers and associated disconnects in a ring bus configuration. ITCT will loop the Belle River - Fitz #2 345kV circuit into the new J793 substation. ITCT will upgrade relay panels at the Fitz and Belle River Power Plant Stations to accommodate the new generator J793. | MI | 2021-05-14 | GIP |  | 2021-05-14 | 345 | 0 | 9734993
A in MTEP20 | East | ITCT | 15880 | Navarre - River Rouge 120 kV Rebuild | Rebuild the 2.9 miles of 954 ACSR conductor to 2156 ACSR on the Navarre – River Rouge 120 kV line and upgrade station equipment at both ends. | MI | 2025-12-31 | BRP |  | 2025-12-31 | 120 | 0 | 9728000
A in MTEP20 | Central | DEI | 18334 | Rebuild Connersville to Glenwood 69 kV | 6920 rebuild from Connersville to Glenwood with 477ACSR and light-duty steel poles | IN |  | Other | Reliability | 2021-12-31 | 69 | 0 | 9665000
A in MTEP20 | East | ITCT | 15959 | Hager - Sunset 120 kV Rebuild | The proposed solution is to rebuild 4.33 miles of the Sunset – Hager 120kV circuit using 2156 ACSR conductor with single circuit steel structures and upgrade station equipment at Hager and Sunset stations. | MI | 2025-12-31 | BRP |  | 2025-12-31 | 120 | 0 | 9657000
A in MTEP20 | West | ITCM | 17726 | Savanna 69kV Substation Expansion | ITC will be expanding the Savanna 69kV Substation to a Ring Bus capable of 6-positions. Most new 69kV equipment will be capable of 1200A or greater. ITC will install a 161/69kV 150MVA transformer at Savanna. The 161/69kV transformer position and the Metform position will be capable of 2000A or greater. There will be several phases for the 69kV. | IL | 2021-12-31 | Other | Age and Condition | 2021-12-31 | 69 | 69 | 9535800
A in MTEP20 | South | Entergy-MS | 19287 | Webb 115 kV: Substation Expansion (J908) | This project will expand the 115 kV Webb substation to facilitate the generation interconnection project J908. | MS | 2023-06-01 | GIP |  | 2023-06-01 | 115 | 0 | 9417000
A in MTEP20 | Central | AmerenIL | 17644 | Upgrade Decatur Route 51 138 kV substation | Install initial 138 kV 4-position (ultimate 6-position) ring bus at the Decatur Route 51 substation location | IL | 2022-06-01 | Other | Reliability | 2022-06-01 | 138 | 0 | 9400000
A in MTEP20 | Central | AmerenMO | 17830 | Upgrade Gasconade-Osage 161 kV line | Replace both shield wires and replace structures as needed. | MO | 2021-12-01 | Other | Age and Condition | 2021-12-01 | 138 | 0 | 9400000
A in MTEP20 | Central | AmerenIL | 17825 | Reconfigure Lawrenceville South 138 kV substation | Reconfigure the Lawrenceville South substation to a 6-position ultimate ring bus. | IL | 2023-12-01 | Other | Age and Condition | 2023-12-01 | 138 | 0 | 9200000
A in MTEP20 | East | ITCT | 15883 | Bismarck-Stephens #2 120 kV Rebuild | Rebuild approximately 3.61 miles of 795 ACSS and 954 ACSR conductors to 2156 ACSR on the Bismarck – Stephens #2 120 kV line. | MI | 2024-12-31 | BRP |  | 2024-12-31 | 120 | 0 | 9100000
A in MTEP20 | Central | PPI | 18163 | New Ursa-Big Neck 69 kV Line | New 12.4-mile 69 kV line in Adams Electric Cooperative | IL | 2023-12-31 | Other | Reliability | 2023-12-31 | 69 | 69 | 9024000
A in MTEP20 | West | ATC | 18848 | Blount - East Campus, 69kV, (6907), Replace Damaged Underground Cable | -Replace 1.9 miles of damaged High Pressure Fluid Filled (HPFF) cable with new HPFF using existing pipe. -Damage caused by Blount SS event in July of 2019. | WI | 2020-09-30 | Other | Age and Condition | 2020-09-30 | 69 | 0 | 9000000
A in MTEP20 | East | METC | 18424 | J758 Generator Interconnection (Network Upgrades) - Mud Lake | Build a new 138 kV 3 Breaker ring substation cut in from the Verona - Foundry 138 kV circuit. Changes will require upgraded relaying at Verona 138kV station. | MI | 2022-04-08 | GIP |  | 2022-04-08 | 138 | 0 | 8995000
A in MTEP20 | Central | PPI | 18155 | New Burton-Ursa 69 kV Line | New 16.3-mile 69 kV line in Adams Electric Cooperative | IL | 2021-12-31 | Other | Reliability | 2021-12-31 | 69 | 69 | 8945250
A in MTEP20 | Central | DEI | 18287 | Terre Haute S. Vigo to HE Middletown Jct 69kV Rebuild | Rbld 6901 circuit from TH Haute S. Vigo sub, pole 802-1158, to HE Middletown Jct, pole 802-1315, using light-duty steel poles, 477ACSR conductor & OPGW static. Rpl switch #64LB with two 2000A switches | IN |  | Other | Reliability | 2022-06-01 | 69 | 0 | 8768000
A in MTEP20 | Central | AmerenMO | 18319 | Upgrade Fredericktown-Heritage 161 kV line (7011) | Replace poles for OPGW installation. Structure replacements will increase the rating to 120 degrees C. | MO | 2021-06-01 | Other | Age and Condition | 2021-06-01 | 161 | 0 | 8700000
A in MTEP20 | West | ITCM | 17725 | Savanna 161kV Substation Expansion | TC will be expanding the Savanna Substation to a Ring Bus capable of 6-positions. The new 161kV equipment will be capable of 2000A. There will be several phases for the 161kV. | IL | 2021-12-31 | Other | Age and Condition | 2021-12-31 | 161 | 161 | 8695200
A in MTEP20 | Central | PPI | 18166 | New Virginia-Saidora 69 kV Line | New 14.9-mile 69 kV line in Menard Electric Cooperative | IL | 2023-12-31 | Other | Reliability | 2023-12-31 | 69 | 69 | 8640000
A in MTEP20 | East | METC | 19545 | Grand Rapids Area Project | Construct two 138kV circuits (~ 2 miles, new ROW on new double circuit structures) to cut in the Chopin – Northridge 138kV line into Meyer 138kV. Install (3) new 138kV breaker at Myer to facilitate new lines come into Meyer and remediate sag limit on the Chopin – Meyer, Meyer – Northridge and Meyer – Tallmadge #2 138kV lines. | MI | 2025-06-01 | BRP |  | 2025-06-01 | 138 | 0 | 8540000
A in MTEP20 | West | XEL | 18006 | Osprey - Hawkins 115kV Rebuild | Wreck out and rebuild of approximately 11.36 miles of 115kV line between Osprey and Hawkins substations for aging conditions | WI | 2022-06-15 | Other | Reliability | 2022-06-15 | 115 | 0 | 8500000
A in MTEP20 | Central | AmerenIL | 16987 | New Benton NW 138 kV Ring bus | Install 6 position ultimate ring bus. | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 138 | 0 | 8500000
A in MTEP20 | Central | AmerenIL | 17981 | Rebuild North Champaign 138 kV substation | Rebuild the North Champaign 138 kV substation to a ring bus configuration. | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 138 | 0 | 8500000
A in MTEP20 | Central | AmerenIL | 9734 | New North Utica 138 kV substation | Construct 138 kV breaker station in North LaSalle-Fox River-1646 138 kV line. | IL | 2023-12-01 | Other | Load Growth | 2023-12-01 | 138 | 34.5 | 8400000
A in MTEP20 | Central | AmerenIL | 13708 | New Athens Dutch Hill 138 kV substation ring bus | Add 138 kV ring Bus. Initial 3-position (ultimate 4-position) | IL | 2021-12-01 | Other | Reliability | 2022-12-01 | 138 | 0 | 8376000
A in MTEP20 | Central | DEI | 18286 | Rebuild Brownstown Sw Sta to Pumpkin Center 69 kV | 6952 Rbld Pt 2 Brownstown Sw Sta to Pumpkin Center; 10.7 mi. - 477acsr ; Replace the 6952-69123 tie switch on pole #813-1535-02 located just outside Pumpkin Center substation | IN |  | Other | Reliability | 2021-12-31 | 69 | 0 | 8361000
A in MTEP20 | West | ITCM | 17730 | Savanna-Clay 34kV to 69kV Rebuild | ITC will rebuild approximately 7.75 miles of 34.5kV to 69kV standards from Savanna Substation to Clay Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. | IL | 2025-12-30 | Other | Age and Condition | 2025-12-30 | 69 | 69 | 8262000
A in MTEP20 | East | METC | 17365 | J717_J728 Generator Interconnection | Build a new 138 kV 3 Breaker ring substation cut in from the Bullock - Warren 138 kV circuit. Install OPGW from the new station to Warren 138 kV sub. | MI | 2020-07-30 | GIP |  | 2020-07-30 | 138 | 0 | 8191000
A in MTEP20 | Central | DEI | 18328 | Rebuild Greencastle N. to Morton Jct. 69 kV | 6933 rebuild from Greencastle N. to Morton Jct. with 477ACSR and light-duty steel poles | IN |  | Other | Reliability | 2021-07-22 | 69 | 0 | 8084000
A in MTEP20 | Central | DEI | 18845 | Greenwood Clark Twnshp 230kV Ring bus | Greenwood Clark Twnshp: add (2) CBs to complete a 3-position 230kV Ring bus; replace misc. 230kV and 69kV equipment in-kind | IN |  | Other | Reliability | 2021-12-31 | 230 | 69 | 8053000
A in MTEP20 | South | Entergy-AR | 18725 | Searcy Price 161kV: Expand 161kV Station (J893) | The Searcy Price 161kV substation will be upgraded to incorporate a new POI for J893, a 100 MW photovoltaic generator project. Transmission Network Upgrades for this interconnection include two new 161kV circuit breakers, 161kV disconnect switches, expanding the existing 161kV operating bus, substation yard, control house, and additional relay control panels. | AR | 2021-08-01 | GIP |  | 2021-08-01 | 161 | 0 | 8045000
A in MTEP20 | Central | AmerenIL | 17973 | Rebuild Centerville 138 kV substation | Rebuild the Centerville 138 kV substation to a Ring bus configuration. | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 138 | 0 | 8000000
A in MTEP20 | Central | AmerenIL | 17977 | New Mt. Vernon West 345/138 kV transformer No. 2 | Install 2nd 345-138 kV transformer at Mt. Vernon West Substation | IL | 2023-06-01 | Other | Reliability | 2023-06-01 | 345 | 138 | 8000000
A in MTEP20 | Central | AmerenIL | 17983 | Rebuild South Belleville 138 kV substation | Rebuild the South Belleville 138 kV substation to a ring bus configuration. | IL | 2023-06-01 | Other | Reliability | 2023-06-01 | 138 | 0 | 8000000
A in MTEP20 | Central | PPI | 18161 | New Bluff Springs-Virginia 69 kV Line | New 13.8-mile 69 kV line in Menard Electric Cooperative | IL | 2023-12-31 | Other | Reliability | 2023-12-31 | 69 | 69 | 8000000
A in MTEP20 | West | ATC | 18051 | Sheboygan County SS, DIC, substation rebuild | Sheboygan County SS, DIC, substation rebuild | WI | 2022-12-31 | Other | Load Growth | 2022-12-31 | 138 | 0 | 8000000
A in MTEP20 | West | ITCM | 17732 | Eddyville Industrial Complex 161kV Substation Expansion | ITC will expand the Eddyville Industrial Complex 161kV substation to the north. ITC will construct a five position 161kV ring bus North of the existing Eddyville Industrial Complex substation. All new terminal equipment will be capable of 2000A minimum. ITCM will terminate the Beacon – Tri County and EIC – Tri County 161kV circuits into these breakers. | IA | 2023-05-31 | Other | Reliability | 2023-05-31 | 161 | 161 | 7956038
A in MTEP20 | West | ITCM | 18846 | Creston Roundhouse 69kV Substation Interconnection | Per Alliant’s request, ITC will construct a 3-terminal straight bus with tie breaker at the proposed Creston Roundhouse substation. All ITC terminal equipment will be capable of 2000A minimum and Alliant will own the land and joint use assets. In addition, ITC line equipment will use T2-4/0. | IA | 2022-12-15 | Other | Load Growth | 2022-12-15 | 69 | 69 | 7863016
A in MTEP20 | Central | AmerenIL | 13705 | New North Nashville 138 kV substation | Install initial 3 position 138 kV ring bus (ultimate 4 position) at North Nashville Substation. | IL | 2021-12-01 | BRP |  | 2021-12-01 | 138 | 0 | 7810000
A in MTEP20 | East | ITCT | 15900 | Rebuild Wayne - Newburgh #1 120 kV | Rebuild approximately 2.7 miles of 795 ACSS conductor to 2156 ACSS on the Wayne – Newburgh #1 120 kV circuit. Also, upgrade station equipment at both Wayne and Newburgh 120 kV. | MI | 2025-12-31 | BRP |  | 2025-12-31 | 120 | 0 | 7720000
A in MTEP20 | Central | AmerenMO | 16552 | Replace Tyson 345/138 kV Transformer | Replace XFMR 1 with a hardened unit and replace the 138kV XFMR 1 breaker and Replace XFMR 3 breaker. | MO | 2022-12-01 | Other | Age and Condition | 2022-12-01 | 345 | 138 | 7600000
A in MTEP20 | Central | AmerenMO | 18309 | New Fredericktown 138 kV substation | Install 138 kV ring bus at Fredericktown Substation | MO | 2022-12-01 | Other | Reliability | 2022-12-01 | 138 | 0 | 7500000
A in MTEP20 | Central | PPI | 18160 | New Arenzville-Bluff Springs 69 kV Line | New 10.3-mile 69 kV line tying Illinois Electric Cooperative to Menard Electric Cooperative | IL | 2023-12-31 | Other | Reliability | 2023-12-31 | 69 | 69 | 7459000
A in MTEP20 | Central | PPI | 18157 | New Kuhlman 138/69 kV Substation | "1) Establish 138 kV substation connecting to the Ameren Meredosia to Frederick 138 kV line 2) New PPI Kuhlman 138/69 kV substation" | IL | 2022-12-31 | Other | Reliability | 2022-12-31 | 138 | 69 | 7425000
A in MTEP20 | Central | DEI | 2864 | Reconductor Centerton to Martinsville 69kV - 69163 ckt. | Reconductor the 69kV-69163 ckt - 3.47 miles of 366ACSR 80C and 0.23 miles of 477ACSR 80C to 954ACSR 100C | IN | 2021-06-01 | Other | Reliability | 2023-06-01 | 69 | 0 | 7400000
A in MTEP20 | Central | DEI | 18304 | Batesville 345kV and 138kV breaker replacements | Batesville 345: Replace (1) 345kV circuit switcher with 345kV SF6 gas circuit breaker ; replace 345kv WT ; Replace (6) 138kV oil circuit breakers with SF6 gas circuit breakers - 13831, 13833, 13839, 13864, 13874, 138345-3 ; replace 13833 and 13874 WTs ; | IN |  | Other | Reliability | 2022-06-01 | 345 | 138 | 7334000
A in MTEP20 | West | MEC | 18124 | Sub T FD-Boone Jct 161 kV Reconductor | Reconductor MidAmerican's portion of the Sub T FD-Boone Jct 161 kV line and upgrade substation terminal equipment at Sub T FD. | IA | 2020-12-31 | GIP |  | 2020-12-31 | 161 | 0 | 7322500
A in MTEP20 | West | ATC | 18567 | J821 GIC Zenith SS - Generator Interconnection Facilities and Network Upgrades | A 99.9 MW wind farm in Marathon County, Wisconsin. Customer has requested a Point of Interconnection (POI) at a new Zenith Substation. | WI | 2021-08-27 | GIP |  | 2021-08-27 | 115 | 0 | 7235132
A in MTEP20 | Central | DEI | 18332 | Knightstown to Carthage 69kV Rebuild | 69140 rebuild from Knightstown to Carthage with 477ACSR and light-duty steel poles | IN |  | Other | Reliability | 2021-12-31 | 69 | 0 | 7201000
A in MTEP20 | Central | AmerenIL | 15266 | Reconfigure Fayetteville Bee Hollow 138 kV substation to ring bus | Install initial 3-position ring bus at the existing Fayetteville Bee Hollow substation location. | IL | 2023-06-01 | Other | Reliability | 2023-06-01 | 138 | 0 | 7200000
A in MTEP20 | Central | AmerenIL | 16707 | New Kazad 138 kV Substation in St. Joseph area | Install new ring bus substation at the intersection of VERM-NCMP-1396 and GIFF-SDNY-1588. Install 4 positions initial, 6-positions ultimate. Rebuild the existing Vermillion-N. Champaign-1396 138 kV line to 2000A in both directions from the new substation. Upgrade terminal equipment at Vermillion to 2000A including switch 1328, bus conductor and relay load limit. Upgrade terminal equipment at North Champaign to 2000A including 795 AAC bus conductor and re-tap 1 CT. | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 138 | 0 | 7200000
A in MTEP20 | Central | DEI | 18327 | Rebuild Dresser to S. Vigo 69 kV | 6901 rebuild from Dresser to S. Vigo with 477ACSR and light-duty steel poles | IN |  | Other | Reliability | 2021-07-16 | 69 | 0 | 7162000
A in MTEP20 | East | ITCT | 18184 | Rebuild Red Run – Logan 2 – Sloan 120 kV | Rebuild approximately 2.8 miles utilizing 954 ACSR on double circuit structures and upgrade terminal equipment at Sloan. | MI | 2024-06-01 | BRP |  | 2024-06-01 | 120 | 0 | 7095000
A in MTEP20 | Central | AmerenIL | 17972 | Rebuild Salem West 138 kV substation | Rebuild the Salem West 138 kV substation to a ring bus configuration. | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 138 | 0 | 7000000
A in MTEP20 | West | ATC | 18053 | Waupaca SS, DIC, transformer addition | ATC to expand the Waupaca Substation to accommodate a new 138-kV bus section, new bus-tie breaker, add two line breakers, reposition ATC’s 14-Mvar capacitor banks, and replace power-line carrier with optical ground wire (OPGW) from Waupaca – Harrison North. | WI | 2022-06-01 | Other | Load Growth | 2022-06-01 | 138 | 0 | 6900000
A in MTEP20 | Central | DEI | 18326 | Poseyville to HE Winfield 69kV Rebuild | 69139 Rebuild Part 2: Poseyville to HE Winfield TDSIC ; 4.4 miles - N.O. tie line | IN |  | Other | Reliability | 2021-12-31 | 69 | 0 | 6818000
A in MTEP20 | Central | AmerenIL | 18321 | New Ford County Wind (J845) interconnection | Install new ring bus (Oswald) on the Gibson City South-Paxton East 138 kV line to make the interconnection for J845. | IL | 2021-06-01 | GIP |  | 2021-06-01 | 138 | 0 | 6800000
A in MTEP20 | Central | AmerenIL | 18323 | New Cass County Solar (J859) interconnection | Install a new ring bus (Flanigan) on the Meredosia East-Ipava South 138 kV line to make the interconnection for J859. | IL | 2022-05-31 | GIP |  | 2022-05-31 | 138 | 0 | 6800000
A in MTEP20 | Central | AmerenMO | 17969 | Replace Mason 345/138 kV Transformer | Replace 345/138 kV, 560 MVA Transformer #2 with a 700 MVA unit | MO | 2022-12-01 | BRP |  | 2022-12-01 | 345 | 138 | 6700000
A in MTEP20 | Central | AmerenIL | 16556 | New Bueller 138 kV substation (formerly Grove) | Tap the Macomb West-Niota 138 kV line to install a new ring bus station to supply the PPI Disco Substation. | IL | 2022-06-01 | Other | Load Growth | 2022-06-01 | 138 | 0 | 6600000
A in MTEP20 | Central | AmerenIL | 18320 | New Bennington Wind (J715) interconnection | Install new 138 kV ring bus (Rutland) on the McLean-Oglesby line to make the interconnection for J715. | IL | 2021-05-01 | GIP |  | 2021-05-01 | 138 | 0 | 6600000
A in MTEP20 | West | MDU | 18260 | Greenway Tap-Herried Rebuild | Rebuild Greenway Tap-Herried 41.6 kV line | SD |  | Other | Age and Condition | 2021-12-31 | 41.6 | 0 | 6600000
A in MTEP20 | East | METC | 18425 | Verona - Marshall cut into Mud Lake (J758 Stability Upgrade) | Cut in and extend the Verona - Marshall 138kV line by adding 0.6 miles of 954 ACSR DCT to loop in J758. Add two 138kV 40kA breakers at positions 8M9 and 8W8 at the J758 substation 138kV. | MI | 2022-04-08 | GIP |  | 2022-04-08 | 138 | 0 | 6510000
A in MTEP20 | West | MDU | 17304 | G359, Ellendale 345 Network Upgrades | G359 Network Upgrades at Ellendale 345: four 230 kV 50 Mvar fast-switched capacitors and a new switcher for the 345 kV line reactor on the Big Stone South line | ND | 2020-03-31 | GIP |  | 2020-02-28 | 345 | 0 | 6431000
A in MTEP20 | Central | PPI | 18148 | New Riggston 138 kV substation | Establish 138 kV ring bus to serve proposed Data Center in Illinois Electric Cooperative new load between Jacksonville Industrial Park and Winchester. | IL | 2021-12-31 | Other | Load Growth | 2021-12-31 | 138 | 138 | 6400000
A in MTEP20 | South | LAFA | 14105 | Bonin 69kV Reconfiguration | A reconfiguration of the Bonin 69kV station. | LA | 2021-09-30 | Other | Reliability | 2021-09-30 | 69 | 0 | 6400000
A in MTEP20 | East | METC | 18243 | Battle Creek Transformer 2 Replacement | Replace Battle Creek 345/138kV transformer #2 with a new transformer. | MI | 2023-12-31 | Other | Age and Condition | 2023-12-31 | 345 | 138 | 6400000
A in MTEP20 | Central | AmerenIL | 16990 | New Kline 138 kV substation | Install new 6 position ultimate ring bus at Kline Substation (formerly known as Wanda). | IL | 2022-12-01 | Other | Reliability | 2022-12-01 | 138 | 0 | 6300000
A in MTEP20 | West | MEC | 18177 | Webster-Sub T FD 161 kV Reconductor | Reconductor portion of Webster-Sub T Fort Dodge 161 kV line. | IA | 2021-12-15 | GIP |  | 2021-12-15 | 161 | 0 | 6300000
A in MTEP20 | East | METC | 18055 | Riverview Interconnection | Convert METC Riverview substation from a three-breaker straight bus configuration to a six-breaker ring. Install three 138kV breakers, buswork, and associated disconnects. | MI | 2021-07-02 | Other | Load Growth | 2021-07-02 | 138 | 0 | 6270000
A in MTEP20 | East | METC | 18244 | Gallagher Transformer #2 Replacement | Replace Gallagher 345/138kV Transformer #2 with a new transformer | MI | 2023-12-31 | Other | Age and Condition | 2023-12-31 | 345 | 138 | 6200000
A in MTEP20 | Central | PPI | 18116 | New Kilbourne-Saidora 69 kV Line | New 9.7-mile 69 kV line in Menard Electric Cooperative | IL | 2023-12-31 | Other | Reliability | 2023-12-31 | 69 | 69 | 6195200
A in MTEP20 | South | Entergy-AR | 19065 | Ritchie 230kV: Add POI (J663) | This project will add a point of interconnection to the existing Ritchie 230kV substation for J663. TOIF upgrades include two 230kV dead end structures, two 230kV 3000A disconnect switches, one 230kV 3000A gas circuit breaker, three surge arresters, metering CT's, and relay panels. Relay settings updates will be required to all transmission lines, auto transformer, transfer breaker, and bus diffs where needed. | AR | 2022-05-01 | GIP |  | 2022-05-01 | 230 | 0 | 6114000
A in MTEP20 | West | GRE | 17971 | Westwood 1 115 kV Conversion | Convert the existing GRE/SEA Westwood 1 substation from 69 kV to 115 kV service. Rebuild the existing 69 kV transmission line from Le Sauk to Westwood 1 to West St. Cloud to 115 kV. | MN | 2022-12-02 | Other | Reliability | 2022-12-02 | 115 | 0 | 6020000
A in MTEP20 | Central | IPL | 18138 | Center Substation | Add a total of three new 138 kV breakers and replace three existing 138 kV breakers. | IN | 2021-12-31 | Other | Age and Condition | 2021-12-31 | 138 | 0 | 6000000
A in MTEP20 | West | ATC | 16488 | Tilden SS - Control House Replacement and Breaker & Relay Asset Renewal | • Replace six, 138kV oil breakers with SF6 gas breakers that utilize high creep bushings for mine dust contamination • Retire six bushing potential devices installed on two breakers and replace them with six bus voltage transformers • Install a new ATC owned control house and replace relays with ATC standard models • Replace other equipment including disconnect switches, arresters and bus voltage transformers and junction boxes | MI | 2023-12-01 | Other | Age and Condition | 2023-12-31 | 138 | 138 | 5880000
A in MTEP20 | East | METC | 18164 | Amber - Pere Marquette #2 138 kV | Construct a new line from Amber to Pere Marquette utilizing existing rights of way. Rebuild 0.62 miles from Amber to the Pere Marquette – Stronach 138 kV line with 954 ACSR utilizing future 230 kV double circuit construction initially operated as 138 kV single circuit with adjacent side left vacant for future use. Rebuild 0.72 miles of the existing single circuit Pere Marquette – Stronach 138 kV line with double circuit 138 kV construction and install 954 ACSR conductor on one side for the new Amber – Pere Marquette #2 138 kV line and 795 ACSS conductor on the other side for the existing Pere Marquette – Stronach 138 kV line. | MI | 2024-06-01 | BRP |  | 2024-06-01 | 138 | 0 | 5815000
A in MTEP20 | Central | AmerenMO | 17046 | Upgrade Kelso 345/161 kV substations | Install new 3000 A circuit breaker and motor-operated disconnect switch on 345 kV position V3. Replace the existing Kelso substation 336 MVA auto transformer #1 with a 560 MVA transformer. Replace the existing Kelso substation 161 kV bus tie 1-2 position H7 circuit breaker and bus disconnect switches. Replace the existing Kelso substation 161 kV position H6 circuit breaker and disconnect switch, upgrade the bus conductor of position H6 to achieve a minimum current carrying capability of 3000 A. Replace the existing Kelso substation H3 and H4 161 kV circuit breakers and disconnect switches in the CAPE-KEL-2 and KEL-MINR-2 terminals. Upgrade Kelso substation positions H3 and H4 bus conductors to achieve a minimum current carry capability of 2000 A. Replace the existing Kelso substation 161 kV disconnect switch on position H10. Replace the existing Kelso substation H11 and H12 161 kV disconnect switches (line and bus) in the CAPE-KEL-3) and KEL-MORLEY-3 terminals. | MO | 2022-12-01 | Other | Age and Condition | 2022-12-01 | 345 | 161 | 5800000
A in MTEP20 | East | ITCT | 18179 | Rebuild of Hood – Lily 120 kV | Rebuild approximately 2.6 miles of 3/0 Cu X2 of the Hood – Lily 120 kV circuit utilizing 954 ACSR on 230kV, double circuit structures. | MI | 2024-06-01 | BRP |  | 2024-06-01 | 120 | 0 | 5780000
A in MTEP20 | Central | DEI | 18329 | Dover to Thorntown 69kV Rebuild | 69134 rebuild from Dover to Thorntown with 477ACSR and light-duty steel poles | IN |  | Other | Reliability | 2021-12-31 | 69 | 0 | 5776000
A in MTEP20 | Central | DEI | 18330 | Westland Jct. to Westland 69kV Rebuild | 69166 rebuild from Westland Jct. to Westland with 477ACSR and light-duty steel poles | IN |  | Other | Reliability | 2021-12-31 | 69 | 0 | 5770000
A in MTEP20 | Central | AmerenIL | 18030 | New Meredosia 345 kV shunt reactive device | Install a shunt Reactive device to control voltages at IL-Meredosia 345 kV. | IL | 2021-04-01 | Other | Reliability | 2021-04-01 | 345 | 0 | 5700000
A in MTEP20 | East | METC | 18426 | Mud Lake - Brewer St Tap Rebuild (J758) | Rebuild the 4.4 miles of 336 ACSR from J758 Substation to Convis and Brewer St. Taps with 954 ACSR. | MI | 2022-04-08 | GIP |  | 2022-04-08 | 138 | 0 | 5700000
A in MTEP20 | West | ATC | 19145 | J947 Tennyson SS, Generator Interconnection Facilities and Network Upgrades | Interconnection of a 188 inverter solar farm in Green County, Wisconsin with a 200MW capacity. | WI | 2021-09-30 | GIP |  | 2021-09-30 | 138 | 0 | 5608810
A in MTEP20 | Central | AmerenIL | 18034 | Upgrade Tazewell 138 kV substation | Replace 14 138 kV breakers at Tazewell Substation including: TAZW-138KV BKR 1321-73, TAZW-138KV BKR 1340, TAZW-138KV BKR 1354, TAZW-138KV BKR 1323, TAZW-138KV BKR 1340-63 (TIE), TAZW-138KV BKR 1350 (XFMR 2), TAZW-138KV BKR 1363, TAZW-138KV BKR 1375, TAZW-138KV BKR 1353, TAZW-138KV BKR 1322, TAZW-138KV BKR 1367, TAZW-138KV BKR 1375-53, TAZW-138KV BKR 1327, TAZW-138KV BKR 1321 (XFMR 1) | IL | 2022-12-01 | Other | Age and Condition | 2022-12-01 | 138 | 0 | 5600000
A in MTEP20 | Central | AmerenMO | 18016 | Reconductor Berkley South 161 kV lines 1/2 | Reconductor BERK-S-1 & 2 on branches 1004 and 1005 with composite core conductor. | MO | 2023-12-01 | Other | Reliability | 2023-12-01 | 138 | 0 | 5600000
A in MTEP20 | West | ATC | 18665 | J855 GIC Ebenezer SS - Generator Interconnection Facilities and Network Upgrades | J855 is a 100.8 MW, 28 turbine wind farm in Grant County, Wisconsin with a requested point of interconnection at a new 138kV substation named Ebenezer SS tapping the existing 138kV line, X-16. | WI | 2020-11-06 | GIP |  | 2020-11-06 | 138 | 0 | 5526333
A in MTEP20 | South | Entergy-AR | 19005 | Ritchie 230kV: Expand substation (J834) | The J834 generator interconnection project will require network upgrades at the Entergy Arkansas Ritchie 230kV substation. This will include new interconnection facilites that will consist of two 230kV dead end structures, one 230kV 3000A gas circuit breaker, two 230kV vertical break disconnect switches, 230kV surge arrestors, CCVT's, metering CT's, and all associated relaying panels. There will be 0.4 miles of 666.6 ASCR Falmingo conductor, and 0.3 miles of 7#7 alumoweld conductor installed for the interconnection. Relay settings will be required all all remote end locations as well as the Autotransformer, Transfer Breaker, and the East and West Bus diff. | AR | 2022-05-15 | GIP |  | 2022-05-15 | 230 | 0 | 5511000
A in MTEP20 | Central | DEI | 18285 | WVPA McGrawsville to Bunker Hill 69kV alternate source line | WVPA to build McGrawsville to Bunker Hill 69kV alternate source line - 7.1 miles to be operated N.O. | IN |  | Other | Reliability | 2021-06-01 | 69 | 0 | 5510000
A in MTEP20 | Central | DEI | 18324 | WVPA Delphi South-6988 Tap Line | WVPA to build new 69kV, 6.3 mile, radial, N.O., alternate source to Delphi South (IPC, Indiana Packers Corp.) from the existing 6988 line tapped between Flora and Rockfield | IN | 2023-06-01 | Other | Reliability | 2023-06-01 | 69 | 0 | 5510000
A in MTEP20 | South | Entergy-LA | 13938 | Cheniere 115 kV: Install transmission breakers | Install transmission breakers at the existing Cheniere 115 kV substation, which is located on the Frostkraft - Sterlington 115 kV transmission circuit. | LA |  | Other | Reliability | 2023-12-01 | 115 | 0 | 5390471
A in MTEP20 | Central | DEI | 18288 | Trafalgar Swi Sta to HE Samaria Jct 69kV Rebuild | Rbld transmission line 6949 from Duke Trafalgar Swi Sta & HE Trafalgar sub to HE Samaria Jct using light duty steel poles, 477 ACSR and OPGW. Approximately 4.9 miles. | IN |  | Other | Reliability | 2021-12-31 | 69 | 0 | 5280000
A in MTEP20 | Central | PPI | 18152 | Reconductor Andrew-Amos 69 kV Line | Reconductor 8.9-mile 69 kV line from 336.4 MCM ACSR to 795 MCM ACSR | IL | 2022-12-31 | Other | Reliability | 2022-12-31 | 69 | 69 | 5239200
A in MTEP20 | Central | DEI | 18333 | Greencastle to Greencastle N. 69kV Rebuild | 6933 rebuild from Greencastle to Greencastle N. with 477ACSR and light-duty steel poles | IN |  | Other | Reliability | 2021-12-31 | 69 | 0 | 5231000
A in MTEP20 | South | Entergy-LA | 18146 | Sherwood Forest 115 kV: Install breakers | Install transmission line breakers at the existing Sherwood Forest 115 kV substation. | LA |  | Other | Reliability | 2023-12-01 | 115 | 0 | 5100000
A in MTEP20 | West | ATC | 18925 | J818 Jefferson SS Generator Interconnection Facilities and Network Upgrades | Interconnection of a 149 MW solar facility located in Jefferson County, Wisconsin. | WI | 2022-04-01 | GIP |  | 2022-04-01 | 138 | 0 | 5032559
A in MTEP20 | Central | AmerenIL | 18044 | Reconfigure Caterpillar quad 138 kV circuits | Reconfigure the Tazewell-Caterpillar 2-1375, Edwards-Caterpillar 1-1374, RS Wallace-Keystone-1396 and the Caterpillar 2-Hines-1357 138 kV circuits on a 1.5 mile section where they share a common structure. | IL | 2024-12-01 | Other | Reliability | 2024-12-01 | 138 | 0 | 5000000
A in MTEP20 | West | XEL | 18130 | Port Wing - Cornucopia 34.5kV Rebuild | Rebuild 9.6 miles of 34.5kV line from Port Wing to Cornucopia to remediate aging condition issues. | WI | 2023-06-15 | Other | Age and Condition | 2023-06-15 | 34.5 | 0 | 5000000
A in MTEP20 | West | XEL | 18131 | Orienta Tap - Iron River 34.5kV Rebuild | Rebuild 9 miles of 34.5kV line from former Orienta tap switch to Iron River to remediate aging condition issues | WI | 2023-06-15 | Other | Age and Condition | 2023-06-15 | 34.5 | 0 | 5000000
A in MTEP20 | West | XEL | 18132 | Cottage Grove Airgas Load Interconnection | New 115kV in and out substation tapped on Chemolite to Cottage Grove 115kV line to serve new Airgas load interconnection | MN | 2020-10-01 | Other | Load Growth | 2020-10-01 | 115 | 13.8 | 5000000
A in MTEP20 | West | ITCM | 9100 | Burlington-4th St-Agency 69kV Rebuild | Rebuild a portion of the Burlington-South Burlington 69kV line and upgrade the Burlington 69kV terminal so the Burlington-South Burlington line is conductor limited. Rebuild the Burlington 4th Street-Agency 69kV line to T2-477 ACSR. | IA | 2021-05-31 | Other | Reliability | 2021-05-31 | 69 | 69 | 4939417.2
A in MTEP20 | Central | AmerenIL | 18032 | New Xenia 345 kV shunt Reactive device | Install a shunt Reactive device to control voltages at Xenia 345 kV | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 345 | 0 | 4900000
A in MTEP20 | Central | AmerenMO | 15268 | Upgrade Selma-Buck Knob 138 kV line (1302) | Upgrade the DPFE-SEL-1302 138 kV line from Selma Substation to the old Buck Knob substation location with conductor capable of 1600A under summer emergency conditions. Upgrade terminal equipment at Selma to 1600A minimum capability. | MO | 2022-06-01 | Other | Age and Condition | 2022-06-01 | 138 | 0 | 4900000
A in MTEP20 | Central | DEI | 18305 | Westwood 345kV / 138kV relays and breakers replacement | Westwood misc station equipment replacement including: upgrade relays on 13806, 13808, 138345-1, Bk2, 138 bus 1 and 2, 138 bus tie ; Replace OCB 13820, 13883 and relays | IN |  | Other | Reliability | 2021-09-02 | 345 | 138 | 4900000
A in MTEP20 | West | MP | 17869 | Superior Transmission Line Relocations | Relocate transmission lines around industrial site to enable development | WI |  | Other | Reliability | 2021-11-01 | 161 | 0 | 4900000
A in MTEP20 | Central | AmerenMO | 17829 | New Loose Creek 345 kV shunt reactor | Install 345 kV shunt reactor at Loose Creek | MO | 2021-12-01 | Other | Reliability | 2021-12-01 | 345 | 0 | 4800000
A in MTEP20 | East | ITCT | 18241 | Stephens Transformer 303 Replacement | Replace Stephens 345/120kV Transformer #303 with a new transformer. | MI | 2023-12-31 | Other | Age and Condition | 2023-12-31 | 345 | 120 | 4800000
A in MTEP20 | East | ITCT | 18178 | Rebuild of Hancock – Lily 120 kV | Rebuild approximately 2 miles of 3/0 Cu X2 of the Hancock - Lily 120 kV circuit utilizing 954 ACSR on 230kV, double-circuit structures. | MI | 2024-06-01 | BRP |  | 2024-06-01 | 120 | 0 | 4680000
A in MTEP20 | Central | AmerenIL | 16705 | Rebuild Pana-Shelbyville South 138 kV line (1430) | Install OPGW and replace shield wire. | IL | 2021-12-01 | Other | Reliability | 2021-12-01 | 138 | 0 | 4600000
A in MTEP20 | West | ITCM | 17980 | Hancock T3 161/69kV Transformer Replacement | Replace the Beaver Channel T1 & T2 75MVA 161/69kV transformers with the spare 150MVA 161/69kV transformer (SN: WT03583) currently located at the Ames substation. Also install a high side breaker for the new transformer at Beaver channel and replace switch 1454. Any new high side equipment should be 1200A minimum and any new low side equipment should be 1600A minimum. Replace the Hancock T3 75MVA 161/69kV transformer with the Beaver Channel T1 75MVA 161/69kV Transformer (SN: 70450A). Also replace the high side circuit switcher 1320 with a 161kV circuit breaker. Re-use switch 1320B if feasible. Any other new required high-side equipment should be 1200A minimum. | IA | 2020-04-30 | Other | Age and Condition | 2020-04-30 | 161 | 69 | 4589958
A in MTEP20 | East | ITCT | 17504 | Abrams Interconnection | Install a new 120kV substation. Extend the Northeast-Skylark line by adding 0.1 miles of 954 ACSR conductor to loop in Abrams interconnection station. Add three 120kV breakers and two bus sections. | MI | 2022-10-31 | Other | Load Growth | 2022-10-31 | 120 | 0 | 4519000
A in MTEP20 | Central | AmerenMO | 18056 | New Mason 138 kV shunt reactive device | Install a shunt Reactive device to control voltages at Mason 3 138 kV bus | MO | 2023-12-01 | Other | Reliability | 2023-12-01 | 138 | 0 | 4500000
A in MTEP20 | West | MEC | 18181 | Black Hawk 345 kV Capacitor | Add 345 kV, 150 MVAR capacitor bank at Black Hawk 345 kV. | IA | 2021-06-30 | GIP |  | 2022-06-30 | 345 | 0 | 4500000
A in MTEP20 | East | ITCT | 18242 | Wayne Transformer 303 Replacement | Replace Wayne 345/120kV Transformer #303 with a new transformer. | MI | 2023-12-31 | Other | Age and Condition | 2023-12-31 | 345 | 120 | 4400000
A in MTEP20 | South | Entergy-AR | 18727 | Marston 161kV: Cut In Switching Station (J944) | Entergy will cut in a new 3 breaker ring bus that will be built by the Interconnection Customer on the Portageville - New Madrid 161kV line section. This bisection will occur near the tenth structure from the New Madrid substation. Approximately 4.52 miles of ADSS fiber shall be installed between Marston and New Madrid. At the remote end Hayti South, the OCB B9150 will be replaced with a SF6 gas circuit breaker rated at 3000 A. | MO | 2022-10-01 | GIP |  | 2022-10-01 | 161 | 0 | 4382000
A in MTEP20 | Central | AmerenIL | 18031 | New Ipava 345 kV shunt Reactive device | Install a shunt Reactive device to control voltages at Ipava 345 kV | IL | 2021-04-01 | Other | Reliability | 2021-04-01 | 345 | 0 | 4300000
A in MTEP20 | East | METC | 15939 | Leoni - Beecher 138 kV Sixed Wire | The proposed solution is to sixed wire 0.21 miles of the Mercer – Cement City Jct. section of the Leoni – Beecher circuit using existing 477 ACSR conductor. Also remediate sag limit on the 6-wired conductor section to increase its summer emergency rating to a minimum of 1196 Amps (286 MVA). | MI | 2025-06-01 | BRP |  | 2025-06-01 | 138 | 0 | 4300000
A in MTEP20 | South | Entergy-LA | 18786 | J909 Station Interconnection Project | This project is to support the interconnection of solar facility J909 at the Amite 115 kV station. | LA |  | GIP |  | 2022-02-15 | 115 | 0 | 4254000
A in MTEP20 | West | ITCM | 17705 | Madrid North 69kV Substation Rebuild Interconnection | IPL has requested ITC to rebuild the Madrid North Substation to a standard single box and double box with a bus tie breaker to accommodate their 25 kV plans which will include two transformers and 25 kV switchgear. ITC will also need to install a new control enclosure, as IPL will be retiring their existing control enclosure to accommodate their new switch gear. The existing 69 kV circuit switcher will be replaced with a new 69 kV breaker, which will allow for future retirement of the bus work associated with the 69/34.5 kV transformer. The existing zig-zag transformer should be removed to allow additional space for the installation of the new ITC owned control enclosure. The 69/34.5 kV transformer will need to remain until the conversion to 69 kV happens between Dawson and Madrid North (covered on EI Sketch ITCMW_16_034). The existing section of 69 kV bus that feeds the 69/34.5 kV transformer, transformer, and low-side breaker should be re-used, and then removed in the future as part of the 69 kV conversion. | IA | 2021-12-31 | Other | Load Growth | 2021-12-31 | 69 | 34 | 4144344
A in MTEP20 | West | ATC | 19268 | J807 J819 J947 MPFCA Common Use Upgrades | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. -J807 is seeking interconnection service for 41.4 MW -J819 is seeking interconnection service for 99.9 MW -J947 is seeking interconnection service for 200 MW | WI | 2021-12-31 | GIP |  | 2021-12-31 | 138 | 0 | 4067713
A in MTEP20 | Central | AmerenIL | 11969 | New Miles-Misissippi 138 kV line | Construct new 138 kV line | IL | 2022-12-01 | Other | Reliability | 2020-12-01 | 138 | 0 | 4000000
A in MTEP20 | West | ATC | 15930 | Pulliam SS, Transformer Retirement and Bus Reconfiguration | -Removal of Transformer T16 coordinated with retirement of Pulliam Generation Station -Bus Reconfiguration, straight bus to ring bus -Additional asset renewal of relays and removal of unnecessary circuit breakers | WI | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 138 | 69 | 4000000
A in MTEP20 | West | ATC | 18020 | Mackinac HVDC System Control Module (SCM) Asset Renewal | The Mackinac HVDC System Control Modules (SCMs) consist of multiple computer Servers which provide programmable control and protection functions - This project replaces the SCM servers following industry standard and OEM recommended life cycle timelines | MI | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 138 | 0 | 4000000
A in MTEP20 | West | MP | 15598 | Badoura Transformer Replacement | Replace existing 230/115 kV transformer at Badoura Substation. Complete 230 kV ring bus with 3 new 230 kV breakers. | MN | 2024-10-31 | BRP |  | 2024-10-31 | 230 | 115 | 4000000
A in MTEP20 | East | MPPA | 18003 | Barlow to Parsons Line Rebuild | Rebuild 2.73 miles of 69kV line between Barlow and Parsons. Replace 2.73 miles of #477 ACSR with .58 miles of twin #1000 MCM copper under airport flight path and 1.42 miles of #795 ACSS. Rebuild requires Switching Station upgrades at Barlow Substation. | MI | 2020-12-31 | Other | Reliability | 2020-12-31 | 69 | 69 | 4000000
A in MTEP20 | Central | DEI | 17484 | Rebuild Wabash River-Water St. 138 kV line (13845) | Wabash River to Water St. 13845 upgrade existing 477ACSR line conductor's maximum operating temperature from 100C to 120C | IN | 2024-06-01 | BRP |  | 2024-06-01 | 138 | 0 | 3950400
A in MTEP20 | East | METC | 18112 | Kenowa 345 kV Breaker Installation | Complete row 33 of the Kenowa substation by adding 3 breakers and associated equipment. This addition creates a breaker-and-a-half scheme at Kenowa. | MI | 2022-12-31 | Other | Reliability | 2022-12-31 | 345 | 0 | 3950000
A in MTEP20 | Central | DEI | 18289 | HE Needmore Jct to HE Needmore 69kV Rebuild | 6949 Part 2B - Rebuild transmission line using light duty steel poles, 477 ACSR and OPGW from “HE Needmore Jct” (pole #825-3379) to the HE Needmore substation (pole #825-3418); approximately 2 miles. | IN |  | Other | Reliability | 2021-12-31 | 69 | 0 | 3881000
A in MTEP20 | Central | DEI | 18308 | New Hunts Creek 138/12 kV substation | Hunts Creek 138/12 kV substation: new sub to be located in the 13855 ckt between LGE Ghent 138 kV and DEI Fairview 138 kV | IN |  | Other | Load Growth | 2021-06-01 | 138 | 12 | 3807000
A in MTEP20 | Central | AmerenMO | 18013 | New Montgomery 345 kV shunt reactor | Install 50 Mvar shunt reactor at Montgomery 345 kV substation. | MO | 2025-12-01 | Other | Reliability | 2025-12-01 | 345 | 0 | 3800000
A in MTEP20 | West | ATC | 14913 | Line Clearance Mitigation Program 2021 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2021. | WI,MI |  | Other | Reliability | 2024-06-30 | 345 | 69 | 3791502
A in MTEP20 | West | ITCM | 17734 | Clinton Perrin 69/24kV Substation Interconnection | IPL requested a new Clinton Perrin 69/24kV substation in Clinton, IA. The new substation in city of Clinton, will provide capacity for industrial load south/west of town and will support retirement of Beaver Channel sub and Mill Creek sub after 25kV conversion. IPL will install a single transformer, 12.5kV substation, 20/33MVA capacity. Transformer will have 25kV option, but will be replaced by a 30/50MVA unit for final 25kV configuration. Installed XFMR will be moved elsewhere at that time. This conversion is estimated to be 10-20 years after completion of this construction. Four feeders will be used from this substation to serve load. Contingency at 12.5kV will be up to max rating of transformer, 33MVA. Contingency at 25kV will be reviewed and updated at a later date, but may be up to future 50MVA top rating of final unit. | IA | 2023-12-31 | Other | Load Growth | 2023-12-31 | 69 | 24 | 3787788
A in MTEP20 | Central | DEI | 18307 | New Westfield East 69/12 kV substation | Westfield East: new sub - 69/12kv - 22.4 MVA xfmr bank, single phase regulators SCADA/IVVC, 2 breakers, and space for second bank. Normal feed from 6917 ckt, alternate from 69142. | IN |  | Other | Load Growth | 2022-06-01 | 69 | 12 | 3767000
A in MTEP20 | Central | AmerenIL | 18085 | Replace Tazewell 345/138 kV transformer No. 1 | Replace 345-138 kV transformer with new 560 MVA unit. | IL | 2022-06-01 | Other | Age and Condition | 2022-06-01 | 345 | 138 | 3750000
A in MTEP20 | Central | AmerenIL | 18086 | Replace Tazewell 345/138 kV transformer no. 2 | Replace 345-138 kV transformer with new 560 MVA unit. | IL | 2024-06-01 | Other | Age and Condition | 2024-06-01 | 345 | 138 | 3750000
A in MTEP20 | Central | AmerenIL | 18088 | Replace Neoga South 345/138 kV transformer | Replace 345-138 kV transformer with new 560 MVA unit. | IL | 2023-06-01 | Other | Age and Condition | 2023-06-01 | 345 | 138 | 3750000
A in MTEP20 | Central | AmerenIL | 18089 | Replace Brokaw 345/138 kV transformer | Replace 345-138 kV transformer with new 560 MVA unit. | IL | 2023-12-01 | Other | Age and Condition | 2023-12-01 | 345 | 138 | 3750000
A in MTEP20 | Central | AmerenIL | 18090 | Replace Albion South 345/138 kV transformer No. 3 | Replace 345-138 kV transformer with new 560 MVA unit. | IL | 2024-12-01 | Other | Age and Condition | 2024-12-01 | 345 | 138 | 3750000
A in MTEP20 | Central | AmerenMO | 18312 | New Blue Bird Solar (J817) interconnection | Add terminal facilities at Warrenton 161 kV substation to interconnect J817, | MO | 2023-06-01 | GIP |  | 2023-06-01 | 161 | 0 | 3700000
A in MTEP20 | Central | IPL | 18135 | Rockville Auto Replace | Replace 345-138 auto with like-for-like replacement | IN | 2020-12-31 | Other | Age and Condition | 2020-12-31 | 345 | 0 | 3700000
A in MTEP20 | Central | IPL | 17564 | Rockville 345 kV Ring Bus | Add one 345 kV breaker to form a ring bus at the Rockville substation. | IN | 2020-12-31 | Other | Reliability | 2020-12-31 | 345 | 0 | 3600000
A in MTEP20 | West | ITCM | 17704 | Cedar Rapids Hunter Field Substation Interconnection | IPL will be building a new 69/24.9 kV substation named Cedar Rapids Hunter Field near the existing Viola’s Corner substation. This new substation will replace Viola’s Corner. The new substation will have 1 new 69/24.9 kV 50 MVA transformer installed initially, with a second transformer to be added in the future as load grows in the area. ITC will build a new 69 kV substation with two single box structures and two breakers installed, one line breaker and one bus tie breaker, and will add an additional line breaker in the future when IPL adds a second transformer. | IA | 2021-12-30 | Other | Load Growth | 2021-12-30 | 69 | 25 | 3578790
A in MTEP20 | South | Entergy-AR | 18099 | El Dorado 115kV: Underrated Breakers | Replace the 115 kV breaker(s) at El Dorado with 63 kA fault interrupting capability. B5820, B6258, B6758, B7158, and B7658 will be replaced. | AR | 2021-06-01 | BRP |  | 2021-06-01 | 115 | 0 | 3562971
A in MTEP20 | East | WPSC | 17204 | Upgrade Vestaburg Transformer | Wolverine to install transformer with increased capacity at the Vestaburg Transmission station in order to support the J589 generation interconnection. The capacity of the new transformer will be 168MVA. | MI | 2020-02-29 | GIP |  | 2020-02-29 | 138 | 0 | 3520000
A in MTEP20 | Central | AmerenIL | 16708 | Reconductor Hines-Pioneer 138 kV line (1326) | Replace existing 927 ACAR conductor with ACCR conductor | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 138 | 0 | 3500000
A in MTEP20 | Central | AmerenMO | 16985 | Rebuild Sioux-Meppen 138 kV Line (4) | Rebuild 3.7 mile Missouri side section (Str. 146-173) of the old Page-Keokuk line w/ T2 conductor. Page-Sioux-4: Rebuild Missouri River crossing (Str. 112-117) w/ 2000A rated conductor. | MO | 2021-06-01 | Other | Age and Condition | 2021-06-01 | 138 | 0 | 3500000
A in MTEP20 | West | MDU | 15784 | Zahl-Corinth 60 kV line | Rebuild Zahl-Corinth 60 kV line | ND | 2023-12-31 | Other | Age and Condition | 2023-09-30 | 60 | 0 | 3500000
A in MTEP20 | West | MP | 18060 | 8 Line Relocation | Relocate & rebuild Fond Du Lac - Thomson 115 kV Line. Add a 115 kV breaker at Fond Du Lac. | MN | 2023-12-31 | Other | Age and Condition | 2023-12-31 | 115 | 0 | 3500000
A in MTEP20 | West | ATC | 17628 | Preble SS, DIC, add 4th transformer and substation rebuild | WPS will: • expand Preble Substation and install a new control house • add the 4th 138/24.9 kV, 22 MVA xfmr with a circuit breaker on the high-side • rebuild and relocate Bank 2 xfmr and upgrade the high-side to a circuit breaker • retire and remove Henry St Substation ATC will: • extend 138 kV bus to the north and the south • relocate both 138 kV line terminals for line X-154 (Highway V – Tower Dr) • replace existing 77/88 MODs with 138 kV line breakers • install a 138 KV bus-tie breaker • retire the 69 kV Henry St Tap on line L-64 (Danz Ave – Finger Road) | WI | 2022-06-01 | Other | Load Growth | 2022-06-01 | 138 | 0 | 3498694
A in MTEP20 | West | ITCM | 18114 | Adams 161kV Breaker and 1/2 Upgrade | Add a breaker to the 161kV bus between breakers 0681 and 0680 and relocate the Rochester and Harmony 161kV lines to terminal positions in the newly formed breaker and 1/2 row (install switches, bus work, dead-end, CCVTs, relays, and all necessary equipment as needed). Add a breaker to the 161kV bus between breakers 0685 and 0682 (install switches, bus work, dead-end, CCVTs, relays, and all necessary equipment as needed). Add a breaker to the 161kV bus between breakers 0790 and 0686 (install switches, bus work, dead-end, CCVTs, relays, and all necessary equipment as needed). All equipment needs to be capable of a minimum of 2000 amp operation. | MN | 2021-09-15 | Other | Reliability | 2021-09-15 | 161 | 161 | 3381530
A in MTEP20 | Central | PPI | 18154 | New Alsey 138 kV shunt reactor device (40 Mvar) | Alsey 138 kV substation - Addition of 40 Mvar reactor - BRP | IL | 2022-12-31 | BRP |  | 2022-12-31 | 138 | 138 | 3240000
A in MTEP20 | West | ATC | 17585 | Colley Road SS, Transformer Replacement and Asset Renewal | • Replace 1975 vintage 93 MVA 138/69/12.47 kV power transformer with a 100 MVA new purchase • Replace four sets of three-phase 1960’s vintage hook-stick disconnect switches | WI | 2023-12-31 | Other | Age and Condition | 2023-12-31 | 138 | 69 | 3150000
A in MTEP20 | West | XEL | 18344 | J587 Blazing Star 2 | New 200MW wind generation interconnection with new 345kV - 115kV substation and generation facilities. | MN | 2020-09-15 | GIP |  | 2020-09-15 | 345 | 115 | 3104000
A in MTEP20 | Central | AmerenIL | 17626 | Rebuild Kickapoo-Limit 138 kV line (1325) | Rebuild line from Kickapoo to Limit to 2000A. Double circuit from Limit to McGrath to supply McGrath radially from Limit. | IL | 2024-12-01 | Other | Reliability | 2024-12-01 | 138 | 0 | 3100000
A in MTEP20 | West | MDU | 18257 | Greenway Substation | Build three breaker 41.6 kV ring bus on at junction of three terminal Wishek-Bowdle-Glenham 41.6 kV line. | SD |  | Other | Reliability | 2021-12-31 | 41.6 | 0 | 3100000
A in MTEP20 | South | Entergy-AR | 19068 | Flat Fork 230kV: Cut In Switching Station (J907) | Entergy Arkansas will construct new surge arrestors, protective relays, RTU, and other supporting equipment at Ritchie 230kV. There will be equipment upgrades performed at Brinkley East substation such as disconnect switches, insulators, station service, protective relays, and other supporting equipment. The Brinkley East - Aubrey 230kV transmission line cut in will consist of two new steel dead end structures, new steel tangent structures, and new monopole structures. The Interconnection Customer will construct the three breaker ring bus substation. | AR | 2022-06-01 | GIP |  | 2022-06-01 | 230 | 0 | 3094660
A in MTEP20 | South | SMEPA | 17004 | Benndale Recip Project | The existing Benndale combustion turbine facility will have two 11MW RICE gas-fired engines installed with a new GSU. The Benndale switching station will be rebuilt and all oil circuit breakers will be replaced with gas circuit breakers and updated relaying package. | MS | 2019-12-25 | GIP |  | 2019-12-25 | 69 | 0 | 3010000
A in MTEP20 | Central | AmerenIL | 18626 | New Delhi 69 kV substation | 69 kV line to new MJM-Delhi substation with 69/12 kV transformer tapping 69 kV line near Jerseyville MJM sub | IL | 2022-06-01 | Other | Load Growth | 2022-06-01 | 69 | 0 | 3000000
A in MTEP20 | East | NIPS | 18484 | J837 J838 GIA Network Upgrades | Reynolds 345kV upgrades to accommodate GI | IN | 2021-08-01 | GIP |  | 2021-08-01 | 345 | 0 | 2979556
A in MTEP20 | South | Entergy-AR | 19728 | Driver 230kV: POI Existing Substation (J1155) | The project involves the expansion of the Driver 230kV substation to interconnect J1155 solar generation project. Upgrades will include installing a new 230kV breaker, CCVT's, conductor for the cut-in, surge arrestors, and CT's. | AR | 2022-09-01 | GIP |  | 2022-09-01 | 230 | 0 | 2949000
A in MTEP20 | Central | PPI | 18123 | New Payson 69 kV Breaker Station | Establish 69 kV breaker station in Adams Electric Cooperative | IL | 2022-12-31 | Other | Reliability | 2022-12-31 | 69 | 69 | 2940400
A in MTEP20 | Central | PPI | 18165 | New Virginia 69 kV Breaker Station | New 69 kV breaker station in Menard Electric Cooperative | IL | 2023-12-31 | Other | Reliability | 2023-12-31 | 69 | 69 | 2929500
A in MTEP20 | South | Entergy-AR | 19727 | Falls 161kV: New Cut In (J1125) | The J1125 135 MW solar project will interconnect to the Wynne South - AECC Wynne East 161kV line section. The cut-in will comprise of four new steel dead-end structures one new steel tangent structure and the removal of two existing structures. New conductors and shield wire will also be installed. Relay panels at the remote end substations of Moses and Parkin will be replaced. | AR | 2023-03-01 | GIP |  | 2023-03-01 | 161 | 0 | 2870660
A in MTEP20 | East | METC | 17384 | J796 (Goss) Network Upgrade | Network upgrades required to connect the J796 project. J796 is capable of 239 MW of solar generation. METC's Goss 138kV station will need to be expanded by adding four 138kv breakers to accommodate the interconnection. | MI | 2021-09-01 | GIP |  | 2021-09-01 | 138 | 0 | 2810000
A in MTEP20 | Central | DEI | 18325 | New NSA Crane ULTF 69/12 kV substation | new sub - "Crane Northwest" to feed NSA Crane ULTF - 17 MW new load to be fed from 69193 ckt - located North of existing NSA owned East and West Substations | IN |  | Other | Load Growth | 2021-06-01 | 69 | 12 | 2800000
A in MTEP20 | West | ITCM | 17967 | Bowen Substation 69kV Conversion | ITC will be converting the Bowen Substation to 69kV. All network path 69kV equipment will be capable of 600A or greater. | IL | 2029-12-30 | Other | Age and Condition | 2029-12-30 | 69 | 69 | 2754375
A in MTEP20 | West | ATC | 12175 | West Middleton - Stage Coach 69 kV (6927), partial rebuild | *Replace the underground cable at West Middleton with a overhead line *Replacement of jumpers, switches and other terminal equipment | WI | 2023-12-31 | Other | Reliability | 2023-12-31 | 69 | 0 | 2735023
A in MTEP20 | West | ITCM | 16710 | J233 J514 GIA Amendment Network Upgrades | The J233 GIA has been amended to include J514, a 65 MVW increase in ERIS and 30 MW of NRIS for the Marshalltown Generating Station. Network upgrades include raising spans on the Marshalltown-Blairstown 115kV and the Blairstown-Prairie Creek 115kV. | IA | 2019-12-31 | GIP |  | 2019-09-02 | 115 | 115 | 2732821
A in MTEP20 | Central | AmerenIL | 18315 | New Galesburg Wind (J844) interconnection | Add 1 BAAH 138 kV leg to the Sandburg Substation and add 1 breaker postion to interconnect J844. | IL | 2021-05-28 | GIP |  | 2021-05-28 | 138 | 0 | 2700000
A in MTEP20 | Central | AmerenMO | 9735 | Upgrade Tyson 138 kV substation | Replace overstressed 138 kV breakers | MO | 2021-12-01 | Other | Reliability | 2021-12-01 | 138 | 138 | 2700000
A in MTEP20 | Central | AmerenIL | 16706 | Rebuild Goose Creek 345 kV ring bus | Rebuild the Goose Creek 345 kV ring bus to 3000A capability. Replace all limiting terminal equipment and bus conductors with equipment capable of 3000A. | IL | 2022-12-01 | Other | Reliability | 2022-12-01 | 345 | 0 | 2600000
A in MTEP20 | Central | AmerenIL | 17828 | Upgrade Kren-Porter Road 138 kV line (1432) | Replace ~6 miles of existing 3 #7 Copperweld shield wire for the entire line. | IL | 2020-06-01 | Other | Age and Condition | 2020-06-01 | 138 | 0 | 2600000
A in MTEP20 | West | MDU | 18254 | Tioga Substation Rebuild | Rebuild Tioga substation due to age and condition | ND |  | Other | Age and Condition | 2021-12-31 | 115 | 60 | 2600000
A in MTEP20 | West | ITCM | 17736 | Waukon Snakeskin 69kV Substation Interconnection | IPL will be constructing the Waukon Snakeskin 2 transformer 69/25kV substation the replace the nearby Waukon substation. ITC will install 2 box structures, 2 line breakers and 1 tie breaker. The cap bank and cap bank breaker at the existing Waukon substation should be moved to the Decorah side of the Waukon Snakeskin substation if possible or a new cap bank and breaker of equivalent effective rating should be installed. All substation equipment should have a minimum rating of 1200A. ITC will also install short in/out tap lines. | IA | 2021-12-31 | Other | Load Growth | 2021-12-31 | 69 | 69 | 2507447
A in MTEP20 | South | Entergy-MS | 19285 | New 230 kV Switching Station Cut-in - J866 POI | Terminal equipment upgrades required to facilitate POI for generation interconnection customer J866. | MS | 2021-06-01 | GIP |  | 2021-07-01 | 230 | 0 | 2502660
A in MTEP20 | Central | AmerenIL | 17345 | Rebuild Auburn North-Jacksonville 138 kV line | Scope is broken into 3 sections: o Structures 644-668 will be a complete rebuild to 1600A with 795 T2 conductor. O Structures 19-49 are single pole wood and will require structure replacements. O Jacksonville-Auburn North – 5 structure raises | IL | 2020-06-01 | Other | Age and Condition | 2020-06-01 | 138 | 0 | 2500000
A in MTEP20 | West | MP | 17184 | Nemadji Transformer Addition | Expand 115 kV ring bus and add new 115/13.8 kV transformer at Nemadji Switching Station for customer | WI | 2020-11-01 | Other | Load Growth | 2021-11-01 | 115 | 13.8 | 2500000
A in MTEP20 | East | ITCT | 18240 | Install Capacitor at Boyne 120 kV | Low voltage is projected to occur at the Golf 120 kV, Houston 120 kV, and Macomb 120 kV buses for shutdown plus contingency scenarios involving a DTE transformer in surrounding area plus either the Macomb – Stephens 120 kV line or the Golf – Bismarck 120 kV line. The low voltage violations were identified in the 2020, 2023, and 2028 peak and off-peak load models. | MI | 2023-12-31 | BRP |  | 2023-12-31 | 120 | 0 | 2430000
A in MTEP20 | Central | IPL | 18145 | Hanna Substation | Replace three 345 kV breakers. | IN | 2021-12-31 | Other | Age and Condition | 2021-12-31 | 345 | 0 | 2400000
A in MTEP20 | West | ITCM | 17741 | ITCM Customer Interconnects with short lead time 2023 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL | 2023-12-31 | Other | Load Growth | 2023-12-31 | 345 | 69 | 2400000
A in MTEP20 | West | ATC | 19265 | J878 GIC Paris SS, Generator Interconnection Facilities and Network Upgrades | Interconnection Customer will install a 200 MW solar farm interconnecting at the Paris SS in Kenosha County, Wisconsin. | WI | 2022-09-30 | GIP |  | 2022-09-30 | 138 | 0 | 2353840
A in MTEP20 | East | ITCT | 18175 | Rebuild the Van Dyke 2 – Sloan 120 kV Line | Rebuild approximately 0.6 miles 795 ACSR utilizing 1431 ACSR on double circuit structures and upgrade terminal station equipment at Sloan. | MI | 2025-06-01 | BRP |  | 2025-06-01 | 120 | 0 | 2350000
A in MTEP20 | East | METC | 18245 | Kenowa 345kV Reactor 33F Replacement | Replace Kenowa 345kV Shunt Reactor #33F with a new reactor. | MI | 2023-12-31 | Other | Age and Condition | 2023-12-31 | 345 | 0 | 2350000
A in MTEP20 | East | ITCT | 18168 | Reconductor of Bismarck - Red Run 230 kV | Reconductor approximately 2 miles of the Bismarck – Red Run 230 kV circuit utilizing 1431 ACSR and upgrade terminal station equipment at Bismarck and Red Run. | MI | 2024-06-01 | BRP |  | 2024-06-01 | 230 | 0 | 2344000
A in MTEP20 | West | ATC | 17526 | J886 GIC Kewaunee SS Interconnection Facilities and Network Upgrades | To modify the existing 138kV Kewaunee Substation to provide transmission interconnection of the J866 with a total summer capacity of 150MW. | WI | 2020-08-01 | GIP |  | 2020-08-01 | 138 | 0 | 2293039
A in MTEP20 | South | Entergy-AR | 19726 | Bob White 161kV: Cut In Switching Station (J1007) | This project will cut in the J1007 161kV substation on the Marion - Marked Tree 161kV substation. J1007 is a 180 MW solar generating facility with an executed generator interconnection agreement. | AR | 2023-06-01 | GIP |  | 2023-06-01 | 161 | 0 | 2276660
A in MTEP20 | East | ITCT | 16015 | Sunset - Quaker 120 kV Rebuild | The proposed solution is to rebuild 0.259 mile of the Sunset – Quaker 120kV circuit using 2156 ACSR conductor with single circuit steel structures and replace terminal equipment and station equipment at Quaker Pos HD and Sunset Pos HN. | MI | 2025-12-31 | BRP |  | 2025-12-31 | 120 | 0 | 2260000
A in MTEP20 | South | Entergy-AR | 18094 | Hot Springs 115kV SPOF | Install dual primary protection on the 115 kV bus schemes at Hot Springs. | AR | 2022-06-01 | BRP |  | 2022-12-31 | 115 | 0 | 2256239
A in MTEP20 | West | ATC | 18019 | Glenview SS, Transformer Retirement and Breaker & Relay Asset Renewal | -Retire and dispose of the T1 Power Transformer including the station power -Replace 5 69kV oil circuit breakers and 2 138kV oil circuit breakers -Replace 8 disconnect switches -Install line arresters on the E-57 and GLWG21 138kV line terminals and retire bus 1 and 2 arresters | WI | 2023-12-31 | Other | Age and Condition | 2023-12-31 | 138 | 69 | 2200000
A in MTEP20 | East | METC | 18073 | Reconductor Argenta - Riverview 138kV | The proposed solution is to reconductor approximately 3 miles of the Argenta - Riverview 138kV circuit using 1431 ACSR conductor. Also upgrade relay at Argenta pos. 14MB to meet or exceed 385 MVA (1612 Amps). | MI | 2024-06-01 | BRP |  | 2024-06-01 | 138 | 0 | 2200000
A in MTEP20 | Central | AmerenMO | 17065 | Upgrade Tegeler 138 kV substation | Install a new 2000 A circuit breaker and associated disconnect switches in the TGLR-BLAN-6756 138 kV line terminal. Replace the existing 1600 A circuit breaker and associated 1200 A disconnect switches and 1590 kcmil AAC bus conductor at position H5 with equipment capable of carrying 2000 A during summer emergency conditions. Increase relay load limit. Replace the existing 1200 A disconnect switches and 1590 kcmil AAC bus conductor in position H9 to match the capability of the 2000 A circuit breaker. Install 2 circuit switchers on the high-side of the new and existing 138/34.5 kV transformers, having a minimum continuous current rating of 600 A. | MO | 2021-12-01 | Other | Age and Condition | 2021-12-01 | 138 | 0 | 2100000
A in MTEP20 | West | MEC | 18151 | Granger Tap-100th St & 54th Ave 161 kV Reconductor | Reconductor Granger Tap-100th St & 54th Ave 161 kV line with T2-795 ACSR Drake. | IA | 2021-12-31 | GIP |  | 2021-12-31 | 161 | 0 | 2085000
A in MTEP20 | South | SMEPA | 18180 | Missionary 230kV Reactor Bank | Add new bay and breaker at Missionary 230 kV substation. Add new Reactor Bank (Single Stage 30 MVAR) at Missionary 230 kV substation. | MS | 2021-03-01 | Other | Reliability | 2021-03-01 | 230 | 0 | 2055000
A in MTEP20 | Central | AmerenIL | 17827 | Upgrade Cottage Hills-Stallings 161 kV line (1622) | Replace ~4 miles of existing 3 #7 Copperweld shield wire from Str. 51-Wanda Sub | IL | 2020-12-01 | Other | Age and Condition | 2020-12-01 | 138 | 0 | 2000000
A in MTEP20 | Central | AmerenIL | 18041 | Upgrade Ottawa 138 kV substation | Install new line breaker on the HENN-OGLE-1516 line at Ottawa Substation. | IL | 2022-12-01 | Other | Reliability | 2022-12-01 | 138 | 0 | 2000000
A in MTEP20 | Central | AmerenIL | 18042 | Upgrade Wedron-Fox River 138 kV line (1652) | Install new line breaker on the OTTA-FOXR-1652 circuit at Wedron Fox River Substation. | IL | 2022-12-01 | Other | Reliability | 2022-12-01 | 138 | 0 | 2000000
A in MTEP20 | Central | AmerenIL | 18080 | Upgrade Meredosia E 138 kV substation | Replace breakers MERE-138KV BT 1938, MERE-138KV BT 1958, MERE-138KV BKR 1957, MERE-138KV BKR 1947 and MERE-138KV BT 1948 at Meredosia East Substation. | IL | 2023-12-01 | Other | Age and Condition | 2023-12-01 | 138 | 0 | 2000000
A in MTEP20 | Central | AmerenIL | 18625 | New MJM-Nutwood 69 kV line | New 69 kV loop feed to the MJM-Nutwood 69/12kV substation | IL | 2022-12-31 | Other | Reliability | 2022-12-31 | 69 | 0 | 2000000
A in MTEP20 | Central | IPL | 18142 | Mooresville Substation | Add a total of two new 138 kV breakers and convert the substation to a ring bus. | IN | 2021-12-31 | Other | Age and Condition | 2021-12-31 | 138 | 0 | 2000000
A in MTEP20 | South | AECC | 18805 | NUCOR Cap Bank | AECC to install a 60 MVAR capacitor bank at Hickman North substation in Mississippi County Electric. | AR | 2021-06-01 | BRP |  | 2021-06-01 | 161 | 0 | 2000000
A in MTEP20 | South | Entergy-LA | 15568 | Oak Grove 138kV : Add Breaker | Install transmission breakers at the existing Oak Grove 138 kV substation, located on the Willow Glen to Gonzales 138 kV transmission circuit. | LA |  | Other | Reliability | 2022-12-01 | 138 | 0 | 2000000
A in MTEP20 | West | CMMPA | 18118 | Windom_Transmission_Upgrade | Windom Municipal Utilities (WMU) has two transmission lines that source the Power Plant Substation. The south transmission line is sourced from the ITC substation located south of the city. This line is approximately 1.5 miles. The east transmission line interconnects with an ITC 69 kV transmission line on the east side of the city. This line is approximately 1.36 miles. It appears both transmission lines were constructed circa 1971. WMU has indicated it would like to relocate the south transmission line along the 1st Avenue between the Power Plant substation and 6th Street. This section of line has two overhead distribution circuits under built on the transmission structures. WMU indicated that the distribution lines could be converted to underground. In addition, WMU has requested a cost estimate to construct a new 69 kV transmission to the north of the city for a possible future substation. This new segment would replace the existing east transmission line that interconnects with ITC east of the city. | MN |  | Other | Age and Condition | 2021-12-15 | 69 | 0 | 2000000
A in MTEP20 | East | CETO | 18886 | Jaguar 138 kV Lines | Construct two new 138 kV lines from CE's new Morrow South Substation to METC's new Jaguar station. | MI | 2022-12-31 | Other | Load Growth | 2022-12-31 | 138 | 0 | 2000000
A in MTEP20 | East | ITCT | 17744 | ITCT Customer Interconnections - Year 2023 | Customer interconnection requests and retirements less than $1 million with in service date in year 2023. | MI | 2023-12-31 | Other | Load Growth | 2023-12-31 | 120 | 0 | 2000000
A in MTEP20 | East | METC | 17745 | METC Customer Interconnections - Year 2023 | Customer interconnection requests and retirements less than $1 million with in service dates in the year 2023. | MI | 2023-12-31 | Other | Load Growth | 2023-12-31 | 138 | 0 | 2000000
A in MTEP20 | Central | SIGE | 15961 | Rebuild Y31-1 NW - ORS 69 kV | Rebuild ~2.1 miles of 69 kV overhead transmission between the Northwest and Ohio River Station substations (line Y31-1). | IN | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 69 | 0 | 1930000
A in MTEP20 | Central | AmerenIL | 18096 | Upgrade Goose Creek 345 kV substation | Replace breakers GOSC-345KV BKR 4545, GOSC-345KV BKR 4575 and GOSC-345KV LT BKR 4555 at Goose Creek Substation. | IL | 2023-12-01 | Other | Age and Condition | 2023-12-01 | 345 | 0 | 1800000
A in MTEP20 | South | Entergy-LA | 18785 | J639 Station Interconnection Project | This project is to support the interconnection of solar project J639 on 230 kV line 731 (Addis to Big Cajun). | LA | 2021-06-01 | GIP |  | 2022-10-20 | 230 | 0 | 1790777
A in MTEP20 | West | ATC | 19225 | J864 Lone Rock SS Generator Interconnection Facilities and Network Upgrades | Interconnection of a 49.98 MW solar farm at the Lone Rock SS. | WI | 2022-09-01 | GIP |  | 2022-09-01 | 69 | 0 | 1767400
A in MTEP20 | South | Entergy-AR | 18100 | Danville 161kV: Install Cap Bank | Install a 24 MVAR cap bank at Danville 161kV | AR | 2023-06-01 | Other | Reliability | 2023-06-01 | 161 | 0 | 1755533
A in MTEP20 | Central | AmerenIL | 17826 | Upgrade Greenville McCord-South Centralia 138 kV line (1419) | Replace ~22 miles of existing 5/16" HS Steel Shield Wire with 1 3/8" E.H.S. Steel Shield Wire and 1 OPGW | IL | 2022-12-01 | Other | Age and Condition | 2022-12-01 | 138 | 0 | 1700000
A in MTEP20 | Central | AmerenIL | 18314 | New McLean County Wind (J826) interconnection | Add breaker position to existing ring bus at Weedman 138 kV Substation for the J826 interconnection. | IL | 2021-05-28 | GIP |  | 2021-05-28 | 138 | 0 | 1700000
A in MTEP20 | Central | SIGE | 15950 | Hemenway 69/12 kV Dist. T1 Repl. | Replace 69/12 kV distribution transformer T1 at the Hemenway substation | IN | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 69 | 0 | 1700000
A in MTEP20 | Central | SIGE | 15958 | Rockport 69/12 kV T2 Repl. | Replace 69/12 kV distribution transformer T2 at the Rockport substation | IN | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 69 | 12 | 1700000
A in MTEP20 | Central | AmerenMO | 16504 | Reconfigure Viburnum 161/34 kV Substation | Install 2 161 kV line breakers and 1 161 kV circuit switcher on the transformer to split the CLK-CMCO-2 line and create 2 circuits into Viburnum Substation. | MO | 2023-12-01 | Other | Reliability | 2023-12-01 | 161 | 34 | 1600000
A in MTEP20 | Central | AmerenMO | 17805 | Rebuild Campbell-Maline 138 kV lines 1/2 | Replace existing conductor with composite core conductor on branches 93 and 94. | MO | 2021-12-10 | Other | Reliability | 2021-12-01 | 138 | 0 | 1600000
A in MTEP20 | Central | AmerenMO | 17909 | Upgrade Campbell-Euclid 161 kV line | Replace shield wires on the Campbell-Euclid-4 circuit. Replace structures and crossarms as needed. | MO | 2021-12-01 | Other | Age and Condition | 2021-12-01 | 138 | 0 | 1600000
A in MTEP20 | West | MRES | 18906 | McLeod Cap Bank Addition | The August 2016 West DPP cycle identified a network upgrade at the McLeod 230 kV bus. The project involves adding a switchable 50 MVAR capacitor bank to mitigate low voltages. | MN |  | GIP |  | 2021-09-01 | 230 | 0 | 1600000
A in MTEP20 | West | MP | 17870 | National Taconite Breaker Replacements | Replace existing breakers and associated equipment at National Taconite Substation | MN |  | Other | Age and Condition | 2021-12-31 | 115 | 0 | 1580000
A in MTEP20 | East | ITCT | 18525 | Brownstown 3 345 kV - Upgrade 345 kV Switches | Upgrade five (5) 345 kV switches (“ED”, “FD”, “FH”, “FK”, “FO”) at Brownstown 3 345 kV station. | MI | 2021-12-31 | Other | Reliability | 2021-12-31 | 345 | 0 | 1560000
A in MTEP20 | West | GRE | 17986 | Lake Jennie Tap 69 kV Line Rebuild | Rebuild 2.77 miles of Lake Jennie Tap line. | MN | 2021-11-01 | Other | Age and Condition | 2021-11-01 | 69 | 0 | 1550000
A in MTEP20 | West | MEC | 18183 | Midport 161 kV Capacitor | Add 161 kV, 50 MVAR capacitor at Midport. Includes addition of 161 kV circuit breakers on 161 kV line terminals. | IA | 2021-12-31 | GIP |  | 2021-12-31 | 161 | 0 | 1545000
A in MTEP20 | West | ITCM | 17724 | Sixth Street 115kV Substation Retirement | Once the remaining 34.5 kV lines at the Sixth St Substation are converted to 69 kV, the remaining substation equipment should be retired, including any control enclosures and fence, etc. The 34.5 kV lines will be connected to bypass the substation as part of the conversion work, but the 115 kV lines will need to be connected to bypass the substation as part of the substation retirement project. The communications currently routed through Sixth Street will also need to be moved/removed before the retirement can be completed. | IA | 2023-12-31 | Other | Age and Condition | 2023-01-31 | 115 | 34 | 1506540
A in MTEP20 | East | ITCT | 17124 | Frisbie - Midtown 120kV Cable Relocation | Relocate the Frisbie-Midtown underground circuit out of the current location in the Milwaukee Ave bridge over I-75. Utilize 954 ACSR on overhead structures from each side of I-75. | MI | 2021-06-01 | Other | Other Local Needs | 2021-06-01 | 120 | 0 | 1500000
A in MTEP20 | East | METC | 17997 | Donaldson Creek Interconnection Phase 2 | Build a new breaker row 13, breakers 13B7 and 13M9 with associated switches and terminate a new WPSC line to Rodgers. | MI | 2022-06-01 | Other | Other Local Needs | 2022-06-01 | 138 | 0 | 1450000
A in MTEP20 | West | ATC | 19246 | J864 J870 J871 J947 MPFCA Common Use Upgrades | Each individual Customer is responsible for a proportionate percentage share of the Common Use Upgrades estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU - J864 Customer is seeking interconnection service for 49.98 MW - J870 Customer is seeking interconnection service for 200 MW - J871 Customer is seeking interconnection service for 100 MW - J947 Customer is seeking interconnection service for 200 MW | WI | 2021-03-31 | GIP |  | 2021-03-31 | 138 | 0 | 1406518
A in MTEP20 | Central | AmerenIL | 17604 | Upgrade Stallings-Roxford 345 kV line (4581) | Upgrade 345 kV switches V4A and V4b to 3000A. Remove the 2000A wave trap. Install OPGW. | IL | 2023-12-01 | Other | Reliability | 2023-12-01 | 345 | 0 | 1400000
A in MTEP20 | West | GRE | 17988 | Lake Mary 115 kV Conversion | Convert the GRE/REA Lake Mary substation from 41.6 kV to 115 kV service. | MN | 2021-12-31 | Other | Reliability | 2022-11-30 | 115 | 0 | 1400000
A in MTEP20 | West | XEL | 17989 | EREPC Wellington Interconnection | Install new 3 way switch and 4 mile 69Kv line to new EREPC Wellington substation | MN | 2020-09-01 | Other | Load Growth | 2020-09-01 | 69 | 0 | 1320000
A in MTEP20 | Central | AmerenMO | 17344 | Upgrade Berkeley 138 kV Substation | Replace 138 kV bus tie 1-2 and 2-3 breakers. Upgrade position to 2000A. | MO | 2021-12-01 | Other | Age and Condition | 2021-12-01 | 138 | 0 | 1300000
A in MTEP20 | Central | AmerenMO | 17625 | Upgrade McClay 138 kV Substation | Add breakers to each of the 138 kV lines and upgrade relays. | MO | 2022-12-01 | Other | Reliability | 2022-12-01 | 138 | 0 | 1300000
A in MTEP20 | West | MP | 15593 | 25 Line Upgrade | Increase rating of Hibbing - Virginia 115 kV Line | MN | 2022-10-31 | BRP |  | 2022-03-31 | 115 | 0 | 1280000
A in MTEP20 | West | MP | 15592 | Hibbing 14 Line Upgrade | Increase rating of Hibbing - 14 Line Tap 115 kV Line | MN | 2022-10-31 | BRP |  | 2021-10-31 | 115 | 0 | 1230000
A in MTEP20 | West | ITCM | 18113 | J523 Generator Interconnection Network Upgrades | Add two 161kV breakers in series with the bus-tie breaker 6620 to create a breaker and 1/2 row. Relocate the line for the Adams 345/161kV transformer from the existing terminal to a new terminal position on a breaker and 1/2 row (install dead end, coordinate relocation of metering with Xcel, and replace necessary equipment to accommodate the relocation of the transformer terminal). All new equipment must be capable of 2000 amp operation. | MN | 2021-09-15 | GIP |  | 2021-09-15 | 161 | 161 | 1217897
A in MTEP20 | Central | AmerenIL | 17907 | New Prairie Wolf Solar Farm (J949) interconnection | Add terminal facilities including one 138 kV breaker at Kansas Substation. | IL | 2021-10-01 | GIP |  | 2021-10-01 | 138 | 0 | 1200000
A in MTEP20 | Central | AmerenIL | 18039 | Upgrade Havana 138 kV substation | Replace breakers HAV-138KV BKR 1406, HAV-138KV BT BKR 1302 and HAV-138KV BKR 1422 at Havana Substation. | IL | 2022-12-01 | Other | Age and Condition | 2022-12-01 | 138 | 0 | 1200000
A in MTEP20 | Central | AmerenIL | 18316 | New Big River Solar (J853) interconnection | Add terminal facilities to the Norris City North 138 kV bus to interconnect J853. | IL | 2021-05-28 | GIP |  | 2021-05-28 | 138 | 0 | 1200000
A in MTEP20 | Central | PPI | 18120 | Upgrade Berlin-Amos 69 kV Line | Upgrade 3-mile portion of Berlin to Amos 69 kV line from 4/0 ACSR to 336.4 MCM ACSR associated with fiber and distribution installation | IL | 2021-12-31 | Other | Age and Condition | 2021-12-31 | 69 | 69 | 1200000
A in MTEP20 | Central | PPI | 18159 | Upgrade East Lanesville 138/69 kV transformer | Upgrade existing 37.33 MVA transformer with 84 MVA unit. Existing transformer will be moved to Kuhlman | IL | 2022-12-31 | Other | Reliability | 2022-12-31 | 138 | 69 | 1200000
A in MTEP20 | Central | SIGE | 15860 | Broadview 69/12 kV Dist. T2 Repl | Replace 69/12 kV distribution transformer T2 at the Broadview substation | IN | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 69000 | 0 | 1200000
A in MTEP20 | Central | SIGE | 15940 | East Industrial Trans. Repl. | Replace the 69/12 kV distribution transformer at the East Industrial substation. | IN | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 69 | 0 | 1200000
A in MTEP20 | Central | SIGE | 15948 | Fairlawn 69/12 kV Dist. T1 Repl. | Replace the 69/12 kV distribution transformer T1 at the Fairlawn substation. | IN | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 69 | 0 | 1200000
A in MTEP20 | Central | SIGE | 15949 | Fuquay 69/12 kV Dist. T1 Repl. | Replace 69/12 kV distribution transformer T1 at the Fuquay substation | IN | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 69 | 0 | 1200000
A in MTEP20 | Central | SIGE | 15960 | St. Phillips 69/12 kV T1 Repl. | Replace 69/12 kV distribution transformer T1 at the St. Phillips substation | IN | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 69 | 12 | 1200000
A in MTEP20 | West | MEC | 18127 | Sycamore: 345 kV Equipment Upgrades | At the Sycamore substation, replace two 345 kV circuit breakers, associated disconnect switches, and jumpers to increase the rating of the Grimes-Sycamore 345 kV south line. | IA | 2021-06-30 | GIP |  | 2021-06-30 | 345 | 0 | 1200000
A in MTEP20 | West | MEC | 18280 | Floyd 161-69 kV Transformer Terminal Upgrade | Replace terminal equipment adjacent to Floyd Substation 161-69 kV Transformer AB. | IA |  | Other | Reliability | 2020-11-01 | 161 | 69 | 1200000
A in MTEP20 | West | XEL | 17985 | Rosemount 2nd XFMR | Add second 115/34.5 kV transformer to Rosemount Substation | MN | 2020-12-15 | Other | Reliability | 2020-12-15 | 115 | 34.5 | 1200000
A in MTEP20 | West | OTP | 10043 | Jamestown 345 Breaker Addition | Install an additional 345 kV breaker to meet TPL-001-4 Compliance Standard. | ND | 2020-07-03 | BRP |  | 2020-07-03 | 345 | 0 | 1178852
A in MTEP20 | Central | AmerenMO | 18139 | Upgrade Labadie 345 kV substation | Upgrade switches and CTs to 3000A. Labadie 345 kV bus-tie 2-3 Upgrade | MO | 2022-12-01 | BRP |  | 2022-12-01 | 345 | 0 | 1100000
A in MTEP20 | Central | SIGE | 15987 | Berry Plastics Dist. XFMR Repl. | Replace one of the distribution transformers serving Berry Plastics. (PSP project) | IN | 2021-12-31 | Other | Age and Condition | 2024-12-31 | 69 | 0 | 1100000
A in MTEP20 | East | ITCT | 18205 | Upgrade Red Run 120 kV Station Equipment | Upgrade the station equipment at Redrun 120 kV station. | MI | 2023-12-31 | BRP |  | 2023-12-31 | 120 | 0 | 1100000
A in MTEP20 | East | ITCT | 19607 | Brownstown - Navarre #2 230 kV Sag Remediation | Remediate the sag on the Brownstown - Navarre #2 230 kV circuit up to the conductor limit and upgrade station equipment at Navarre 230 kV Station | MI | 2024-06-01 | BRP |  | 2024-06-01 | 230 | 0 | 1070000
A in MTEP20 | West | MEC | 18128 | Raun: Retire 13 kV Reactors | Retire the three 13.8 kV reactors at Raun substation and replace relaying and switching device on Raun 345 kV reactor | IA | 2021-06-01 | Other | Reliability | 2021-06-01 | 345 | 0 | 1030000
A in MTEP20 | East | ITCT | 16024 | River Rouge 120 kV Capacitor | Install a three 18 MVAR capacitors at River Rouge 120 kV station. | MI | 2023-12-31 | BRP |  | 2023-12-31 | 120 | 0 | 1030000
A in MTEP20 | East | METC | 18384 | Sag Remediation Bullock - Saginaw River | Increase the sag limits on the Bullock to Gleaner J and Gleaner J to Hacket J sections of the Bullock - Saginaw River 138 kV circuit | MI | 2020-12-31 | GIP |  | 2020-12-31 | 138 | 0 | 1024800
A in MTEP20 | Central | SIGE | 18268 | Grandview Generation Interconnect | Installation of Interconnection Facilities and Network Upgrades for generation interconnection project J783 at the Grandview 69 kV substation. | IN | 2021-04-01 | GIP |  | 2021-04-01 | 69 | 0 | 1017496
A in MTEP20 | Central | AmerenIL | 18045 | Upgrade Murdock 138 kV substation | Install a 138 kV circuit switcher on the high-side of XFMR #1 at Murdock Substation. | IL | 2023-06-01 | Other | Reliability | 2023-06-01 | 138 | 0 | 1000000
A in MTEP20 | Central | AmerenIL | 18705 | Bypass Coffeen 345 kV Switchyard | Bypass the Coffeen 345 kV switchyard by re-terminating the lines at the Coffeen North 345 kV substation. | IL | 2020-06-01 | Other | Reliability | 2020-06-01 | 345 | 0 | 1000000
A in MTEP20 | Central | AmerenMO | 17865 | Upgrade Lakeshire 161 kV substation | Replace 40 kA breakers on positions H and U for cap banks 2A and 2B with 50 kA breakers. | MO | 2022-12-01 | Other | Reliability | 2022-12-01 | 138 | 0 | 1000000
A in MTEP20 | West | GRE | 18025 | Cannon River Park 115 kV Substation | Construct a new 115 kV transmission line from Cannon River Park to the Cannon River Park tap in the Xcel 0832 line near the Xcel Faribault Energy Park. | MN | 2021-03-05 | Other | Load Growth | 2021-03-05 | 115 | 0 | 1000000
A in MTEP20 | West | MP | 18064 | Hibbing Breaker Replacements | Replace existing 115 kV circuit breakers and associated equipment at Hibbing Substation | MN | 2022-10-31 | Other | Age and Condition | 2022-10-31 | 115 | 0 | 1000000
A in MTEP20 | East | CETO | 17993 | Muskegon #2 Line Rebuild | Rebuild a portion of the Muskegon #2 138 kV Line, approximately 2.1 miles, utilizing 138 kV single circuit construction | MI | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 138 | 0 | 1000000
A in MTEP20 | East | WPSC | 18015 | Cadillac Substation Line Modifications | Line modifications including structure relocation and switch replacement in order to accommodate a new Cadillac distribution station. | MI | 2021-12-31 | Other | Load Growth | 2021-12-31 | 69 | 0 | 1000000
A in MTEP20 | Central | BREC | 18012 | Hardinsburg Upgrade | Add a 161 kV breaker and upgrade protection equipment | KY | 2022-06-01 | Other | Reliability | 2023-06-01 | 161 | 0 | 980000
A in MTEP20 | East | METC | 18133 | Station Eq. Upgrades Pere Marquette 138 kV 5M9 & 7W8 | Upgrade two breakers (at positions 5M9 and 7W8) and other terminal station equipment at the Pere Marquette 138 kV station. | MI | 2022-12-31 | BRP |  | 2022-12-31 | 138 | 0 | 970000
A in MTEP20 | East | ITCT | 18313 | Sag Remediation of Bauer - Pontiac 345 kV | Raise the sag limit on the 2-954 ACSR 54/7 conductor span of the Bauer - Pontiac 345 kV circuit to achieve a summer emergency rating of at least 1258 MVA. | MI | 2020-12-31 | GIP |  | 2020-12-31 | 345 | 0 | 961200
A in MTEP20 | West | OTP | 19685 | OTP Hoot Lake 115/41.6 kV Transformer Replacement | Replace Hoot Lake 115/41.6 kV Transformer with 115/41.6/34.5 kV Transformer with higher capacity and LTC. | MN | 2021-12-31 | Other | Age and Condition | 2021-12-31 | 115 | 41.6 | 950000
A in MTEP20 | West | ITCM | 17966 | Metform Substation 69kV Conversion | ITC will be converting the Metform Substation to 69kV. All network path 69kV equipment will be capable of 1200A or greater. All network path switches will need to be replaced to be capable of 1200A or greater. ITC will retire the bypass bus and switches. | IL | 2021-12-31 | Other | Age and Condition | 2021-12-31 | 69 | 69 | 925200
A in MTEP20 | West | ATC | 19269 | J864 J870 J871 MPFCA Common Use Upgrades | Each individual Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. -J864 Customer is seeking interconnection service for 49.98 MW -J870 Customer is seeking interconnection service for 200 MW -J871 Customer is seeking interconnection service for 100 MW | WI | 2021-03-31 | GIP |  | 2021-03-31 | 138 | 0 | 915243
A in MTEP20 | South | SMEPA | 18224 | Batesville 161 kV Bus Reconfigure | Reconfigure the Batesville 161kV substation so that the Batesville - Batesville TVA ties lines do not share a common breaker. | MS | 2022-06-01 | BRP |  | 2022-06-01 | 161 | 0 | 910000
A in MTEP20 | Central | AmerenIL | 17864 | Upgrade Cahokia 345/138 kV substation | Replace OCB H27 on the C-GRAT-3 position and OCB H35 on the C-RUSL-2 positon with symmetrically rated SF6 55 kA circuit breakers. | IL | 2020-12-01 | Other | Reliability | 2022-12-01 | 138 | 0 | 900000
A in MTEP20 | Central | AmerenIL | 18322 | New City of Roses Wind (J848) interconnection | Add terminal facilities at the Pana 138 kV Substation to make the inteconnection for J848. | IL | 2021-05-28 | GIP |  | 2021-05-28 | 138 | 0 | 900000
A in MTEP20 | Central | AmerenIL | 18706 | Bypass Duck Creek 345 kV Switchyard | Bypass the Duck Creek 345 kV switchyard. | IL | 2020-06-01 | Other | Reliability | 2020-06-01 | 345 | 0 | 900000
A in MTEP20 | Central | IPL | 17884 | Replace Southeast #4 Breaker | Replacement of one (1) 138 kV breaker at Southeast, #4 | IN | 2025-12-31 | BRP |  | 2025-12-31 | 138 | 0 | 900000
A in MTEP20 | Central | IPL | 17885 | Replace Southeast #6 Breaker | Replacement of one (1) 138 kV breaker at Southeast, #6 | IN | 2025-12-31 | BRP |  | 2025-12-31 | 138 | 0 | 900000
A in MTEP20 | Central | IPL | 17886 | Replace Southeast #8 Breaker | Replacement of one (1) 138 kV breaker at Southeast, #8 | IN | 2021-12-31 | BRP |  | 2025-12-31 | 138 | 0 | 900000
A in MTEP20 | Central | IPL | 17887 | Replace Stout South #1A Breaker | Replacement of one (1) 138 kV breaker at Stout South #1A | IN | 2023-12-31 | BRP |  | 2023-12-31 | 138 | 0 | 900000
A in MTEP20 | Central | IPL | 17888 | Replace Southport #2 Breaker | Replacement of one (1) 138 kV breaker at Southport, #2 | IN | 2023-12-31 | BRP |  | 2023-12-31 | 138 | 0 | 900000
A in MTEP20 | East | WPSC | 14005 | Hammond Bay Interconnection Line | Construct approximately 2 miles of new transmission line to connect the Hammond Bay Distribution Station to METC’s 138 kV transmission line. | MI | 2023-12-31 | Other | Load Growth | 2022-12-31 | 138 | 0 | 900000
A in MTEP20 | West | XEL | 18444 | J526 Panther - HUC-McLeod upgrade | Replace structures on HUC - McLeod 230kV line to increase capacity to accommodate J526 wind generation. | MN | 2020-03-31 | GIP |  | 2020-03-31 | 230 | 0 | 880000
A in MTEP20 | West | ATC | 18566 | J807 GIC Falcon SS Addition - Generator Interconnection Facilities and Network Upgrades | A 41.4 MW wind farm in Lafeyette County, Wisconsin. Customer has requested a Point of Interconnection (POI) at a new terminal at the existing 138kV Falcon Substation. | WI | 2021-08-27 | GIP |  | 2021-08-27 | 138 | 0 | 870186
A in MTEP20 | East | METC | 18043 | Sag Remediation Scott Lake - Argenta 138kV | The proposed solution is to remediate sag limit on the Scott Lake - Trowbridge 138kV section to increase its summer emergency rating to a minimum of 219 MVA (917 Amps) and also remediate sag limit on the Trowbridge - Argenta 138kV section to increase its summer emergency rating to a minimum of 235 MVA (985 Amps). | MI | 2023-12-31 | BRP |  | 2023-12-31 | 138 | 0 | 830000
A in MTEP20 | East | METC | 18004 | Sag Remediation Meyer - Briggs & Stratton Jct. 138kV | The proposed solution is to remediate the sag limit on the 6.02 mile-long length of 795 ACSR conductor of the Tanner – Briggs & Stratton Jct. 138kV section to increase its summer emergency rating to a minimum of 262 MVA/1096 Amps. Also completely remediate the sag limit on the 8.25 mile-long length of 795 ACSR conductor of the Meyer - Tanner 138kV line to conductor limit. | MI | 2023-12-31 | BRP |  | 2023-12-31 | 138 | 0 | 807000
A in MTEP20 | Central | AmerenIL | 18037 | Upgrade Decatur N 27th Street 138 kV substation | Replace breakers N27D-138KV BKR 1522 and N27D-138KV BKR 1602 at Decatur North 27th street. | IL | 2022-12-01 | Other | Age and Condition | 2022-12-01 | 138 | 0 | 800000
A in MTEP20 | Central | AmerenIL | 18081 | Upgrade Newton 138 kV substation | Replace 138 kV breakers NWTY-138KV LT 1869 and NWTY-138KV LT 1868 at the Newton switchyard. | IL | 2023-12-01 | Other | Age and Condition | 2023-12-01 | 138 | 0 | 800000
A in MTEP20 | Central | AmerenIL | 18093 | Upgrade Fargo 138 kV substation | Replace breakers FARG-138KV BKR & LINE 1394 and FARG-138KV BKR 1371 at Fargo Substation. | IL | 2024-12-01 | Other | Age and Condition | 2024-12-01 | 138 | 0 | 800000
A in MTEP20 | Central | AmerenIL | 18095 | Upgrade Gibson City S 138 kV substation | Replace breakers GBCS-138KV LINE 1524 and GBCS-138KV LINE 1522 at Gibson City South Substation. | IL | 2024-12-01 | Other | Age and Condition | 2024-12-01 | 138 | 0 | 800000
A in MTEP20 | Central | AmerenIL | 18105 | Upgrade Makanda N 138 kV substation | Replace breakers MAKN-138KV LINE 1674 and MAKN-138KV LINE 1672 at Makanda North Substation. | IL | 2019-09-12 | Other | Age and Condition | 2024-06-01 | 138 | 0 | 800000
A in MTEP20 | Central | AmerenIL | 18106 | Upgrade Marblehead N 138 kV substation | Replace breakers MRBN-138KV LINE 1852 and MRBN-161/138KV XFMR 1 at Marblehead north substation. | IL | 2024-06-01 | Other | Age and Condition | 2024-06-01 | 161 | 138 | 800000
A in MTEP20 | Central | AmerenIL | 18108 | Upgrade Watseka 138 kV substation | Replace breakers WATK-138KV LINE 1372 and WATK-138KV LINE 1374 at Watseka Substation. | IL | 2024-12-01 | Other | Age and Condition | 2024-12-01 | 138 | 0 | 800000
A in MTEP20 | Central | AmerenIL | 18279 | Upgrade South Ottawa 138 kV substation | Install 138 kV bus-tie breaker at the switch 1516 position at South Ottawa | IL | 2022-12-01 | Other | Reliability | 2022-12-01 | 138 | 0 | 800000
A in MTEP20 | West | MEC | 18050 | Sub 77: Add 161 kV Circuit Breaker | Add new 161 kV circuit breaker at Sub 77 on the 161 kV line terminal to Sub 91. | IA | 2021-12-01 | Other | Reliability | 2021-12-01 | 161 | 0 | 800000
A in MTEP20 | East | ITCT | 19526 | Stephens 120 kV Install Breaker GP | Install the GP breaker between Bus 105 and 106 at the Stephens 120 kV station including the associated GQ disconnect, and replacement of GO disconnect | MI | 2022-12-31 | Other | Reliability | 2022-12-31 | 120 | 0 | 786389
A in MTEP20 | West | MEC | 18125 | Grimes-Beaver Creek 345 kV Uprate | Replace structures to uprate the Grimes-Beaver Creek 345 kV line. | IA | 2020-12-31 | GIP |  | 2020-12-31 | 345 | 0 | 753000
A in MTEP20 | Central | AmerenMO | 17824 | Upgrade Spencer Creek 345 kV substation | Replace switches on 345kv pos V3, V5, V6, V7 and reactor position. | MO | 2021-12-01 | Other | Age and Condition | 2021-12-01 | 345 | 0 | 700000
A in MTEP20 | West | MP | 17871 | Laskin Breaker Replacements | Replace breakers and associated equipment at Laskin Substation | MN | 2023-12-31 | Other | Age and Condition | 2023-12-31 | 115 | 0 | 700000
A in MTEP20 | West | MP | 18065 | Verndale Substation Modernization | Replace existing 115 kV circuit breakers at Verndale Substation | MN | 2024-12-31 | Other | Age and Condition | 2024-12-31 | 115 | 0 | 700000
A in MTEP20 | West | XEL | 17984 | New Turtle Lake Sub | A new substation will be built to replace existing distribution Turtle Lake sub allow future load. Existing Turtle Lake sub will be retired once distribution conversion is complete. | WI | 2021-06-15 | Other | Reliability | 2021-06-15 | 69 | 23.9 | 700000
A in MTEP20 | South | SMEPA | 18182 | Cole Road 69 kV Capacitor Bank | Install new 69kV capacitor bank at Cole Road substation. | MS | 2021-03-01 | Other | Reliability | 2021-03-01 | 69 | 0 | 660000
A in MTEP20 | East | ITCT | 18745 | Reconductor Bunce Creek- Scott (B3N) 220kV | The proposed solution is to reconductor approximately 0.44 mile of the Bunce Creek- Scott (B3N) 220kV circuit using 795 ACSS conductor. | MI | 2024-06-01 | BRP |  | 2024-06-01 | 220 | 0 | 660000
A in MTEP20 | South | SMEPA | 17524 | Batesville 161kV Ties Reconductor | Cooperative Energy’s Network Upgrades shall consist of reconductoring both Batesville to Batesville TVA 161kV tie lines with Aluminum Conductor Composite Reinforced (ACCR) conductor. | MS | 2021-06-01 | GIP |  | 2021-06-01 | 161 | 0 | 650000
A in MTEP20 | Central | SIGE | 15952 | Culley 138 kV OCB 2200 2277 Repl. | Replace two 138 kV oil circuit breakers (OCBs) with gas circuit breakers (GCBs). Breaker numbers 2200 and 2277 | IN | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 138 | 0 | 615000
A in MTEP20 | Central | SIGE | 15953 | Replace Heidelbach OCB - 2177 2277 | Replace two 138 kV oil circuit breakers (OCBs) with gas circuit breakers (GCBs) at the Heidelbach station - breaker numbers 2177 & 2277. | IN | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 138 | 0 | 615000
A in MTEP20 | Central | AmerenIL | 17866 | Upgrade Neoga 345/138 kV substation | Replace OCB 1402 on the HUTY-NEGS-1 position with a symmetrically rated 40 kA SF6 breaker. | IL | 2022-12-01 | Other | Reliability | 2022-12-01 | 138 | 0 | 600000
A in MTEP20 | Central | AmerenMO | 17346 | Upgrade Rivermines 138 kV substation | Replace 138kV breakers on bus tie 1-2 and bus tie 2-3 | MO | 2022-12-01 | Other | Age and Condition | 2022-12-01 | 138 | 0 | 600000
A in MTEP20 | Central | AmerenMO | 17867 | Upgrade Gray Summit 345/161 kV substation | Replace the Bus-Tie 1-2 breaker at Gray Summit with a symmetrically rated 40 kA circuit breaker. | MO | 2022-12-01 | Other | Reliability | 2022-12-01 | 138 | 0 | 600000
A in MTEP20 | West | ATC | 19267 | J807 J864 J870 J871 J947 MPFCA Common Use Upgrades | Each individual Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. -J807 Customer is seeking interconnection service for 41.4 MW -J864 Customer is seeking interconnection service for 49.98 MW -J870 Customer is seeking interconnection service for 200 MW -J871 Customer is seeking interconnection service for 100 MW -J947 Customer is seeking interconnection service for 200 MW | WI | 2021-03-31 | GIP |  | 2021-03-31 | 138 | 0 | 537753
A in MTEP20 | East | CETO | 17991 | CE Pole & Line Equipment Replacement Program - 2022 | Replace damaged or defective poles, towers, cross arms, insulators, guying, and switches, as needed, to maintain the lines' condition | MI | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 138 | 0 | 530000
A in MTEP20 | East | ITCT | 18201 | Sag Remediation of Hunters Creek – Stratford 120 kV | Remediate the sag on the Hunters Creek – Stratford 120 kV line to at least 175 MVA for summer emergency rating. | MI | 2023-12-31 | BRP |  | 2023-12-31 | 120 | 0 | 510000
A in MTEP20 | East | CETO | 17994 | Four Mile-Northridge 138 kV Lines | Construct two new 138 kV lines from Four Mile Substation to the new Northridge Substation | MI | 2022-12-31 | Other | Other Local Needs | 2022-12-31 | 138 | 0 | 500000
A in MTEP20 | East | CETO | 18272 | Dort-Mott Lake 138 kV Lines | Construct two new 138 kV lines from Dort Substation to the new Mott Lake Substation | MI | 2024-06-01 | Other | Other Local Needs | 2024-06-01 | 138 | 0 | 500000
A in MTEP20 | Central | AmerenIL | 18035 | Upgrade Eastern 138 kV substation | Replace TAZW-138KV BKR 1321-73 at Eastern Substation | IL | 2022-12-01 | Other | Age and Condition | 2022-12-01 | 138 | 0 | 500000
A in MTEP20 | Central | AmerenIL | 18036 | Upgrade Pioneer 138 kV substation | Replace breaker PION-138KV LINE 1326 at Pioneer Substation. | IL | 2022-12-01 | Other | Age and Condition | 2022-12-01 | 138 | 0 | 500000
A in MTEP20 | Central | AmerenIL | 18075 | Upgrade North Decatur 138 kV substation | Replace 138 kV breaker NDEC-138KV BKR 1602 at North Decatur Substation. | IL | 2023-12-01 | Other | Age and Condition | 2023-12-01 | 138 | 0 | 500000
A in MTEP20 | Central | AmerenIL | 18076 | Upgrade Steeleville 138 kV substation | Replace 138 kV breaker STVL-138KV BKR 1636 at Steeleville Substation. | IL | 2023-12-01 | Other | Age and Condition | 2023-12-01 | 138 | 0 | 500000
A in MTEP20 | Central | AmerenIL | 18077 | Upgrade Vermilion 138 kV substataion | Replace 138 kV breaker VERM-138KV BKR 1306 at Vermilion Substation. | IL | 2023-12-01 | Other | Age and Condition | 2023-12-01 | 138 | 0 | 500000
A in MTEP20 | Central | AmerenIL | 18078 | Upgrade Carbondale NW 138 kV substation | Replace 138 kV breaker CDNW-138KV LINE 1744 at Carbondale NW Substation. | IL | 2023-12-01 | Other | Age and Condition | 2023-12-01 | 138 | 0 | 500000
A in MTEP20 | Central | AmerenIL | 18079 | Upgrade Mason City W 138 kV substation | Replace 138 kV breaker MSCW-138KV LINE 1684 at Mason City West substation. | IL | 2023-12-01 | Other | Age and Condition | 2023-12-01 | 138 | 0 | 500000
A in MTEP20 | Central | AmerenIL | 18091 | Upgrade Clinton 345 kV substation | Replace breaker CLNT-345KV BKR 4506 at Clinton switchyard. | IL | 2023-12-01 | Other | Age and Condition | 2023-12-02 | 345 | 0 | 500000
A in MTEP20 | Central | AmerenIL | 18092 | Replace East Galesburg 138/69 kV transformer | Replace breaker EGAL-138/69KV AUTO XFMR 2 at East Galesburg Substation. | IL | 2024-12-01 | Other | Age and Condition | 2024-12-01 | 138 | 0 | 500000
A in MTEP20 | Central | AmerenIL | 18098 | Upgrade Grand Tower 138 kV substation | Replace breaker GDTY-138KV LT 1449 at Grand Tower Switchyard. | IL | 2024-12-01 | Other | Age and Condition | 2024-12-01 | 138 | 0 | 500000
A in MTEP20 | Central | AmerenIL | 18102 | Upgrade Hines 138 kV substation | Replace breaker HINE-138KV BKR & LINE 1357 at Hines Substation. | IL | 2023-12-01 | Other | Age and Condition | 2023-12-01 | 138 | 0 | 500000
A in MTEP20 | Central | AmerenIL | 18104 | Upgrade Latham 345 kV substation | Replace breaker LATM-345KV POS V19 at Latham Substation. | IL | 2023-12-01 | Other | Age and Condition | 2023-12-01 | 345 | 0 | 500000
A in MTEP20 | Central | AmerenIL | 18107 | Upgrade Tilton Energy Center 138 kV substation | Replace breaker TEC-138KV LINE TIE BKR 1320 at Tilton Energy Center. | IL | 2023-12-01 | Other | Age and Condition | 2023-12-01 | 138 | 0 | 500000
A in MTEP20 | Central | AmerenIL | 18310 | New Dressor Plains Solar (J811) interconnection | Add terminal facilities to Ramsey East Substation. | IL | 2021-05-28 | GIP |  | 2021-05-28 | 138 | 0 | 500000
A in MTEP20 | Central | AmerenMO | 12428 | Replace Stoddard 161 kV breakers | Replace 1-161 kV breaker at Stoddard | MO | 2021-12-01 | Other | Reliability | 2021-12-01 | 161 | 0 | 500000
A in MTEP20 | Central | DEI | 18306 | New H.E. Batesville 138/12 kV new substation | H.E. Batesville 138/12 kV substation: new sub to be located in the 13833 ckt between Batesville 138 kV and Laurel 138 kV | IN |  | Other | Load Growth | 2021-12-31 | 138 | 12 | 500000
A in MTEP20 | East | METC | 18187 | Sag Remediation Pere Marquette – Stronach 138 kV | Completely remediate the sag on the Pere Marquette – Stronach 138 kV line and replace terminal equipment at the Stronach end of the line. | MI | 2023-12-31 | BRP |  | 2023-12-31 | 138 | 0 | 465000
A in MTEP20 | West | ATC | 19226 | J807 J819 J864 J870 J871 J947 MPFCA Common Use Upgrades | Each individual Customer is responsible for a proportionate percentage share of the Common Use Upgrades estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. -J807 Customer is seeking interconnection service for 41.4 MW -J819 Customer is seeking interconnection service for 99.9 MW -J864 Customer is seeking interconnection service for 49.98 MW -J870 Customer is seeking interconnection service for 200 MW -J871 Customer is seeking interconnection service for 100 MW -J947 Customer is seeking interconnection service for 200 MW | WI | 2021-03-31 | GIP |  | 2021-03-31 | 69 | 0 | 440000
A in MTEP20 | East | ITCT | 18200 | Sag Remediation of Hemphill – Hunters Creek 120 kV | Remediate the sag on the Hemphill – Hunters Creek 120 kV line up to the conductor’s limit. | MI | 2023-12-31 | BRP |  | 2023-12-31 | 120 | 0 | 430000
A in MTEP20 | East | CETO | 17990 | CE Substation Equipment Replacement Program - 2022 | Replace damaged or defective substation equipment with new equipment | MI | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 138 | 0 | 410000
A in MTEP20 | Central | PPI | 18115 | Relocate Kampsville Capacitor Bank to Pearl | Move 2.4 MVAR capacitor bank from Kampsville to Pearl Substation | IL | 2020-12-31 | Other | Reliability | 2020-12-31 | 69 | 69 | 400000
A in MTEP20 | Central | PPI | 18167 | New Smithfield 69 kV capacitor bank (4.8 Mvar) | Addition of 4.8 Mvar capacitor bank in Spoon River Electric Cooperative | IL | 2024-12-31 | Other | Reliability | 2024-12-31 | 69 | 69 | 400000
A in MTEP20 | Central | PPI | 18169 | New Macomb 69 kV capacitor bank (4.8 Mvar) | Addition of 4.8 Mvar capacitor bank in McDonough Power Cooperative | IL | 2026-12-31 | Other | Reliability | 2026-12-31 | 69 | 69 | 400000
A in MTEP20 | West | ATC | 19245 | J807 J819 J850 MPFCA Common Use Upgrades | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. - J807 is seeking interconnection service for 41.4 MW - J819 is seeking interconnection service for 99.9 MW - J850 is seeking interconnection service for 250 MW | WI | 2021-03-31 | GIP |  | 2021-03-31 | 138 | 0 | 372880
A in MTEP20 | West | MDU | 19485 | Big Stone-Browns Valley 230 Line Structure Replacements | GI network upgrade to replace structures on Big Stone-Browns Valley 230 kV line. | SD | 2020-06-22 | GIP |  | 2020-06-22 | 230 | 0 | 350000
A in MTEP20 | West | MEC | 18188 | Diamond Trail-Hills 345 kV Uprate | Replace structures to uprate the Diamond Trail (J530 POI) - Hills 345 kV line. | IA | 2020-06-30 | GIP |  | 2020-06-30 | 345 | 0 | 350000
A in MTEP20 | West | XEL | 18033 | Hydro Lane Expansion | Expand Hydro Lane substation to support increased customer load | MN | 2020-05-15 | Other | Load Growth | 2020-05-15 | 69 | 12.5 | 350000
A in MTEP20 | West | XEL | 18038 | Kinnickinick Substation Rebuild | Build new Kinnickinick Distribution substation near existing Kinnickinick substation. | WI |  | Other | Age and Condition | 2020-12-15 | 69 | 23.9 | 350000
A in MTEP20 | Central | CWLP | 18140 | Reconductor Chatham Main-Chatham Independence 138 kV line | Reconductor Chatham Main - Chatham Independence 138 kV line with 795 ACSS. | IL | 2021-03-01 | BRP |  | 2021-03-01 | 138 | 0 | 350000
A in MTEP20 | West | ITCM | 17738 | Thompson MacTavish 69kV Substation Interconnection | ITC will install an ~0.02 mile tap line to IPL’s new Thompson MacTavish 69/24.9kV Distribution Substation. This substation will be Open Air Single Bus with a 12/20MVA 69/24.9kV transformer and high side breaker. The substation will be located on one of the two land options available to IPL. The Thompson and Buffalo Center substations will be retired on future EI sketches once IPL moves the loads from those substations to Thompson MacTavish. Coordinate with IPL and DPC for outages. | IA | 2025-12-31 | Other | Load Growth | 2025-12-31 | 69 | 69 | 346800
A in MTEP20 | East | ITCT | 19565 | Trenton Channel 120 kV - Upgrade HH Station Equipment | Upgrade station equipment at Trenton Channel 120 kV position HH. | MI | 2024-06-01 | BRP |  | 2024-06-01 | 120 | 0 | 335000
A in MTEP20 | East | CETO | 17992 | Rebuild Hodenpyl Line | Rebuild the Hodenpyl 138 kV Line, approximately 0.6 miles, utilizing 138 kV single circuit construction | MI | 2021-12-31 | Other | Age and Condition | 2021-12-31 | 138 | 0 | 330000
A in MTEP20 | West | MEC | 18174 | Bondurant-Montezuma 345 kV Uprate | Replace structures to uprate the Bondurant-Montezuma 345 kV line. | IA | 2020-06-30 | GIP |  | 2020-06-30 | 345 | 0 | 320000
A in MTEP20 | Central | BREC | 18071 | Reid and Reid EHV Capacitor Re-Size | Re-size two existing capacitors by replacing the cans with larger cans. | KY | 2019-10-01 | Other | Reliability | 2019-10-01 | 161 | 0 | 300000
A in MTEP20 | Central | PPI | 18122 | Upgrade St. David 69 kV Substation | Replace St. David OCB with SF6 breaker and new relays | IL | 2020-12-31 | Other | Age and Condition | 2020-12-31 | 69 | 69 | 280000
A in MTEP20 | South | Entergy-AR | 19725 | Plum Point Network Upgrades (J1146) | Network Upgrades associated with GIA J1146 for 10 MW's of incremental NRIS at Plum Point Generation Facility. This includes reviewing and updating relay settings at San Souci 500kV Switch Station, Driver 500kV substation, and Dell 500kV substation. | AR | 2020-10-10 | GIP |  | 2020-10-10 | 500 | 0 | 275000
A in MTEP20 | West | ITCM | 16865 | J504 Generator Inteconnection | The DAEC 161 kV substation will be expanded to accommodate the J504 terminal, including the addition of breaker position 5953. New equipment should be capable of 2000A. | IA | 2020-10-15 | GIP |  | 2020-10-15 | 161 | 161 | 273780
A in MTEP20 | East | WPSC | 14004 | Hagensville Interconnection Line | Construct approximately 0.25 miles of new 138kV transmission line to connect the Grand Lake Distribution Station to METC’s 138 kV Port Calcite to Rockport transmission line. | MI | 2023-12-31 | Other | Other Local Needs | 2022-12-31 | 138 | 0 | 260000
A in MTEP20 | West | MP | 18109 | 15th Ave West Transformer Addition | Add 115/34.5 kV transformer to existing 15th Ave West Substation. This project includes the transmission equipment necessary to accommodate the new transformer. | MN | 2023-12-31 | Other | Reliability | 2022-12-31 | 115 | 34.5 | 250000
A in MTEP20 | Central | CWLP | 18134 | New Palomino 69 kV capacitor banks | New capacitor banks (x2 @ 20 Mvar) to the Palomino substation. In adding two capacitor banks to the Palomino substation, we will also be retiring the existing cap bank at Palomino. | IL | 2021-03-01 | BRP |  | 2021-03-01 | 69 | 0 | 250000
A in MTEP20 | Central | CWLP | 18172 | New Taintor 69 kV capacitor banks (x2 20 Mvar) | Add two (2) 20 MVAR capacitor banks at Taintor Substation | IL | 2021-03-01 | Other | Reliability | 2021-03-01 | 69 | 0 | 250000
A in MTEP20 | Central | DEI | 18335 | New Tate and Lyle Generation | Tate and Lyle (old Staley) Generation - existing sub on the 13808 ckt; 2 units -32.8MW each - non-MISO queue | IN |  | Other | Reliability | 2021-04-01 | 138 | 12 | 250000
A in MTEP20 | West | MP | 18110 | Little Falls Bus Reconfiguration | Reconfigure Little Falls 115 kV bus to eliminate line-connected transformer configuration | MN | 2025-12-31 | Other | Reliability | 2025-12-31 | 115 | 34 | 250000
A in MTEP20 | West | ITCM | 16866 | J498/J499/J500 Generator Interconnection | One span on the Poweshiek - Reasnor kV line will be raised to mitigate sag limits and increase the summer rating to 366 MVA (1313 A). | IA | 2019-12-01 | GIP |  | 2019-11-07 | 161 | 161 | 240000
A in MTEP20 | West | ATC | 18849 | J870 Highland SS Interconnection Facilities | A 300 MW solar farm in Grant and Iowa County, Wisconsin. Customer has requested a Point of Interconnection (POI) at Highland Substation that taps the existing X-17 line between Eden and Wyoming Valley Substations. | WI | 2020-08-01 | GIP |  | 2020-08-01 | 138 | 0 | 230118
A in MTEP20 | East | ITCT | 18198 | Sag Remediation of Airport – Tulsa 120 kV | Remediate the sag on the Airport – Tulsa 120 kV line section up to the conductor’s limit. | MI | 2023-12-31 | BRP |  | 2023-12-31 | 120 | 0 | 230000
A in MTEP20 | West | MEC | 18126 | Franklin-Wall Lake 161 kV Uprate | Replace structures to uprate the Franklin-Wall Lake 161 kV line. | IA | 2020-06-30 | GIP |  | 2020-06-30 | 161 | 0 | 220000
A in MTEP20 | West | OTP | 18504 | OTP Hankinson to Wahpeton Network Upgrades-G736/J442 | This project consists of upgrades to Otter Tail Power Company’s substations and transmission lines to accommodate the interconnection of a wind generators, G736/J442, to the Big Stone South substation. Three Facility upgrades are needed: • Hankinson Substation • Wahpeton substation • Wahpeton to Hankinson 230 kV line | ND | 2020-06-02 | GIP |  | 2020-03-10 | 230 | 0 | 219567
A in MTEP20 | West | ITCM | 17739 | Calmar Prairie Farmer 69kV Substation Interconnection | ITC will install an ~0.02 mile tap line to IPL’s new Calmar Prairie Farmer 69/24.9kV Distribution Substation. The transformer will have a highside breaker installed by IPL. This substation will be located near the existing Calmar substation. IPL has provided four proposed locations. The Calmar and Ossian substations will be retired on future EI sketches once IPL moves the loads from those substations to Calmar Prairie Farmer. | IA | 2021-12-31 | Other | Load Growth | 2021-12-31 | 69 | 69 | 205200
A in MTEP20 | West | OTP | 18364 | OTP Oslo 115 kV Switch Replacement | Replace 600 Amp Switch at OTP Oslo with 1200 Amp Switch. | MN | 2022-11-30 | Other | Reliability | 2022-11-30 | 115 | 0 | 200000
A in MTEP20 | West | ATC | 19247 | J807 J819 J850 J947 MPFCA Common Use Upgrades | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. - J807 is seeking interconnection service for 41.4 MW - J819 is seeking interconnection service for 99.9 MW - J850 is seeking interconnection service for 250 MW - J947 is seeking interconnection service for 200 MW | WI | 2021-03-01 | GIP |  | 2021-03-01 | 138 | 0 | 199855
A in MTEP20 | West | ATC | 19248 | J807 J819 J870 J947 MPFCA Common Use Upgrades | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. - J807 is seeking interconnection service for 41.4 MW - J819 is seeking interconnection service for 99.9 MW - J870 is seeking interconnection service for 200 MW - J947 is seeking interconnection service for 200 MW | WI | 2021-03-01 | GIP |  | 2021-03-01 | 138 | 0 | 181784
A in MTEP20 | East | WPSC | 18021 | Eastport 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate facility equipment replacement. | MI | 2021-12-31 | Other | Age and Condition | 2021-12-31 | 69 | 0 | 170000
A in MTEP20 | East | WPSC | 18022 | Westwood 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate facility equipment replacement. | MI | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 69 | 0 | 170000
A in MTEP20 | East | WPSC | 18023 | Eaton Rapids 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate facility equipment replacement. | MI | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 69 | 0 | 170000
A in MTEP20 | East | WPSC | 18024 | Atlanta 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate station equipment replacement. | MI | 2021-12-31 | Other | Age and Condition | 2022-12-31 | 69 | 0 | 170000
A in MTEP20 | East | WPSC | 18026 | Hawks 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate equipment replacement at station. | MI | 2022-12-31 | Other | Age and Condition | 2022-12-31 | 69 | 0 | 170000
A in MTEP20 | East | WPSC | 18027 | Hammond Bay 138kV BUS Replacement | 138kV BUS replacement in order to accommodate voltage increase. | MI | 2023-12-31 | Other | Age and Condition | 2021-12-31 | 138 | 0 | 170000
A in MTEP20 | East | WPSC | 18028 | Hagensville 138kV BUS replacement | Install BUS to 138kV standard to accommodate voltage conversion. | MI | 2023-12-31 | Other | Age and Condition | 2021-12-31 | 138 | 0 | 170000
A in MTEP20 | West | ITCM | 17735 | Clinton South 69kV Substation Retirement | Retire all ITC owned equipment in the Clinton South 69/distribution sub and reroute the 69kV line to bypass the Clinton South sub. | IA | 2024-12-31 | Other | Load Growth | 2024-12-31 | 69 | 69 | 161873
A in MTEP20 | West | XEL | 19406 | Chisago Capacitor Retirement | Chisago 34.5kV capacitors on the tertiary of TR9 and TR10 have failed catastrophically. There is currently no operational or planning need for the capacitors at this time and they will be retired. | MN |  | Other | Age and Condition | 2020-12-01 | 34.5 | 0 | 156000
A in MTEP20 | Central | BREC | 18765 | Relocate Reid EHV 345/161 kV Transformer | Reallocate existing transformers - move one existing Reid EHV 161/345 kV transformer to Otter Creek (steel mill project). | KY | 2021-03-01 | Other | Reliability | 2021-03-01 | 345 | 161 | 150000
A in MTEP20 | Central | CWLP | 18171 | Reconductor Chatham Independence-Spaulding 138 kV line | Reconductor Chatham Ind.-Spaulding 138 kV line with 795 ACSS. | IL | 2021-03-01 | BRP |  | 2021-03-01 | 138 | 0 | 150000
A in MTEP20 | South | AECC | 16884 | Helena Industrial Breaker Removal | Remove inline breaker at the AECC Helena Industrial Switching Station | AR | 2021-06-01 | Other | Other Local Needs | 2021-06-01 | 115 | 0 | 150000
A in MTEP20 | East | METC | 18825 | Island Rd - Replace White Bus and Position 177 Conductor | Replace the 4/0 CU and 1/0 CU bus conductor at Island Rd White bus and Position 177 to achieve a rating of at least 141 MVA (590 amps). | MI | 2022-05-01 | GIP |  | 2022-05-01 | 138 | 0 | 134000
A in MTEP20 | West | MEC | 19646 | Franklin to Wall Lake 161 kV Line Structure Replacement | Line structure replacements to increase line ratings. | IA | 2021-12-31 | BRP |  | 2021-12-31 | 161 | 0 | 125000
A in MTEP20 | West | MEC | 18121 | Deere Northeast-Washburn 161 kV Uprate | Replace limiting substation terminal equipment at Deere Northeast and Washburn to increase the rating of the Deere Northeast-Washburn 161 kV line. | IA | 2020-10-31 | GIP |  | 2020-10-31 | 161 | 0 | 100000
A in MTEP20 | South | Entergy-LA | 18136 | Scott to Lafayette 69 kV: Upgrade Station Equipment | Upgrade all station equipment to achieve a through path rating of 588 Amps. | LA | 2021-06-01 | Other | Reliability | 2021-06-01 | 69 | 0 | 50000
A in MTEP20 | West | MEC | 18119 | Lundquist-Deere Northeast 161 kV Uprate | Replace terminal equipment at Deere Northeast substation to increase 161 kV line rating. | IA | 2020-10-31 | GIP |  | 2020-10-31 | 161 | 0 | 50000
A in MTEP20 | South | Entergy-MS | 18226 | Refuge 115 kV Equipment Upgrade | Upgrade switches at the Cooperative Energy owned Refuge 115kV GOAB with higher amp rated switches. | MS | 2021-03-01 | BRP |  | 2021-03-01 | 115 | 0 | 25000
A in MTEP20 | Central | CWLP | 18141 | Upgrade Interstate 138 kV substation | Replace the wavetrap on the Interstate - Lanesville 138 kV line (at Interstate Sub) with a 2000A wave trap. This will increase the rating of the line. | IL | 2021-03-01 | BRP |  | 2021-03-01 | 138 | 0 | 20000
A in MTEP20 | West | MRES | 18645 | Hutchinson Jumper Replacement | Overloads on the Hutchinson 230/115 kV transformer were observed in the MTEP19 results. The transformer is limited by a couple sets of jumpers. To increase the transformer capacity the jumpers will be replaced. | MN |  | BRP |  | 2021-06-01 | 115 | 0 | 20000
A in MTEP20 | East | ITCT | 17995 | J752 Network Upgrades | Install Relay and communication cutoff switch at Ringle 345 kV station for the J752 expansion of J161. | MI | 2019-10-31 | GIP |  | 2019-10-31 | 345 | 0 | 17904.43
A in MTEP20 | West | ITCM | 17733 | J504 Generator Inteconnection-TOIF | The GIA between ITCM, Duane Arnold Solar, LLC (NextEra Energy) and MISO has been executed to facilitate the interconnection of project J504, a 60 MVA solar generating facility rated 51 MW gross and 50MW net with a Point of Interconnection at the DAEC 161 kV substation. The Interconnection Customer is responsible for costs associated with the TOIF. | IA | 2020-10-15 | GIP |  | 2020-10-15 | 161 | 161 | 0
A in MTEP20 | West | ITCM | 18111 | J523 Generator Interconnection-TOIF | Install new terminal for J523 gen-tie line. This work includes installing switch, dead-end, CCVT's, switches, and relay panels (see GIA for further details). | MN | 2021-09-15 | GIP |  | 2021-09-15 | 161 | 161 | 0
A in MTEP20 | South | AXLA | 19408 | Sterkx – Willow Glen 138 kV Reconductor | Line re-conductor driven by aging infrastructure. | LA |  | Other | Age and Condition | 2021-06-01 | 138 | 0 | TBD
A in MTEP20 | South | Entergy-MS | 19785 | Twinkletown 230 kV: Expand Substation (J962) | Interconnect new J962 100 MW generator to the existing Twinkletown 230 kV substation. | MS | 2022-06-30 | GIP |  | 2022-06-30 | 230 | 0 | TBD
A in MTEP20 | Central | AmerenIL | 16144 | Replace Newton 345/138 kV transformer | Replace the existing Newton 345-138 kV unit #1 with a new 700 MVA unit | IL | 2023-06-01 | BRP |  | 2023-06-01 | 345 | 138 | TBD
A in MTEP20 | Central | AmerenIL | 16709 | Upgrade Ashley-Venice 138 kV line at Venice substation | Replace 2 1200A switches and 1000 Kcmil CU bus conductor with equipment having 2000A capability. Upgrade the position to 2000A. | IL | 2021-12-01 | Other | Reliability | 2021-12-01 | 138 | 0 | TBD
A in MTEP20 | Central | AmerenMO | 15487 | New Vessel 138 kV Ring Bus | Install 4 position ring bus | MO | 2022-06-01 | Other | Reliability | 2022-06-01 | 138 | 0 | TBD
A in MTEP20 | Central | AmerenMO | 17224 | New Pershall 138/12 kV distribution Substation | Install main-tie-main straight bus substation connecting to Berkeley-Sioux-1 and Berkeley-Sioux-2 lines. | MO | 2022-06-01 | Other | Load Growth | 2022-06-01 | 138 | 12 | TBD
A in MTEP20 | Central | AmerenMO | 17665 | New Barrett Station 138/12 kV Transformer No. 2 | Install 3 breakers in a main-tie-main configuration with an open bus tie to facilitate the installation of a 2nd transformer. Install circuit switchers on the existing and new transformers. | MO | 2021-12-31 | Other | Load Growth | 2021-12-31 | 138 | 12 | TBD
A in MTEP20 | Central | AmerenMO | 17685 | New Creve Coeur 138/12 kV substation | Tap the Mason-Meramec-1 & 2 lines to provide a main-tie-main configuration for new 138-12 kV substation. | MO | 2027-12-01 | Other | Load Growth | 2027-12-01 | 138 | 12 | TBD
A in MTEP20 | Central | AmerenMO | 17686 | New Dougherty Ferry 138/12 kV substation | Tap the Mason-Meramec-1 & 2 lines to provided a main-tie-main configuration for the installation of a new 138-12 kV substation. | MO | 2023-12-01 | Other | Load Growth | 2023-12-01 | 138 | 12 | TBD
A in MTEP20 | Central | AmerenMO | 17945 | New Highway M 138/12 kV substation | Install 2 unit 138-12.47 kV substation on a site adjacent to the Dardenne Substation. | MO | 2024-12-01 | Other | Load Growth | 2024-12-01 | 138 | 12.47 | TBD
A in MTEP20 | Central | AmerenMO | 17947 | New Fountain Lakes 138/12 kV transformer No. 2 | Add 2nd 138-12 kV unit at Fountain Lakes Substation. | MO | 2023-12-01 | Other | Load Growth | 2023-12-01 | 138 | 12.47 | TBD

## Facility Legend
MTEP Database Export October 5, 2020
Facility Table Field Legend
Project table has blue highlighted header. A project may have multiple facilties.
Facility table has beige highlighted header. A project's facilities may have different in service dates.
Facilty Table Field Legend
Field | Description
Target Appendix | Target appendix for the MTEPyy planning cycle. Example: "A in MTEP15" projects were reviewed in MTEP15.
Region | MISO Planning Region: Central, East, West or South
Geographic Location by TO Member System | Project geographic location by Transmission Owner member systems
PrjID | Indicates the Facility's Project. Projects may have multiple facilities.
Facility ID | Facility ID: MISO facility identifier
Expected ISD | Expected In Service Date for this facility
From Sub | From substation for transmission line or location of transformer or other equipment
To Sub | To substation for transmission line or transformer designation
Ckt | Circuit identifier
Max kV | Maximum voltage of this facility
Min kV | Minumum voltage of this facility (transformer low-side voltage)
Facility Rating | Rating of the facility in applicable units. Typically Summer rate
Facility Description | Brief description of transmission facility
State | State the facility is located in
Miles Upg. | Transmission line miles on existing rights of way (ROW)
Miles New | Transmission line miles on new rights of way (ROW)
Plan Status | Indicates status of project in planning or implementation. Conceptual, Proposed, Planned, Last Milestone Achieved, Under Construction and In Service
Estimated Cost | Total estimated facility cost
Cost Shared | Y if facility is cost shared per Attachment FF
Postage Stamp | Y if facility has postage stamp cost allocation per Attachment FF
MISO Facility | Y for facilities under MISO functional control. NT for non-transferred facilities under Agency Agreements

## MTEP20 A Facilities
Target Appendix | Planning Region | Geographic Location by TO Member System | PrjID | Facility ID | Facility Type | Expected ISD | From Sub | To Sub | Ckt | Max kV | Min kV | Facility Rating | Description | State | Miles Up-grade | Miles New | Estimated Cost
A in MTEP20 | Central | DEI | 2864 | 5017 | LNrc | 2023-06-01 | Centeron | Martinsville | 1 | 69 |  | 153 | Reconductor the 69kV-69163 ckt - 3.47 miles of 366ACSR 80C and 0.23 miles of 477ACSR 80C to 954ACSR 100C | IN | 3.7 |  | 7400000
A in MTEP20 | West | ATC | 4727 | 8956 | LNrc | 2024-12-31 | Winona SS | Atlantic SS | 1 | 69 |  | 56 | Reconductor Winona - Atlantic (Winona69) 69kV line with new insulators and 477 conductor | MI | 22 |  | 11900000
A in MTEP20 | West | ATC | 4727 | 25329 | LNrb | 2024-12-31 | Winona SS | Atlantic SS |  | 69 |  |  | Pole and Insulator Asset Renewal Only | MI |  |  | 2000000
A in MTEP20 | West | ATC | 4727 | 8958 | LNrb | 2024-12-31 | Atlantic |  | 1 | 69 |  | 105 | Facility likely to be withdrawn | MI | 1.32
A in MTEP20 | West | ATC | 4727 | 8957 | LNrb | 2024-12-31 | Winona |  | 1 | 69 |  | 147 | Facility likely to be withdrawn | MI | 11.24
A in MTEP20 | West | ITCM | 9100 | 20813 | LNrb | 2021-05-31 | Burlington | Burlington 4th Street | 1 | 69 | 69 | 132 MVA | Rebuid 0.77 miles of 69kV line and upgrade terminal equipment above the conductor rating of 132 MVA. | IA | 0.77 |  | 1363309.2
A in MTEP20 | West | ITCM | 9100 | 24948 | TEQ | 2021-05-31 | Burlington | Burlington South | 1 | 69 | 69 | 132 MVA | Upgrade the terminal equipment on the Burlington terminal 6994 so the line is conductor limited (132MVA minimum). | IA |  |  | 26160
A in MTEP20 | West | ITCM | 9100 | 24729 | LNrb | 2021-05-31 | Burlington 4th Street | South Burlington | 1 | 69 | 69 | 111 MVA | Rebuild a small section of 69kV line to T2-477 ACSR. | IA | 0.05
A in MTEP20 | West | ITCM | 9100 | 20814 | LNrb | 2021-05-31 | Burlington 4th Street | Agency | 1 | 69 | 69 | 101 MVA | Rebuild the 4th Street-Agency 69kV line to T2-477. | IA | 2.51 |  | 3549948
A in MTEP20 | Central | AmerenMO | 9721 | 21104 | LNrc | 2022-12-01 | Tegeler | Franklin | 1 | 138 | 138 | 240 | Reconductor to 1200 A summer emergency capability | MO | 18.25 |  | 10300000
A in MTEP20 | Central | AmerenMO | 9721 | 21105 | LNrc | 2022-12-01 | Bland | Tegeler | 1 | 138 | 138 | 240 | Reconductor to 1200 A summer emergency capability | MO | 16.75 |  | 16900000
A in MTEP20 | Central | AmerenIL | 9723 | 21107 | SUB | 2019-06-01 | Fishhook |  |  | 138 | 138 | 240 | Construct 138 kV breaker station in East Quincy-Meredosia-2 138 kV lline. | IL |  |  | 10500000
A in MTEP20 | Central | AmerenIL | 9734 | 21119 | SUB | 2023-12-01 | North Utica |  |  | 138 | 34.5 | 255 | Construct 138 kV breaker station in North LaSalle-Fox River-1646 138 kV line. | IL |  |  | 8400000
A in MTEP20 | Central | AmerenMO | 9735 | 21120 | SUB | 2021-12-01 | Tyson | Marshall | 1 | 138 | 138 | 399 | Replace overstressed breaker at Tyson | MO |  |  | 900000
A in MTEP20 | Central | AmerenMO | 9735 | 21122 | SUB | 2021-12-01 | Tyson | Arnold | 3 | 138 | 138 | 240 | Replace overstressed breaker at Tyson | MO |  |  | 900000
A in MTEP20 | Central | AmerenMO | 9735 | 21121 | SUB | 2021-12-01 | Tyson | Marshall | 2 | 138 | 138 | 399 | Replace overstressed breaker at Tyson. | MO |  |  | 900000
A in MTEP20 | West | OTP | 10043 | 21445 | CB | 2020-07-03 | Jamestown 345 |  |  | 345 |  |  | Add an additional 345 kV breaker to create a 4 breaker ring bus. | ND |  |  | 1178852
A in MTEP20 | Central | AmerenIL | 11925 | 21877 | TX | 2023-06-01 | Massac |  | 1 | 345 | 161 | 560 | Install 345/161 kV, 560 MVA transformer | IL |  |  | 22800000
A in MTEP20 | Central | AmerenIL | 11925 | 25209 | TX | 2023-06-01 | Massac |  | 2 | 345 | 161 | 560 | Install 345/161 kV, 560 MVA transformer | IL |  |  | 22800000
A in MTEP20 | Central | AmerenIL | 11925 | 21878 | LNcnv | 2023-06-01 | Massac | Jordan | 1 | 345 |  | 1206 | Rebuild from 230 kV to 345 kV use. | IL | 47.62 |  | 66800000
A in MTEP20 | Central | AmerenIL | 11926 | 21879 | TX | 2023-12-01 | Jordan |  |  | 345 | 138 | 560 | Install 345/138 kV, 560 MVA transformer | IL |  |  | 27400000
A in MTEP20 | Central | AmerenIL | 11926 | 21880 | LNcnv | 2023-12-01 | Jordan | Derby |  | 345 |  | 1200 | Rebuild line from 230 kV to 345 kV use. | IL | 19.9 |  | 28700000
A in MTEP20 | Central | AmerenIL | 11969 | 21937 | LN | 2020-12-01 | Miles | Mississippi | 1 | 138 |  | 399 | Construct new 138 kV line | IL |  | 1.7 | 4000000
A in MTEP20 | Central | AmerenIL | 11969 | 21939 | CB | 2020-12-01 | Mississippi |  |  | 138 |  | 478 | Install 138 kV breaker | IL
A in MTEP20 | Central | AmerenIL | 11969 | 21938 | CB | 2020-12-01 | Miles |  |  | 138 |  | 478 | Install 138 kV breaker | IL
A in MTEP20 | West | ATC | 12175 | 22293 | LNrb | 2023-12-31 | West Middleton | Stagecoach |  | 69 |  |  | Rebuild West Middleton - Stagecoach 69KV | WI | 4 |  | 2735023
A in MTEP20 | Central | AmerenIL | 12176 | 22295 | SUB | 2024-12-01 | West Frankfort, East |  |  | 345 |  | 50 | Reconfigure existing ring to BAAH and install 345 kV shunt reactor | IL |  |  | 14800000
A in MTEP20 |  | AmerenIL | 12176 | 25426 | IND | 2023-12-01 | Norris City North |  |  | 345 |  |  | Add 50 MVAR Reactor | IL |  |  | 4900000
A in MTEP20 | Central | AmerenMO | 12428 | 22434 | CB | 2021-12-01 | Stoddard | Morley | 1 | 161 |  | 280 | Replace 161 kV breaker at Stoddard terminal | MO |  |  | 500000
A in MTEP20 | Central | AmerenIL | 13705 | 22773 | SUB | 2021-12-01 | North Nashville | Install 138 kV ring bus |  | 138 |  |  | Install initial 3-position (ultimate 4-position) 138 kV ring bus at North Nashville Substation. | IL |  |  | 7810000
A in MTEP20 | Central | AmerenIL | 13708 | 22776 | SUB | 2022-12-01 | New Athens Dutch Hill | Install 138 kV ring bus |  | 138 |  |  | Add 138 kV ring Bus. Initial 3-position (ultimate 4-position) | IL |  |  | 8376000
A in MTEP20 | Central | AmerenIL | 13709 | 22777 | SwSta | 2022-12-01 | Putnam | BAAH Substation |  | 138 |  |  | Install new 138kV BAAH substation on new site near Hennepin. | IL |  |  | 18100000
A in MTEP20 | Central | AmerenIL | 13709 | 23288 | LN | 2022-12-01 | Hennepin | Putnam |  | 138 |  |  | Install new 138 kV lines between the new Putnam Substation and Hennepin Substation | IL |  |  | 4200000
A in MTEP20 | Central | AmerenIL | 13793 | 22855 | SUB | 2022-12-01 | El Paso | Install 138 kV ring bus |  | 138 |  |  | Install initial 4-position ring bus at El Paso Substation for in/out supply. | IL |  |  | 11400000
A in MTEP20 | Central | AmerenIL | 13797 | 22859 | LNcnv | 2022-12-01 | Albion South | Norris City North | 1 | 345 | 138 |  | Rebuild the existing 138 kV circuit to 2000A. Double circuit the line for new 3000A 345 kV circuit. | IL |  |  | 74000000
A in MTEP20 | South | Entergy-LA | 13925 | 23000 | Dist | 2023-06-01 | Choudrant |  |  | 230 |  |  | 230 kV distribution substation | LA |  |  | 56225000
A in MTEP20 | South | Entergy-LA | 13925 | 23001 | LN | 2023-06-01 | Mt Olive | Choudrant | 1 | 230 |  | 519 | Construct approximately 14 miles of 230 kV transmission line from the new substation that terminates into the existing Mt Olive substation. | LA |  | 14
A in MTEP20 | South | Entergy-LA | 13938 | 23023 | SUB | 2023-12-01 | Cheniere |  |  | 115 |  |  | Cheniere 115 kV substation breaker installation | LA |  |  | 5390471
A in MTEP20 | South | Entergy-TX | 13943 | 23030 | Dist | 2024-06-01 | Southern Point |  |  | 138 |  |  | Construct a new 138 kV substation that replaces the existing Speedway 138 kV substation. | TX |  |  | 22000000
A in MTEP20 | East | WPSC | 14004 | 23120 | LN | 2022-12-31 | Haggensville Junction | Haggensville |  | 138 |  |  | Install new 138kV line | MI |  | 0.25 | 260000
A in MTEP20 | East | WPSC | 14005 | 23121 | LNrb | 2022-12-31 | Hammond Bay Junction | Hammond Bay |  | 138 |  |  | Rebuild line | MI |  | 2 | 900000
A in MTEP20 | South | LAFA | 14105 | 23255 | BUS | 2021-09-30 | Bonin 69kV |  |  | 69 |  |  | Replace bus work | LA |  |  | 700000
A in MTEP20 | South | LAFA | 14105 | 23257 | RLY | 2021-09-30 | Bonin 69kV |  |  | 69 |  |  | Relaying, communications, and control building | LA |  |  | 2200000
A in MTEP20 | South | LAFA | 14105 | 23256 | SUB | 2021-09-30 | Bonin 69kV |  |  | 69 |  |  | Replace breakers and associated equipment. | LA |  |  | 3500000
A in MTEP20 | West | GRE | 14366 | 24460 | LNrb | 2024-06-14 | Litchfield Tap | Svea Tap | 1 | 69 |  |  | Rebuild 24 miles of the Litchfield Tap to Svea Tap line to 115 kV design. The line will continue to operate at 69 kV at this time. | MN | 24 |  | 18350000
A in MTEP20 | West | ATC | 14907 | 23478 | SUB | 2024-06-30 | NA |  |  | 138 | 69 |  | Distribution Interconnection 2021 | WI,MI |  |  | 20124594
A in MTEP20 | West | ATC | 14909 | 23464 | SUB | 2024-06-30 | NA |  |  | 345 | 69 |  | Small Capital Project and Asset Renewal 2021 | WI,MI |  |  | 38913412
A in MTEP20 | West | ATC | 14911 | 23467 | COM | 2024-06-30 | NA |  |  | 345 | 69 |  | Communication Reliability Upgrades 2021 | WI,MI |  |  | 10927208
A in MTEP20 | West | ATC | 14913 | 23470 | LNup | 2024-06-30 | NA |  |  | 345 | 69 |  | Line Clearance Mitigation Projects 2021 | WI,MI |  |  | 3791502
A in MTEP20 | West | ATC | 14915 | 23473 | SUB | 2024-06-30 | NA |  |  | 345 | 69 |  | Physical Security 2021 | WI,MI |  |  | 17908909
A in MTEP20 | Central | AmerenIL | 15265 | 23496 | BUS | 2023-06-01 | Carbondale NE | Substation |  | 138 |  |  | Install initial 3-position ring bus at Carbondale NE Substation | IL |  |  | 12500000
A in MTEP20 | Central | AmerenIL | 15266 | 23497 | BUS | 2023-06-01 | Fayetteville Bee Hollow |  |  | 138 |  |  | Install initial 3-position ring bus at the Fayetteville Bee Hollow Substation location | IL |  |  | 7200000
A in MTEP20 | Central | AmerenMO | 15268 | 23499 | LNrc | 2022-06-01 | Dupo Ferry | Selma | 1302 | 138 |  |  | Rebuild the 138 kV line from Selma to the former Buck Knob Substation | MO |  |  | 4900000
A in MTEP20 | Central | AmerenMO | 15487 | 23570 | SUB | 2022-06-01 | Vessel | Substation |  | 138 |  |  | Install 4-position ring bus | MO
A in MTEP20 | Central | AmerenIL | 15504 | 23593 | SwSta | 2022-06-01 | Dempsey | Substation |  | 138 |  |  | Install new 138 kV ring bus at the Blue Mound tap on the Pana-Route 51 Decatur-1462 line. | IL |  |  | 11700000
A in MTEP20 | South | Entergy-LA | 15568 | 23606 | SUB | 2022-12-01 | Oak Grove |  |  | 138 |  |  | Add breakers at Oak Grove 138 kV substation | LA |  |  | 2000000
A in MTEP20 | West | MP | 15592 | 23620 | LNup | 2021-10-31 | Hibbing | 14 Line Tap |  | 115 |  | 120/120 | Increase operating temperature from 55C to 100C, will be limited by terminal equipment which will be upgraded with MTEP Project #18064 | MN | 6 |  | 1230000
A in MTEP20 | West | MP | 15593 | 23621 | LNup | 2022-03-31 | Hibbing | Virginia |  | 115 |  | 90/114 | Increase operating temperature from 50C to 75C, will be limited by terminal equipment which will be upgraded with MTEP Project #18064 | MN | 28 | 0 | 1280000
A in MTEP20 | West | MP | 15598 | 23630 | TX | 2024-10-31 | Badoura 230 | Badoura 115 |  | 230 | 115 | 187 | Move existing Hilltop 1TR to Badoura. This transformer does not have LTCs. | MN | 0 | 0 | 400000
A in MTEP20 |  | MP | 15598 | 25762 | SUB | 2024-10-31 | Badoura 230 |  |  | 230 |  |  | New EEE building and expand 230 kV bus to a 3-position ring bus with 3 new 230 kV breakers | MN |  |  | 3600000
A in MTEP20 | South | Entergy-LA | 15645 | 23646 | CB | 2022-06-01 | Nelson |  |  | 230 |  |  | Add breaker so Nelson L698 is connected to the Nelson 138 kV bus via double bus double breaker | LA |  |  | 10600000
A in MTEP20 | South | Entergy-TX | 15648 | 23652 | Dist | 2024-06-01 | Castle |  |  | 230 |  |  | New substation southwest of Dobbin | TX |  |  | 50510000
A in MTEP20 | South | Entergy-TX | 15648 | 23654 | LN | 2024-06-01 | Castle | Cut in point |  | 230 |  |  | Cut the Castle 230 kV station in and out on the Ponderosa to Grimes 230 kV line. 230 kV breakers will be installed at Castle. | TX
A in MTEP20 | West | MDU | 15784 | 23809 | LNrb | 2023-09-30 | Zahl | Corinth |  | 60 |  |  | Rebuild 60 kV line | ND | 16 |  | 3500000
A in MTEP20 | East | METC | 15809 | 23841 | LNrb | 2024-12-31 | Four Mile (Northridge) | North Belding | 1 | 138 |  |  | The proposed solution is to rebuild 8.38 miles Alpine Jct. – Rogue River Jct. and Rogue River Jct. – Cannon Jct. sections of the Four Mile – North Belding 138kV line using 954 ACSR conductor. | MI | 8.38 |  | 11700000
A in MTEP20 | Central | SIGE | 15860 | 23942 | TX | 2022-12-31 | Broadview |  | T2 | 69000 |  |  | Replace 69/12 kV distribution transformer T2 at the Broadview substation | IN |  |  | 1200000
A in MTEP20 | West | XEL | 15877 | 23972 | LNrb | 2022-06-15 | Long Lake | Baytown | 1 | 115 |  |  | 115kV line from Long Lake to Baytown will be upgraded | MN |  |  | 10000000
A in MTEP20 | East | ITCT | 15880 | 23975 | LNrb | 2025-12-31 | Navarre | River Rouge | 1 | 120 |  |  | Rebuild the 2.9 miles of 954 ACSR conductor to 2156 ACSR on the Navarre – River Rouge 120 kV line. | MI | 2.9 |  | 9120000
A in MTEP20 | East | ITCT | 15880 | 23977 | TEQ | 2025-12-31 | River Rouge |  |  | 120 |  |  | Upgrade station equipment at River Rouge. | MI |  |  | 241000
A in MTEP20 | East | ITCT | 15880 | 23976 | TEQ | 2025-12-31 | Navarre |  |  | 120 |  |  | Upgrade station equipment at Navarre. | MI |  |  | 367000
A in MTEP20 | East | ITCT | 15883 | 23980 | LNrb | 2024-12-31 | Bismarck | Stephens | 2 | 120 |  |  | Rebuild approximately 3.61 miles of 795 ACSS and 954 ACSR conductors to 2156 ACSR on the Bismarck – Stephens #2 120 kV line. | MI | 3.6 |  | 9100000
A in MTEP20 | East | ITCT | 15890 | 23992 | LNrb | 2025-12-31 | Pontiac | Walton | 1 | 120 |  |  | Rebuild approximately 4.8 miles of 477 ACSR X2 and 1431 ACSR conductors from Pontiac to Giddings 2 Tap to Walton using 2156 ACSR. Also, upgrade station equipment at Pontiac 120kV and Walton 120 kV. | MI | 4.8 |  | 10700000
A in MTEP20 | East | ITCT | 15890 | 23994 | TEQ | 2025-12-31 | Walton |  |  | 120 |  |  | Upgrade station equipment at Walton. | MI |  |  | 165000
A in MTEP20 | East | ITCT | 15890 | 23993 | TEQ | 2025-12-31 | Pontiac |  |  | 120 |  |  | Upgrade station equipment at Pontiac. | MI |  |  | 162000
A in MTEP20 | East | METC | 15896 | 24001 | LNrb | 2024-12-31 | Battle Creek | Morrow | 1 | 138 |  |  | rebuild 19.38 miles from Str #008E57412E to Str #008E8623 of the Battle Creek – Morrow #1 138kV circuit using 954 ACSR conductor with future double-circuit steel structures and leave adjacent side vacant for future circuit and also rebuild 3.3 miles from Str #008E8623 to Morrow station of 477 ACSR conductor to 954 ACSR conductor with double circuit steel structures. | MI | 11.63 |  | 41000000
A in MTEP20 | East | ITCT | 15900 | 24005 | LNrb | 2025-12-31 | Wayne | Newburgh | 1 | 120 |  |  | Rebuild approximately 2.7 miles of 795 ACSS conductor to 2156 ACSS on the Wayne – Newburgh #1 120 kV circuit. | MI | 2.7 |  | 6810000
A in MTEP20 | East | ITCT | 15900 | 24007 | TEQ | 2025-12-31 | Newburgh |  |  | 120 |  |  | Upgrade station equipment at Newburgh. | MI |  |  | 220000
A in MTEP20 | East | ITCT | 15900 | 24006 | CB | 2025-12-31 | Wayne |  |  | 120 |  |  | Replace breaker at Wayne 120kV position "HD" and upgrade terminal equipment. | MI |  |  | 690000
A in MTEP20 | West | ATC | 15930 | 24043 | SUB | 2022-12-31 | Pulliam |  |  | 138 | 69 |  | Asset Renewal | WI |  |  | 4000000
A in MTEP20 | East | METC | 15939 | 24052 | LNrb | 2025-06-01 | Leoni | Beecher | 1 | 138 |  |  | Sixed wire 0.21 miles of the Mercer – Cement City Jct. section of the Leoni – Beecher circuit using existing 477 ACSR conductor. Also remediate sag limit on the 6-wired conductor section to increase its summer emergency rating to a minimum of 1196 Amps (286 MVA). | MI | 0.21 |  | 4300000
A in MTEP20 | Central | SIGE | 15940 | 24053 | TX | 2022-12-31 | East Industrial |  |  | 69 |  |  | Replace 69/12 kV distribution transformer | IN |  |  | 1200000
A in MTEP20 | Central | SIGE | 15948 | 24064 | TX | 2022-12-31 | Fairlawn |  | T1 | 69 |  |  | Replace 69/12 kV distribution transformer T1 at Fairlawn substation | IN |  |  | 1200000
A in MTEP20 | Central | SIGE | 15949 | 24065 | TX | 2022-12-31 | Fuquay |  | T1 | 69 |  |  | Replace 69/12 kV transformer T1 at Fuquay substation | IN |  |  | 1200000
A in MTEP20 | Central | SIGE | 15950 | 24066 | TX | 2022-12-31 | Hemenway |  | T1 | 69 |  |  | Replace 69/12 kV distribution transformer T1 at Hemenway substation | IN |  |  | 1700000
A in MTEP20 | Central | SIGE | 15952 | 24071 | CB | 2022-12-31 | Culley |  |  | 138 |  |  | Replace two 138 kV breakers at Culley - 2200 and 2277 | IN |  |  | 615000
A in MTEP20 | Central | SIGE | 15953 | 24073 | CB | 2022-12-31 | Heidelbach |  |  | 138 |  |  | Replace two 138 kV breakers at Heidelbach - 2177 & 2277 | IN |  |  | 615000
A in MTEP20 | Central | SIGE | 15958 | 24079 | TX | 2022-12-31 | Rockport |  | T2 | 69 | 12 |  | Replace 69/12 kV distribution transformer T2 at Rockport susbtation | IN |  |  | 1700000
A in MTEP20 | East | ITCT | 15959 | 24082 | LNrb | 2025-12-31 | Hager | Sunset | 1 | 120 |  |  | Rebuild 4.33 miles of the Sunset – Hager 120kV circuit using 2156 ACSR conductor with single circuit steel structures. | MI | 4.33 |  | 9240000
A in MTEP20 | East | ITCT | 15959 | 25257 | TEQ | 2025-12-31 | Sunset |  |  | 120 |  |  | Upgrade station equipment at Sunset 120kV station. | MI |  |  | 277000
A in MTEP20 | East | ITCT | 15959 | 24083 | TEQ | 2025-12-31 | Hager |  |  | 120 |  |  | Replace terminal equipment at Hager Pos HD. | MI |  |  | 140000
A in MTEP20 | Central | SIGE | 15960 | 24080 | TX | 2022-12-31 | St. Phillips |  | T1 | 69 | 12 |  | Replace 69/12 kV distribution transformer T1 | IN |  |  | 1200000
A in MTEP20 | Central | SIGE | 15961 | 24081 | LNrb | 2022-12-31 | Northwest | Ohio River Station | Y31 | 69 |  |  | Rebuild ~2.1 miles of 69 kV overhead line between Northwest and Ohio River Station (Y31-1) | IN | 2.1 |  | 1930000
A in MTEP20 | Central | SIGE | 15987 | 24118 | TX | 2024-12-31 | Berry Plastics |  |  | 69 |  |  | Replace one of the 69 kV distribution transformers serving Berry Plastics | IN |  |  | 1100000
A in MTEP20 | East | ITCT | 16015 | 24151 | LNrb | 2025-12-31 | Sunset | Quaker | 1 | 120 |  |  | The proposed solution is to rebuild 0.259 mile of the Sunset – Quaker 120kV circuit using 2156 ACSR conductor with single circuit steel structures and replace terminal equipment and station equipment at Quaker Pos HD and Sunset Pos HN. | MI | 0.26 |  | 2000000
A in MTEP20 | East | ITCT | 16015 | 24153 | TEQ | 2025-12-31 | Quaker |  |  | 120 |  |  | The proposed solution is to rebuild 0.259 mile of the Sunset – Quaker 120kV circuit using 2156 ACSR conductor with single circuit steel structures and replace terminal equipment and station equipment at Quaker Pos HD and Sunset Pos HN. | MI |  |  | 130000
A in MTEP20 | East | ITCT | 16015 | 24152 | TEQ | 2025-12-31 | Sunset |  |  | 120 |  |  | The proposed solution is to rebuild 0.259 mile of the Sunset – Quaker 120kV circuit using 2156 ACSR conductor with single circuit steel structures and replace terminal equipment and station equipment at Quaker Pos HD and Sunset Pos HN. | MI |  |  | 130000
A in MTEP20 | East | ITCT | 16024 | 24173 | CAP | 2023-12-31 | River Rouge |  |  | 120 |  |  | Install a three 18 MVAR capacitors at River Rouge 120 kV station. | MI |  |  | 1030000
A in MTEP20 | Central | AmerenIL | 16144 | 24225 | TX | 2023-06-01 | Newton | Substation |  | 345 | 138 |  | Replace the existing 345-138 kV unit 1 transformer with a new 700 MVA unit. | IL
A in MTEP20 | West | ATC | 16486 | 24308 | SUB | 2023-12-31 | Arcadian SS |  |  | 345 | 138 |  | Renew power transformers, control house, relays, breakers, switches | WI |  |  | 40000000
A in MTEP20 | West | ATC | 16488 | 24313 | SUB | 2023-12-31 | Tilden SS |  |  | 138 | 138 |  | Asset Renewal of Circuit Breakers, Switches, PT's, Relays, and install New Control Building | MI |  |  | 5880000
A in MTEP20 | Central | AmerenMO | 16491 | 24315 | LNrb | 2021-12-01 | Sioux-Meppen | Sioux-Huster |  | 138 |  |  | Sioux-Huster-1/Sioux-Meppen North-4: Rebuild ~9 miles of triple circuit 138 kV lattice tower line to double-circuit steel poles. | MO,IL |  |  | 17100000
A in MTEP20 | Central | AmerenMO | 16504 | 24322 | SUBmisc | 2023-12-01 | Viburnum | Substation |  | 161 | 34 |  | Install 2 161 kV line breakers and 1 161 kV circuit switcher on the transformer to split the CLK-CMCO-2 line and create 2 circuits into Viburnum Substation. | MO |  |  | 1600000
A in MTEP20 | Central | AmerenMO | 16552 | 24350 | SUB | 2022-12-01 | Tyson | Substation |  | 345 | 138 |  | Replace XFMR 1 with a hardened unit and replace the 138kV XFMR 1 breaker and Replace XFMR 3 breaker. | MO |  |  | 7600000
A in MTEP20 | Central | AmerenMO | 16555 | 24353 | SUB | 2024-06-01 | Bugle |  |  | 345 | 138 |  | Relocate the existing 138 kV Page substation to the new Bugle site. 138kV to be built as breaker and a half arrangement. | MO |  |  | 27500000
A in MTEP20 |  | AmerenMO | 16555 | 25379 | LN | 2024-06-01 | MRPD | Bugle |  | 345 |  |  | New 345 kV line extension from Bugle 345/138 kV Substation to Mason-Sioux-7 345 kV line (3000 A). | MO
A in MTEP20 |  | AmerenMO | 16555 | 25378 | SwSta | 2024-06-01 | MRPD |  |  | 345 |  |  | MRPD 345 kV ring bus (in S-MASN-7 line) | MO
A in MTEP20 | Central | AmerenIL | 16556 | 24354 | SwSta | 2022-06-01 | Bueller | Substation |  | 138 |  |  | Install a new 138 kV ring bus tapping the Macomb West-Niota 138 kV line | IL |  |  | 6600000
A in MTEP20 | Central | AmerenIL | 16704 | 24384 | LNrb | 2023-12-01 | Salem West | Mt Vernon West | 1332 | 138 |  |  | Rebuild line to 2000A. Upgrade terminal equipment at Salem West to 2000A including 1272 ACSR bus conductor and switch 1330. | IL |  |  | 13200000
A in MTEP20 | Central | AmerenIL | 16705 | 24385 | LNrb | 2021-12-01 | Pana | Shelbyville South | 1430 | 138 |  |  | Install OPGW | IL |  |  | 4600000
A in MTEP20 | Central | AmerenIL | 16706 | 24386 | TEQ | 2022-12-01 | Goose Creek | Substation |  | 345 |  |  | Rebuild the Goose Creek 345 kV ring bus to 3000A capability. Replace all limiting terminal equipment and bus conductors with equipment capable of 3000A. | IL |  |  | 2600000
A in MTEP20 | Central | AmerenIL | 16707 | 24387 | SwSta | 2023-12-01 | Vermillion | N. Champaign | 1396 | 138 |  |  | Install new ring bus substation at the intersection of VERM-NCMP-1396 and GIFF-SDNY-1588. Install 4 positions initial, 6-positions ultimate. Rebuild the existing Vermillion-N. Champaign-1396 138 kV line to 2000A in both directions from the new substation. Upgrade terminal equipment at Vermillion to 2000A including switch 1328, bus conductor and relay load limit. Upgrade terminal equipment at North Champaign to 2000A including 795 AAC bus conductor and re-tap 1 CT. | IL |  |  | 7200000
A in MTEP20 | Central | AmerenIL | 16708 | 24388 | LNrc | 2023-12-01 | Hines | Pioneer | 1326 | 138 |  |  | Replace existing 927 ACAR conductor with ACCR conductor | IL |  |  | 3500000
A in MTEP20 | Central | AmerenIL | 16709 | 24389 | TEQ | 2021-12-01 | Ashley | Venice | 2 | 138 |  |  | Replace 2 1200A switches and 1000 Kcmil CU bus conductor with equipment having 2000A capability at Venice Substation | IL
A in MTEP20 | West | ITCM | 16710 | 24390 | LNup | 2020-01-16 | Marshalltown | Blairstown | 1 | 115 | 115 |  | Raise structures on the line to mitigate sag limits. | IA |  |  | 1052821
A in MTEP20 | West | ITCM | 16710 | 24391 | LNup | 2019-09-02 | Blairstown | Prairie Creek | 1 | 115 | 115 |  | Raise structures to mitigate sag limits. | IA |  |  | 1680000
A in MTEP20 | West | ITCM | 16844 | 24427 | SwSta | 2019-11-21 | Bison | Switch Station |  | 345 | 345 | 3000 amp | TOIF faclities at the new Bison 345kV switch station dedicated to the J495 generating facility. | IA |  |  | 0
A in MTEP20 | West | ITCM | 16844 | 24429 | LN | 2019-10-18 | Colby | Ledyard | 1 | 345 | 345 |  | TO-funded, 345kV Colby-Ledyard Line Tap Network Upgrade for J495. Tap of the Ledyard-Colby 345 kV line roughly 7 miles east of the Ledyard station for the line taps into the new Bison 345kV Switch Station. | IA |  |  | 2520000
A in MTEP20 | West | ITCM | 16844 | 24428 | SwSta | 2019-10-18 | Bison | Switch Station |  | 345 | 345 | 3000 amps | TO-Funded, 345 kV Bison Switching Station Network Upgrade for J495. ITCM will construct a 3 terminal, 3 breaker 345kV switch station for the interconnection of J495. | IA |  |  | 8142026
A in MTEP20 | West | ITCM | 16864 | 24430 | LNrb | 2020-10-01 | Irvine | Poweshiek | 1 | 161 | 161 | 1595 amp | The Poweshiek to Irvine 161 kV line is to be rebuilt on existing ROW with a conductor having a minimum summer rating of 1,595A. | IA | 9.43 |  | 10500000
A in MTEP20 | West | ITCM | 16864 | 24431 | SUBmisc | 2020-10-01 | Poweshiek | Substation |  | 161 | 161 | 343 MVA | Upgrade teriminal limits for generator interconnection J475. | IA |  |  | 500000
A in MTEP20 | West | ITCM | 16865 | 24432 | SUBmisc | 2020-10-15 | DAEC | Substation |  | 161 | 161 | 2000 amp | The DAEC 161 kV substation will be expanded to accommodate the J504 terminal, including the addition of breaker position 5953. New equipment should be capable of 2000A. | IA |  |  | 273780
A in MTEP20 | West | ITCM | 16866 | 24433 | LNup | 2019-11-07 | Poweshiek | Reasnor | 1 | 161 | 161 | 366 MVA | One span on the Poweshiek - Reasnor kV line will be raised to mitigate sag limits and increase the summer rating to 366 MVA (1313 A). | IA |  |  | 240000
A in MTEP20 | South | AECC | 16884 | 24484 | SwSta | 2021-06-01 | Helena Industrial |  |  | 115 |  |  | Remove line breaker | AR |  |  | 150000
A in MTEP20 | Central | AmerenIL | 16944 | 24442 | SUB | 2022-12-01 | Louisville South | Substation |  | 345 | 138 |  | Install new 345 kV ring bus at the Louisville South Substation location tapping the Newton-Xenia-1 line. Install 560 MVA 345-138 kV transformer and connect to the Louisville South 138 kV bus. | IL |  |  | 25200000
A in MTEP20 | Central | AmerenIL, AmerenMO | 16984 | 24450 | LNrb | 2021-12-01 | Sioux | Meppen North | 4 | 138 |  |  | Rebuild existing river crossing (structures 173-179) | IL,MO |  |  | 45700000
A in MTEP20 | Central | AmerenMO | 16985 | 24451 | LNrb | 2021-06-01 | Sioux | Meppen | 4 | 138 |  |  | Rebuild 3.7 mile Missouri side section (Str. 146-173) of the old Page-Keokuk line w/ T2 conductor. Page-Sioux-4: Rebuild Missouri River crossing (Str. 112-117) w/ 2000A rated conductor. | MO |  |  | 3500000
A in MTEP20 | Central | AmerenMO | 16986 | 24452 | LNrb | 2023-12-02 | Page | Sioux | 4 | 138 |  |  | Page-Sioux-4: Rebuild existing Missouri River crossing (Str. 112-117) due to aging infrastructure | MO |  |  | 26657745
A in MTEP20 | Central | AmerenIL | 16987 | 24453 | SUB | 2023-12-01 | Benton NW | Substation |  | 138 |  |  | Install 6 position ultimate ring bus at Benton NW. | IL |  |  | 8500000
A in MTEP20 | Central | AmerenIL | 16988 | 24454 | LN | 2023-12-01 | Fogarty | Limit |  | 138 |  |  | Install new 138 kV line from Fogart to Limit | IL |  |  | 12300000
A in MTEP20 |  | AmerenIL | 16988 | 25375 | SwSta | 2023-12-01 | McGrath |  |  | 138 |  |  | 3 position ring | IL |  |  | 5600000
A in MTEP20 | Central | AmerenIL | 16988 | 24608 | SUB | 2023-12-01 | Limit | Substation |  | 138 |  |  | Install new ring bus at Limit | IL |  |  | 6700000
A in MTEP20 | Central | AmerenIL | 16990 | 24456 | SUB | 2022-12-01 | Wanda | Substation |  | 138 |  |  | Install new 6 position ultimate ring bus at Wanda Substation. | IL |  |  | 6300000
A in MTEP20 | South | SMEPA | 17004 | 25268 | GEN | 2019-12-25 | Benndale GT (J888) |  |  | 69 |  |  | The existing Benndale combustion turbine facility will have two 11MW RICE gas-fired engines installed | MS
A in MTEP20 | South | SMEPA | 17004 | 25270 | SwSta | 2019-12-25 | Benndale GT (J888) |  |  | 69 |  |  | The Benndale switching station will be rebuilt and all oil circuit breakers will be replaced with gas circuit breakers and updated relaying package | MS |  |  | 2350000
A in MTEP20 | South | SMEPA | 17004 | 25269 | TX | 2019-12-25 | Benndale GT (J888) |  |  | 69 |  |  | Install new GSU | MS |  |  | 660000
A in MTEP20 | Central | AmerenMO | 17046 | 24473 | SUB | 2022-12-01 | Kelso | Substation |  | 345 | 161 |  | Install new 3000 A circuit breaker and motor-operated disconnect switch on 345 kV position V3. Replace the existing Kelso substation 336 MVA auto transformer #1 with a 560 MVA transformer. Replace the existing Kelso substation 161 kV bus tie 1-2 position H7 circuit breaker and bus disconnect switches. Replace the existing Kelso substation 161 kV position H6 circuit breaker and disconnect switch, upgrade the bus conductor of position H6 to achieve a minimum current carrying capability of 3000 A. Replace the existing Kelso substation H3 and H4 161 kV circuit breakers and disconnect switches in the CAPE-KEL-2 and KEL-MINR-2 terminals. Upgrade Kelso substation positions H3 and H4 bus conductors to achieve a minimum current carry capability of 2000 A. Replace the existing Kelso substation 161 kV disconnect switch on position H10. Replace the existing Kelso substation H11 and H12 161 kV disconnect switches (line and bus) in the CAPE-KEL-3) and KEL-MORLEY-3 terminals. | MO |  |  | 5800000
A in MTEP20 | Central | AmerenMO | 17065 | 24480 | SUB | 2021-12-01 | Tegeler | Substation |  | 138 |  |  | Install a new 2000 A circuit breaker and associated disconnect switches in the TGLR-BLAN-6756 138 kV line terminal. Replace the existing 1600 A circuit breaker and associated 1200 A disconnect switches and 1590 kcmil AAC bus conductor at position H5 with equipment capable of carrying 2000 A during summer emergency conditions. Increase relay load limit. Replace the existing 1200 A disconnect switches and 1590 kcmil AAC bus conductor in position H9 to match the capability of the 2000 A circuit breaker. Install 2 circuit switchers on the high-side of the new and existing 138/34.5 kV transformers, having a minimum continuous current rating of 600 A. | MO |  |  | 2100000
A in MTEP20 | South | Entergy-MS | 17086 | 24482 | LN | 2022-12-01 | South Brandon | East Brandon |  | 115 |  |  | Build a new 115kV line from South Brandon to East Brandon | MS |  |  | 3510000
A in MTEP20 |  | Entergy-MS | 17086 | 25469 | CB | 2022-12-01 | Whitfield |  |  | 115 |  |  | Entergy - Install substation breakers at Whitfield 115kV substation | MS |  |  | 6182989
A in MTEP20 | South | Entergy-MS | 17086 | 24483 | TAP | 2022-12-01 | South Brandon |  |  | 115 |  |  | Tap L540A(East Whitfield - South Brandon) | MS |  |  | 260000
A in MTEP20 | East | ITCT | 17124 | 24492 | LNrl | 2021-06-01 | Frisbie | Midtown | 1 | 120 |  |  | Relocate approximately 1500 ft of underground pipe type cable that is currently under the Milwaukee Street bridge over I-75 in the city of Detroit. | MI | 0.7 |  | 1500000
A in MTEP20 | West | MP | 17184 | 24509 | SUB | 2021-11-01 | Nemadji |  |  | 115 | 13.8 | 39.2 | New 115/13.8 kV transformer, ring bus, breaker, circuit switcher, and associated equipment | WI |  |  | 2500000
A in MTEP20 | East | WPSC | 17204 | 24512 | TX | 2020-02-29 | Vestaburg |  |  | 138 |  |  | Vestaburg 138/69kV transformer | MI |  |  | 3520000
A in MTEP20 | Central | AmerenMO | 17224 | 24513 | SUB | 2022-06-01 | Pershall | Substation |  | 138 | 12 |  | Install main-tie-main straight bus substation connecting to Berkeley-Sioux-1 and Berkeley-Sioux-2 lines. | MO
A in MTEP20 | Central | AmerenIL | 17285 | 24521 | SwSta | 2023-12-01 | Quiver | Substation |  | 138 |  |  | Install new ring bus installation at the intersection of Mason City West – Fogarty -1346 and San Jose Rail – Interstate – 1318 138 kV line. | IL |  |  | 13000000
A in MTEP20 | West | MDU | 17304 | 24524 | CAP | 2020-02-28 | Ellendale 345 |  |  | 230 |  |  | four 230kV, 50 Mvar fast-switched capacitors | ND |  |  | 5497000
A in MTEP20 | West | MDU | 17304 | 24525 | CB | 2020-02-28 | Ellendale 345 |  |  | 345 |  |  | Add new 345 kV reactor switcher | ND |  |  | 934000
A in MTEP20 | Central | AmerenIL | 17324 | 24527 | SUB | 2020-10-15 | Mason | Substation |  | 138 |  |  | Install ultimate 6 position ring bus at Mason (IL) substation to provide interconnection for J1055 Glacier Sands wind farm. | IL |  |  | 10000000
A in MTEP20 | Central | AmerenMO | 17344 | 24528 | SUB | 2021-12-01 | Berkeley | Substation |  | 138 |  |  | Replace 138 kV bus tie 1-2 and 2-3 breakers. Upgrade position to 2000A | MO |  |  | 1300000
A in MTEP20 | Central | AmerenIL | 17345 | 24529 | LNrb | 2020-06-01 | Auburn North | Jacksonville IP | 1306 | 138 |  |  | Scope is broken into 3 sections: o Structures 644-668 will be a complete rebuild to 1600A with 795 T2 conductor. O Structures 19-49 are single pole wood and will require structure replacements. O Jacksonville-Auburn North – 5 structure raises | IL |  |  | 2500000
A in MTEP20 | Central | AmerenMO | 17346 | 24530 | SUBmisc | 2022-12-01 | Rivermines | Substation |  | 138 |  |  | Replace 138kV breakers on bus tie 1-2 and bus tie 2-3 | MO |  |  | 600000
A in MTEP20 | East | ITCT | 17364 | 24531 | SwSta | 2021-05-14 | J793 - New 345kV Station |  |  | 345 |  |  | Install a new 345 kV station with 3-345 kV breakers and associated disconnects in a ring bus configuration. | MI |  |  | 8238281
A in MTEP20 | East | ITCT | 17364 | 24534 | RLY | 2021-05-14 | Belle River |  |  | 345 |  |  | ITCT will upgrade the relay panel at Belle River Power Plant 345kV station to accommodate J793 generator interconnection. | MI |  |  | 140916
A in MTEP20 | East | ITCT | 17364 | 24533 | RLY | 2021-05-14 | Fitz |  |  | 345 |  |  | ITCT will upgrade the relay panel at Fitz 345kV station to accommodate J793 generator interconnection. | MI |  |  | 140916
A in MTEP20 | East | ITCT | 17364 | 24532 | TAP | 2021-05-14 | Belle River | Fitz | 2 | 345 |  |  | ITCT will loop the Belle River - Fitz #2 345kV circuit into the new J793 substation. | MI |  |  | 1214880
A in MTEP20 | East | METC | 17365 | 24535 | SUB | 2020-07-30 | J717_J728 |  |  | 138 |  |  | Construct a new 138 kV 3 breaker ring station | MI |  |  | 6728000
A in MTEP20 | East | METC | 17365 | 24802 | SUBmisc | 2020-07-30 | Warren |  |  | 138 |  |  | Replace Relaying to accommodate OPGW and replace terminal equipment to achieve 287 MVA | MI |  |  | 320000
A in MTEP20 | East | METC | 17365 | 24536 | LINE | 2020-07-30 | Warren | Bullock | 1 | 138 |  |  | Cut the Warren - Bullock 138 kV circuit into the new J717_J728 interconnection station. Install OPGW from the new station to Warren | MI |  | 0.1 | 1143000
A in MTEP20 | East | METC | 17384 | 24537 | SUB | 2021-09-01 | Goss |  |  | 138 |  |  | Install a 40kA breaker at Goss 138kV position 11B7. | MI |  |  | 790000
A in MTEP20 | East | METC | 17384 | 24538 | SUB | 2021-09-01 | Goss |  |  | 138 |  |  | Add three 40kA breakers at Goss 138kV positions 9B7, 9M9, and 9W8. | MI |  |  | 2020000
A in MTEP20 | West | MDU | 17466 | 24557 | LN | 2021-07-31 | Mandan | Napoleon SW | 1 | 230 |  |  | Remove Heskett substation and reconnect the Mandan-Heskett 230 and Heskett-Wishek 230 line together to form new Mandan-Wishek 230 line | ND |  |  | 1000000
A in MTEP20 | West | MDU | 17466 | 24571 | LN | 2023-05-31 | Mandan | Heskett #4 | 1 | 115 |  |  | Re-terminate Heskett-Heskett #4 interconnection line to Mandan substation | ND |  |  | 1000000
A in MTEP20 | West | MDU | 17466 | 24570 | LN | 2022-06-30 | Mandan | Heskett #3 | 1 | 115 |  |  | Re-terminate Heskett-Heskett #3 interconnection line to Mandan substation | ND |  |  | 1000000
A in MTEP20 | West | MDU | 17466 | 24569 | LN | 2022-06-30 | Mandan | Mandan 38th St | 1 | 115 |  |  | Re-terminate Mandan-Heskett 115 kV line to the Mandan 38th St substation | ND |  |  | 1000000
A in MTEP20 | West | MDU | 17466 | 24568 | LN | 2021-11-30 | Mandan 38th St | Judson | 1 | 41.6 |  |  | Re-terminate Heskett-Judson 41.6 kV line to Mandan 38th St substation | ND |  |  | 1000000
A in MTEP20 | West | MDU | 17466 | 24567 | LN | 2021-11-30 | Mandan 38th St | Mandan Refinery | 1 | 41.6 |  |  | Re-terminate Heskett-Mandan Refinery 41.6 kV line to Mandan 38th St substation | ND |  |  | 1000000
A in MTEP20 | West | MDU | 17466 | 24566 | LN | 2021-11-30 | Mandan 38th St | Plainsview | 1 | 69 |  |  | Re-terminate Heskett-Plainsview 69 kV line to Mandan 38th St substation | ND |  |  | 1000000
A in MTEP20 | West | MDU | 17466 | 24565 | LN | 2021-11-30 | Mandan 38th St | Colllins | 1 | 115 |  |  | Re-terminate Heskett-Collins 115 kV line to the Mandan 38th St substation | ND |  |  | 1000000
A in MTEP20 | West | MDU | 17466 | 24564 | LNrl | 2021-11-30 | Mandan | Beulah |  | 115 |  |  | Move Beulah 115 kV line to new terminal in Mandan substation to allow for second 230/115 transformer | ND |  |  | 1000000
A in MTEP20 | West | MDU | 17466 | 24563 | SUB | 2021-11-30 | Mandan 38th St |  |  | 115 | 41.6 |  | New 115/69/41.6 kV substation: 4 breaker 115 kV ring bus, one 115/69 kV transformer, one 115/41.6 kV transformer, 69 kV bus and 41.6 kV bus | ND |  |  | 7000000
A in MTEP20 | West | MDU | 17466 | 24562 | SwSta | 2021-11-30 | Mandan |  |  | 115 |  |  | Expand 115 kV breaker and a half bus to accommodate 230/115 transformer and line move from Heskett: seven new 115 breakers | ND |  |  | 6500000
A in MTEP20 | West | MDU | 17466 | 24559 | SwSta | 2021-07-31 | Mandan |  |  | 230 |  |  | Add one 230 kV breaker to accommodate move of Mandan-Wishek 230 kV line | ND |  |  | 500000
A in MTEP20 | West | MDU | 17466 | 24558 | TX | 2020-11-30 | Mandan |  |  | 230 | 115 | 224 | Move Heskett 230/115 kV transformer to Mandan substation | ND |  |  | 1000000
A in MTEP20 | Central | DEI | 17484 | 24560 | LNup | 2024-06-01 | Wabash River Sta. | Water St. | 1 | 138 |  | 198 | Wabash River to Water St. 13845 upgrade existing 477ACSR line conductor's maximum operating temperature from 100C (198MVA) to 120C (228MVA) | IN | 8.13 |  | 3950400
A in MTEP20 | East | ITCT | 17504 | 24575 | SUB | 2022-10-31 | Abrams |  |  | 120 |  |  | Install new 120kV station including two 40kA line breakers and one 40kA section breaker. | MI |  |  | 3400000
A in MTEP20 | East | ITCT | 17504 | 24578 | RLY | 2022-10-31 | Skylark |  |  | 120 |  |  | Upgrade position HD relaying at Skylark. | MI |  |  | 173000
A in MTEP20 | East | ITCT | 17504 | 24577 | RLY | 2022-10-31 | Northeast |  |  | 120 |  |  | Upgrade position JE relaying. | MI |  |  | 173000
A in MTEP20 | East | ITCT | 17504 | 24576 | LN | 2022-10-31 | Northeast | Skylark | 1 | 120 |  |  | Loop-in Abrams 120kV by extending the Northeast – Skylark 120kV circuit with 954 ACSR | MI |  | 0.1 | 773000
A in MTEP20 | South | SMEPA | 17524 | 25538 | LNrc | 2021-06-01 | Batesville | Batesville TVA |  | 161 |  |  | Reconductor both Batesville to Batesville TVA 161kV tie lines with Aluminum Conductor Composite Reinforced (ACCR) conductor. | MS |  |  | 650000
A in MTEP20 | West | ATC | 17525 | 24579 | SUB | 2020-08-01 | Highland SS |  |  | 138 |  |  | Highland Substation Network Upgrades | WI |  |  | 4557241
A in MTEP20 |  | ATC | 17525 | 25358 | SUBmisc | 2021-12-31 | Dodgeville SS |  |  | 138 | 69 |  | Dodgeville SS - Network Upgrades for Y-138 Sectionalization | WI |  |  | 51516
A in MTEP20 |  | ATC | 17525 | 25357 | SUBmisc | 2021-12-31 | Eden SS |  |  | 138 | 69 |  | Eden SS - Network Upgrades related to Y-138 Sectionalization | WI |  |  | 51516
A in MTEP20 |  | ATC | 17525 | 25356 | LNup | 2021-12-31 | Eden SS | Spring Green SS | X-17 | 138 |  |  | X-17 uprate will consist of rerating the X-17 line from Highland SS to Spring Green SS | WI |  |  | 2981519
A in MTEP20 |  | ATC | 17525 | 25355 | LNup | 2021-12-31 | Eden SS | Dodgeville SS | Y-138 | 138 | 69 |  | Y-138 Sectionalization, transmission line upgrades will consist of construction of ~2.6 miles of new dbl circuit | WI |  |  | 7761083
A in MTEP20 | West | ATC | 17525 | 24583 | SUB | 2021-12-31 | Highland SS |  |  | 138 |  |  | Highland Substation - Adding a fourth position and expanding the site to support a 100 MVA autotransformer and loop in of Y-138. | WI |  |  | 5810131
A in MTEP20 | West | ATC | 17525 | 24582 | SUB | 2020-08-01 | Spring Green |  |  | 138 |  |  | Spring Green Substation Network Upgrades | WI |  |  | 51516
A in MTEP20 | West | ATC | 17525 | 24581 | SUB | 2020-08-01 | Eden |  |  | 138 |  |  | Eden Substation Network Upgrades | WI |  |  | 51516
A in MTEP20 | West | ATC | 17525 | 24580 | LNup | 2020-08-01 | Eden | Wyoming Valley |  | 138 |  |  | X-17 Network Upgrade | WI |  |  | 864481
A in MTEP20 | West | ATC | 17526 | 24584 | SUB | 2020-08-01 | Kewaunee |  |  | 138 |  |  | Kewaunee Substation Network Upgrades | WI |  |  | 1571480
A in MTEP20 | West | ATC | 17526 | 24585 | SUB | 2020-08-01 | Kewaunee |  |  | 138 |  |  | Kewaunee Substation Interconnection Facilities | WI |  |  | 721559
A in MTEP20 | Central | IPL | 17564 | 24623 | SUB | 2020-12-31 | Rockville 345 kV |  |  | 345 |  |  | New 345 kV breaker | IN |  |  | 3600000
A in MTEP20 | Central | AmerenIL | 17565 | 24591 | LN | 2025-06-01 | Oreana | Decatur N 27th Street |  | 138 |  |  | Install new 138 kV line. | IL |  |  | 8400000
A in MTEP20 |  | AmerenIL | 17565 | 25377 | TEQ | 2025-06-01 | Decatur 27th Street |  |  | 138 |  |  | Add line position | IL |  |  | 1700000
A in MTEP20 |  | AmerenIL | 17565 | 25376 | TEQ | 2025-06-01 | Oreana |  |  | 138 | 69 |  | Add line position | IL |  |  | 2100000
A in MTEP20 | West | ATC | 17585 | 24593 | SUB | 2023-12-31 | Colley Road SS |  |  | 138 | 69 |  | Transformer Replacement and Breaker & Relay Asset Renewal | WI |  |  | 3150000
A in MTEP20 | Central | AmerenIL | 17604 | 24595 | SUBmisc | 2023-12-01 | Stallings | Roxford | 4581 | 345 |  |  | Upgrade 345 kV switches V4A and V4b to 3000A. Remove the 2000A wave trap. Install OPGW. | IL |  |  | 1400000
A in MTEP20 | Central | AmerenMO | 17605 | 24596 | LNrc | 2022-12-01 | Page | Berkeley | 1&2 | 138 |  |  | Reconductor the Page-Berkeley-1&2 circuits with ACCR conductor. | MO |  |  | 11300000
A in MTEP20 | Central | AmerenMO | 17624 | 24606 | SUB | 2023-12-01 | Pike | Substation |  | 161 |  |  | Rebuild the Pike 161 kV substation to a Ring bus configuration. | MO |  |  | 13400000
A in MTEP20 | Central | AmerenMO | 17625 | 24607 | SUB | 2022-12-01 | McClay | Substation |  | 138 |  |  | Add breakers to each of the 138 kV lines and upgrade relays. | MO |  |  | 1300000
A in MTEP20 | Central | AmerenIL | 17626 | 24609 | LNrb | 2024-12-01 | Kickapoo | Limit | 1325 | 138 |  |  | Rebuild line from Kickapoo to Limit to 2000A. Double circuit from Limit to McGrath to supply McGrath radially from Limit. | IL |  |  | 3100000
A in MTEP20 | Central | AmerenIL | 17627 | 24610 | LNrb | 2022-12-01 | Fogarty | Kickapoo | 1672 | 138 |  |  | Rebuild line to 2000A. | IL |  |  | 14400000
A in MTEP20 | West | ATC | 17628 | 24611 | SUB | 2022-06-01 | Preble SS |  |  | 138 |  |  | ATC will extend 138 kV bus and add line and bus-tie breakers | WI |  |  | 3498694
A in MTEP20 | Central | AmerenIL | 17644 | 24617 | SUB | 2022-06-01 | Decatur Route 51 | Substation |  | 138 |  |  | Install initial 138 kV 4-position (ultimate 6-position) ring bus at the Decatur Route 51 substation locattion | IL |  |  | 9400000
A in MTEP20 | West | GRE | 17664 | 24726 | SUB | 2023-09-30 | Portage Lake |  |  | 115 | 69 |  | Interconnect the new Portage Lake 115/69 kV substation to the Minnesota Power 13 Line at or near the existing GRE/MLEC Kimberly substation. | MN |  |  | 6800000
A in MTEP20 | West | GRE | 17664 | 24727 | LN | 2023-09-30 | Palisade | Portage Lake | 1 | 69 |  |  | Build a new 69 kV transmission line from near the existing GRE/MLEC Palisade substation to the new GRE Portage Lake substation. | MN |  | 9.5 | 5901117
A in MTEP20 |  | MP | 17664 | 25924 | LN | 2023-09-30 | Portage Lake |  |  | 115 |  |  | MP 115 kV line extensions | MN |  |  | 500000
A in MTEP20 | Central | AmerenMO | 17665 | 24618 | SUB | 2021-12-31 | Barrett Station | Substation |  | 138 | 12 |  | Install 3 breakers in a main-tie-main configuration with an open bus tie to facilitate the installation of a 2nd transformer. Install circuit switchers on the existing and new transformers. | MO
A in MTEP20 | Central | AEP | 17684 | 24620 | SUB | 2023-02-15 | Greentown 765kV |  |  | 765 | 138 | 750 | 6 765kV Breakers and 1 765/138kV Transformer. | IN |  |  | 70000000
A in MTEP20 | Central | AmerenMO | 17685 | 24621 | SUB | 2027-12-01 | Creve Coer | Substation |  | 138 | 12 |  | Tap the Mason-Meramec-1 & 2 lines to provide a main-tie-main configuration for new 138-12 kV substation. | MO
A in MTEP20 | Central | AmerenMO | 17686 | 24622 | SUB | 2023-12-01 | Dougherty Ferry | Substation |  | 138 | 12 |  | Tap the Mason-Meramec-1 & 2 lines to provided a main-tie-main configuration for the installation of a new 138-12 kV substation. | MO
A in MTEP20 | West | ITCM | 17704 | 24626 | SUB | 2021-12-30 | Cedar Rapids Hunter Field | Substation |  | 69 | 25 | 50 MVA | IPL will be building a new 69/24.9 kV substation named Cedar Rapids Hunter Field near the existing Viola’s Corner substation. This new substation will replace Viola’s Corner. The new substation will have 1 new 69/24.9 kV 50 MVA transformer installed initially, with a second transformer to be added in the future as load grows in the area. ITC will build a new 69 kV substation with two single box structures and two breakers installed, one line breaker and one bus tie breaker, and will add an additional line breaker in the future when IPL adds a second transformer. | IA |  |  | 2460120
A in MTEP20 | West | ITCM | 17704 | 24793 | RLY | 2021-12-30 | Beverly | Substation |  | 69 | 69 |  | Upgrade relays at Beverly sub on the Beverly - Fairfax #2 69 kV line to allow for Hunter Field sub addition. | IA |  |  | 100140
A in MTEP20 | West | ITCM | 17704 | 24792 | RLY | 2021-12-30 | Fairfax | Substation |  | 69 | 69 |  | Upgrade relays at Fairfax sub on the Beverly - Fairfax #2 69 kV line to allow for Hunter Field sub addition. | IA |  |  | 100140
A in MTEP20 | West | ITCM | 17704 | 24627 | LN | 2021-12-30 | Beverly | Fairfax | 2 | 69 | 69 |  | Line taps for new Cedar Rapids Hunter Field substation. | IA |  |  | 918390
A in MTEP20 | West | ITCM | 17705 | 24628 | SUB | 2021-12-31 | Madrid North | Substation |  | 69 | 34 |  | IPL has requested ITC to rebuild the Madrid North Substation to a standard single box and double box with a bus tie breaker to accommodate their 25 kV plans which will include two transformers and 25 kV switchgear. ITC will also need to install a new control enclosure, as IPL will be retiring their existing control enclosure to accommodate their new switch gear. The existing 69 kV circuit switcher will be replaced with a new 69 kV breaker, which will allow for future retirement of the bus work associated with the 69/34.5 kV transformer. The existing zig-zag transformer should be removed to allow additional space for the installation of the new ITC owned control enclosure. The 69/34.5 kV transformer will need to remain until the conversion to 69 kV happens between Dawson and Madrid North (covered on EI Sketch ITCMW_16_034). The existing section of 69 kV bus that feeds the 69/34.5 kV transformer, transformer, and low-side breaker should be re-used, and then removed in the future as part of the 69 kV conversion. | IA |  |  | 3544344
A in MTEP20 | West | ITCM | 17705 | 24630 | TAP | 2021-12-31 | Huxley Industrial | Madrid North | 1 | 69 | 69 |  | Line tap for Madrid North Sub. | IA |  |  | 300000
A in MTEP20 | West | ITCM | 17705 | 24629 | TAP | 2021-12-31 | Boone Quartz | Madrid North | 1 | 69 | 69 |  | Linte tap for Madrid North Sub. | IA |  |  | 300000
A in MTEP20 | West | ITCM | 17724 | 24631 | SUB | 2023-12-31 | Sixth Street | Substation |  | 115 | 34 |  | Once the remaining 34.5 kV lines at the Sixth St Substation are converted to 69 kV, the remaining substation equipment should be retired, including any control enclosures and fence, etc. The communications currently routed through Sixth Street will also need to be moved/removed before the retirement can be completed. | IA |  |  | 366540
A in MTEP20 | West | ITCM | 17724 | 24632 | LN | 2023-01-31 | Stoney Point | Saints Run | 1 | 115 | 115 |  | Reroute the 115kV lines to bypass the Sixth Street substation. | IA |  |  | 1140000
A in MTEP20 | West | ITCM | 17725 | 24633 | SUB | 2021-12-31 | Savanna | Substation |  | 161 | 161 |  | TC will be expanding the Savanna Substation to a Ring Bus capable of 6-positions. The new 161kV equipment will be capable of 2000A. There will be several phases for the 161kV. | IL |  |  | 7249200
A in MTEP20 | West | ITCM | 17725 | 24635 | TAP | 2021-12-31 | Savanna | Galena | 1 | 161 | 161 |  | Line tap work required for the Savanna 161kV sub expansion. | IL |  |  | 723000
A in MTEP20 | West | ITCM | 17725 | 24634 | TAP | 2021-12-31 | Savanna | York | 1 | 161 | 161 |  | Line tap work required for the Savanna 161kV sub expansion. | IL |  |  | 723000
A in MTEP20 | West | ITCM | 17726 | 24636 | SUB | 2021-12-31 | Savanna | Substation |  | 69 | 69 |  | ITC will be expanding the Savanna 69kV Substation to a Ring Bus capable of 6-positions. Most new 69kV equipment will be capable of 1200A or greater. ITC will install a 161/69kV 150MVA transformer at Savanna. The 161/69kV transformer position and the Metform position will be capable of 2000A or greater. There will be several phases for the 69kV. | IL |  |  | 7942800
A in MTEP20 | West | ITCM | 17726 | 24637 | TAP | 2021-12-31 | Savanna | Substation |  | 69 | 69 |  | Line tap work required to connect the 69kV lines at Savanna sub. | IL |  |  | 1593000
A in MTEP20 | West | ITCM | 17727 | 24638 | SUB | 2021-12-31 | York | Substation |  | 69 | 69 |  | Phase 1. ITC will be expanding the York Substation to include a 161/69kV 150MVA transformer. All new 69kV equipment will be capable of 2000A. A tie switch will be added to the 161kV. | IL |  |  | 7485000
A in MTEP20 |  | ITCM | 17727 | 25304 | LN | 2025-12-31 | York | Sub |  | 69 | 69 |  | Phase 2. ITC will be retiring the 34.5kV out of the York Substation. No additional 161kV equipment will be needed to accommodate this work. All new 69kV equipment will be capable of 1200A or greater. | IL |  |  | 136200
A in MTEP20 |  | ITCM | 17727 | 25303 | SUB | 2021-12-31 | York | Substation |  | 161 | 161 |  | Phase 1. ITC will be expanding the York Substation to include a 161/69kV 150MVA transformer. All new 69kV equipment will be capable of 2000A. A tie switch will be added to the 161kV. | IL |  |  | 1275600
A in MTEP20 | West | ITCM | 17727 | 24639 | SUB | 2025-12-30 | York | Substation |  | 69 | 69 |  | Phase 2. ITC will be retiring the 34.5kV out of the York Substation. No additional 161kV equipment will be needed to accommodate this work. All new 69kV equipment will be capable of 1200A or greater. | IL |  |  | 879600
A in MTEP20 | West | ITCM | 17728 | 24640 | LNrb | 2020-12-30 | Savanna | Metform | 1 | 69 | 69 |  | ITC will rebuild approximately 6 miles of the Savanna – Metform – York 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 1200A or higher | IL |  |  | 9274800
A in MTEP20 | West | ITCM | 17728 | 25237 | TAP | 2021-12-31 | Danisco | Tap |  | 69 | 69 |  | Construct new line tap to Danisco Substation | IL |  |  | 271200
A in MTEP20 | West | ITCM | 17728 | 24641 | LNrb | 2020-12-30 | Dansico | York | 1 | 69 | 69 |  | ITC will need to investigate the Danisco to York 34.5kV to determine if the insulators are capable of 69kV operation. If not, ITC will reinsulate the Danisco to York 34.5kV line with 69kV insulators. The existing conductor is 954 ACSR and does not need to be replaced due to ampacity needs. The static is 3/8 steel. | IL |  |  | 1203600
A in MTEP20 | West | ITCM | 17729 | 24642 | LN | 2025-12-30 | Argo Fay | York | 1 | 69 | 69 |  | ITC will build a new 69kV line approximately 6 miles from the York Substation to the Argo Fay Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. | IL |  | 6 | 8986800
A in MTEP20 | West | ITCM | 17729 | 24646 | LN | 2025-12-30 | Argo Fay | Savanna | 1 | 34 | 34 |  | ITC will retire approximately 6 miles of 34.5kV line between Argo Fay and the Savanna substation | IL |  |  | 540000
A in MTEP20 | West | ITCM | 17729 | 24645 | LN | 2025-12-30 | Argo Fay | Clay | 1 | 34 | 34 |  | ITC will retire approximately 6 miles of 34.5kV line between Argo Fay and the Clay substation. | IL |  |  | 360000
A in MTEP20 | West | ITCM | 17729 | 24644 | LNrb | 2025-12-30 | Argo Fay | Chadwick | 1 | 69 | 69 |  | ITC will rebuild approximately 6.5 miles of the Argo Fay Substation to the Chadwick Substation 34.5kV line to 69kV Standards. The overhead conductor will have an ampacity of 600A or higher. | IL | 6.5 |  | 5088000
A in MTEP20 | West | ITCM | 17729 | 24643 | LN | 2025-12-30 | Chadwick | Clay | 1 | 69 | 69 |  | ITC will build a new 69kV line approximately 6.5 miles from the Clay Substation to the Chadwick Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. | IL |  | 6.5 | 7375200
A in MTEP20 | West | ITCM | 17730 | 24650 | LNrb | 2025-12-30 | Savanna | Clay | 1 | 69 | 69 |  | ITC will rebuild approximately 7.75 miles of 34.5kV to 69kV standards from Savanna Substation to Clay Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. | IL | 7.75 |  | 8262000
A in MTEP20 | West | ITCM | 17731 | 24647 | LNrb | 2025-12-30 | Savanna | Eaton | 1 | 69 | 69 |  | ITC will rebuild approximately 1.66 miles of the Savanna – Eaton 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. | IL |  |  | 2537746
A in MTEP20 | West | ITCM | 17731 | 24649 | LNrb | 2025-12-30 | Bowen | Savanna | 1 | 69 | 69 |  | ITC will rebuild approximately 3.80 miles of the Bowen – Savanna 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. | IL |  |  | 5775600
A in MTEP20 | West | ITCM | 17731 | 24648 | LNrb | 2025-12-30 | Bowen | Eaton | 1 | 69 | 69 |  | ITC will rebuild approximately 0.85 miles of the Bowen – Eaton 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. | IL |  |  | 2164800
A in MTEP20 | West | ITCM | 17732 | 24651 | SUB | 2023-05-31 | EIC | Substation |  | 161 | 161 |  | In order to mitigate an N-1-1 issue at the Cargill Eddyville plant, ITC will expand the Eddyville Industrial Complex 161kV substation to the North. ITC will construct a five position 161kV ring bus North of the existing Eddyville Industrial Complex substation. All new terminal equipment will be capable of 2000A minimum. | IA |  |  | 5488862
A in MTEP20 | West | ITCM | 17732 | 25288 | TAP | 2023-05-31 | Bridgeport North | EIC | 1 | 161 | 161 |  | ITCM will terminate the circuit into the southwestern most position using the standard 1600A conductor | IA | 0.1 |  | 432000
A in MTEP20 | West | ITCM | 17732 | 24654 | SUBmisc | 2023-05-31 | Tri County | Substation |  | 161 | 161 |  | ITC will need to update the relay settings at Tri County | IA |  |  | 278376
A in MTEP20 | West | ITCM | 17732 | 24653 | TAP | 2023-05-31 | EIC | Tri County | 1 | 161 | 161 |  | Using the existing structures, ITC will terminate the 161kV circuit to the Eastern most breaker of the EIC expansion using the standard 1600A conductor. | IA | 0.1 |  | 720000
A in MTEP20 | West | ITCM | 17732 | 24652 | TAP | 2023-05-31 | Beacon | Tri County | 1 | 161 | 161 |  | ITC will install one 90 deg. double dead end structure and terminate the 161kV circuits into two Western most breaker positions at the EIC substation using the standard 1600A conductor. | IA | 0.1 |  | 1036800
A in MTEP20 | West | ITCM | 17733 | 24655 | SUB | 2020-10-15 | DAEC | Substation |  | 161 | 161 |  | The DAEC 161 kV substation will be expanded to accommodate the J504 interconnection. The TOIF will include the terminal facilities dedicated to the interconnection of J504, including the dead-end structure, disconnect switch, relay panel, CCVT’s, insulators, etc. New equipment should be capable of 2000A. The Interconnection Customer is responsible for costs associated with the TOIF. | IA |  |  | 0
A in MTEP20 | West | ITCM | 17734 | 24656 | SUB | 2023-12-31 | Clinton Perrin | Substation |  | 69 | 24 | 33 MVA | A new substation in city of Clinton, will provide capacity for industrial load south/west of town and will support retirement of Beaver Channel sub and Mill Creek sub after 25kV conversion. IPL will install a single transformer, 12.5kV substation, 20/33MVA capacity. Transformer will have 25kV option, but will be replaced by a 30/50MVA unit for final 25kV configuration. Installed XFMR will be moved elsewhere at that time. This conversion is estimated to be 10-20 years after completion of this construction. Four feeders will be used from this substation to serve load. Contingency at 12.5kV will be up to max rating of transformer, 33MVA. Contingency at 25kV will be reviewed and updated at a later date, but may be up to future 50MVA top rating of final unit. | IA |  |  | 2434248
A in MTEP20 | West | ITCM | 17734 | 24892 | SUBmisc | 2023-12-31 | Clinton 2nd Street | Substation |  | 69 | 69 |  | Perform relay upgrades and install fiber equipment related to the installation of the new Clinton Perrin 69/24.9/12.5kV substation. | IA |  |  | 400320
A in MTEP20 | West | ITCM | 17734 | 24891 | SUBmisc | 2023-12-31 | Beaver Channel | Substation |  | 69 | 69 |  | Perform relay upgrades and install fiber equipment related to the installation of the new Clinton Perrin 69/24.9/12.5kV substation. | IA |  |  | 316020
A in MTEP20 | West | ITCM | 17734 | 24657 | TAP | 2023-12-31 | Beaver Channel | Clinton 2nd Street | 1 | 69 | 69 |  | Tap the 69kV line for in and out feeds for the new Clinton Perrin 69/24.9/12.5kV distribution substation. Add fiber on the 69kV line from Beaver Channel-Clinton Perrin-Clinton 2nd Street. | IA |  |  | 637200
A in MTEP20 | West | ITCM | 17735 | 24658 | SUB | 2024-12-31 | Clinton South | Substation |  | 69 | 69 |  | Retire all ITC owned equipment in the Clinton South sub. | IA |  |  | 137873
A in MTEP20 | West | ITCM | 17735 | 24659 | LN | 2024-12-31 | Beaver Channel | Clinton South |  | 69 | 69 |  | Retire the in and out taps at the Clinton South sub and reroute the 69kV line to bypass the site. | IA |  | 0.1 | 24000
A in MTEP20 | West | ITCM | 17736 | 24660 | SUB | 2021-12-31 | Waukon Snakeskin | Substation |  | 69 | 69 |  | IPL will be constructing the Waukon Snakeskin 2 transformer 69/25kV substation the replace the nearby Waukon substation. ITC will install 2 box structures, 2 line breakers and 1 tie breaker. The cap bank and cap bank breaker at the existing Waukon substation should be moved to the Decorah side of the Waukon Snakeskin substation if possible or a new cap bank and breaker of equivalent effective rating should be installed. All substation equipment should have a minimum rating of 1200A. | IA |  |  | 2248847
A in MTEP20 | West | ITCM | 17736 | 24661 | TAP | 2021-12-31 | Decorah | Lansing | 1 | 69 | 69 |  | Line taps for the new Waukon Snakeskin sub. Tap the line between the Ludlow sub and the existing Waukon sub. | IA |  |  | 258600
A in MTEP20 | West | ITCM | 17738 | 24663 | TAP | 2025-12-31 | Thompson MacTavish | Line taps |  | 69 | 69 |  | New in and out line taps for the new Thompson MacTavish substation. | IA |  |  | 346800
A in MTEP20 | West | ITCM | 17739 | 24664 | TAP | 2021-12-31 | Calmar Prairie Farmer | Line taps |  | 69 | 69 |  | ITC will install an ~0.02 mile tap line to IPL’s new Calmar Prairie Farmer 69/24.9kV Distribution Substation. The transformer will have a high side breaker installed by IPL. This substation will be located near the existing Calmar substation. IPL has provided four proposed locations. | IA |  |  | 205200
A in MTEP20 | West | ITCM | 17740 | 24665 | LN | 2023-12-31 | ITCM Asset Blanket for 2023 | Throughout system |  | 345 | 69 |  | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA,MN,IL |  |  | 37080000
A in MTEP20 | West | ITCM | 17741 | 24666 | LN | 2023-12-31 | Blanket for Customer Interconnections under $1 million for 2023 | Throughout system |  | 345 | 69 |  | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL |  |  | 2400000
A in MTEP20 | East | ITCT | 17744 | 24667 | SUBmisc | 2023-12-31 | Blanket for Customer Interconnections | Throughout System |  | 120 |  |  | Blanket for customer interconnections and retirements less than $1 million with in service date in the year 2023 | MI |  |  | 2000000
A in MTEP20 | East | METC | 17745 | 24668 | SUBmisc | 2023-12-31 | Blanket for Customer Interconnections | Throughout System |  | 138 |  |  | Blanket for customer interconnections and retirements less than $1 million with in service dates in the year 2023. | MI |  |  | 2000000
A in MTEP20 | Central | AmerenMO | 17804 | 24680 | LNrb | 2023-12-01 | Lutesville | St. Francois | 1 | 345 |  |  | Rebuild 63 miles of 345kV wood H-frame circuit | MO |  |  | 32800000
A in MTEP20 | Central | AmerenMO | 17805 | 24681 | LNrb | 2021-12-01 | Campbell | Maline | 1&2 | 138 |  |  | Replace existing conductor with composite core conductor on branches 93 and 94. | MO |  |  | 1600000
A in MTEP20 | Central | AmerenMO | 17824 | 24683 | SUBmisc | 2021-12-01 | Spencer Creek | Substation |  | 345 |  |  | Replace switches on 345kv pos V3, V5, V6, V7 and reactor position. | MO |  |  | 700000
A in MTEP20 | Central | AmerenIL | 17825 | 24684 | SUB | 2023-12-01 | Lawrenceville South | Substation |  | 138 |  |  | Reconfigure the Lawrenceville South substation to a 6-position ultimate ring bus. | IL |  |  | 9200000
A in MTEP20 | Central | AmerenIL | 17826 | 24685 | LNup | 2022-12-01 | Greenville McCord | South Centralia | 1419 | 138 |  |  | Replace ~22 miles of existing 5/16" HS Steel Shield Wire with 1 3/8" E.H.S. Steel Shield Wire and 1 OPGW. | IL |  |  | 1700000
A in MTEP20 | Central | AmerenIL | 17827 | 24686 | LNup | 2020-12-01 | Cottage Hills | Stallings | 1622 | 138 |  |  | Replace ~4 miles of existing 3 #7 Copperweld shield wire from Str. 51-Wanda Sub | IL |  |  | 2000000
A in MTEP20 | Central | AmerenIL | 17828 | 24687 | LNup | 2020-06-01 | Kren | O'Fallon Porter Road | 1432 | 138 |  |  | Replace ~6 miles of existing 3 #7 Copperweld shield wire for the entire line | IL |  |  | 2600000
A in MTEP20 | Central | AmerenMO | 17829 | 24688 | IND | 2021-12-01 | Loose Creek | Substation |  | 345 |  |  | Install 345 kV shunt reactor. | MO |  |  | 4800000
A in MTEP20 | Central | AmerenMO | 17830 | 24689 | LNup | 2021-12-01 | Gasco | Osage | 2 | 138 |  |  | Replace both shield wires and replace structures as needed | MO |  |  | 9400000
A in MTEP20 | East | METC | 17844 | 24691 | LN | 2022-10-28 | Salt River | Summerton_Bullock |  | 138 |  |  | The Summerton - Bullock 138 kV circuit will be cut into the Salt River substation to form a Bullock - Salt River and Salt River - Summerton 138 kV circuit. | MI |  | 15 | 33846000
A in MTEP20 | East | METC | 17844 | 24692 | SUB | 2022-10-28 | Salt River |  |  | 138 |  |  | Expand the Salt River 138 kV substation by completing Row 6 and 8 to terminate the new Salt River - Summerton and Bullock - Salt River 138 kV circuits. Scope includes 2 new breakers and associated disconnects. | MI |  |  | 1647000
A in MTEP20 | Central | AmerenMO | 17845 | 24693 | LN | 2023-12-01 | Wittenberg | Trail of Tears |  | 161 | 138 |  | Install 12 miles of new 138 kV line from Wittenberg Substation to Trail of Tears Substation. Install new 161-138 kV transformer at Trail of Tears Substation. | MO |  |  | 38500000
A in MTEP20 | Central | WVPA | 17845 | 24712 | SwSta | 2023-12-01 | Wittenberg | Substation |  | 138 |  |  | Install new Wittenberg ring bus switching station on the Grand Tower-Perryville line | MO
A in MTEP20 | Central | WVPA | 17845 | 24714 | LN | 2023-12-01 | Trail of Tears | Charmin |  | 161 |  |  | Install new 161 kV line from Trail of Tears to Charmin Bulk Substation. Install 2 breakers at Charmin Bulk Substation. | MO
A in MTEP20 | Central | WVPA | 17845 | 24713 | SUB | 2023-12-01 | Trail of Tears | Substation |  | 161 |  |  | Reconfigure Trail of Tears substation to BAAH. | MO
A in MTEP20 | Central | AmerenIL | 17864 | 24694 | CB | 2022-12-01 | Cahokia |  |  | 138 |  |  | Replace OCB H27 on the C-GRAT-3 position and OCB H35 on the C-RUSL-2 positon with symetrically rated SF6 55 kA circuit breakers. | IL |  |  | 900000
A in MTEP20 | Central | AmerenMO | 17865 | 24695 | CB | 2022-12-01 | Lakeshire |  |  | 138 |  |  | Replace 40 kA breakers on positions H and U for cap banks 2A and 2B with 50 kA breakers. | MO |  |  | 1000000
A in MTEP20 | Central | AmerenIL | 17866 | 24696 | CB | 2022-12-01 | Neoga |  |  | 138 |  |  | Replace OCB 1402 on the HUTY-NEGS-1 position with a symetrically rated 40 kA SF6 breaker. | IL |  |  | 600000
A in MTEP20 | Central | AmerenMO | 17867 | 24697 | CB | 2022-12-01 | Gray Summit |  |  | 138 |  |  | Replace the Bus-Tie 1-2 breaker at Gray Summit with a symetrically rated 40 kA circuit breaker. | MO |  |  | 600000
A in MTEP20 | West | MP | 17869 | 25265 | LNrl | 2021-11-01 | Stinson | Gary |  | 115 |  |  | Relocate existing Stinson - Gary 115 kV Line (will become Enbridge East - Enbridge South after completion of Nemadji 115 kV Project) | WI |  | 0.5 | 2000000
A in MTEP20 | West | MP | 17869 | 25267 | LNrl | 2021-11-01 | Stinson | Gordon |  | 161 |  |  | Relocate existing Stinson - Gordon 161 kV Line (double circuit with Stinson - Bayfront 115 kV) | WI |  | 0.75 | 2000000
A in MTEP20 | West | MP | 17869 | 25266 | LNrl | 2021-11-01 | Stinson | Bayfront |  | 115 |  |  | Relocate existing Stinson - Bayfront 115 kV Line (double circuit with Stinson - Gordon 161 kV) | WI |  | 0.75 | 900000
A in MTEP20 | West | MP | 17870 | 24930 | CB | 2021-12-31 | National Tac 78L |  |  | 115 |  |  | Replace circuit breaker & associated equipment | MN |  |  | 385000
A in MTEP20 | West | MP | 17870 | 24935 | CB | 2021-12-31 | National Tac 3H |  |  | 115 |  |  | Replace circuit breaker & associated equipment | MN |  |  | 270000
A in MTEP20 | West | MP | 17870 | 24934 | CB | 2021-12-31 | National Tac 2H |  |  | 115 |  |  | Replace circuit breaker & associated equipment | MN |  |  | 270000
A in MTEP20 | West | MP | 17870 | 24933 | CB | 2021-12-31 | National Tac 1H |  |  | 115 |  |  | Replace circuit breaker & associated equipment | MN |  |  | 270000
A in MTEP20 | West | MP | 17870 | 24931 | CB | 2021-12-31 | National Tac 14L |  |  | 115 |  |  | Replace circuit breaker & associated equipment | MN |  |  | 385000
A in MTEP20 | West | MP | 17871 | 24927 | CB | 2023-12-31 | Laskin 34-38MW |  |  | 115 |  |  | Replace circuit breaker & associated equipment | MN |  |  | 350000
A in MTEP20 | West | MP | 17871 | 24929 | CB | 2023-12-31 | Laskin 5H |  |  | 115 |  |  | Replace circuit breaker & associated equipment | MN |  |  | 350000
A in MTEP20 | Central | IPL | 17884 | 24698 | CB | 2025-12-31 | Southeast |  |  | 138 |  |  | Southeast #4 | IN |  |  | 900000
A in MTEP20 | Central | IPL | 17885 | 24699 | CB | 2025-12-31 | Southeast |  |  | 138 |  |  | 138 kV Breaker | IN |  |  | 900000
A in MTEP20 | Central | IPL | 17886 | 24700 | CB | 2025-12-31 | Southeast |  |  | 138 |  |  | 138 kV breaker | IN |  |  | 900000
A in MTEP20 | Central | IPL | 17887 | 24701 | CB | 2023-12-31 | Stout South |  |  | 138 |  |  | 138 kV Breaker | IN |  |  | 900000
A in MTEP20 | Central | IPL | 17888 | 24702 | CB | 2023-12-31 | Southport |  |  | 138 |  |  | 138 kV Breaker | IN |  |  | 900000
A in MTEP20 | Central | AmerenIL | 17904 | 24703 | SwSta | 2023-12-01 | Highland Area | Substation |  | 138 |  |  | Install new Highland area ring bus. | IL |  |  | 8800000
A in MTEP20 | Central | AmerenIL | 17904 | 24705 | LN | 2023-12-01 | Highland Area | Aviston |  | 138 |  |  | Install new 16.5 mile 138 kV line between Highland and Aviston. | IL |  |  | 21000000
A in MTEP20 | Central | AmerenIL | 17904 | 24704 | SUB | 2023-12-01 | Aviston | Substation |  | 138 |  |  | Re-configure Aviston Substation to a ring bus. | IL |  |  | 5900000
A in MTEP20 | Central | AmerenIL | 17905 | 24708 | TX | 2022-06-01 | Hull |  |  | 161 | 138 |  | Install new 161-138 kV transformer at Finn (formerly Hull) substation. | IL |  |  | 3500000
A in MTEP20 | Central | AmerenMO | 17905 | 24706 | SUB | 2022-06-01 | Finn | Substation |  | 161 |  |  | Install new 161 kV Hannibal area ring bus. | MO |  |  | 5800000
A in MTEP20 | Central | AmerenMO | 17905 | 24711 | LNrb | 2022-06-01 | Peno | Spalding | 2 | 161 |  |  | Double circuit the PENO-SPLD-2 line from Spalding to the Marion tap. | MO |  |  | 4700000
A in MTEP20 | Central | AmerenMO | 17905 | 24710 | SwSta | 2022-06-01 | Spalding | Substation |  | 161 |  |  | Re-configure the existing Spalding substation to a ring bus and add a position for a new line to the New Hannibal Substation. | MO |  |  | 6200000
A in MTEP20 | Central | AmerenMO | 17905 | 24709 | CB | 2022-06-01 | Marion | Substation |  | 161 |  |  | Install new 161 kV bus-tie breaker at Marion Substation. | MO |  |  | 3300000
A in MTEP20 | Central | AmerenMO | 17905 | 24707 | LNrb | 2022-06-01 | Marion Tap | Marion |  | 161 |  |  | Rebuild the PENO-SPLD-2 line at the Marion tap to the Mississippi River, through the new Hannibal area Substation and the existing Marion Substation. | MO |  |  | 6800000
A in MTEP20 | Central | AmerenIL | 17907 | 24716 | TEQ | 2021-10-01 | Kansas | Substation |  | 138 |  |  | Add terminal facilities including one 138 kV breaker at Kansas Substation. | IL |  |  | 1200000
A in MTEP20 | Central | AmerenMO | 17908 | 24717 | LNrb | 2024-12-01 | Bland | Franks | 3 | 345 |  |  | Rebuild approximately 44 miles 345kV line to 3000A. | MO |  |  | 48400000
A in MTEP20 | Central | AmerenMO | 17909 | 24718 | LNup | 2021-12-01 | Campbell | Euclid | 4 | 138 |  |  | Replace shield wires on the Campbell-Euclid-4 circuit. Replace structures and crossarms as needed. | MO |  |  | 1600000
A in MTEP20 | Central | AmerenIL | 17910 | 24720 | LNrb | 2024-12-01 | Grand Tower | Carbondale NW to West Frankfort |  | 345 | 138 |  | Rebuild ~36 miles of the Grand Tower-Carbondale NW-W. Frankfort 138 kV line double circuit 345 kV. | IL |  |  | 75600000
A in MTEP20 | West | GRE | 17944 | 24723 | LNrb | 2021-09-30 | Heron Lake | Round Lake | 1 | 69 |  |  | Rebuild entire FE-RH line (from Heron Lake substation to Round Lake substation) | MN | 23.8 |  | 13232725
A in MTEP20 | Central | AmerenMO | 17945 | 24724 | SUB | 2024-12-01 | Hwy M | Substation |  | 138 | 12.47 |  | Install 2 unit 138-12.47 kV substation on a site adjacent to the Dardenne Substation. | MO
A in MTEP20 | Central | AmerenMO | 17947 | 24728 | SUB | 2023-12-01 | Fountain Lakes | Substation |  | 138 | 12.47 |  | Add 2nd 138-12 kV unit at Fountain Lakes | MO
A in MTEP20 | West | GRE | 17964 | 24730 | LNrb | 2022-12-31 | Blue Earth | Wilbert Tap | 1 | 69 |  |  | Rebuild 69 kV line from Blue Earth to East Chain to Wilbert Tap. | MN | 21.9 |  | 12273125
A in MTEP20 | West | ITCM | 17966 | 24732 | SUB | 2021-12-31 | Metform | Substation |  | 69 | 69 |  | ITC will be converting the Metform Substation to 69kV. All network path 69kV equipment will be capable of 1200A or greater. All network path switches will need to be replaced to be capable of 1200A or greater. ITC will retire the bypass bus and switches. | IL |  |  | 925200
A in MTEP20 | West | ITCM | 17967 | 24734 | SUB | 2029-12-30 | Bowen | Substation |  | 69 | 69 |  | ITC will be converting the Bowen Substation to 69kV. All network path 69kV equipment will be capable of 600A or greater. | IL |  |  | 2754375
A in MTEP20 | Central | AmerenMO | 17969 | 24738 | TX | 2022-12-01 | Mason | Substation |  | 345 | 138 |  | Replace 345/138 kV, 560 MVA Transformer #2 with a 700 MVA unit | MO |  |  | 6700000
A in MTEP20 | West | GRE | 17970 | 24740 | LNrb | 2023-12-29 | Howard Lake | Maple Lake | 1 | 69 |  |  | Rebuild the 69 kV line from Howard Lake to Highland to Maple Lake to 115 kV design standard | MN | 16 |  | 10402000
A in MTEP20 | West | GRE | 17971 | 24741 | LNcnv | 2022-12-02 | Le Sauk | West St. Cloud | 1 | 115 |  |  | Rebuild the existing 69 kV line from Le Sauk to Westwood 1 to West St. Cloud to 115 kV. | MN | 3.25 |  | 6020000
A in MTEP20 | Central | AmerenIL | 17972 | 24742 | SUB | 2023-12-01 | Salem West | Substation |  | 138 |  |  | Rebuild the Salem West 138 kV substation to a ring bus configuration. | IL |  |  | 7000000
A in MTEP20 | Central | AmerenIL | 17973 | 24743 | SUB | 2023-12-01 | Centerville | Substation |  | 138 |  |  | Rebuild the Centerville 138 kV substation to a Ring bus configuration. | IL |  |  | 8000000
A in MTEP20 | Central | AmerenIL | 17974 | 24744 | SUB | 2023-12-01 | Crab Orchard | Substation |  | 138 |  |  | Tap the Shawnee-West Frankfort east-4564 line and install 345kV ring bus to make the connection. | IL |  |  | 28000000
A in MTEP20 | Central | AmerenIL | 17975 | 24745 | TX | 2023-12-01 | Rising | Substation |  | 345 | 138 |  | Install 2nd 345-138 kV transformer at Rising Substation | IL |  |  | 11000000
A in MTEP20 | Central | AmerenIL | 17976 | 24746 | SUB | 2023-12-01 | Redhawk | Substation |  | 345 | 138 |  | Tap the Coffeen-Roxford-4551 line and install 345kV ring bus to make the connection for a new 345-138 kV transformer at Redhawk Substation. | IL |  |  | 22400000
A in MTEP20 | Central | AmerenIL | 17977 | 24747 | TX | 2023-06-01 | Mt. Vernon West | Substation |  | 345 | 138 |  | Install 2nd 345-138 kV transformer at Mt. Vernon West Substation. | IL |  |  | 8000000
A in MTEP20 | Central | AmerenIL | 17978 | 24748 | SUB | 2022-12-01 | Belleville 17th street | Substation |  | 138 |  |  | Rebuild the Belleville 17th street 138 kV substation to a ring bus configuration. | IL |  |  | 10000000
A in MTEP20 | West | ITCM | 17980 | 24749 | SUB | 2020-04-30 | Hancock | Substation |  | 161 | 69 | 75 MVA | Replace the Hancock T3 75MVA 161/69kV transformer with the Beaver Channel T1 75MVA 161/69kV Transformer (SN: 70450A). Also replace the high side circuit switcher 1320 with a 161kV circuit breaker. Re-use switch 1320B if feasible. Any other new required high-side equipment should be 1200A minimum. | IA |  |  | 1013142
A in MTEP20 | West | ITCM | 17980 | 24851 | SUB | 2020-04-30 | Beavr Channel | Substation | T1&T2 | 161 | 69 | 150 MVA | Replace the Beaver Channel T1 & T2 75MVA 161/69kV transformers with the spare 150MVA 161/69kV transformer (SN: WT03583) currently located at the Ames substation. Also install a high side breaker for the new transformer at Beaver channel and replace switch 1454. Any new high side equipment should be 1200A minimum and any new low side equipment should be 1600A minimum. | IA |  |  | 3576816
A in MTEP20 | Central | AmerenIL | 17981 | 24751 | SUB | 2023-12-01 | North Champaign | Substation |  | 138 |  |  | Rebuild the North Champaign 138 kV substation to a ring bus configuration. | IL |  |  | 8500000
A in MTEP20 | Central | AmerenIL | 17982 | 24752 | SUB | 2023-12-01 | Maroa | Substation |  | 345 |  |  | Install new Maroa 345 kV ring bus substation. | IL |  |  | 12000000
A in MTEP20 | Central | AmerenIL | 17983 | 24753 | SUB | 2023-06-01 | South Belleville | Substation |  | 138 |  |  | Rebuild the South Belleville 138 kV substation to a ring bus configuration. | IL |  |  | 8000000
A in MTEP20 | West | XEL | 17984 | 24755 | SUB | 2021-06-15 | Turtle Lake |  |  | 69 | 23.9 |  | A new substation will be built to replace existing Turtle Lake sub. 14MVA, 69:23.9kV, two feeders with 336A regulators. Coordinating with Twin Town Area Upgrade T-Line project requiring a 10MVAR, 69kV cap bank at this sub. | WI |  |  | 700000
A in MTEP20 | West | XEL | 17985 | 24756 | TX | 2020-12-15 | Rosemount |  |  | 115 | 34.5 |  | Add 115/34.5 kV 70 MVA transformer (TR02) to Rosemount Substation | MN |  |  | 1200000
A in MTEP20 | West | GRE | 17986 | 24757 | LNrb | 2021-11-01 | Lake Jennie | Lake Jennie Tap | 1 | 69 |  |  | Rebuild 2.77 of 3.79 miles of the Lake Jennie to Lake Jennie Tap. | MN | 2.77 |  | 1550000
A in MTEP20 | West | GRE | 17988 | 24760 | LN | 2022-11-30 | Lake Mary | Lake Mary Tap | 1 | 115 |  |  | Build ~1.0 mile of new 115 kV from the GRE/REA Lake Mary substation to the new Lake Mary Tap in the ______115 kV line ~1.0 mile west of the OTP Alexandria substation. | MN |  | 1 | 1400000
A in MTEP20 | West | XEL | 17989 | 24759 | TAP | 2020-09-01 | Wellington |  |  | 69 |  |  | Install a new 69kV 3-way motor operated switch on line 0721 between Franklin and Fairfax, and radial 4 mi 69 kV line to a new EREPC substation | MN |  |  | 1320000
A in MTEP20 | East | CETO | 17990 | 24761 | TEQ | 2022-12-31 | CE Substation Equipment Replacements - 2022 |  |  | 138 |  |  | Replace damaged or defective substation equipment, not including breakers, with new equipment | MI |  |  | 410000
A in MTEP20 | East | CETO | 17991 | 24762 | LNup | 2022-12-31 | CE Pole & Line Equipment Replacement Program - 2022 |  |  | 138 |  |  | Replace damaged or defective poles, towers, cross arms, insulators, guying, and switches, as needed, to maintain the lines' condition | MI |  |  | 530000
A in MTEP20 | East | CETO | 17992 | 24763 | LNrb | 2021-12-31 | Hodenpyl | Hodenpyl Jct | 1 | 138 |  |  | Rebuild the Hodenpyl 138 kV Line, approximately 0.6 miles, utilizing 138 kV single circuit construction | MI | 0.6 |  | 330000
A in MTEP20 | East | CETO | 17993 | 24764 | LNrb | 2022-12-31 | Muskegon Heights | Cobb | 2 | 138 |  |  | Rebuild a portion of the Muskegon #2 138 kV Line, approximately 2.1 miles, utilizing 138 kV single circuit construction | MI | 2.1 |  | 1000000
A in MTEP20 | East | CETO | 17994 | 24765 | LN | 2022-12-31 | Four Mile | Northridge | 1 | 138 |  |  | Approximately 0.5 miles of 138 kV line from Four Mile 138/46 kV Substation to the new Northridge Station. Existing METC structures and/or conductors will be utilized if made available and are in good condition. | MI |  | 0.5 | 250000
A in MTEP20 | East | CETO | 17994 | 24766 | LN | 2022-12-31 | Four Mile | Northridge | 2 | 138 |  |  | Approximately 0.5 miles of 138 kV line from Four Mile 138/46 kV Substation to the new Northridge Station. Existing METC structures and/or conductors will be utilized if made available and are in good condition. | MI |  | 0.5 | 250000
A in MTEP20 | East | ITCT | 17995 | 24767 | RLY | 2019-10-31 | Ringle |  |  | 345 |  |  | Install Relay and communication cutoff switch at Ringle for the J752 expansion of J161. | MI |  |  | 17904.43
A in MTEP20 | East | METC | 17997 | 24769 | SwSta | 2022-06-01 | Donaldson Creek |  |  | 138 |  |  | Build a new breaker row 13, breakers 13B7 and 13M9 with associated switches and terminate a new WPSC line to Rodgers | MI |  |  | 1450000
A in MTEP20 | East | ITCT | 17998 | 24770 | LN | 2024-06-01 | Stone Pool | Temple | 1 | 120 |  |  | The proposed solution is to build a new circuit (approximately 1.25 miles) from the Stone Pool 120 kV Station to the Temple 120 kV station utilizing 3200 Kcmil underground cable. | MI |  | 1.25 | 16770000
A in MTEP20 | East | ITCT | 17998 | 25192 | SUB | 2024-06-01 | Temple |  |  | 120 |  |  | Install breaker and associated equipment | MI |  |  | 950000
A in MTEP20 | East | ITCT | 17998 | 25191 | SUB | 2024-06-01 | Stone Pool |  |  | 120 |  |  | Install Breaker and associated equipment | MI |  |  | 950000
A in MTEP20 | East | MPPA | 18003 | 24778 | LNrb | 2022-11-01 | Barlow | Parsons |  | 69 | 69 | 143.4 | 2.73 mile 69kV Line | MI | 2.73 | 0 | 3000000
A in MTEP20 | East | MPPA | 18003 | 24779 | SwSta | 2020-12-31 | Barlow |  |  | 69 | 69 | 143.3 | Upgrade Barlow Switching Station | MI |  |  | 1000000
A in MTEP20 | East | METC | 18004 | 24777 | LNup | 2023-12-31 | Meyer | Briggs & Stratton Jct | 1 | 138 |  |  | Remediate the sag limit on the 6.02 mile-long length of 795 ACSR conductor of the Tanner – Briggs & Stratton Jct. 138kV section to increase its summer emergency rating to a minimum of 262 MVA/1096 Amps. Also completely remediate the sag limit on the 8.25 mile-long length of 795 ACSR conductor of the Meyer - Tanner 138kV line to conductor limit. | MI |  |  | 807000
A in MTEP20 | West | XEL | 18006 | 24781 | LNrb | 2022-06-15 | Osprey | Hawkins | 1 | 115 |  |  | Wreck out and rebuild approximately 11.36 miles of 115kV between Osprey and Hawkins to remediate aging condition issues | WI | 11.36 |  | 8500000
A in MTEP20 | West | XEL | 18007 | 24782 | LNrb | 2023-01-31 | Prentice | Phillips Tap | 1 | 115 |  |  | Rebuild 14.8 miles of 115kV line from Prentice to Phillips Tap to remediate reliability issues from aging condition of the line | WI |  |  | 10000000
A in MTEP20 | East | WPSC | 18011 | 24791 | LNrb | 2023-12-31 | Atlanta | Airport | 1 | 138 |  |  | Rebuild and upgrade 31.5 miles of 138 kV with double circuit steel poles, 795ACSS conductor, and OPGW. | MI |  | 15.5 | 15500000
A in MTEP20 | Central | BREC | 18012 | 24788 | SUB | 2023-06-01 | Hardinsburg |  |  | 161 |  |  | Add 161 kV breaker and upgrade protection equipment | KY |  |  | 980000
A in MTEP20 | Central | AmerenMO | 18013 | 24787 | IND | 2025-12-01 | Montgomery | Substation |  | 345 |  |  | Install 50 Mvar reactor at Montgomery Substation | MO |  |  | 3800000
A in MTEP20 | East | WPSC | 18015 | 24790 | LNrb | 2021-12-31 | Cadillac |  |  | 69 |  |  | Line modifications including new structures and switches in order to accommodate a new Cadillac distribution station. | MI | 1 |  | 1000000
A in MTEP20 | Central | AmerenMO | 18016 | 24794 | LNrc | 2023-12-01 | Berkeley | Sioux | 1 & 2 | 138 |  |  | Reconductor BERK-S-1 & 2 on branches 1004 and 1005 with composite core conductor. | MO |  |  | 5600000
A in MTEP20 | West | ATC | 18017 | 24795 | LNrb | 2022-12-31 | Petenwell SS | Saratoga SS | X-43 | 138 |  |  | Rebuild Saratoga to Petenwell (X-43) 138kV to 1030 Amp Maximum Rating | WI | 22.7 |  | 23840000
A in MTEP20 | West | ATC | 18017 | 24797 | SUB | 2022-12-31 | Saratoga |  |  | 138 |  |  | Uprate conductors and wave trap | WI |  |  | 85000
A in MTEP20 | West | ATC | 18017 | 24796 | SUB | 2022-12-31 | Petenwell |  |  | 138 |  |  | Uprate conductors and CT | WI |  |  | 575000
A in MTEP20 | West | ATC | 18019 | 24799 | SUB | 2023-12-31 | Glenview |  |  | 138 | 69 |  | Transformer retirement and Breaker and Relay Asset Renewal | WI |  |  | 2200000
A in MTEP20 | West | ATC | 18020 | 24800 | HVDC | 2022-12-31 | Mackinac HVDC |  |  | 138 |  |  | SCM IT/OT Asset Renewal | MI |  |  | 4000000
A in MTEP20 | East | WPSC | 18021 | 24801 | SUBmisc | 2021-12-31 | Eastport |  |  | 69 |  |  | Bus replacement. | MI |  |  | 170000
A in MTEP20 | East | WPSC | 18022 | 24803 | SUBmisc | 2022-12-31 | Westwood |  |  | 69 |  |  | 69kV BUS replacement | MI |  |  | 170000
A in MTEP20 | East | WPSC | 18023 | 24804 | SUBmisc | 2022-12-31 | Eaton Rapids |  |  | 69 |  |  | Rebuild the existing 69kV BUS to accommodate distribution equipment replacement. | MI |  |  | 170000
A in MTEP20 | East | WPSC | 18024 | 24805 | SUBmisc | 2022-12-31 | Atlanta |  |  | 69 |  |  | 69kV BUS replacement. | MI |  |  | 170000
A in MTEP20 | West | GRE | 18025 | 24835 | LN | 2021-03-05 | Cannon River Park | Cannon River Park Tap | 1 | 115 |  |  | Construct a new 115 kV transmission line from Cannon River Park to the Cannon River Park tap. | MN |  | 0.34 | 1000000
A in MTEP20 | East | WPSC | 18026 | 24806 | SUBmisc | 2022-12-31 | Hawks |  |  | 69 |  |  | BUS replacement | MI |  |  | 170000
A in MTEP20 | East | WPSC | 18027 | 24807 | SUBmisc | 2021-12-31 | Hammond Bay |  |  | 138 |  |  | 138kV BUS replacement. | MI |  |  | 170000
A in MTEP20 | East | WPSC | 18028 | 24808 | SUBmisc | 2021-12-31 | Hagensville |  |  | 138 |  |  | 138kV BUS | MI |  |  | 170000
A in MTEP20 | West | XEL | 18029 | 24809 | LNrb | 2021-06-01 | West St. Cloud | Millwood | 69 | 69 |  |  | Rebuild 24 miles of 69kV line from West St. Cloud - Millwood | MN |  |  | 10400000
A in MTEP20 | Central | AmerenIL | 18030 | 24810 | DVAR | 2021-04-01 | Meredosia | Substation |  | 345 |  |  | Install a shunt Reactive device to control voltages at IL-Meredosia 345 kV | IL |  |  | 5700000
A in MTEP20 | Central | AmerenIL | 18031 | 24811 | IND | 2021-04-01 | Ipava | Substation |  | 345 |  |  | Install a shunt Reactive device to control voltages at Ipava 345 kV | IL |  |  | 4300000
A in MTEP20 | Central | AmerenIL | 18032 | 24812 | DVAR | 2023-12-01 | Xenia | Substation |  | 345 |  |  | Install a shunt Reactive device to control voltages at Xenia 345 kV | IL |  |  | 4900000
A in MTEP20 | West | XEL | 18033 | 24813 | BUS | 2020-05-15 | Hydro Lane |  |  | 69 | 12.5 |  | Expand 69kV bus at Hydro Lane substation to accommodate increasing distribution feeding capacity for new customer load. | MN |  |  | 350000
A in MTEP20 | Central | AmerenIL | 18034 | 24814 | CB | 2022-12-01 | Tazewell | Substation |  | 138 |  |  | Replace 14 138 kV breakers at Tazewell Substation including: TAZW-138KV BKR 1321-73, TAZW-138KV BKR 1340, TAZW-138KV BKR 1354, TAZW-138KV BKR 1323, TAZW-138KV BKR 1340-63 (TIE), TAZW-138KV BKR 1350 (XFMR 2), TAZW-138KV BKR 1363, TAZW-138KV BKR 1375, TAZW-138KV BKR 1353, TAZW-138KV BKR 1322, TAZW-138KV BKR 1367, TAZW-138KV BKR 1375-53, TAZW-138KV BKR 1327, TAZW-138KV BKR 1321 (XFMR 1) | IL |  |  | 5600000
A in MTEP20 | Central | AmerenIL | 18035 | 24815 | CB | 2022-12-01 | Eastern | Substation |  | 138 |  |  | Replace TAZW-138KV BKR 1321-73 at Eastern Substation | IL |  |  | 500000
A in MTEP20 | Central | AmerenIL | 18036 | 24816 | CB | 2022-12-01 | Pioneer | Substation |  | 138 |  |  | Replace breaker PION-138KV LINE 1326 at Pioneer Substation. | IL |  |  | 500000
A in MTEP20 | Central | AmerenIL | 18037 | 24817 | CB | 2022-12-01 | Decatur N. 27th Street | Substation |  | 138 |  |  | Replace breakers N27D-138KV BKR 1522 and N27D-138KV BKR 1602 at Decatur North 27th street. | IL |  |  | 800000
A in MTEP20 | West | XEL | 18038 | 24819 | SUB | 2020-12-15 | Kinnickinick |  |  | 69 | 23.9 |  | Build new Kinnickinick Distribution substation near existing Kinnickinick substation. Existing substation equipment is nonstandard equipment and is beyond expected end of life and requires rebuild | WI |  |  | 350000
A in MTEP20 | Central | AmerenIL | 18039 | 24818 | CB | 2022-12-01 | Havana | Substation |  | 138 |  |  | Replace breakers HAV-138KV BKR 1406, HAV-138KV BT BKR 1302 and HAV-138KV BKR 1422 at Havana Substation. | IL |  |  | 1200000
A in MTEP20 | Central | AmerenIL | 18041 | 24821 | CB | 2022-12-01 | Ottawa | Substation |  | 138 |  |  | Install new line breaker on the HENN-OGLE-1516 line at Ottawa Substation. | IL |  |  | 2000000
A in MTEP20 | Central | AmerenIL | 18042 | 24822 | CB | 2022-12-01 | Wedron Fox River | Substation |  | 138 |  |  | Install new line breaker on the OTTA-FOXR-1652 circuit at Wedron Fox River Substation. | IL |  |  | 2000000
A in MTEP20 | East | METC | 18043 | 24824 | LNup | 2023-12-31 | Scott Lake | Argenta | 1 | 138 |  |  | Remediate sag limit on the Scott Lake - Trowbridge 138kV section to increase its summer emergency rating to a minimum of 219 MVA (917 Amps) and also remediate sag limit on the Trowbridge - Argenta 138kV section to increase its summer emergency rating to a minimum of 235 MVA (985 Amps). | MI |  |  | 830000
A in MTEP20 | Central | AmerenIL | 18044 | 24823 | LNrb | 2024-12-01 | Caterpillar 2 | Hines | 1357 | 138 |  |  | Reconfigure the Tazewell-Caterpillar 2-1375, Edwards-Caterpillar 1-1374, RS Wallace-Keystone-1396 and the Caterpillar 2-Hines-1357 138 kV circuits on a 1.5 mile section where they share a common structure. | IL |  |  | 5000000
A in MTEP20 | Central | AmerenIL | 18045 | 24825 | SUBmisc | 2023-06-01 | Murdock | Substation |  | 138 |  |  | Install a 138 kV circuit switcher on the high-side of XFMR #1 at Murdock Substation. | IL |  |  | 1000000
A in MTEP20 | West | MEC | 18050 | 24830 | SUB | 2021-12-01 | Sub 77 |  |  | 161 |  | 2,000 A | New 161 kV circuit breaker and associated equipment on line terminal to Sub 91 to separate the 161 kV line from the 161-13.2 kV distribution transformer. | IA |  |  | 800000
A in MTEP20 | West | ATC | 18051 | 24831 | SUB | 2022-12-31 | Sheboygan County SS |  |  | 138 |  |  | Substation Rebuild | WI |  |  | 8000000
A in MTEP20 | West | ATC | 18052 | 24832 | SUB | 2023-12-31 | Barneveld |  |  | 69 |  |  | new substation | WI |  |  | 12300000
A in MTEP20 | West | ATC | 18053 | 24833 | SUB | 2022-06-01 | Waupaca |  |  | 138 |  |  | Transformer addition | WI |  |  | 6900000
A in MTEP20 | East | METC | 18055 | 24837 | SwSta | 2021-07-02 | Riverview |  |  | 138 |  |  | Convert METC Riverview station from a straight bus configuration to a six breaker ring bus. Install buswork, three 138kV breakers, and associated disconnects. | MI |  |  | 5720000
A in MTEP20 | East | METC | 18055 | 24839 | LINE | 2021-07-02 | Argenta | Riverview | 1 | 138 |  |  | Re-terminate Argenta-Riverview 138kV circuit at Riverview ring bus. | MI |  |  | 275000
A in MTEP20 | East | METC | 18055 | 24838 | LINE | 2021-07-02 | Morrow | Riverview | 1 | 138 |  |  | Re-terminate Morrow-Riverview 138kV circuit at Riverview ring bus. | MI |  |  | 275000
A in MTEP20 | Central | AmerenMO | 18056 | 24836 | DVAR | 2023-12-01 | Mason | Substation |  | 138 |  |  | Install a shunt Reactive device to control voltages at Mason 3 138 kV bus | MO |  |  | 4500000
A in MTEP20 | West | MP | 18060 | 24920 | CB | 2023-12-31 | Fond Du Lac 8L |  |  | 115 |  |  | Add circuit breaker & associated equipment at Fond Du Lac | MN | 0 | 0 | 500000
A in MTEP20 | West | MP | 18060 | 24922 | LNrl | 2023-12-31 | Fond Du Lac | Thomson |  | 115 |  |  | Relocate & rebuild transmission line | MN | 0.5 | 2.5 | 3000000
A in MTEP20 | West | ITCM | 18061 | 24843 | SUB | 2022-05-30 | Mason City Industrial | Substation |  | 161 | 24.9 |  | ITCM will interconnect Alliant Energy’s Mason City Industrial 161/24.9kV distribution substation with in/out taps to the Emery-Lime Creek 161kV line and install four (4) 161kV breakers in a ring bus configuration at the 161kV distribution substation. IPL will install a single distribution transformer initially to serve a load of ~18MW. IPL will install a second distribution transformer in the future to accommodate load growth and load moved from 69kV distribution substations. | IA |  |  | 4659607
A in MTEP20 | West | ITCM | 18061 | 25236 | RLY | 2022-05-30 | Emery | Substation |  | 161 | 161 |  | Make necessary relaying changes at Emery to accommodate the Mason City Industrial substation. | IA |  |  | 168240
A in MTEP20 | West | ITCM | 18061 | 24844 | TAP | 2022-05-30 | Emery | Lime Creek | 2 | 161 | 161 |  | ITCM will interconnect Alliant Energy’s Mason City Industrial 161/24.9kV distribution substation with in/out taps to the Emery-Lime Creek 161kV line #2 (east line). | IA |  |  | 4920000
A in MTEP20 | West | MP | 18064 | 24914 | CB | 2022-10-31 | Hibbing 14L | 14L Tap |  | 115 |  | 182/214 | Replace existing circuit breaker & associated equipment | MN |  |  | 350000
A in MTEP20 | West | MP | 18064 | 24916 | CB | 2022-10-31 | Hibbing 44L | 44L Tap |  | 115 |  |  | Replace existing circuit breaker & associated equipment | MN |  |  | 300000
A in MTEP20 | West | MP | 18064 | 24915 | CB | 2022-10-31 | Hibbing 25L | Virginia 25L |  | 115 |  | 90/114 | Replace existing circuit breaker & associated equipment | MN |  |  | 350000
A in MTEP20 | West | MP | 18065 | 24909 | CB | 2024-12-31 | Verndale 133L |  |  | 115 |  |  | Replace existing circuit breaker & associated equipment | MN |  |  | 350000
A in MTEP20 | West | MP | 18065 | 24910 | CB | 2024-12-31 | Verndale 24L |  |  | 115 |  |  | Replace existing circuit breaker and associated equipment | MN |  |  | 350000
A in MTEP20 | Central | BREC | 18071 | 24852 | CAP | 2019-10-01 | Reid Substation |  |  | 161 |  | 93.6 MVar | Improve voltages after retirement of HMP&L Station Two Units 1 and 2 | KY |  |  | 150000
A in MTEP20 | Central | BREC | 18071 | 24853 | CAP | 2019-10-01 | Reid EHV |  |  | 161 |  | 86.3 MVAR | Improve voltages after retirement of HMP&L Station Two Units 1 and 2 by replacing the cans of an existing capacitor with larger cans. | KY |  |  | 150000
A in MTEP20 | East | METC | 18073 | 24854 | LNrc | 2024-06-01 | Argenta | Riverview |  | 138 |  |  | Reconductor approximately 3 miles of the Argenta - Riverview 138kV circuit using 1431 ACSR conductor | MI | 3 |  | 2100000
A in MTEP20 |  | METC | 18073 | 25348 | SUBmisc | 2024-06-01 | Argenta |  |  | 138 |  |  | Upgrade relay at Argenta pos. 14MB to meet or exceed 385 MVA (1612 Amps) | MI |  |  | 63000
A in MTEP20 | East | METC | 18073 | 25264 | SUBmisc | 2024-06-01 | Riverview |  |  | 138 |  |  | Substation equipment replacement | MI |  |  | 37000
A in MTEP20 | Central | AmerenIL | 18075 | 24857 | CB | 2023-12-01 | North Decatur | Substation |  | 138 |  |  | Replace 138 kV breaker NDEC-138KV BKR 1602 at North Decatur Substation. | IL |  |  | 500000
A in MTEP20 | Central | AmerenIL | 18076 | 24858 | CB | 2023-12-01 | Steeleville | Substation |  | 138 |  |  | Replace 138 kV breaker STVL-138KV BKR 1636 at Steeleville Substation. | IL |  |  | 500000
A in MTEP20 | Central | AmerenIL | 18077 | 24860 | CB | 2023-12-01 | Vermilion | Substation |  | 138 |  |  | Replace 138 kV breaker VERM-138KV BKR 1306 at Vermilion Substation. | IL |  |  | 500000
A in MTEP20 | Central | AmerenIL | 18078 | 24863 | CB | 2023-12-01 | Carbondale NW | Substation |  | 138 |  |  | Replace 138 kV breaker CDNW-138KV LINE 1744 at Carbondale NW Substation. | IL |  |  | 500000
A in MTEP20 | Central | AmerenIL | 18079 | 24865 | CB | 2023-12-01 | Mason City West | Substation |  | 138 |  |  | Replace 138 kV breaker MSCW-138KV LINE 1684 at Mason City West substation. | IL |  |  | 500000
A in MTEP20 | Central | AmerenIL | 18080 | 24866 | CB | 2023-12-01 | Meredosia East | Substation |  | 138 |  |  | Replace breakers MERE-138KV BT 1938, MERE-138KV BT 1958, MERE-138KV BKR 1957, MERE-138KV BKR 1947 and MERE-138KV BT 1948 at Meredosia East Substation. | IL |  |  | 2000000
A in MTEP20 | Central | AmerenIL | 18081 | 24868 | CB | 2023-12-01 | Newton | Switchyard |  | 138 |  |  | Replace 138 kV breakers NWTY-138KV LT 1869 and NWTY-138KV LT 1868 at the Newton switchyard. | IL |  |  | 800000
A in MTEP20 | Central | AmerenIL | 18085 | 24871 | TX | 2022-06-01 | Tazewell | Substation |  | 345 | 138 |  | Replace 345-138 kV transformer #1 with new 560 MVA unit. | IL |  |  | 3750000
A in MTEP20 | Central | AmerenIL | 18086 | 24872 | TX | 2024-06-01 | Tazewell | Substation |  | 345 | 138 |  | Replace 345-138 kV transformer #2 with new 560 MVA unit. | IL |  |  | 3750000
A in MTEP20 | Central | AmerenIL | 18088 | 24874 | TX | 2023-06-01 | Neoga South | Substation |  | 345 | 138 |  | Replace 345-138 kV transformer #2 with new 560 MVA unit. | IL |  |  | 3750000
A in MTEP20 | Central | AmerenIL | 18089 | 24875 | TX | 2023-12-01 | Brokaw | Substation |  | 345 | 138 |  | Replace 345-138 kV transformer #1 with new 560 MVA unit. | IL |  |  | 3750000
A in MTEP20 | Central | AmerenIL | 18090 | 24876 | TX | 2024-12-01 | Albion South | Substation |  | 345 | 138 |  | Replace 345-138 kV transformer with new 560 MVA unit. | IL |  |  | 3750000
A in MTEP20 | Central | AmerenIL | 18091 | 24877 | CB | 2023-12-02 | Clinton | Switchyard |  | 345 |  |  | Replace breaker CLNT-345KV BKR 4506 at Clinton switchyard. | IL |  |  | 500000
A in MTEP20 | Central | AmerenIL | 18092 | 24878 | CB | 2024-12-01 | East Galesburg | Substation |  | 138 |  |  | Replace breaker EGAL-138/69KV AUTO XFMR 2 at East Galesburg Substation. | IL |  |  | 500000
A in MTEP20 | Central | AmerenIL | 18093 | 24879 | CB | 2024-12-01 | Fargo | Substation |  | 138 |  |  | Replace breakers FARG-138KV BKR & LINE 1394 and FARG-138KV BKR 1371 at Fargo Substation. | IL |  |  | 800000
A in MTEP20 | South | Entergy-AR | 18094 | 24881 | RLY | 2022-12-31 | Hot Springs 115kV |  |  | 115 |  |  | Install dual primary protection bus schemes. | AR |  |  | 2256239
A in MTEP20 | Central | AmerenIL | 18095 | 24880 | CB | 2024-12-01 | Gibson City South | Substation |  | 138 |  |  | Replace breakers GBCS-138KV LINE 1524 and GBCS-138KV LINE 1522 at Gibson City South Substation. | IL |  |  | 800000
A in MTEP20 | Central | AmerenIL | 18096 | 24882 | CB | 2023-12-01 | Goose Creek | Substation |  | 345 |  |  | Replace breakers GOSC-345KV BKR 4545, GOSC-345KV BKR 4575 and GOSC-345KV LT BKR 4555 at Goose Creek Substation. | IL |  |  | 1800000
A in MTEP20 | South | Entergy-AR | 18097 | 24884 | IND | 2023-06-01 | Pleasant Hill 500kV |  |  | 500 |  |  | Add two 100 MVAR reactors at Pleasant Hill 500kV | AR |  |  | 16333119
A in MTEP20 | Central | AmerenIL | 18098 | 24883 | CB | 2024-12-01 | Grand Tower | Switchyard |  | 138 |  |  | Replace breaker GDTY-138KV LT 1449 at Grand Tower Switchyard. | IL |  |  | 500000
A in MTEP20 | South | Entergy-AR | 18099 | 24885 | CB | 2021-06-01 | El Dorado 115kV |  |  | 115 |  |  | Replace (5) 115 kV breakers at El Dorado EHV with 63 kA fault interrupting capability | AR |  |  | 3562971
A in MTEP20 | South | Entergy-AR | 18100 | 24886 | CAP | 2023-06-01 | Danville 161kV |  |  | 161 |  |  | Install a 24MVAR cap bank at Danville 161kV | AR |  |  | 1755533
A in MTEP20 | South | Entergy-AR | 18101 | 24887 | Dist | 2024-06-01 | Hot Springs Plemmons |  |  | 115 | 13.8 |  | Build a new substation with a single 40 MVA 115/13.8 kV LTC transformer. | AR |  |  | 10904173
A in MTEP20 | Central | AmerenIL | 18102 | 24888 | CB | 2023-12-01 | Hines | Substation |  | 138 |  |  | Replace breaker HINE-138KV BKR & LINE 1357 at Hines Substation. | IL |  |  | 500000
A in MTEP20 | South | Entergy-AR | 18103 | 24890 | Dist | 2024-06-01 | Screeton 115kV |  |  | 115 | 13.8 |  | Build a new substation between the Hazen substation and the Carlisle Substation along the Carlisle – Hazen 115 kV transmission line near the town of Screeton. The new station will contain a single 40MVA 115/13.8kV LTC transformer. | AR |  |  | 15132530
A in MTEP20 | Central | AmerenIL | 18104 | 24889 | CB | 2023-12-01 | Latham | Substation |  | 345 |  |  | Replace breaker LATM-345KV POS V19 at Latham Substation. | IL |  |  | 500000
A in MTEP20 | Central | AmerenIL | 18105 | 24893 | CB | 2024-06-01 | Makanda North | Substation |  | 138 |  |  | Replace breakers MAKN-138KV LINE 1674 and MAKN-138KV LINE 1672 at Makanda North Substation. | IL |  |  | 800000
A in MTEP20 | Central | AmerenIL | 18106 | 24894 | CB | 2024-06-01 | Marblehead North | Substation |  | 161 | 138 |  | Replace breakers MRBN-138KV LINE 1852 and MRBN-161/138KV XFMR 1 at Marblehead north substation. | IL |  |  | 800000
A in MTEP20 | Central | AmerenIL | 18107 | 24895 | CB | 2023-12-01 | Tilton Energy Center | Switchyard |  | 138 |  |  | Replace breaker TEC-138KV LINE TIE BKR 1320 at Tilton Energy Center. | IL |  |  | 500000
A in MTEP20 | Central | AmerenIL | 18108 | 24896 | CB | 2024-12-01 | Watseka | Substation |  | 138 |  |  | Replace breakers WATK-138KV LINE 1372 and WATK-138KV LINE 1374 at Watseka Substation. | IL |  |  | 800000
A in MTEP20 | West | MP | 18109 | 24899 | TEQ | 2022-12-31 | 15th Ave West |  |  | 115 | 34.5 |  | High-side terminal equipment to accommodate a new 115/34.5 kV transformer | MN | 0 | 0 | 250000
A in MTEP20 | West | MP | 18110 | 24898 | BUS | 2025-12-31 | Little Falls |  |  | 115 | 34 |  | Modify bus connection so that 115/34 kV transformer is no longer line-connected on 115 kV side | MN |  |  | 250000
A in MTEP20 | West | ITCM | 18111 | 24900 | SUBmisc | 2021-09-15 | Adams | Substation |  | 161 | 161 |  | Install new terminal for J523 gen-tie line. This work includes installing switch, dead-end, CCVT's, switches, and relay panels (see GIA for further details). | MN |  |  | 0
A in MTEP20 | East | METC | 18112 | 24902 | SUB | 2022-12-31 | Kenowa |  |  | 345 |  |  | Complete row 33 of the Kenowa substation by adding 3 breakers and associated equipment. This addition creates a breaker-and-a-half scheme at Kenowa. | MI |  |  | 3950000
A in MTEP20 | West | ITCM | 18113 | 24906 | SUBmisc | 2021-09-15 | Adams | Substation |  | 161 | 161 |  | Add two 161kV breakers in series with the bus-tie breaker 6620 to create a breaker and 1/2 row. Relocate the line for the Adams 345/161kV transformer from the existing terminal to a new terminal position on a breaker and 1/2 row (install dead end, coordinate relocation of metering with Xcel, and replace necessary equipment to accommodate the relocation of the transformer terminal). All new equipment must be capable of 2000 amp operation. | MN |  |  | 1217897
A in MTEP20 | West | ITCM | 18114 | 24911 | SUBmisc | 2021-09-15 | Adams | Substation |  | 161 | 161 |  | Add a breaker to the 161kV bus between breakers 0681 and 0680 and relocate the Rochester and Harmony 161kV lines to terminal positions in the newly formed breaker and 1/2 row (install switches, bus work, dead-end, CCVTs, relays, and all necessary equipment as needed). Add a breaker to the 161kV bus between breakers 0685 and 0682 (install switches, bus work, dead-end, CCVTs, relays, and all necessary equipment as needed). Add a breaker to the 161kV bus between breakers 0790 and 0686 (install switches, bus work, dead-end, CCVTs, relays, and all necessary equipment as needed). All equipment needs to be capable of a minimum of 2000 amp operation. | MN |  |  | 2696760
A in MTEP20 | West | ITCM | 18114 | 24913 | TAP | 2021-09-15 | Adams | Harmony | 1 | 161 | 161 |  | Relocate the 161kV terminal for the conversion of the Adams substation to breaker and 1/2. | MN |  |  | 684770
A in MTEP20 | West | ITCM | 18114 | 24912 | TAP | 2021-09-15 | Adams | Rochester | 1 | 161 | 161 |  | Relocate the 161kV terminal for the conversion of the Adams substation to breaker and 1/2. | MN
A in MTEP20 | Central | PPI | 18115 | 24917 | CAP | 2020-12-31 | Pearl |  |  | 69 | 69 | 2.4 | Reliability. Kampsville substation is prone to Illinois River flooding making capacitor bank unavailable | IL |  |  | 400000
A in MTEP20 | Central | PPI | 18116 | 24924 | LN | 2023-12-31 | Saidora | Kilbourne | 1 | 69 | 69 | 50 | New 8.67-mile 69 kV line in Menard Electric Cooperative | IL |  | 8.67 | 6195200
A in MTEP20 | West | MEC | 18117 | 24921 | LNrc | 2020-10-31 | Washburn | Hazleton | 1 | 161 |  | 335 MVA | Reconductor Washburn-Hazleton 161 kV line with T2-556 ACSR Dove | IA | 28.53 |  | 16625000
A in MTEP20 | West | MEC | 18117 | 24923 | TEQ | 2020-10-31 | Washburn |  |  | 161 |  | 335 MVA | Washburn substation terminal equipment upgrades associated with reconductor project. | IA |  |  | 75000
A in MTEP20 | West | CMMPA | 18118 | 25537 | LNrl | 2021-12-15 | Windom Muni | Windom SW | 1 | 69 |  |  | Line relocation and rebuild due to age and condition | MN |  |  | 2000000
A in MTEP20 | West | MEC | 18119 | 24928 | TEQ | 2020-10-31 | Deere Northeast |  |  | 161 |  | 272 MVA | Upgrade Deere Northeast substation terminal equipment to increase Lundquist-Deere Northeast 161 kV line rating. | IA |  |  | 50000
A in MTEP20 | Central | PPI | 18120 | 24932 | LNrc | 2021-12-31 | Berlin | Amos | 1 | 69 | 69 | 50 | Upgrade 3-mile portion of Berlin to Amos 69 kV line from 4/0 ACSR to 336.4 MCM ACSR associated with fiber and distribution installation | IL | 3 |  | 1200000
A in MTEP20 | West | MEC | 18121 | 24936 | TEQ | 2020-10-31 | Deere Northeast |  |  | 161 |  | 272 MVA | Replace limiting substation terminal equipment to increase the rating of the Deere Northeast-Washburn 161 kV line. | IA |  |  | 50000
A in MTEP20 | West | MEC | 18121 | 24938 | TEQ | 2020-10-31 | Washburn |  |  | 161 |  | 272 MVA | Replace limiting substation terminal equipment to increase the rating of the Deere Northeast-Washburn 161 kV line. | IA |  |  | 50000
A in MTEP20 | Central | PPI | 18122 | 24937 | CB | 2020-12-31 | St. David |  |  | 69 | 69 | 50 | Replace St. David OCB with SF6 breaker and new relays | IL |  |  | 280000
A in MTEP20 | Central | PPI | 18123 | 24940 | SwSta | 2022-12-31 | Payson Breaker |  |  | 69 | 69 | 50 | Establish 69 kV breaker station in Adams Electric Cooperative | IL |  |  | 2940400
A in MTEP20 | West | MEC | 18124 | 24941 | LNrc | 2020-12-31 | Sub T Fort Dodge | Boone Jct | 1 | 161 |  | 327 MVA | Reconductor MidAmerican's potion of the Sub T FD-Boone Jct 161 kV line with T2-556 ACSR Dove. | IA | 13.24 |  | 7155000
A in MTEP20 | West | MEC | 18124 | 24942 | TEQ | 2020-12-31 | Sub T Fort Dodge |  |  | 161 |  | 327 MVA | Substation terminal equipment upgrades associated with the Sub T FD-Boone Jct 161 kV line reconductor | IA |  |  | 167500
A in MTEP20 | West | MEC | 18125 | 24943 | LNup | 2020-12-31 | Grimes | Beaver Creek | 1 | 345 |  | 1,222 MVA | Replace structures to uprate line | IA | 43.4 |  | 753000
A in MTEP20 | West | MEC | 18126 | 24945 | LNup | 2020-06-30 | Franklin | Wall Lake | 1 | 161 |  | 204 MVA | Replace structures to increase line rating | IA | 17.72 |  | 220000
A in MTEP20 | West | MEC | 18127 | 24946 | CB | 2021-06-30 | Sycamore |  |  | 345 |  | 1,319 MVA | Replace two 345 kV circuit breakers, associated disconnect switches, and jumpers to increase the rating of the Grimes-Sycamore 345 kV south line. | IA |  |  | 1200000
A in MTEP20 | West | MEC | 18128 | 24947 | IND | 2021-06-01 | Raun Substation |  |  | 13.8 |  |  | Retire three 13.8 kV reactors at Raun substation. | IA |  |  | 1000000
A in MTEP20 |  | MEC | 18128 | 25557 | IND | 2021-06-01 | Raun Substation |  |  | 345 |  |  | Install RL switcher for the 345 kV reactor and replace replaying | IA |  |  | 30000
A in MTEP20 | West | MEC | 18129 | 24949 | SUB | 2022-07-01 | 25th Street NW |  |  | 161 |  |  | New 161 kV distribution substation | IA |  |  | 12760000
A in MTEP20 | West | MEC | 18129 | 24950 | TAP | 2022-07-01 | 25th Street NW |  |  | 161 |  | 410 | Four new 161 kV line taps into the 25th Avenue NW Substation from the future Bondurant - 50th Avenue NW lines. | IA |  |  | 175000
A in MTEP20 | West | XEL | 18130 | 24951 | LNrb | 2023-06-15 | Port Wing | Bayfield | 1 | 34.5 |  |  | Rebuild 9.6 miles of 34.5kV line from Port Wing to Bayfield to remediate reliability issues due to aging condition of the line. | WI |  |  | 5000000
A in MTEP20 | West | XEL | 18131 | 24952 | LNrb | 2023-06-15 | Iron River | Port Wing | 1 | 34.5 |  |  | Rebuild 9 miles of 34.5kV line from Iron River to Port Wing to remediate aging condition issues. | WI |  |  | 5000000
A in MTEP20 | West | XEL | 18132 | 24953 | SUB | 2020-10-01 | Jamaica |  |  | 115 | 13.8 |  | New in and out 115kV Jamaica sub interconnecting at 115kV line from Chemolite to Cottage Grove to serve new Airgas load interconnection | MN |  |  | 5000000
A in MTEP20 | East | METC | 18133 | 24954 | SUB | 2022-12-31 | Pere Marquette |  |  | 138 |  |  | Upgrade two breakers (at positions 5M9 and 7W8) and other overloaded station equipment at the Pere Marquette 138 kV station. | MI |  |  | 970000
A in MTEP20 | Central | CWLP | 18134 | 25109 | CAP | 2021-03-01 | Palomino |  |  | 69 |  |  | Remove existing Cap bank and add two new 20 MVAR cap banks | IL |  |  | 250000
A in MTEP20 | Central | IPL | 18135 | 24955 | TX | 2020-12-31 | Rockville |  |  | 345 |  |  | like-for-like replacement | IN |  |  | 3700000
A in MTEP20 | South | Entergy-LA | 18136 | 24957 | TEQ | 2021-06-01 | Scott |  |  | 69 |  |  | Upgrade all through path equipment to at least 588 Amps capacity | LA |  |  | 50000
A in MTEP20 | West | MEC | 18137 | 24956 | SUB | 2022-06-01 | South Waukee |  |  | 161 | 13.2 | 33 | New 161 kV distribution substation | IA |  |  | 7597000
A in MTEP20 | West | MEC | 18137 | 24959 | LN | 2022-06-01 | Booneville | South Waukee |  | 161 |  | 410 | New 161 kV line from Booneville | IA |  |  | 3157000
A in MTEP20 | West | MEC | 18137 | 24958 | LN | 2022-06-01 | Grimes | South Waukee |  | 161 |  | 410 | New 161 kV line from Grimes | IA |  |  | 1234000
A in MTEP20 | Central | IPL | 18138 | 24961 | SUB | 2021-12-31 | Center |  |  | 138 |  |  | 3 new 138 kV breaker | IN |  |  | 3000000
A in MTEP20 | Central | IPL | 18138 | 24962 | CB | 2021-12-31 | Center |  |  | 138 |  |  | Replace 3 138 kV Breakers | IN |  |  | 3000000
A in MTEP20 | Central | AmerenMO | 18139 | 24960 | SUBmisc | 2022-12-01 | Labadie | Switchyard |  | 345 |  |  | Upgrade switches and CTs to 3000A on the Labadie 345 kV bus-tie 2-3 position. | MO |  |  | 1100000
A in MTEP20 | Central | CWLP | 18140 | 25106 | LNrc | 2021-03-01 | Chatham Main | Chatham Independence | 1 | 138 |  | 330 | Reconductor to 795 ACSS | IL | 2.6 |  | 350000
A in MTEP20 | Central | CWLP | 18141 | 24996 | SUBmisc | 2021-03-01 | Interstate | Lanesville | 1 | 138 |  | 478 MVA | Replacing the wavetrap at the Interstate Substation (on Interstate - Lanesville 138 kV line) with a 2000 A wave trap | IL |  |  | 20000
A in MTEP20 | Central | IPL | 18142 | 24963 | SUB | 2021-12-31 | Mooresville |  |  | 138 |  |  | 2 new 139 kV breakers | IN |  |  | 2000000
A in MTEP20 | Central | IPL | 18145 | 24964 | CB | 2021-12-31 | Hanna |  |  | 345 |  |  | Replace three 345 kV breakers #25,28,29 | IN |  |  | 2400000
A in MTEP20 | South | Entergy-LA | 18146 | 24968 | CB | 2023-12-01 | Sherwood Forest |  |  | 115 |  |  | Install transmission line breakers at the existing Sherwood Forest 115 kV substation. | LA |  |  | 5100000
A in MTEP20 | East | METC | 18147 | 24966 | LNrb | 2022-05-01 | Bard Road | Warren |  | 138 |  |  | Rebuild 16.4 miles of the Bard Road – Clare Junction section of the Bard Road – Warren 138kV circuit and to rebuild 3.3 miles of the Clare Junction – Warren section of the Bard Road – Warren 138kV circuit with 954 ACSR utilizing future 230 kV double circuit construction initially operated as 138 kV single circuit with adjacent side left vacant for future use. | MI | 19.7 |  | 23776000
A in MTEP20 |  | METC | 18147 | 25542 | COM | 2022-05-01 | Clare Jct |  |  | 138 |  |  | Install communications | MI |  |  | 55246
A in MTEP20 | East | METC | 18147 | 25193 | TEQ | 2022-05-01 | Warren |  |  | 138 |  |  | Replace buswork at Warren position 377 | MI |  |  | 63000
A in MTEP20 | East | METC | 18147 | 25186 | TEQ | 2022-05-01 | Bard Road |  |  | 138 |  |  | Upgrade terminal equipment at Bard Road position BM37. | MI |  |  | 24000
A in MTEP20 | Central | PPI | 18148 | 24967 | SwSta | 2021-12-31 | IEC Data Center |  |  | 138 | 138 | 229 | Establish 138 kV ring bus to serve proposed Data Center in Illinois Electric Cooperative new load between Jacksonville Industrial Park and Winchester. | IL |  |  | 6400000
A in MTEP20 | West | MEC | 18151 | 24975 | LNrc | 2021-12-31 | Granger Tap | 100th St & 54th Ave | 1 | 161 |  | 513 MVA | Reconductor line with T2-795 ACSR Drake | IA | 0.97 |  | 2035000
A in MTEP20 | West | MEC | 18151 | 24978 | TEQ | 2021-12-31 | 100th St & 54th Ave |  |  | 161 |  | 513 MVA | Upgrade substation terminal equipment to support reconductor of Granger Tap-100th St & 54th Ave 161 kV line | IA |  |  | 50000
A in MTEP20 | Central | PPI | 18152 | 25056 | LNrc | 2022-12-31 | Andrew | Amos | 1 | 69 | 69 | 115 | Reconductor 8.9-mile 69 kV line from 336.4 MCM ACSR to 795 MCM ACSR | IL | 8.9 |  | 5239200
A in MTEP20 | Central | PPI | 18154 | 24971 | IND | 2022-12-31 | Alsey |  |  | 138 | 138 | 40 | Addition of 40 MVAR reactor at Alsey 138 kV substation | IL |  |  | 3240000
A in MTEP20 | Central | PPI | 18155 | 24973 | LN | 2021-12-31 | Burton | Ursa |  | 69 | 69 | 50 | New 16.3-mile 69 kV line in Adams Electric Cooperative | IL |  | 16.3 | 8945250
A in MTEP20 | Central | PPI | 18157 | 24976 | LN | 2022-12-31 | Ameren Kuhlman | PPI Kuhlman |  | 138 | 138 | 229 | New 1.0-mile 138 kV line in Illinois Electric Cooperative | IL |  | 1 | 1425000
A in MTEP20 | Central | PPI | 18157 | 24979 | SUB | 2022-12-31 | PPI Kuhlman | Arenzville | 1 | 138 | 69 | 37.3 | New PPI Kuhlman 138/69 kV substation | IL |  |  | 6000000
A in MTEP20 | Central | PPI | 18159 | 24980 | TX | 2022-12-31 | East Lanesville |  |  | 138 | 69 | 84 | Upgrade existing 37.33 MVA transformer with 84 MVA unit. Existing transformer will be moved to Kuhlman | IL |  |  | 1200000
A in MTEP20 | Central | PPI | 18160 | 24981 | LN | 2023-12-31 | Arenzville | Bluff Springs | 1 | 69 | 69 | 50 | New 10.3-mile 69 kV line tying Illinois Electric Cooperative to Menard Electric Cooperative | IL |  | 10.3 | 7459000
A in MTEP20 | Central | PPI | 18161 | 24982 | LN | 2023-12-31 | Bluff Springs | Virginia |  | 69 | 69 | 50 | New 13.8-mile 69 kV line in Menard Electric Cooperative | IL |  | 13.8 | 8000000
A in MTEP20 | Central | PPI | 18162 | 24983 | LN | 2023-12-31 | Ellisville | Kington | 1 | 69 | 69 | 50 | New 18.0-mile 69 kV line tying McDonough Power Cooperative to Spoon River Electric Cooperative | IL |  | 18 | 11925000
A in MTEP20 | Central | PPI | 18163 | 24984 | LN | 2023-12-31 | Ursa | Big Neck | 1 | 69 | 69 | 50 | New 12.4-mile 69 kV line in Adams Electric Cooperative | IL |  | 12.4 | 9024000
A in MTEP20 | East | METC | 18164 | 24985 | LN | 2024-06-01 | Amber | Pere Marquette |  | 138 |  |  | Construct a new line from Amber to Pere Marquette utilizing existing rights of way. Rebuild 0.62 miles from Amber to the Pere Marquette – Stronach 138 kV line with 954 ACSR utilizing future 230 kV double circuit construction initially operated as 138 kV single circuit with adjacent side left vacant for future use. Rebuild 0.72 miles of the existing single circuit Pere Marquette – Stronach 138 kV line with double circuit 138 kV construction and install 954 ACSR conductor on one side for the new Amber – Pere Marquette #2 138 kV line and 795 ACSS conductor on the other side for the existing Pere Marquette – Stronach 138 kV line. | MI |  |  | 3870000
A in MTEP20 | East | METC | 18164 | 25231 | SUB | 2024-06-01 | Amber |  |  | 138 |  |  | Install 1 new 3000 A, 138 kV breaker and associated equipment at Amber. | MI |  |  | 885000
A in MTEP20 | East | METC | 18164 | 25195 | SUB | 2024-06-01 | Pere Marquette |  |  | 138 |  |  | Install 1 new 3000 A, 138 kV breaker and associated equipment at Pere Marquette. | MI |  |  | 1060000
A in MTEP20 | Central | PPI | 18165 | 24986 | SwSta | 2023-12-31 | Virginia |  |  | 69 | 69 | 50 | New 69 kv breaker station near Virginia | IL |  |  | 2929500
A in MTEP20 | Central | PPI | 18166 | 24987 | LN | 2023-12-31 | Virginia | Saidora | 1 | 69 | 69 | 50 | New 14.9-mile 69 kV line in Menard Electric Cooperative | IL |  | 14.9 | 8640000
A in MTEP20 | Central | PPI | 18167 | 24988 | CAP | 2024-12-31 | Smithfield |  |  | 69 | 69 | 4.8 | Addition of 4.8 MVAR capacitor bank in Spoon River Electric Cooperative | IL |  |  | 400000
A in MTEP20 | East | ITCT | 18168 | 24990 | LNrc | 2024-06-01 | Bismarck | Red Run | 1 | 230 |  |  | Reconductor approximately 2 miles utilizing 1431 ACSR and upgrade terminal station equipment at Bismarck and Red Run. | MI | 2 |  | 2250000
A in MTEP20 | East | ITCT | 18168 | 24992 | TEQ | 2024-06-01 | Red Run |  |  | 230 |  |  | Upgrade terminal equipment at Red Run 230 kV station. | MI |  |  | 47000
A in MTEP20 | East | ITCT | 18168 | 24991 | TEQ | 2024-06-01 | Bismarck |  |  | 230 |  |  | Upgrade terminal equipment at Bismarck 230 kV station. | MI |  |  | 47000
A in MTEP20 | Central | PPI | 18169 | 24989 | CAP | 2026-12-31 | Macomb |  |  | 69 | 69 | 4.8 | Addition of 4.8 MVAR capacitor bank in McDonough Power Cooperative | IL |  |  | 400000
A in MTEP20 | Central | CWLP | 18171 | 25107 | LNrc | 2021-03-01 | Chatham Independence | Spaulding | 1 | 138 |  | 330 | Reconductor with 795 ACSS | IL | 1.1 |  | 150000
A in MTEP20 | Central | CWLP | 18172 | 25108 | CAP | 2021-03-01 | Taintor |  |  | 69 |  |  | Add two 20 MVAR cap banks to Taintor Sub | IL |  |  | 250000
A in MTEP20 | West | MEC | 18174 | 24999 | LNup | 2020-06-30 | Bondurant | Montezuma | 1 | 345 |  | 1083 MVA | Replace structures to increase line rating | IA | 49.91 |  | 320000
A in MTEP20 | East | ITCT | 18175 | 25000 | LNrb | 2025-06-01 | Van Dyke 2 | Sloan | 1 | 120 |  |  | Rebuild approximately 0.6 miles 795 ACSR utilizing 1431 ACSR on double circuit structures | MI | 0.6 |  | 2210000
A in MTEP20 | East | ITCT | 18175 | 25001 | TEQ | 2025-06-01 | Sloan |  |  | 120 |  |  | Upgrade terminal equipment at Sloan 120 kV station. | MI |  |  | 140000
A in MTEP20 | West | MEC | 18176 | 25004 | BUS | 2022-12-01 | Several Locations |  |  | 345 |  |  | New 345 kV circuit breakers and expand to ring bus. | IA |  |  | 31000000
A in MTEP20 | West | MEC | 18177 | 25002 | LNrc | 2021-12-15 | Webster | Sub T Fort Dodge | 1 | 161 |  | 231 MVA | Reconductor existing 477 ACSR portion of Webster-Sub T Fort Dodge with T2-556 ACSR Dove | IA | 8 |  | 6300000
A in MTEP20 | East | ITCT | 18178 | 25003 | LNrb | 2024-06-01 | Hancock | Lily | 1 | 120 |  |  | Rebuild approximately 2 miles of 3/0 Cu X2 utilizing 954 ACSR on 230kV, double-circuit structures. | MI | 2 |  | 4400000
A in MTEP20 | East | ITCT | 18178 | 25260 | TEQ | 2024-06-01 | Lily |  |  | 120 |  |  | Replace terminal equipment at Lily 120kV station. | MI |  |  | 140000
A in MTEP20 | East | ITCT | 18178 | 25259 | TEQ | 2024-06-01 | Hancock |  |  | 120 |  |  | Replace terminal equipment at Hancock. | MI |  |  | 140000
A in MTEP20 | East | ITCT | 18179 | 25005 | LNrb | 2024-06-01 | Hood | Lily | 1 | 120 |  |  | Rebuild approximately 2.6 miles of 3/0 Cu X2 utilizing 954 ACSR on 230kV, double circuit structures. | MI | 2.6 |  | 5730000
A in MTEP20 | East | ITCT | 18179 | 25261 | TEQ | 2024-06-01 | Lily |  |  | 120 |  |  | Replace terminal equipment at Lily 120kV station. | MI |  |  | 50000
A in MTEP20 | South | SMEPA | 18180 | 25291 | CB | 2021-03-01 | Missionary |  |  | 230 |  |  | Add new bay and breaker at Missionary 230 kV substation. | MS |  |  | 1055000
A in MTEP20 | South | SMEPA | 18180 | 25292 | IND | 2021-03-01 | Missionary |  |  | 230 |  |  | Add new Reactor Bank (Single Stage 30 MVAR) at Missionary 230 kV substation. | MS |  |  | 1000000
A in MTEP20 | West | MEC | 18181 | 25006 | CAP | 2022-06-30 | Black Hawk |  |  | 345 |  | 150 MVAR | Add 345 kV, 150 MVAR capacitor bank | IA |  |  | 4500000
A in MTEP20 | South | SMEPA | 18182 | 25293 | CAP | 2021-03-01 | Cole Road |  |  | 69 |  |  | Relocate Paulding 69kV cap bank to Cole Road 69kV substation. | MS |  |  | 660000
A in MTEP20 | West | MEC | 18183 | 25009 | CAP | 2021-12-31 | Midport |  |  | 161 |  | 50 MVAR | 161 kV, 50 MVAR capacitor bank | IA |  |  | 1545000
A in MTEP20 | East | ITCT | 18184 | 25007 | LNrb | 2024-06-01 | Red Run | Sloan | 1 | 120 |  |  | Rebuild approximately 2.8 miles utilizing 954 ACSR on double circuit structures. | MI | 2.8 |  | 7010000
A in MTEP20 | East | ITCT | 18184 | 25008 | TEQ | 2024-06-01 | Sloan |  |  | 120 |  |  | Upgrade terminal equipment at Sloan 120 kV station. | MI |  |  | 85000
A in MTEP20 | East | METC | 18187 | 25012 | LNup | 2023-12-31 | Pere Marquette | Stronach |  | 138 |  |  | Completely remediate the sag on the Pere Marquette – Stronach 138 kV line. | MI |  |  | 335000
A in MTEP20 | East | METC | 18187 | 25013 | TEQ | 2023-12-31 | Stronach |  |  | 138 |  |  | Replace terminal equipment at the Stronach end of the line. | MI |  |  | 130000
A in MTEP20 | West | MEC | 18188 | 25014 | LNup | 2020-06-30 | Diamond Trail | Hills | 1 | 345 |  | 956 MVA | Replace structures to uprate line | IA | 33.19 |  | 350000
A in MTEP20 | East | METC | 18190 | 25018 | SwSta | 2024-06-01 | Calvary |  |  | 138 |  |  | Rebuild Dort 138 kV station with a new control house at a new site approximately 0.5 miles to the south utilizing new equipment in a four-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called Calvary. | MI |  |  | 13875000
A in MTEP20 | East | METC | 18190 | 25027 | LINE | 2024-06-01 | Garfield | Calvary |  | 138 |  |  | Re-terminate the Garfield - Dort 138 kV line at Calvary | MI |  |  | 1070000
A in MTEP20 | East | METC | 18190 | 25025 | LINE | 2024-06-01 | Goss | Calvary |  | 138 |  |  | Re-terminate the Goss - Dort 138 kV line at Calvary | MI |  |  | 2350000
A in MTEP20 | East | METC | 18190 | 25024 | LINE | 2024-06-01 | Thetford | Calvary | 2 | 138 |  |  | Re-terminate the Thetford - Dort #2 138 kV line at Calvary | MI |  |  | 435000
A in MTEP20 | East | METC | 18190 | 25023 | LINE | 2024-06-01 | Thetford | Calvary | 1 | 138 |  |  | Re-terminate the Thetford - Dort #1 138 kV line at Calvary | MI |  |  | 1400000
A in MTEP20 | East | METC | 18190 | 25022 | LINE | 2024-06-01 | Beveridge | Calvary |  | 138 |  |  | Re-terminate the Beveridge - Dort 138 kV line at Calvary | MI |  |  | 485000
A in MTEP20 | East | METC | 18190 | 25021 | LINE | 2024-06-01 | Weadock | Calvary |  | 138 |  |  | Re-terminate the Weadock - Dort 138 kV line at Calvary | MI |  |  | 1710000
A in MTEP20 | East | ITCT | 18198 | 25038 | LNup | 2023-12-31 | Airport | Tulsa | 1 | 120 |  |  | Remediate the sag on this 120 kV line up to the conductor’s limit. | MI |  |  | 230000
A in MTEP20 | East | ITCT | 18200 | 25040 | LNup | 2023-12-31 | Hemphill | Hunters Creek | 1 | 120 |  |  | Remediate the sag on this 120 kV line up to the conductor’s limit. | MI |  |  | 430000
A in MTEP20 | East | ITCT | 18201 | 25041 | LNup | 2023-12-31 | Hunters Creek | Stratford | 1 | 120 |  |  | Remediate the sag on this 120 kV line to at least 175 MVA for summer emergency rating. | MI |  |  | 510000
A in MTEP20 | East | ITCT | 18205 | 25045 | TEQ | 2023-12-31 | Red Run |  |  | 120 |  |  | Upgrade the station equipment at Red Run 120 kV station. | MI |  |  | 1100000
A in MTEP20 |  | SMEPA | 18224 | 25434 | CB | 2022-06-01 | Batesville 161kV |  |  | 161 |  |  | Add new 161kV breaker to Batesville 161kV ring bus to accommodate bus reconfigure. | MS |  |  | 215000
A in MTEP20 |  | SMEPA | 18224 | 25437 | SUBmisc | 2022-06-01 | Batesville 161kV |  |  | 161 |  |  | Additional structure, conductor, and equipment needed to accommodate bus reconfigure. | MS |  |  | 50000
A in MTEP20 | South | SMEPA | 18224 | 25436 | BUS | 2022-06-01 | Batesville 161kV |  |  | 161 |  |  | Add new 161kV breaker bay to Batesville 161kV ring bus to accommodate bus reconfigure. | MS |  |  | 430000
A in MTEP20 |  | SMEPA | 18224 | 25435 | CB | 2022-06-01 | Batesville 161kV |  |  | 161 |  |  | Add new 161kV breaker to Batesville 161kV ring bus to accommodate bus reconfigure. | MS |  |  | 215000
A in MTEP20 | South | Entergy-MS | 18226 | 25294 | TEQ | 2021-03-01 | Refuge |  |  | 115 |  |  | Cooperative Energy plans to upgrade the 1200 A switches at Refuge GOAB. | MS |  |  | 25000
A in MTEP20 | South | Entergy-LA | 18227 | 25053 | Dist | 2026-06-01 | Norris Road |  |  | 138 |  |  | New 138 kV distribution station to be cut into the Youngsville to Segura 138 kV line. Includes ~3 miles of in and out transmission line. | LA |  | 6 | 39200000
A in MTEP20 | South | Entergy-LA | 18233 | 25062 | SUB | 2025-06-01 | Start |  |  | 115 |  |  | Area load growth. | LA |  |  | 39505305
A in MTEP20 | South | Entergy-LA | 18233 | 25063 | LN |  | Alto |  |  | 115 |  |  | Area load growth. In and out from Alto to Start. | LA
A in MTEP20 | East | METC | 18238 | 25073 | SwSta | 2024-12-31 | Morrow (Jaguar) |  |  | 138 |  |  | The proposed solution is to rebuild Morrow 138 kV station at a new site approximately 1.35 miles to the north utilizing new equipment in a five-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called JK Ave. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance and outages to be performed in a safe and efficient manner. | MI |  |  | 16775000
A in MTEP20 | East | METC | 18238 | 25082 | LN | 2024-12-31 | Battle Creek | Morrow (Jaguar) | 2 | 138 |  |  | Cut new station into the Battle Creek - Morrow #2 138 kV line | MI |  |  | 170000
A in MTEP20 | East | METC | 18238 | 25081 | LN | 2024-12-31 | Battle Creek | Morrow (Jaguar) | 1 | 138 |  |  | Cut new station into the Battle Creek - Morrow #1 138 kV line | MI |  |  | 843000
A in MTEP20 | East | METC | 18238 | 25080 | LN | 2024-12-31 | Argenta | Morrow (Jaguar) |  | 138 |  |  | Cut new station into the Argenta - Morrow 138 kV line | MI |  |  | 1043000
A in MTEP20 | East | METC | 18238 | 25079 | LN | 2024-12-31 | Warner | Morrow (Jaguar) |  | 138 |  |  | Cut new station into the Bradley - Morrow 138 kV line | MI |  |  | 170000
A in MTEP20 | East | METC | 18238 | 25078 | LN | 2024-12-31 | Riverview | Morrow (Jaguar) |  | 138 |  |  | Cut new station into the Riverview - Morrow 138 kV line | MI |  |  | 773000
A in MTEP20 | East | METC | 18238 | 25077 | LN | 2024-12-31 | Cork Street | Morrow (Jaguar) |  | 138 |  |  | Cut new station into the Cork Street - Morrow 138 kV line | MI |  |  | 1910000
A in MTEP20 | East | METC | 18238 | 25075 | LN | 2024-12-31 | Batavia | Morrow (Jaguar) |  | 138 |  |  | Cut new station into the Batavia - Morrow 138 kV line | MI |  |  | 616000
A in MTEP20 | East | ITCT | 18240 | 25066 | CAP | 2023-12-31 | Boyne |  |  | 120 |  |  | Install 51 MVAR capacitor (18 & 33 MVAR banks) at Boyne 120 kV station to maintain acceptable voltage levels within this region of the Oakland area. | MI |  |  | 2430000
A in MTEP20 | East | ITCT | 18241 | 25067 | TX | 2023-12-31 | Stephens |  |  | 345 | 120 |  | Replace Stephens 345/120kV transformer #303 | MI |  |  | 4800000
A in MTEP20 | East | ITCT | 18242 | 25068 | TX | 2023-12-31 | Wayne |  |  | 345 | 120 |  | Replace Wayne transformer 303 with a new transformer | MI |  |  | 4400000
A in MTEP20 | East | METC | 18243 | 25069 | TX | 2023-12-31 | Battle Creek |  |  | 345 | 138 |  | Replace Transformer #2 with a new unit | MI |  |  | 6400000
A in MTEP20 | East | METC | 18244 | 25070 | TX | 2023-12-31 | Gallagher |  |  | 345 | 138 |  | Replace Gallagher Transformer #2 with a new Transformer | MI |  |  | 6200000
A in MTEP20 | East | METC | 18245 | 25071 | IND | 2023-12-31 | Kenowa |  |  | 345 |  |  | Replace Kenowa 345kV Shunt Reactor #33F with a new reactor | MI |  |  | 2350000
A in MTEP20 | South | Entergy-TX | 18248 | 25083 | Dist | 2024-06-01 | Millbend |  |  | 138 |  |  | Build ~ 7miles of new transmission line to cut the new Millbend 138 kV station into the existing New Caney to Parkway 138 kV line. | TX |  | 7 | 65400000
A in MTEP20 | Central | AmerenIL | 18249 | 25084 | LINE | 2023-12-01 | Corbin | Substation |  | 138 |  |  | Install a 100 MVAR statcom | IL |  |  | 91400000
A in MTEP20 | Central | AmerenIL | 18250 | 25085 | SUB | 2023-06-01 | Robinson area | Substation |  | 138 |  |  | Install new 138 kV substation by Re-routing the Robinson – Newton 138 kV line and the Robinson – Lawrenceville 138 kV line in and out of the new substation site. | IL |  |  | 78000000
A in MTEP20 | Central | AmerenIL | 18250 | 25086 | SUBmisc | 2023-06-01 | Robinson Area | Substation |  | 138 |  |  | Install an 70 Mvar Statcom. | IL
A in MTEP20 | South | Entergy-TX | 18251 | 25087 | LNrb | 2022-03-01 | Alligator Bayou | Fort Worth |  | 69 |  |  | Rebuild 69 kV between Alligator Bayou and Fort Worth Pipe | TX | 7 |  | 10400000
A in MTEP20 | West | MDU | 18254 | 25090 | SUB | 2021-12-31 | Tioga |  |  | 115 | 60 |  | Rebuild Tioga Substation | ND |  |  | 2600000
A in MTEP20 | South | Entergy-TX | 18255 | 25091 | LNrb | 2023-06-01 | Fort Worth | Kolbs |  | 69 |  |  | Rebuild the line between Fort Worth and Kolbs 69 kV stations. | TX | 5 |  | 14100000
A in MTEP20 | West | MDU | 18257 | 25092 | SwSta | 2021-12-31 | Greenway |  |  | 41.6 |  |  | three breaker ring bus | SD |  |  | 3100000
A in MTEP20 | South | Entergy-TX | 18259 | 25094 | CB | 2023-06-01 | Lacon |  |  | 138 |  |  | Add a 138 kV breaker at Lacon 138 kV | TX |  |  | 10000000
A in MTEP20 | West | MDU | 18260 | 25095 | LNrb | 2021-12-31 | Greenway Tap | Herried | 1 | 41.6 |  |  | rebuild Greenway Tap-Herried 41.6 kV line | SD | 25 |  | 6600000
A in MTEP20 | Central | AmerenIL | 18263 | 25097 | LN | 2025-06-01 | Fargo | Hines |  | 138 |  |  | Construct a new line between the Fargo 138 kV substation and the Hines 138 kV substation. | IL |  |  | 18720000
A in MTEP20 | Central | AmerenMO | 18267 | 25102 | SwSta | 2023-12-01 | Labadie | Montgomery | 4 | 345 |  |  | Tap the Ameren Missouri Labadie-Montgomery 345kV line via a new 3-breaker, 345kV ring bus near the intersection of the line and the AECI (Central Electric Power Coop) 161kV line west of Charrette. | MO |  |  | 13000000
A in MTEP20 | Central | AmerenMO | 18267 | 25104 | TX | 2023-12-01 | Wright City Substation | AECI |  | 345 | 161 |  | Install new 345/161kV step down transformer at Wright City (AECI). | MO
A in MTEP20 | Central | AmerenMO | 18267 | 25103 | LNrb | 2023-12-01 | Ameren Wright City Area Sub | AECI Wright City Sub |  | 345 | 161 |  | Rebuild the existing 161kV line between the tap point and the AECI Wright City Substation as double-circuit 345/161kV. | MO |  |  | 26100000
A in MTEP20 | Central | SIGE | 18268 | 25112 | SUB | 2021-04-01 | Grandview 69 kV |  |  | 69 |  |  | Complete ring bus and add terminal for GI project J783 | IN |  |  | 885456
A in MTEP20 | Central | SIGE | 18268 | 25117 | SUBmisc | 2021-04-01 | Rockport 69 kV |  |  | 69 |  |  | Replace three 600 amp 69 kV switches with 1200 amp switches for GI project J783 | IN |  |  | 60622
A in MTEP20 | Central | SIGE | 18268 | 25115 | SUBmisc | 2021-04-01 | Grandview 69 kV |  |  | 69 |  |  | Replace two 600 amp 69 kV bus switches at Grandview with 1200 amp switches for GI project J783 | IN |  |  | 71418
A in MTEP20 | Central | AmerenIL | 18269 | 25110 | LN | 2025-06-01 | LaSalle | North Utica |  | 138 |  |  | Construct a new line between LaSalle 138 kV substation and a new North Utica area ring bus. | IL |  |  | 16000000
A in MTEP20 | Central | AmerenIL | 18269 | 25113 | CB | 2025-06-01 | LaSalle | Substation |  | 138 |  |  | Add two line breaker at the LaSalle 138 kV substation. | IL
A in MTEP20 | Central | AmerenIL | 18269 | 25111 | SwSta | 2025-06-01 | North Utica Area | Substation |  | 138 |  |  | Construct a new 138 kV ring bus breaking the North Lassalle – Fox River 138 kV line. | IL |  |  | 9400000
A in MTEP20 | East | CETO | 18272 | 25118 | LN | 2024-06-01 | Dort | Mott Lake | 1 | 138 |  |  | Approximately 0.5 miles of 138 kV line from Dort 138/46 kV Substation to the new Mott Lake Station. Existing METC structures and/or conductors will be utilized if made available and are in good condition. | MI |  | 0.5 | 250000
A in MTEP20 | East | CETO | 18272 | 25119 | LN | 2024-06-01 | Dort | Mott Lake | 2 | 138 |  |  | Approximately 0.5 miles of 138 kV line from Dort 138/46 kV Substation to the new Mott Lake Station. Existing METC structures and/or conductors will be utilized if made available and are in good condition. | MI |  | 0.5 | 250000
A in MTEP20 | Central | AmerenIL | 18275 | 25129 | LNrb | 2023-12-01 | Holland NW | Neoga S |  | 345 |  |  | Construct a 345 kV double circuit on the exisitng Holland Northwest-Neoga South-4509 line R.O.W. replacing structures. Target rating: 3000 A summer emergency. | IL |  |  | 32000000
A in MTEP20 | East | NIPS | 18276 | 25132 | LNrb | 2023-05-01 | Maple | LNG | 1 | 138 |  |  | Rebuild line with 1590 ACSR | IN | 8 |  | 16000000
A in MTEP20 | East | NIPS | 18276 | 25133 | SUBmisc | 2023-05-01 | LNG |  |  | 138 |  |  | Disc switches, conductor | IN |  |  | 2000000
A in MTEP20 | East | NIPS | 18278 | 25136 | LNrb | 2023-05-01 | LNG | Stillwell | 1 | 138 |  |  | Rebuild LNG to Stillwell line to 1590 ACSR | IN | 8 |  | 12000000
A in MTEP20 | East | NIPS | 18278 | 25137 | SUBmisc | 2023-05-01 | LNG |  |  | 138 |  |  | Disc switches, conductor | IN |  |  | 2000000
A in MTEP20 | Central | AmerenIL | 18279 | 25134 | CB | 2022-12-01 | South Ottawa | Bus-Tie |  | 138 |  |  | Install 138 kV bus-tie breaker at the switch 1516 position at South Ottawa | IL |  |  | 800000
A in MTEP20 | West | MEC | 18280 | 25138 | TEQ | 2020-11-01 | Floyd |  |  | 161 | 69 | 125 MVA | Replace terminal equipment adjacent to Floyd Substation 161-69 kV Transformer AB along with 161 kV breaker addition, 69 kV breaker replacement, and protective relaying upgrades. Existing terminal equipment limits the thermal rating of Floyd Substation 161-69 kV Transformer AB. Replacing limiting terminal equipment will allow use of Floyd Substation 161-69 kV Transformer AB's nameplate thermal ratings. | IA |  |  | 1200000
A in MTEP20 | Central | DEI | 18284 | 25139 | INT | 2021-03-15 | J754 345kV Switching Station |  |  | 345 |  |  | J754 - 345kV 3-breaker ring bus substation to be constructed in the Cayuga-Nucor 34501 line | IN |  |  | 19655000
A in MTEP20 | Central | DEI | 18284 | 25140 | INT | 2021-10-31 | J754 Gen. Station | J754 345kV Switching Station |  | 345 |  |  | J754 - 300MW wind farm and 345 line to point of interconnect | IN |  | 1 | 0
A in MTEP20 | Central | DEI | 18285 | 25141 | LN | 2021-06-01 | McGrawsville | Bunker Hill |  | 69 |  | 99 | WVPA to design and build McGrawsville to Bunker Hill 69kV alternate source line - 7.1 miles to be operated N.O. | IN |  | 7.1 | 5510000
A in MTEP20 | Central | DEI | 18286 | 25142 | LNrc | 2021-12-31 | Brownstown Sw Sta | Pumpkin Center |  | 69 |  | 99 | 6952 Rbld Pt 2 Brownstown Sw Sta to Pumpkin Center; 10.7 mi. - 477acsr ; Replace the 6952-69123 tie switch on pole #813-1535-02 located just outside Pumpkin Center substation | IN | 10.4 |  | 8361000
A in MTEP20 | Central | DEI | 18287 | 25143 | LNrc | 2022-06-01 | Terre Haute S. Vigo | HE Middletown Jct |  | 69 |  | 99 | Rbld 6901 circuit from TH Haute S. Vigo sub, pole 802-1158, to HE Middletown Jct, pole 802-1315, using light-duty steel poles, 477ACSR conductor & OPGW static. Rpl switch #64LB with two 2000A switches | IN | 5 |  | 8768000
A in MTEP20 | Central | DEI | 18288 | 25144 | LNrc | 2021-12-31 | Trafalgar Swi Sta | HE Samaria Jct |  | 69 |  | 99 | Rbld transmission line 6949 from Duke Trafalgar Swi Sta & HE Trafalgar sub to HE Samaria Jct using light duty steel poles, 477 ACSR and OPGW. Approximately 4.9 miles. | IN | 4.9 |  | 5280000
A in MTEP20 | Central | DEI | 18289 | 25145 | LNrc | 2021-12-31 | HE Needmore Jct | HE Needmore sub |  | 69 |  | 99 | 6949 Part 2B - Rebuild transmission line using light duty steel poles, 477 ACSR and OPGW from “HE Needmore Jct” (pole #825-3379) to the HE Needmore substation (pole #825-3418); approximately 2 miles. | IN | 2 |  | 3881000
A in MTEP20 | Central | DEI | 18290 | 25146 | GEN | 2021-07-16 | W. Laf. Purdue 138 | non-MISO queue gens |  | 138 | 12 |  | Purdue University CHP Generation - 15.5MW gas turbines with HRSG unit - non-MISO queue; non-BES | IN |  |  | 13310000
A in MTEP20 | Central | DEI | 18304 | 25147 | CB | 2022-06-01 | Batesville 345 |  |  | 345 | 138 |  | Batesville: Replace (1) 345kV circuit switcher with 345kV SF6 gas circuit breaker ; replace 345kv WT ; Replace (6) 138kV oil circuit breakers with SF6 gas circuit breakers - 13831, 13833, 13839, 13864, 13874, 138345-3 ; replace 13833 and 13874 WTs ; | IN |  |  | 7334000
A in MTEP20 | Central | DEI | 18305 | 25148 | CB | 2021-09-02 | Westwood | brkrs and relays |  | 345 | 138 |  | Westwood misc station equipment replacement including: upgrade relays on 13806, 13808, 138345-1, Bk2, 138 bus 1 and 2, 138 bus tie ; Replace OCB 13820, 13883 and relays | IN |  |  | 4900000
A in MTEP20 | Central | DEI | 18306 | 25149 | Dist | 2021-12-31 | H.E. Batesville | new dist sub |  | 138 | 12 |  | H.E. Batesville 138/12kV substation: new sub to be located in the 13833 ckt between Batesville 345 and Laurel | IN |  |  | 500000
A in MTEP20 | Central | DEI | 18307 | 25150 | Dist | 2022-06-01 | Westfield East | new dist sub |  | 69 | 12 |  | Westfield East: new sub - 69/12kv - 22.4 MVA xfmr bank, single phase regulators SCADA/IVVC, 2 breakers, and space for second bank. Normal feed from 6917 ckt, alternate from 69142. | IN |  | 3.6 | 3767000
A in MTEP20 | Central | DEI | 18308 | 25151 | Dist | 2021-06-01 | Hunts Creek | new dist sub |  | 138 | 12 |  | Hunts Creek 138/12kV substation: new sub to be located in the 13855 ckt between LGE Ghent and DEI Fairview | IN |  | 4 | 3807000
A in MTEP20 | Central | AmerenMO | 18309 | 25152 | SUB | 2022-12-01 | Fredericktown | Substation |  | 138 |  |  | Install new 138 kV ring bus at Fredericktown Substation. | MO |  |  | 7500000
A in MTEP20 | Central | AmerenIL | 18310 | 25153 | INT | 2021-05-28 | Ramsey East | Substation |  | 138 |  |  | Add terminal facilities to Ramsey East Substation For J811 interconnection. | IL |  |  | 500000
A in MTEP20 | Central | AmerenIL | 18311 | 25154 | INT | 2021-10-29 | Louisville South | Substation |  | 138 |  |  | Re-configure Louisville South 138 kV substation to BAAH bus. Add terminal facilities for J813 connection. | IL |  |  | 24000000
A in MTEP20 | Central | AmerenMO | 18312 | 25155 | INT | 2023-06-01 | Warrenton | Substation |  | 161 |  |  | Add terminal facilities at Warrenton 161 kV substation to interconnect J817, | MO |  |  | 3700000
A in MTEP20 | East | ITCT | 18313 | 25160 | LNup | 2020-12-31 | Bauer | Pontiac | 1 | 345 |  |  | Remediate the Sag limit to achieve a summer emergency rating of at least 258 MVA | MI |  |  | 961200
A in MTEP20 | Central | AmerenIL | 18314 | 25156 | INT | 2021-05-28 | Weedman | Substation |  | 138 |  |  | Add breaker position to existing ring bus at Weedman Substation for the J826 interconnection. | IL |  |  | 1700000
A in MTEP20 | Central | AmerenIL | 18315 | 25157 | INT | 2021-05-28 | Sandburg | Substation |  | 138 |  |  | Add 1 BAAH 138 kV leg to the Sandburg Substation and add 1 breaker postion to interconnect J844. | IL |  |  | 2700000
A in MTEP20 | Central | AmerenIL | 18316 | 25158 | INT | 2021-05-28 | Norris City North | Substation |  | 138 |  |  | Add terminal facilities to the Norris City North 138 kV bus to interconnect J853. | IL |  |  | 1200000
A in MTEP20 | Central | AmerenMO | 18319 | 25162 | LNup | 2021-06-01 | Fredericktown M&A | Heritage | 7011 | 161 |  |  | Replace poles for OPGW installation. Structure replacements will increase the rating to 120 degrees C. | MO |  |  | 8700000
A in MTEP20 | Central | AmerenIL | 18320 | 25163 | INT | 2021-05-01 | McLean | Oglesby |  | 138 |  |  | Install new 138 kV ring bus on the McLean-Oglesby line to make the interconnection for J715. | IL |  |  | 6600000
A in MTEP20 | Central | AmerenIL | 18321 | 25164 | INT | 2021-06-01 | Gibson City South | Paxton East |  | 138 |  |  | Install new ring bus on the Gibson City South-Paxton East 138 kV line to make the interconnection for J845. | IL |  |  | 6800000
A in MTEP20 | Central | AmerenIL | 18322 | 25165 | INT | 2021-05-28 | Pana | Substation |  | 138 |  |  | Add terminal facilities at the Pana Substation to make the inteconnection for J848. | IL |  |  | 900000
A in MTEP20 | Central | AmerenIL | 18323 | 25166 | INT | 2022-05-31 | Meredosia East | Ipava South |  | 138 |  |  | Install a new ring bus on the Meredosia East-Ipava South 138 kV line to make the interconnection for J859. | IL |  |  | 6800000
A in MTEP20 | Central | DEI | 18324 | 25167 | LN | 2023-06-01 | Delphi South | new line jct |  | 69 |  | 99 | WVPA to build new 69kV, 6.3 mile, radial, N.O., alternate source to Delphi South (IPC, Indiana Packers Corp.) from the existing 6988 line tapped between Flora and Rockfield | IN |  | 6.3 | 5510000
A in MTEP20 | Central | DEI | 18325 | 25168 | Dist | 2021-06-01 | Crane Northwest | new dist sub |  | 69 | 12 | 99 | new sub - "Crane Northwest" to feed NSA Crane ULTF - 17 MW new load to be fed from 69193 ckt - located North of existing NSA owned East and West Substations | IN |  | 0.8 | 2800000
A in MTEP20 | Central | DEI | 18326 | 25169 | LNrc | 2021-12-31 | Poseyville | HE Winfield |  | 69 |  | 99 | 69139 Rebuild Part 2: Poseyville to HE Winfield TDSIC ; 4.4 miles - N.O. tie line | IN | 4.4 |  | 6818000
A in MTEP20 | Central | DEI | 18327 | 25170 | LNrc | 2021-07-16 | Dresser | S. Vigo |  | 69 |  | 99 | 6901 rebuild from Dresser to S. Vigo with 477ACSR and light-duty steel poles | IN | 6 |  | 7162000
A in MTEP20 | Central | DEI | 18328 | 25171 | LNrc | 2021-07-22 | Greencastle N. | Morton Jct. |  | 69 |  | 99 | 6933 rebuild from Greencastle N. to Morton Jct. with 477ACSR and light-duty steel poles | IN | 6.8 |  | 8084000
A in MTEP20 | Central | DEI | 18329 | 25172 | LNrc | 2021-12-31 | Dover | Thorntown |  | 69 |  | 99 | 69134 rebuild from Dover to Thorntown with 477ACSR and light-duty steel poles | IN | 4.6 |  | 5776000
A in MTEP20 | Central | DEI | 18330 | 25173 | LNrc | 2021-12-31 | Westland Jct. | Westland |  | 69 |  | 99 | 69166 rebuild from Westland Jct. to Westland with 477ACSR and light-duty steel poles | IN | 6.6 |  | 5770000
A in MTEP20 | Central | DEI | 18331 | 25174 | LNrc | 2021-12-31 | Whitesville | Advance |  | 69 |  | 99 | 69154 rebuild from Whitesville to Advance with 477ACSR Oval @ 120C and light-duty steel poles | IN | 10.3 |  | 14410000
A in MTEP20 | Central | DEI | 18332 | 25175 | LNrc | 2021-12-31 | Knightstown | Carthage |  | 69 |  | 99 | 69140 rebuild from Knightstown to Carthage with 477ACSR and light-duty steel poles | IN | 4.9 |  | 7201000
A in MTEP20 | Central | DEI | 18333 | 25176 | LNrc | 2021-12-31 | Greencastle | Greencastle N. |  | 69 |  | 99 | 6933 rebuild from Greencastle to Greencastle N. with 477ACSR and light-duty steel poles | IN | 3.45 |  | 5231000
A in MTEP20 | Central | DEI | 18334 | 25177 | LNrc | 2021-12-31 | Connersville | Glenwood |  | 69 |  | 99 | 6920 rebuild from Connersville to Glenwood with 477ACSR and light-duty steel poles | IN | 8.65 |  | 9665000
A in MTEP20 | Central | DEI | 18335 | 25178 | GEN | 2021-04-01 | Tate and Lyle (old Staley) | non-MISO queue gens |  | 138 | 12 |  | Tate and Lyle (old Staley) Generation - existing sub on the 13808 ckt; 2 units -32.8MW each - non-MISO queue | IN |  |  | 250000
A in MTEP20 | West | XEL | 18344 | 25180 | SUB | 2020-09-15 | J587 Blazing Star 2 |  |  | 115 |  |  | New 115kV J587 Blazing Star substation including 2 115kV breaker bays. | MN |  |  | 3104000
A in MTEP20 | West | XEL | 18344 | 25184 | BUS | 2020-09-15 | Steep Bank Lake |  |  | 345 |  |  | Upgrade of Steep Bank Lake from 3-breaker ring to 4-breaker ring including new 345kV circuit breaker and associated bus upgrades. | MN
A in MTEP20 | West | XEL | 18344 | 25183 | LN | 2020-09-15 | Steep Bank Lake | J460 Blazing Star 1 | 2 | 345 |  |  | New Radial 0.05 mile 345kV line and 48 fiber OPGW from Steep Bank Lake to J460 Blazing Star 1 to feed new 345kV/115kV transformer at Blazing Star 1 | MN |  | 0.05
A in MTEP20 | West | XEL | 18344 | 25182 | SUB | 2020-09-15 | J587 Blazing Star 1 |  |  | 345 | 115 |  | New 115kV/345kV 225MVA step up transformer at Blazing Star 1 substation to feed Blazing Star 2 substation | MN
A in MTEP20 | West | XEL | 18344 | 25181 | LN | 2020-09-15 | J460 Blazing Star 1 | J587 Blazing Star 2 | 1 | 115 |  |  | New radial 8 mile 115kV line and 48 fiber OPGW from Blazing Star 1 to Blazing Star 2 | MN |  | 8
A in MTEP20 | West | XEL | 18345 | 25185 | LNrb | 2022-09-15 | Helena | Scott County | 1 | 345 |  |  | Rebuild of Helena - Scott County 345kV line for Affected Systems upgrade for J587 Blazing Star 2 | MN | 16.59 |  | 34000000
A in MTEP20 | West | OTP | 18364 | 25189 | TEQ | 2022-11-30 | OTP Oslo 115 kV |  |  | 115 |  | 239 | Replace 600 Amp Switch at OTP Oslo with 1200 Amp Switch. | MN |  |  | 200000
A in MTEP20 | East | METC | 18384 | 25194 | LNup | 2020-12-31 | Bullock | Saginaw River |  | 138 |  |  | Increase the sag limits on the Bullock to Gleaner J and Gleaner J to Hacket J sections of the Bullock - Saginaw River 138 kV circuit | MI |  |  | 1024800
A in MTEP20 | East | METC | 18424 | 25196 | SUB | 2022-04-08 | Mud Lake |  |  | 138 |  |  | Construct Mud Lake 138kV station as a breaker and half station with 3 breakers. | MI |  |  | 5544000
A in MTEP20 | East | METC | 18424 | 25198 | RLY | 2022-04-08 | Verona |  |  | 138 |  |  | Upgrade Verona position 588 relaying to accomodate the changes | MI |  |  | 161000
A in MTEP20 | East | METC | 18424 | 25197 | LN | 2022-04-08 | Verona | Foundry |  | 138 |  |  | Extend the Verona - Foundry 138kV line, to loop in Mud Lake 138kV. | MI |  |  | 3290000
A in MTEP20 | East | METC | 18425 | 25199 | LN | 2022-04-08 | Verona | Marshall |  | 138 |  |  | Cut in and extend the Verona - Marshall 138kV line by adding 0.6 miles of 954 ACSR DCT to loop into Mud Lake 138 kV station. | MI |  | 1.2 | 4150000
A in MTEP20 | East | METC | 18425 | 25202 | RLY | 2022-04-08 | Marshall |  |  | 138 |  |  | Upgrade the relaying at Marshall section 10 | MI |  |  | 180000
A in MTEP20 | East | METC | 18425 | 25201 | RLY | 2022-04-08 | Verona |  |  | 138 |  |  | Upgrade the relaying at Verona position 388. | MI |  |  | 180000
A in MTEP20 | East | METC | 18425 | 25200 | SUB | 2022-04-08 | Mud Lake |  |  | 138 |  |  | Extend the White bus to start row 10. Install two 40kA breakers at position 8M9 and 8W8. | MI |  |  | 2000000
A in MTEP20 | East | METC | 18426 | 25203 | LNrb | 2022-04-08 | Mud Lake | Foundry |  | 138 |  |  | Rebuild the 4.4 miles of 336 ACSR from Mud Lake 138 kV Substation to Convis and Brewer St. Taps with 954 ACSR. Fiber should be strung on the 0.6 mile section between Convis and J758 substation. | MI | 4.4 |  | 5700000
A in MTEP20 | West | XEL | 18444 | 25205 | LNrb | 2020-03-31 | Panther | HUC Mcleod | 1 | 230 |  |  | Replace structures on 230kV line from Panther to HUC-McLeod to increase capacity to support J526 wind generation interconnection | MN |  |  | 880000
A in MTEP20 | East | NIPS | 18484 | 25210 | SUB | 2021-08-01 | 17REYNOLDS |  |  | 345 |  |  | 345/138 transformer will move to bay 6 at Transmission Owner’s Reynolds substation, new breaker in bay 6, lead line from Generating Facility will be accommodated into bay 5. | IN |  |  | 2979556
A in MTEP20 | West | OTP | 18504 | 25211 | SUBmisc | 2020-03-10 | Hankinson 230 |  |  | 230 |  |  | Replace wave trap at Hankinson on the Wahpeton to Hankinson 230 kV line. | ND |  |  | 25000
A in MTEP20 | West | OTP | 18504 | 25213 | LNup | 2020-06-02 | Wahpeton 230 | Hankinson 230 |  | 230 |  |  | Structures along the line will be required to be replaced. The existing Wahpeton to Hankinson 230 kV transmission line is rated at 257 MVA during summer conditions. This sub-project upgrades the Hankinson to Wahpeton 230 kV transmission line to a rating of 368.2 MVA during summer conditions. | ND |  |  | 169567
A in MTEP20 | West | OTP | 18504 | 25212 | SUBmisc | 2020-03-10 | Wahpeton 230 |  |  | 230 |  |  | Replace wave trap at Wahpeton on the Wahpeton to Hankinson 230 kV line. | ND |  |  | 25000
A in MTEP20 | West | XEL | 18505 | 25214 | LNrb | 2023-03-01 | Jim Falls | Holcombe | 1 | 115 |  |  | Rebuild 115kV line from Jim Falls to Holcombe to prevent overload under contingency. | WI |  |  | 15000000
A in MTEP20 | East | ITCT | 18525 | 25216 | TEQ | 2021-12-31 | Brownstown |  |  | 345 |  |  | Upgrade five (5) 345 kV switches (“ED”, “FD”, “FH”, “FK”, “FO”) at Brownstown 3 345 kV station. | MI |  |  | 1560000
A in MTEP20 | West | ATC | 18566 | 25220 | SUB | 2021-08-27 | Falcon SS |  |  | 138 |  |  | Network Upgrades | WI |  |  | 668951
A in MTEP20 | West | ATC | 18566 | 25221 | SUB | 2021-08-27 | Falcon SS |  |  | 138 |  |  | Interconnection Facilities | WI |  |  | 201235
A in MTEP20 | West | ATC | 18567 | 25222 | SUB | 2021-08-27 | Zenith SS |  |  | 115 |  |  | Network Upgrades | WI |  |  | 5735088
A in MTEP20 | West | ATC | 18567 | 25226 | SUB | 2021-08-27 | Zenith SS |  |  | 115 |  |  | Interconnection Facilities | WI |  |  | 508554
A in MTEP20 | West | ATC | 18567 | 25225 | SUB | 2021-08-27 | Wien SS |  |  | 115 |  |  | Network Upgrades | WI |  |  | 94815
A in MTEP20 | West | ATC | 18567 | 25224 | SUB | 2021-08-27 | McMillan SS |  |  | 115 |  |  | Network Upgrades | WI |  |  | 94815
A in MTEP20 | West | ATC | 18567 | 25223 | LN | 2021-08-27 | Wien SS | McMillan | B-54 | 115 |  |  | B-54 Line Loop into J821 Zenith SS | WI |  |  | 801860
A in MTEP20 | West | ATC | 18568 | 25228 | LN | 2023-11-30 | Howards Grove SS | Erdman SS |  | 138 |  |  | New Line | WI |  | 7 | 25000000
A in MTEP20 | Central | AmerenIL | 18625 | 25242 | LN | 2022-12-31 | NUTWOOD 69.0 | 2HARDIN 69.0 | 1 | 69 |  | 84 | New loop feed to MJM-Nutwood 69/12kV Substation | IL |  | 6 | 2000000
A in MTEP20 | Central | AmerenIL | 18626 | 25243 | LN | 2022-06-01 | Jerseyville 69.0 | New Delhi 69/12kV Substation | 1 | 69 |  | 84 | Build new 69kV line for new substation | IL |  | 4 | 3000000
A in MTEP20 | West | MRES | 18645 | 25247 | TEQ | 2021-06-01 | Mcleod 115 kV |  |  | 115 |  |  | Replace overloaded jumpers. | MN |  |  | 20000
A in MTEP20 | West | ATC | 18665 | 25248 | SUB | 2020-11-06 | Ebenezer SS |  |  | 138 |  |  | Network Upgrades | WI |  |  | 4543328
A in MTEP20 | West | ATC | 18665 | 25252 | INT | 2020-11-06 | Ebenezer SS |  |  | 138 |  |  | interconnection Facilities Upgrades | WI |  |  | 230090
A in MTEP20 | West | ATC | 18665 | 25251 | SUB | 2020-11-06 | Nelson Dewey SS |  |  | 138 |  |  | Network Upgrades | WI |  |  | 51516
A in MTEP20 | West | ATC | 18665 | 25250 | SUB | 2020-11-06 | Eden SS |  |  | 138 |  |  | Network Upgrades | WI |  |  | 51516
A in MTEP20 | West | ATC | 18665 | 25249 | LNup | 2020-11-06 | Lancaster SS | Eden SS |  | 138 |  |  | X-16 Line Upgrades | WI |  |  | 649883
A in MTEP20 | East | NIPS | 18685 | 25263 | INT | 2023-04-15 | 17EWINAMAC | 17MONTICELLO | 1 | 138 |  |  | East Winamac to Monticello 138kV Line | IN |  |  | 15990564
A in MTEP20 | Central | AmerenIL | 18705 | 25274 | Remove | 2020-06-01 | Roxford | Coffeen | 1 | 345 |  |  | Reterminate existing Coffeen-Roxford 345 kV line at Coffeen North | IL
A in MTEP20 | Central | AmerenIL | 18705 | 25277 | LN | 2020-06-01 | Coffeen North | Roxford | 1 | 345 |  |  | Reterminate Coffeen-Roxford line at Coffeen North | IL |  |  | 500000
A in MTEP20 | Central | AmerenIL | 18705 | 25276 | LN | 2020-06-01 | Pana | Coffeen North | 1 | 345 |  |  | Reterminate Coffeen-Pana line at Coffeen North | IL |  |  | 500000
A in MTEP20 | Central | AmerenIL | 18705 | 25275 | Remove | 2020-06-01 | Coffeen | Pana | 1 | 345 |  |  | Reterminate Coffeen-Pana at Coffeen North | IL
A in MTEP20 | Central | AmerenIL | 18706 | 25278 | Remove | 2020-06-01 | Duck Creek | Ipava | 1 | 345 |  |  | Connect the Duck Creek-Ipava and Duck Creek-Maple Ridge lines, bypassing the Duck Creek 345 kV Switchyard | IL |  |  | 300000
A in MTEP20 | Central | AmerenIL | 18706 | 25280 | LN | 2020-06-01 | Ipava | Maple Ridge | 1 | 345 |  |  | Connect the Duck Creek-Ipava and Duck Creek-Maple Ridge lines, bypassing the Duck Creek 345 kV Switchyard | IL |  |  | 300000
A in MTEP20 | Central | AmerenIL | 18706 | 25279 | Remove | 2020-06-01 | Duck Creek | Maple Ridge | 1 | 345 |  |  | Connect the Duck Creek-Ipava and Duck Creek-Maple Ridge lines, bypassing the Duck Creek 345 kV Switchyard | IL |  |  | 300000
A in MTEP20 | South | Entergy-AR | 18725 | 25281 | INT | 2021-08-01 | Searcy Price |  |  | 161 |  |  | POI for J893 to interconnect a 100 MW Solar Facility | AR |  |  | 8045000
A in MTEP20 | South | Entergy-AR | 18726 | 25282 | INT | 2023-02-01 | Locust Creek |  |  | 161 |  |  | Construct a new 3 breaker 161kV substation to interconnect a 180 MW solar generation project. | AR |  |  | 13077000
A in MTEP20 | South | Entergy-AR | 18727 | 25283 | INT | 2022-10-01 | Marston |  |  | 161 |  |  | A new 3 breaker ring bus connected to the New Madrid - Portageville 161kV line | MO |  |  | 4382000
A in MTEP20 | East | METC | 18728 | 25284 | LNrb | 2024-12-31 | Cobb | Sternberg | 1 | 138 |  |  | Rebuild approximately 8 miles of the Cobb - Sternberg 138kV circuit using 954 ACSR conductor with single circuit steel structures. | MI | 8 |  | 10200000
A in MTEP20 |  | METC | 18728 | 25564 | TEQ | 2024-12-31 | CHOPIN |  |  | 138 |  |  | Terminate fiber in station | MI |  |  | 50000
A in MTEP20 |  | METC | 18728 | 25556 | TEQ | 2024-12-31 | Sternberg |  |  | 138 |  |  | Upgrade line entrance at Sternberg | MI |  |  | 200000
A in MTEP20 | East | ITCT | 18745 | 25289 | LNrb | 2024-06-01 | Bunce Creek | Scott (B3N) |  | 220 |  |  | Reconductor approximately 0.44 mile of the Bunce Creek- Scott (B3N) 220kV circuit using 795 ACSS conductor. | MI | 0.44 |  | 660000
A in MTEP20 | Central | BREC | 18765 | 25290 | TX | 2021-03-01 | Reid EHV |  |  | 345 | 161 | 336 | Reallocate existing transformers - move one existing Reid EHV 161/345 kV transformer to Otter Creek (steel mill project). | KY |  |  | 150000
A in MTEP20 | South | Entergy-LA | 18785 | 25295 | INT | 2022-10-20 | Addis | Big Cajun |  | 230 |  |  | To support the interconnection of J639 | LA |  |  | 1790777
A in MTEP20 | South | Entergy-LA | 18786 | 25296 | INT | 2022-02-15 | Amite |  |  | 115 |  |  | Supporting the interconnection of J909 | LA |  |  | 4254000
A in MTEP20 | South | Entergy-LA | 18787 | 25297 | SUB | 2022-10-15 | Oak Ridge |  |  | 115 |  |  | This project consists of transforming the existing 115 kV yard from single bus to dual bus, expanding the existing substation site, installing a new control house, and installing shielding and light fixtures to accommodate the connection of the Interconnection Customer’s transmission line. | LA |  |  | 11314000
A in MTEP20 | South | AECC | 18805 | 25298 | CAP | 2021-06-01 | Hickman North |  |  | 161 |  |  | Install a 60 MVAR capacitor bank | AR |  |  | 2000000
A in MTEP20 | East | METC | 18825 | 25302 | BUS | 2022-05-01 | Island Rd |  |  | 138 |  |  | Replace the 4/0 CU and 1/0 CU bus conductor at Island Rd White bus and Position 177 to achieve a rating of at least 141 MVA (590 amps). | MI |  |  | 134000
A in MTEP20 | Central | DEI | 18845 | 25307 | SUB | 2021-12-31 | Greenwood Clark Twnshp | 230kV ring bus |  | 230 | 69 |  | Greenwood Clark Twnshp: add (2) CBs to complete a 3-position 230kV Ring bus; replace misc. 230kV and 69kV equipment in-kind | IN | 0 | 0 | 8053000
A in MTEP20 | West | ITCM | 18846 | 25308 | SUB | 2022-12-15 | Creston Roundhouse | Substation |  | 69 | 69 |  | Per Alliant’s request, ITC will construct a 3-terminal straight bus with tie breaker at the proposed Creston Roundhouse substation. All ITC terminal equipment will be capable of 2000A minimum and Alliant will own the land and joint use assets. In addition, ITC line equipment will use T2-4/0. | IA |  |  | 4505464
A in MTEP20 | West | ITCM | 18846 | 25313 | TAP | 2022-12-15 | Creston East | CKT 4220 | 1 | 69 | 69 |  | ITC will terminate the circuit into Creston Roundhouse using T2-4/0. | IA |  | 0.1 | 207600
A in MTEP20 | West | ITCM | 18846 | 25312 | SUB | 2022-12-15 | Creston | Creston East |  | 69 | 69 |  | Retire ITC assets at Creston and Creston East | IA |  |  | 1318152
A in MTEP20 | West | ITCM | 18846 | 25311 | TAP | 2022-12-15 | Creston East | Creston | 1 | 69 | 69 |  | ITC will tie the existing Creston- Summit Lake and Creston – Creston East 69kV circuits together using T2- 4/0 creating a Creston Roundhouse- Summit Lake Circuit. It would be ideal to tie the circuits together near the existing Creston Substation. This circuit will be terminated into the Creston Roundhouse substation using T2-4/0. | IA |  | 0.1 | 207600
A in MTEP20 | West | ITCM | 18846 | 25310 | TAP | 2022-12-15 | Creston | Mount Ayr | 1 | 69 | 69 |  | ITC will terminate the 69kV circuit into Creston Roundhouse using T2-4/0 | IA |  | 0.33 | 984000
A in MTEP20 | West | ITCM | 18846 | 25309 | LNup | 2022-12-15 | Creston East | Creston D.O.E. | 1 | 69 | 69 |  | Retrofit with OPGW and terminate the circuit into Creston Roundhouse using T2-4/0 | IA | 4.77 |  | 640200
A in MTEP20 | West | ITCM | 18847 | 25314 | SUB | 2021-12-31 | Big Cedar | Substation |  | 345 | 161 |  | Build a new 345 kV 3 row breaker and 1/2 "Big Cedar" substation capable of 7 rows for future expansion and two new 345/161 kV transformers, and 161 kV bus. | IA |  |  | 50042797
A in MTEP20 | West | ITCM | 18847 | 25328 | LN | 2021-12-31 | Fairfax | Oakridge | 1 | 69 | 69 |  | IPL has also requested that the existing 69 kV double circuit line be relocated as part of this project. The Beverly – Fairfax #2 and Fairfax – Oakridge 69 kV line will be moved to follow the railroad tracks up to Edgewood Rd, then follow Edgewood Rd to meet up with the existing line route. | IA |  |  | 846977
A in MTEP20 | West | ITCM | 18847 | 25327 | LN | 2021-12-31 | Beverly | Fairfax | 2 | 69 | 69 |  | IPL has also requested that the existing 69 kV double circuit line be relocated as part of this project. The Beverly – Fairfax #2 and Fairfax – Oakridge 69 kV line will be moved to follow the railroad tracks up to Edgewood Rd, then follow Edgewood Rd to meet up with the existing line route. | IA |  |  | 846977
A in MTEP20 | West | ITCM | 18847 | 25326 | SUB | 2021-12-31 | New Customer Sub #2 | Substation |  | 161 | 161 |  | Build new 161 kV ring bus sub for new customer load connection. | IA |  |  | 7354564
A in MTEP20 | West | ITCM | 18847 | 25325 | SUB | 2021-12-31 | New Customer Sub #1 | Substation |  | 161 | 161 |  | Build new 161 kV ring bus sub for new customer load connection. | IA |  |  | 7354564
A in MTEP20 | West | ITCM | 18847 | 25324 | LNug | 2021-12-31 | Big Cedar | New customer substations |  | 161 | 161 |  | Build phase 1 underground lines from Big Cedar to new customer substations. | IA |  |  | 19927364
A in MTEP20 | West | ITCM | 18847 | 25323 | SUB | 2021-12-31 | Morgan Valley | Substation |  | 345 | 345 |  | Add new terminal at Morgan Valley for 2nd Morgan Valley - Big Cedar line and build out Morgan Valley to full 4 position breaker and 1/2 configuration. | IA |  |  | 3930658
A in MTEP20 | West | ITCM | 18847 | 25322 | SUB | 2021-12-31 | Big Cedar | Substation |  | 345 | 161 |  | Purchase land for Big Cedar substation. | IA |  |  | 2160000
A in MTEP20 | West | ITCM | 18847 | 25321 | TAP | 2021-12-31 | Morgan Valley | Big Cedar | 2 | 345 | 345 |  | Add the second circuit on existing Beverly - Morgan Valley to create a second Morgan Valley - Big Cedar 345 kV line. | IA |  |  | 5620952
A in MTEP20 | West | ITCM | 18847 | 25320 | TAP | 2021-12-31 | Beverly | Morgan Valley | 1 | 345 | 345 |  | Tap Beverly - Morgan Valley to bring it into the new Big Cedar Substation creating Morgan Valley - Big Cedar #1 and Big Cedar - Beverly 345 kV lines. | IA |  |  | 6542935.2
A in MTEP20 | West | ATC | 18848 | 25315 | LNrb | 2020-09-30 | Blount | East Campus | 6907 | 69 |  |  | Replace damaged HPFF with new XLPE cable | WI |  |  | 9000000
A in MTEP20 | West | ATC | 18849 | 25316 | SUB | 2020-08-01 | Highland SS |  |  | 138 |  |  | Interconnection Facilities | WI |  |  | 230118
A in MTEP20 | East | CETO | 18886 | 25333 | LN | 2022-12-31 | Morrow South | Jaguar | 1 | 138 |  |  | Approximately 3.0 miles of 138 kV line from the new Morrow South 138/46 kV Substation to METC's new Jaguar station. | MI |  | 3 | 1000000
A in MTEP20 | East | CETO | 18886 | 25334 | LN | 2022-12-31 | Morrow South | Jaguar | 2 | 138 |  |  | Approximately 3.0 miles of 138 kV line from the new Morrow South 138/46 kV Substation to METC's new Jaguar station. | MI |  | 3 | 1000000
A in MTEP20 | West | MRES | 18906 | 25342 | CAP | 2021-09-01 | McLeod 230 kV |  |  | 230 |  |  | Switchable 50 MVAR capacitor bank on the McLeod 230 kV bus | MN |  |  | 1600000
A in MTEP20 |  | ATC | 18925 | 25343 | SUB | 2022-04-01 | Jefferson SS |  |  | 138 |  |  | Jefferson SS Upgrades | WI |  |  | 437008
A in MTEP20 | West | ATC | 18925 | 25347 | INT | 2022-04-01 | Jefferson SS |  |  | 138 |  |  | J818 Transmission Interconnection Facilities | WI |  |  | 474237
A in MTEP20 |  | ATC | 18925 | 25346 | LNup | 2022-04-01 | Concord | Cooney | 9042 | 138 |  |  | Concord - Cooney (9042) 138kV, transmission line upgrade | WI |  |  | 3363101
A in MTEP20 |  | ATC | 18925 | 25345 | SUB | 2022-04-01 | Jefferson SS |  |  | 138 |  |  | Jefferson SS Relay and Substation Upgrades | WI |  |  | 633739
A in MTEP20 |  | ATC | 18925 | 25344 | SUB | 2022-04-01 | Crawfish River SS |  |  | 138 |  |  | Crawfish River SS Upgrades | WI |  |  | 124474
A in MTEP20 | South | Entergy-AR | 18946 | 25349 | INT | 2022-06-01 | Kuhn Road 161kV |  |  | 161 |  |  | Point of Interconnection at the existing Kuhn Road 161kV substation. The 161kV bus will be expanded to accommodate a new breaker and disconnect switches. | AR |  |  | 6999000
A in MTEP20 | South | Entergy-AR | 18946 | 25350 | LNrb | 2022-06-01 | Kuhn Road | Ebony |  | 161 |  |  | Rebuild the existing Kuhn Road - Ebony 161kV line to a minimum rating of 229 MVA as detailed in the generator interconnection agreement. | AR | 2 |  | 4161000
A in MTEP20 | West | OTP | 18947 | 25351 | LNrc | 2021-03-01 | Ellendale 230 kV | Oakes 230 kV |  | 230 |  | 822.6 | Reconductor 24 mile 230 kV line with 954 ACSS. | ND | 24 |  | 7673300
A in MTEP20 | West | OTP | 18947 | 25354 | LNup | 2021-03-01 | Forman 230 kV | Hankinson 230 kV |  | 230 |  | 451.2 | Replace Twelve 230 kV Structures for Clearance Mitigations. | ND |  |  | 1415550
A in MTEP20 | West | OTP | 18947 | 25353 | SUBmisc | 2021-03-01 | Forman 230 kV |  |  | 230 |  | 796.7 | Replace Four 230 kV Line Switches in Forman Substation. | ND |  |  | 144400
A in MTEP20 | West | OTP | 18947 | 25352 | LNrc | 2021-03-01 | Oakes 230 kV | Forman 230 kV |  | 230 |  | 822.6 | Reconductor 16 miles of 230 kV line with 954 ACSS. | ND | 16 |  | 7266750
A in MTEP20 | West | ATC | 18985 | 25359 | SUB | 2022-12-23 | East Paris SS |  |  | 345 | 138 |  | East Paris Substation 345kV | WI |  |  | 21916113
A in MTEP20 | West | ATC | 18985 | 25365 | SUBmisc | 2022-12-23 | Elkhorn |  |  | 138 |  |  | Elkhorn SS Grounding System Upgrades | WI |  |  | 223683
A in MTEP20 | West | ATC | 18985 | 25364 | SUBmisc | 2022-12-23 | Berryville SS |  |  | 138 |  |  | Berryville SS Grounding System Upgrade | WI |  |  | 328807
A in MTEP20 | West | ATC | 18985 | 25363 | LNup | 2022-12-23 | Arcaidan | Zion | 2222 | 345 |  |  | 2222/PLPL81 Transmission Line Loop in | WI |  |  | 2057187
A in MTEP20 | West | ATC | 18985 | 25360 | SUB | 2022-12-23 | Paris SS |  |  | 138 |  |  | Paris Substation 138kV | WI |  |  | 999311
A in MTEP20 |  | NIPS | 18986 | 25361 | LNrb | 2023-05-01 | Bosserman | New Carlisle | 1 | 138 |  |  | Bosserman to New Carlisle 138kV Double circuit rebuild | IN | 13 |  | 32000000
A in MTEP20 |  | NIPS | 18986 | 25362 | LNrb | 2023-05-01 | Maple | New Carlisle | 1 | 138 |  |  | Maple to NewCarlisle 138kV Rebuild | IN | 8 |  | 16100000
A in MTEP20 | South | Entergy-AR | 19005 | 25366 | INT | 2022-05-15 | Ritchie 230 |  |  | 230 |  |  | Interconnection for J834 at Ritchie 230kV substation. | AR |  |  | 5511000
A in MTEP20 | Central | AmerenIL | 19045 | 25372 | TEQ | 2021-02-01 | West Washington St |  |  | 138 |  |  | New positions for Diamond Star (Rivian) | IL |  |  | 3800000
A in MTEP20 | Central | AmerenIL | 19045 | 25374 | LINE | 2021-02-01 | West Washington St | Diamond Star | 2 | 138 |  |  | New line to serve Rivian load | IL |  |  | 3200000
A in MTEP20 | Central | AmerenIL | 19045 | 25373 | LINE | 2021-02-01 | West Washington St | Diamond Star | 1 | 138 |  |  | New line to serve Rivian load | IL |  |  | 3100000
A in MTEP20 | South | Entergy-AR | 19065 | 25380 | INT | 2022-05-01 | Ritchie 230kV |  |  | 230 |  |  | A project to provide a point of interconnection for J663 at the Ritchie 230kV substation. | AR |  |  | 6114000
A in MTEP20 | South | Entergy-AR | 19068 | 25381 | INT | 2022-06-01 | Flat Fork 230kV |  |  | 230 |  |  | Project to interconnect the J907 100 MW solar generator | AR |  |  | 3094660
A in MTEP20 | West | ATC | 19145 | 25398 | INT | 2021-09-30 | Tennyson SS |  |  | 138 |  |  | Interconnection Facilities | WI |  |  | 230118
A in MTEP20 | West | ATC | 19145 | 25402 | SUBmisc | 2021-09-30 | Nelson Dewey SS |  |  | 138 |  |  | Remote End Work | WI |  |  | 51516
A in MTEP20 | West | ATC | 19145 | 25401 | SUBmisc | 2021-09-30 | Hillman SS |  |  | 138 |  |  | Remote End work | WI |  |  | 51516
A in MTEP20 | West | ATC | 19145 | 25400 | LNup | 2021-09-30 | Nelson Dewey | Hillman | X-15 | 138 |  |  | X-15 Upgrade | WI |  |  | 718419
A in MTEP20 | West | ATC | 19145 | 25399 | SUB | 2021-09-30 | Tennyson |  |  | 138 |  |  | Network Upgrades | WI |  |  | 4557241
A in MTEP20 | West | ATC | 19146 | 25403 | SUB | 2022-09-30 | North Creek SS |  |  | 138 |  |  | Network Upgrades | WI |  |  | 4279074
A in MTEP20 | West | ATC | 19146 | 25411 | INT | 2022-09-30 | North Creek SS |  |  | 138 |  |  | Interconnection Facilities | WI |  |  | 389728
A in MTEP20 | West | ATC | 19146 | 25410 | LNup | 2022-09-30 | North Lake Geneva Tap | Burlington SS | 6541 | 138 |  |  | Line rerate | WI |  |  | 1232351
A in MTEP20 | West | ATC | 19146 | 25409 | LNup | 2022-09-30 | Elkhorn SS | Bristol (ALTE) | X-81 | 138 |  |  | Line rerate | WI |  |  | 790866
A in MTEP20 | West | ATC | 19146 | 25408 | LNrc | 2022-09-30 | Bass Creek SS | Townline Rd SS | X-95 | 138 |  |  | Reconductor | WI |  |  | 4445862
A in MTEP20 | West | ATC | 19146 | 25407 | SUBmisc | 2022-09-30 | West Darien SS |  |  | 138 |  |  | Grounding Improvements | WI |  |  | 220000
A in MTEP20 | West | ATC | 19146 | 25406 | SUBmisc | 2022-09-30 | Southwest Delevan SS |  |  | 138 |  |  | Grounding Improvements | WI |  |  | 220000
A in MTEP20 | West | ATC | 19146 | 25405 | SUBmisc | 2022-09-30 | Bristol SS |  |  | 138 |  |  | Grounding Improvements | WI |  |  | 162800
A in MTEP20 | West | ATC | 19146 | 25404 | LINE | 2022-09-30 | Rock River | Southwest Delevan | X-79 | 138 |  |  | Sectionalize X-79 | WI |  |  | 832691
A in MTEP20 | West | ATC | 19225 | 25427 | SUB | 2022-09-01 | Lone Rock SS |  |  | 69 |  |  | Lone Rock SS Network Upgrades | WI |  |  | 535365
A in MTEP20 | West | ATC | 19225 | 25431 | SUBmisc | 2022-09-01 | Richland Center SS |  |  | 69 |  |  | Ground grid analysis and mitgation | WI |  |  | 220000
A in MTEP20 | West | ATC | 19225 | 25430 | SUBmisc | 2022-09-01 | Lone Rock SS |  |  | 69 |  |  | Ground grid analysis and mitigation | WI |  |  | 220000
A in MTEP20 | West | ATC | 19225 | 25429 | INT | 2022-09-01 | Lone Rock SS |  |  | 69 |  |  | Interconnection Facilities | WI |  |  | 264286
A in MTEP20 | West | ATC | 19225 | 25428 | LNup | 2022-09-01 | Lone Rock | Spring Green | Y-37 | 69 |  |  | Network Upgrades | WI |  |  | 527749
A in MTEP20 | West | ATC | 19226 | 25432 | SUBmisc | 2021-03-31 | Dodgeville SS |  |  | 69 |  |  | Ground gird analysis and mitigation | WI |  |  | 220000
A in MTEP20 | West | ATC | 19226 | 25433 | SUBmisc | 2021-03-31 | Rock Branch |  |  | 69 |  |  | Ground grid analysis and mitigation | WI |  |  | 220000
A in MTEP20 | West | ATC | 19245 | 25438 | LNup | 2021-03-31 | Elkhorn SS | North Lake Geneva SS | X-55 | 138 |  |  | Line uprate | WI |  |  | 372880
A in MTEP20 | West | ATC | 19246 | 25439 | SUBmisc | 2021-03-31 | Eden SS |  |  | 138 |  |  | Grounding Improvements | WI |  |  | 794591
A in MTEP20 |  | ATC | 19246 | 25966 | SUBmisc | 2021-03-31 | Hill Valley SS |  |  | 138 |  |  | Grounding Improvements | WI |  |  | 611927
A in MTEP20 | West | ATC | 19247 | 25440 | SUBmisc | 2021-03-01 | North Monroe SS |  |  | 138 |  |  | Grounding Improvements | WI |  |  | 199855
A in MTEP20 | West | ATC | 19248 | 25441 | SUB | 2021-03-01 | Hillman SS |  |  | 138 |  |  | Grounding Improvements | WI |  |  | 181784
A in MTEP20 |  | ATC | 19265 | 25442 | SUBmisc | 2022-09-30 | Paris SS |  |  | 138 |  |  | Grounding Upgrades | WI |  |  | 380402
A in MTEP20 | West | ATC | 19265 | 25444 | INT | 2022-09-30 | Paris SS |  |  | 138 |  |  | Interconnection Facilities | WI |  |  | 535149
A in MTEP20 |  | ATC | 19265 | 25443 | SUB | 2022-09-30 | Paris SS |  |  | 138 |  |  | Substation Upgrades | WI |  |  | 1438289
A in MTEP20 | West | ATC | 19267 | 25448 | SUBmisc | 2021-03-31 | Nelson Dewey SS |  |  | 138 |  |  | Grounding Improvements | WI |  |  | 537753
A in MTEP20 |  | ATC | 19268 | 25449 | SUBmisc | 2021-12-31 | Darlington SS |  |  | 138 |  |  | Grounding Improvements | WI |  |  | 202295
A in MTEP20 |  | ATC | 19268 | 25453 | SUB | 2021-12-31 | Rock River SS |  |  | 138 |  |  | Replacing switch 559-D and replacing bus | WI |  |  | 182621
A in MTEP20 |  | ATC | 19268 | 25452 | SUB | 2021-12-31 | Hillman SS |  |  | 138 |  |  | Replace the 138/69kV transformer with ATC standard 100 MVA autotransformer | WI |  |  | 3132719
A in MTEP20 | West | ATC | 19268 | 25451 | LNup | 2021-12-31 | North Monroe | Bass Creek | X-12 | 138 |  |  | Line upgrade | WI |  |  | 402454
A in MTEP20 |  | ATC | 19268 | 25450 | SUBmisc | 2021-12-31 | Falcon SS |  |  | 138 |  |  | Grounding Improvements | WI |  |  | 147624
A in MTEP20 |  | ATC | 19269 | 25454 | SUBmisc | 2021-03-31 | Spring Green SS |  |  | 138 |  |  | Grounding Improvements | WI |  |  | 220000
A in MTEP20 | West | ATC | 19269 | 25455 | LNup | 2021-03-31 | Eden SS | Highland SS | X-147 | 138 |  |  | Rerating of the X-147 | WI |  |  | 695243
A in MTEP20 | South | Entergy-MS | 19285 | 25456 | SUB | 2021-07-01 | New 230 kV Switching Station |  |  | 230 |  |  | Terminal equipment upgrades required to facilitate POI for generation interconnection customer J866. | MS |  |  | 2502660
A in MTEP20 | South | Entergy-MS | 19286 | 25457 | SUB | 2022-03-01 | Cotton Blossom |  |  | 230 |  |  | This project will construct a new 230 kV switching station cut into the Canton South - Yandell Road line. | MS |  |  | 11367000
A in MTEP20 | South | Entergy-MS | 19287 | 25458 | SUB | 2023-06-01 | Webb |  |  | 115 |  |  | This project will expand the 115 kV Webb substation to facilitate the interconnection of generation interconnection project J908. | MS |  |  | 9417000
A in MTEP20 | West | XEL | 19406 | 25473 | CAP | 2020-12-01 | Chisago |  |  | 34.5 |  |  | Retiring failed 34.5kV capacitor banks at Chisago TR9 and TR10 tertiaries. | MN |  |  | 156000
A in MTEP20 | South | AXLA | 19408 | 25477 | LNrc | 2021-06-01 | Sterkx | Willow Glen | 1 | 138 |  |  | Reconductor. | LA
A in MTEP20 | West | MDU | 19485 | 25485 | LNup | 2020-06-22 | Big Stone | Browns Valley | 1 | 230 |  |  | Replace structures to increase capacity for J488/J493/J526 GI's. | SD |  |  | 350000
A in MTEP20 | East | ITCT | 19526 | 25501 | SUB | 2022-12-31 | Stephens |  |  | 120 |  |  | Install the GP breaker between Bus 105 and 106 at the Stephens 120 kV station including the associated GQ disconnect, and replacement of GO disconnect | MI |  |  | 786389
A in MTEP20 | East | METC | 19545 | 25505 | LN | 2025-06-01 | Chopin | Northridge | 1 | 138 |  |  | Cut Chopin – Northridge 138kV (formerly Cobb-Four Mile 138kV) into Meyer. Construct two 138kV circuits (~ 2 miles, new ROW on new double circuit structures) to cut in the Chopin – Northridge 138kV line into Meyer 138kV. | MI |  |  | 4000000
A in MTEP20 |  | METC | 19545 | 25510 | LNup | 2025-06-01 | Meyer | Tallmadge | 2 | 138 |  |  | Remediate sag limit Meyer – Tallmadge #2 138kV circuit to conductor limit | MI |  |  | 1100000
A in MTEP20 |  | METC | 19545 | 25509 | LNup | 2025-06-01 | Meyer | Northridge |  | 138 |  |  | Remediate sag limit on the Meyer – Northridge 138kV section to 294 MVA (1228 Amps) of SE rating | MI |  |  | 360000
A in MTEP20 |  | METC | 19545 | 25508 | LNup | 2025-06-01 | Meyer | White Road |  | 138 |  |  | Remediate sag limit on the Meyer – White Road Jct. 138kV section to 222 MVA (927 Amps) of SE rating | MI |  |  | 900000
A in MTEP20 |  | METC | 19545 | 25507 | LNup | 2025-06-01 | Chopin | White Road |  | 138 |  |  | Remediate sag limit on the Chopin – White Road Jct. 138kV section to 218 MVA (911 Amps) of SE rating | MI |  |  | 180000
A in MTEP20 |  | METC | 19545 | 25506 | SUB | 2025-06-01 | Meyer |  |  | 138 |  |  | Install (3) new 138kV breaker and associated disconnect switches at Meyer to facilitate new lines cutting into Meyer | MI |  |  | 2000000
A in MTEP20 | East | ITCT | 19565 | 25511 | TEQ | 2024-06-01 | Trenton Channel |  |  | 120 |  |  | Upgrade station equipment at Trenton Channel 120 kV position HH. | MI |  |  | 335000
A in MTEP20 | East | ITCT | 19607 | 25520 | TEQ | 2024-06-01 | Navarre |  |  | 230 |  |  | Upgrade station equipment at Navarre 230 kV | MI |  |  | 85000
A in MTEP20 | East | ITCT | 19607 | 25521 | LNup | 2024-06-01 | Brownstown | Navarre | 2 | 230 |  |  | Remediate the sag on the Brownstown - Navarre #2 230 kV circuit up to the conductor limit. | MI |  |  | 985000
A in MTEP20 | West | MEC | 19646 | 25525 | LNup | 2021-12-31 | Franklin 161 kV | Wall Lake 161 kV | 1 | 161 |  |  | Line structure replacements to increase the line ratings. | IA |  |  | 125000
A in MTEP20 | South | Entergy-TX | 19665 | 25527 | LN | 2025-06-01 | Deer | Indian (or to the new switching station) |  | 138 |  |  | Build ~16 miles of new 138 kV transmission line from Deer substation to Indian substation (or to the new switching station). The final length of the line is contingent on the solution to construct. | TX |  |  | 28860000
A in MTEP20 |  | Entergy-TX | 19665 | 25530 | SUB | 2025-06-01 | Gulf Livingston |  |  | 138 |  |  | Install transmission upgrades at Gulf Livingston substation - install a new CCVT, transmission relay panel, and conduit/cable. | TX |  |  | 320000
A in MTEP20 |  | Entergy-TX | 19665 | 25529 | SUB | 2025-06-01 | Deer |  |  | 138 |  |  | Install transmission upgrades at Deer substation - Install a new 138kV breaker, CCVT, and 138kV Disconnect switches. | TX |  |  | 500000
A in MTEP20 |  | Entergy-TX | 19665 | 25528 | SwSta | 2025-06-01 | Indian |  |  | 138 |  |  | Build a new 3 breaker ring bus switching station (cut into existing Indian to Gulf Livingston transmission line) approximately 1 mile to the west of Indian Substation. | TX |  |  | 3660000
A in MTEP20 | West | OTP | 19685 | 25539 | TX | 2021-12-31 | Hoot Lake 115 |  |  | 115 | 41.6 | 56 | New 115/41.6/34.5 kV transformer with LTC | MN |  |  | 950000
A in MTEP20 |  | Entergy-AR | 19725 | 25543 | RLY | 2020-10-10 | San Souci 500kV |  |  | 500 |  |  | Review and Update relay settings | AR |  |  | 275000
A in MTEP20 |  | Entergy-AR | 19725 | 25545 | RLY | 2020-10-10 | Driver 500kV |  |  | 500 |  |  | Review and Update relay settings | AR
A in MTEP20 |  | Entergy-AR | 19725 | 25544 | RLY | 2020-10-10 | Dell 500kV |  |  | 500 |  |  | Review and update relay settings | AR
A in MTEP20 |  | Entergy-AR | 19726 | 25546 | INT | 2023-06-01 | Bob White 161kV |  |  | 161 |  |  | Cut in the new Bob White 161kV switching station for the J1007 solar project | AR |  |  | 2276660
A in MTEP20 |  | Entergy-AR | 19727 | 25547 | INT | 2023-03-01 | Falls 161kV |  |  | 161 |  |  | A new interconnection station and cut in for J1125 GIA. | AR |  |  | 2870660
A in MTEP20 |  | Entergy-AR | 19728 | 25548 | INT | 2022-09-01 | Driver 230kV |  |  | 230 |  |  | Interconnection for the J1155 GIA solar project. | AR |  |  | 2949000
A in MTEP20 |  | ATC | 19729 | 25549 | SUB | 2023-11-30 | Superior SS |  |  | 345 |  |  | Network Upgrades | WI |  |  | 15621555
A in MTEP20 |  | ATC | 19729 | 25555 | SUB | 2023-11-30 | Superior SS |  |  | 345 |  |  | Interconnection Facilities | WI |  |  | 1157933
A in MTEP20 |  | ATC | 19729 | 25554 | SUBmisc | 2023-11-30 | Arrowhead SS |  |  | 345 | 230 |  | Grounding Improvements | WI |  |  | 1291386
A in MTEP20 |  | ATC | 19729 | 25553 | SUBmisc | 2023-11-30 | Stone Lake SS |  |  | 345 |  |  | Grounding Improvements | WI |  |  | 419936
A in MTEP20 |  | ATC | 19729 | 25552 | SUBmisc | 2023-11-30 | Arrowhead SS |  |  | 345 | 230 |  | Arrowhead SS Relay Upgrades | WI |  |  | 535063
A in MTEP20 |  | ATC | 19729 | 25551 | SUBmisc | 2023-11-30 | Stone Lake SS |  |  | 345 |  |  | Stone Lake SS Relay Upgrades | WI |  |  | 423319
A in MTEP20 |  | ATC | 19729 | 25550 | LNup | 2023-11-30 | Arrowhead SS | Stone Lake SS | 651 | 345 |  |  | Line 651/W25 Loop into Superior SS | WI |  |  | 1796413
A in MTEP20 |  | Entergy-AR | 19767 | 25563 | INT | 2023-05-01 | Heth 500kV |  |  | 500 |  |  | New 500kV interconnection substation to interconnect J1060 450 MW solar facility. | AR |  |  | 38044000
A in MTEP20 |  | Entergy-MS | 19785 | 25565 | INT | 2022-06-30 | Twinkletown 230 kV |  |  | 230 |  |  | J962 interconnection to existing Twinkletown 230 kV substation. | MS
Note on P1: Upgraded or on existing rights of way