## Projects MTEP22
Target Appendix | App ABC | Planning Region | Geographic Location by TO Member System | PrjId | Prj_Rec_Date | Owner_PrjID | Project Name | Project Description | State1 | State2 | Need Date | System Need | Alternatives | Comments | Submitting Comp. | Board Approved | Allocation Type per FF | Share Status | Other Type | Expected ISD (Min) | Expected ISD (Max) | Max kV | Min kV | Min of Plan Status | Estimated Cost
A in MTEP22 | B | West | ATC | 16766 | 2021-09-15 |  | Small Capital Project and Asset Renewal Program 2023 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2023. | WI,MI | WI,MI | 2026-06-30 | Asset Renewal or Reliability |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2026-06-30 | 2026-06-30 | 345 | 69 | Proposed | 34925540
A in MTEP22 | B | West | ATC | 16767 | 2022-09-02 |  | Communications Reliability Program 2023 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2023. | WI,MI | WI,MI | 2026-06-30 | other, increased reliability |  |  | American Transmission Co. LLC |  | Other |  | Other Local Needs | 2026-06-30 | 2026-06-30 | 0 | 0 | Proposed | 19593713
A in MTEP22 | B | West | ATC | 16768 | 2021-09-15 |  | Line Clearance Mitigation Program 2023 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2023. | WI,MI | WI,MI | 2026-06-30 | Line Clearance |  |  | American Transmission Co. LLC |  | Other |  | Reliability | 2026-06-30 | 2026-06-30 | 345 | 69 | Proposed | 3935020
A in MTEP22 | B | West | ATC | 16769 | 2021-09-15 |  | Physical Security Program 2023 | Physical Security projects typically have shorter project life cycles. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2023. | WI,MI | WI,MI | 2025-01-01 | Physical Security |  |  | American Transmission Co. LLC |  | Other |  | Other Local Needs | 2025-01-01 | 2025-01-01 | 345 | 69 | Proposed | 1859619
A in MTEP22 | B | West | ATC | 16770 | 2021-09-15 |  | Load Interconnection Program 2023 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2023. | WI,MI | WI,MI | 2026-06-30 | Load Interconnection - Coordination with LDC |  |  | American Transmission Co. LLC |  | Other |  | Load Growth | 2026-06-30 | 2026-06-30 | 345 | 69 | Proposed | 18045914
A in MTEP22 | B | West | ATC | 18046 | 2021-09-15 |  | Darlington – Rock Branch, (Y-109), 69kV, Rebuild & OPGW | T-Line Scope o Rebuild approximatley 14 miles of the Y-109 line from Darlington - Rock Branch o Install new conductor IT/Communications o Install fiber and terminate at substations Substation Scope o Fiber terminations at remote ends. o Asset Renewal of substation equipment: -Rock Branch: Replace disconnect switches, jumpers, strain bus and (1) breaker. -Darlington: Replace jumpers and strain bus section. | WI | WI | 2025-12-31 | Asset Renewal - Line Rebuild |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 69 | 0 | Proposed | 16700000
A in MTEP22 | B | West | ATC | 18047 | 2021-09-15 |  | South Beaver Dam - Hubbard, (Y-134), 69kV Rebuild & OPGW | T-Line Scope to replace: • South Beaver Dam SS to Str 230: (~13.2 miles) • Str 230 to Hubbard: (~3.3miles) • Install new conductor and install new OPGW fiber Substation Scope • South Beaver Dam: replace jumpers and 600A switches, fiber terminations • Horicon: replace existing 336 jumpers, fiber terminations. • Hubbard: Fiber terminations, no other work planned. | WI | WI | 2026-12-31 | Asset Renewal - Line Rebuild |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2026-12-31 | 2026-12-31 | 69 | 0 | Proposed | 20100000
A in MTEP22 | B | West | ATC | 18049 | 2022-08-23 |  | Portage St - 3 Mile 69 kV (6901/ESE_6902), Re-insulate & Underground Fiber | 9 mile SW STA – Portage (6901/6902), 69kV, Re-insulate | MI | MI | 2025-12-01 | Asset Renewal - Re-insulation |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2025-12-01 | 2025-12-01 | 69 | 0 | Proposed | 5400000
A in MTEP22 | C | West | ATC | 19525 | 2022-01-18 | PR08542 | Saratoga SS - Control House and Breaker Asset Renewal | • Replace control building and contents • Replace 69kV oil breakers • Replace 2 CCVT’s • Install normally-open GOAB line switch outside the fence to enable the connection of radial lines Y-301 and Y-302 • Retire inoperable 922-A and 923-A breaker bypass switches which will no longer be required with the installation of the new GOAB • Reconductor 138kV Bus 2 to match the higher capacity X-43 line rating • Install Dual batteries to meet future TPL-002-2 standards | WI | WI | 2025-12-01 | Asset Renewal - Substation |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2025-12-01 | 2025-12-01 | 138 | 69 | Proposed | 8200000
A in MTEP22 | C | West | ATC | 19962 | 2021-09-15 | PR08804, F5957 | Nelson Dewey - Bloomington (Y-184), 69kV, rebuild & OPGW | Rebuild and install OPGW on approximately 15 miles on Y-184 from Nelson Dewey substation to Bloomington substation. Like for like wood pole replacement with wood pecker mesh where necessary. | WI | WI | 2025-12-31 | Asset Renewal - Line Rebuild |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 69 | 0 | Proposed | 16300000
A in MTEP22 | C | West | ATC | 19966 | 2022-08-24 |  | Munising Area Reactive Power Project | Install one +/- 10 MVA, 69-kV STATCOM (Static Synchronous Compensator) at Munising substation | MI | MI | 2025-12-31 | Reliability |  |  | American Transmission Co. LLC |  | BRP |  |  | 2025-12-31 | 2025-12-31 | 138 | 0 | Proposed | 10000000
A in MTEP22 | C | West | ATC | 20805 | 2022-01-18 |  | Rock County Reliability Project | To address the limited connections, ATC is proposing to develop 345-138 kV connections at Kittyhawk. The specific scope is likely to be: •add two 500-MVA, 345-138 kV transformers at the Kitty Hawk substation •add a 138 kV line between the Kitty Hawk and Town Line Road substations •loop into Kittyhawk existing Paddock-Town Line and Town Line-Bass Creek 138 kV lines •uprate Rock River-Marine 138 kV line •increase ground grid fault capability at several nearby substations. | WI | WI | 2024-12-31 | Reliability A number of factors drive the need for this project resulting in a variety of TPL-001 Planning Event limitations. While many might be addressed by redispatching 345 and 138 kV generation, the future availability of the 138 kV generation is very uncertain. Also, new 345 and 138 generation additions to parts of the system that aggravate the limitations will make it increasingly difficult to find enough generation to redispatch. In addition, there is long-lead time equipment at the Paddock substation that further aggravates the limitations. In 2020 actual system events highlighted this need and make it a near and long term need. All of this points to the need for an additional 345-138 kV source for the Janesville area. The proposed project is at least one alternative to address these needs. |  |  | American Transmission Co. LLC |  | BRP |  |  | 2024-12-21 | 2024-12-31 | 345 | 69 | Proposed | 49721000
A in MTEP22 | C | West | ATC | 21286 | 2022-05-23 |  | Rocky Run SS Power Transformer Replacement | Replace T1, a 1968 vintage 345/115 kV, 150 MVA power transformer with a 345/115kV, 500 MVA system spare. | WI | WI | 2023-12-31 | Reliability/Asset Renewal - Substation |  |  | American Transmission Co. LLC |  | BRP |  |  | 2023-12-31 | 2023-12-31 | 345 | 115 | Proposed | 5408000
A in MTEP22 | C | West | ATC | 21345 | 2021-09-13 |  | National - Presque Isle SW YD 138 kV (446), Re-insulate & OPGW | - Reinsulate ~50% of structures on the line with like for like porcelain bells. - Replacement of structures (~15% based on ground inspection) for wood pecker damage - Install OPGW | MI | MI | 2025-12-25 | Asset Renewal - Transmission Line |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 138 | 0 | Proposed | 8300000
A in MTEP22 | C | West | ATC | 21346 | 2021-09-13 |  | Ontonagon - Victoria Hy 69 kV (Ontonagon69 69kV), Re-insulate | -Reinsulate ~65% of structures on the line with like for like porcelain bells. - Replacement of structures (~5% based on ground inspection) for wood pecker damage | MI | MI | 2024-12-31 | Asset Renewal - Transmission Line |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 69 | 0 | Proposed | 4750000
A in MTEP22 | C | West | ATC | 21347 | 2021-09-13 |  | Huiskamp - Ruskin 69 kV (6937), Partial Rebuild | Replace 23 legacy steel lattice towers with 23 new structures. | MI | MI | 2025-06-30 | Asset Renewal - Transmission Line |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2025-06-30 | 2025-06-30 | 69 | 0 | Proposed | 7900000
A in MTEP22 | C | West | ATC | 21348 | 2022-01-19 |  | Tower Dr - Pulliam 69 kV (P-16/R-70), Partial Rebuild | Reroute approximately .65 miles of double circuit 69 kV transmission line on steel lattice towers due to condition and performance from ice damage including removal of 10 legacy steel lattice towers with replacement with 7 double circuit steel poles and approximately .65 miles of double circuit conductor and replace with T2 4/0 conductor. | WI | WI | 2024-04-01 | Asset Renewal - Transmission Line |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2024-04-01 | 2024-04-01 | 69 | 0 | Proposed | 4100000
A in MTEP22 | C | West | ATC | 21627 | 2021-09-13 |  | North Lake SS, Power Transformer Asset Renewal | Replace TG2, a 1971 vintage 138/69 kV 47 MVA power transformer with a new 138/69 kV 60 MVA replacement. | MI | MI | 2025-12-31 | Asset Renewal - Substation |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 138 | 69 | Proposed | 4221065
A in MTEP22 | C | West | ATC | 21628 | 2021-09-13 |  | Rockdale and Christiana SS - Control House and Relay Asset Renewal | • Replace Rockdale 138kV control building and contents, reusing three bus differential panels installed in 2011 as appropriate. • Replace X-65 and X-66 line relay panels at Christiana SS and coordinate with Rockdale work. • Install Dual batteries to meet future TPL-002-2 standards in the Rockdale 138kV building. | WI | WI | 2025-12-31 | Asset Renewal - Substation |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 345 | 138 | Proposed | 5800000
A in MTEP22 | C | West | ATC | 21629 | 2021-09-13 |  | Oak Creek, Racine SS and Remote Ends, Control Buildings and Relaying Asset Renewal | • Replace control building and contents at Racine and Oak Creek 138kV. • Replace 9 138kV oil breakers at Racine, Dewey and Lincoln • Replace 21 138kV Model ACBL, ATA-2A and MK-40 at Dewey and Racine • Install approximately 35 relay panels • Provide room for WEC distribution equipment at Racine, demo existing building | WI | WI | 2025-12-31 | Asset Renewal - Substation |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 345 | 138 | Proposed | 20900000
A in MTEP22 | C | West | ATC | 21648 | 2021-09-21 |  | J1000 Comet SS Network Upgrades and Interconnection Facilities | Interconnection Customer shall install a Solar Generating Facility modeled at 50 MW in Grant County, Wisconsin. | WI | WI | 2023-03-27 | Interconnection |  |  | American Transmission Co. LLC |  | GIP |  |  | 2023-03-27 | 2023-03-27 | 138 | 0 | Proposed | 6693598
A in MTEP22 | C | West | ATC | 21812 | 2022-01-19 |  | J1002 Wautoma SS Network Upgrades and Interconnection Facilities | Interconnection Customer shall install a 99 MW solar facility connecting into the Wautoma SS in Waushara County. | WI | WI | 2023-01-26 | Interconnection |  |  | American Transmission Co. LLC |  | GIP |  |  | 2023-01-26 | 2023-01-26 | 138 | 69 | Proposed | 3246667
A in MTEP22 | C | West | ATC | 21813 | 2022-08-24 |  | J1003 North Beaver Dam SS Network Upgrades and Interconnection Facilities | Interconnection Customer shall install a 50MW solar farm interconnecting at North Beaver Dam SS in Dodge County. | WI | WI | 2023-06-06 | Interconnection |  |  | American Transmission Co. LLC |  | GIP |  |  | 2023-06-06 | 2023-06-06 | 138 | 69 | Proposed | 1031386
A in MTEP22 | C | West | ATC | 21814 | 2022-01-19 |  | J986 J1002 MPFCA | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. -J986 is seeking interconnection service for 149.76MW -J1002 is seeking interconnection service for 99 MW | WI | WI | 2023-12-31 | Interconnection |  |  | American Transmission Co. LLC |  | GIP |  |  | 2023-12-31 | 2023-12-31 | 138 | 69 | Proposed | 7507240
A in MTEP22 | C | West | ATC | 21899 | 2022-01-19 |  | Port Washington – Saukville 138 kV (X-132/X-133) partial rebuild | Full rebuild of 3.5 miles of X-132/X-133 and reconductor only for the remaining 1.4 miles due to newer steel poles -Use ATC standard T2 Dove ACSR 556 conductor -Replace legacy lattice towers, install new OPGW and static line | WI | WI | 2025-06-30 | Reliability |  |  | American Transmission Co. LLC |  | BRP |  |  | 2025-06-30 | 2025-06-30 | 138 | 0 | Proposed | 7000000
A in MTEP22 | C | West | ATC | 21915 | 2022-01-19 |  | Fitzgerald SS – Transformer and Breaker Asset Renewal | • Replace T1, a 1972 vintage 345/138 kV, 336 MVA power transformer with a new 345/138 kV 500 MVA standard three phase transformer • Replace three 138 kV oil circuit breakers with SF6 gas, eliminating all oil breakers at this station. • Replace one 138 kV 1600 A disconnect switch and associated jumpers • Remove bus arresters off bus 4 and install line arresters | WI | WI | 2025-12-31 | Asset Renewal - Substation |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 345 | 138 | Proposed | 7897437
A in MTEP22 | C | West | ATC | 21916 | 2021-09-13 |  | Browntown - South Monroe 69 kV (Y-155), Rebuild | Rebuild approximately 8.3 miles on Y-155 from Browntown substation to South Monroe substation. | WI | WI | 2026-12-31 | Asset Renewal - Transmission Line |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2026-12-31 | 2026-12-31 | 69 | 0 | Proposed | 10300000
A in MTEP22 | C | West | ATC | 21917 | 2022-01-18 |  | West Marinette SS – Transformer and Breaker Asset Renewal | West Marinette SS – Transformer and Breaker Asset Renewal | WI | WI | 2025-12-31 | Asset Renewal - Substation |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 138 | 69 | Proposed | 8962353
A in MTEP22 | C | West | ATC | 21918 | 2022-01-31 |  | Pine River - Mich Limestone Loading Dock 69 kV (ESE_6906), Rebuild | • T-Line rebuild of approximately 25.5 miles with steel poles and reconductor • Construction: o Utilize two winter cycles for constructability | MI | MI | 2027-12-31 | Asset Renewal - Transmission Line |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2027-12-31 | 2027-12-31 | 69 | 0 | Proposed | 31100000
A in MTEP22 | C | West | ATC | 21923 | 2022-01-19 |  | Everett GIS Asset Renewal | -Rebuild the GIS substation in the same location and re-use existing HPFF (High-Pressure-FluidFilled) terminations | WI | WI | 2025-12-31 | Asset Renewal - Substation |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 138 | 0 | Proposed | 16968398
A in MTEP22 | C | West | ATC | 21925 | 2022-01-19 |  | Plymouth #5 - New DIC | Plymouth #5 - New DIC | WI | WI | 2025-09-01 | Load Interconnection |  |  | American Transmission Co. LLC |  | Other |  | Load Growth | 2025-09-01 | 2025-09-01 | 138 | 0 | Proposed | 21500000
A in MTEP22 | C | West | ATC | 21926 | 2022-08-24 |  | Harbor – Russell Terminal 138 kV (893K11), Rebuild | Norwich - Harbor 138kV, (893K11), underground line replacement | WI | WI | 2025-12-31 | Asset Renewal - Substation |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 138 | 0 | Proposed | 37000000
A in MTEP22 | C | West | ATC | 22045 | 2021-11-04 |  | J855 J864 J870 J871 MPFCA | Installation of ground conductor, ground rods and possibly ground wells along the perimeter of the Spring Green substaiton. | WI | WI | 2022-12-31 | Interconnection |  |  | American Transmission Co. LLC |  | GIP |  |  | 2022-12-31 | 2022-12-31 | 138 | 0 | Proposed | 220000
A in MTEP22 | C | West | ATC | 22046 | 2021-11-04 | PR08822 | J1188 Sheepkskin SS Network Upgrades and Interconnection Facilities | Installation of a 50MW solar farm located in Rock County, Wisconsin | WI | WI | 2022-06-01 | Interconnection |  |  | American Transmission Co. LLC |  | GIP |  |  | 2022-04-06 | 2022-05-11 | 138 | 0 | M5_In Service | 1129461
A in MTEP22 | C | West | ATC | 22047 | 2021-11-04 |  | J1154 Crawfish River Solar Network Upgrades | Installation of a 75MW solar farm located in Jefferson County, Wisconsin. | WI | WI | 2023-05-15 | Interconnection |  |  | American Transmission Co. LLC |  | GIP |  |  | 2023-05-15 | 2023-05-15 | 138 | 0 | Proposed | 2343684
A in MTEP22 | C | West | ATC | 22048 | 2021-11-04 |  | J986 J1002 J1003 MPFCA | Ground gird mitigation at Roeder substation in Green Lake County, Wisconsin. | WI | WI | 2023-12-31 | Interconnection |  |  | American Transmission Co. LLC |  | GIP |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | Proposed | 220000
A in MTEP22 | C | West | ATC | 22049 | 2021-11-04 |  | J1101 Kewaunee SS Network Upgrades and Interconnection Facilities | Installation of a 20MW battery storage project at the J886 Generating Facility. | WI | WI | 2023-08-15 | Interconnection |  |  | American Transmission Co. LLC |  | GIP |  |  | 2023-08-15 | 2023-08-15 | 345 | 0 | Proposed | 155000
A in MTEP22 | C | West | ATC | 22085 | 2021-11-04 |  | J1002 J1003 MPFCA | Shared work for ground grid upgrades at North Beaver Dam SS, cost shared jointly between J1002 and J1003. J1002 - 5.54% J1003 - 94.46% | WI | WI | 2023-12-31 | Interconnection |  |  | American Transmission Co. LLC |  | GIP |  |  | 2023-12-31 | 2023-12-31 | 138 | 69 | Proposed | 550000
A in MTEP22 | C | West | ATC | 22105 | 2022-01-19 |  | J1042 North Lake Geneva SS Network Upgrades and Interconnection Facilities | Interconnection Customer shall install a 180MW solar farm interconnecting at North Lake Geneva SS in Walworth County. | WI | WI | 2023-09-15 | Interconnection |  |  | American Transmission Co. LLC |  | GIP |  |  | 2023-09-15 | 2023-09-15 | 138 | 0 | Proposed | 1407357
A in MTEP22 | C | West | ATC | 22145 | 2022-01-19 | PR08781, F6068, F6070 | J1153 Holland SS Network Upgrades and Interconnection Facilities | Interconnection Customer shall install a 150 MW solar farm interconnecting at Holland SS in Sheboygan County. | WI | WI | 2022-06-01 | Interconnection |  |  | American Transmission Co. LLC |  | GIP |  |  | 2022-06-14 | 2022-07-20 | 345 | 138 | M5_In Service | 8112107
A in MTEP22 | C | West | ATC | 22146 | 2022-01-19 | PR08819, F6104, F6105 | J1171 Butternut SS Network Upgrades and Interconnection Facilities | Interconnection Customer shall install a 100 MW solar farm interconnecting at Butternut SS in Dodge County. | WI | WI | 2023-12-31 | Interconnection |  |  | American Transmission Co. LLC |  | GIP |  |  | 2023-01-26 | 2023-01-26 | 345 | 138 | Proposed | 3918722
A in MTEP22 | C | West | ATC | 22225 | 2022-01-19 |  | J1042 J1188 MPFCA | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. -J1042 is seeking interconnection service for 180 MW -J1188 is seeking interconnection service for 50 MW | WI | WI | 2023-11-01 | Interconnection |  |  | American Transmission Co. LLC |  | GIP |  |  | 2023-11-01 | 2023-11-01 | 138 | 0 | Proposed | 4365163
A in MTEP22 | C | West | ATC | 22986 | 2022-08-03 |  | Vinburn Substation 69 kV Capacitor Addition | Install a 69 kV capacitor bank configuration and associated automatic control features at Vinburn SS. | WI | WI | 2024-12-31 | Other - Local Needs |  |  | American Transmission Co. LLC |  | BRP |  | Reliability | 2024-12-31 | 2024-12-31 | 69 | 0 | Proposed | 3620000
A in MTEP22 | C | West | ATC | 22987 | 2022-05-23 | PR08815, F6122 | Northview SS, DIC, New Substation | *ATC to install a new 138 kV circuit on new ROW (~0.6 miles) to the new substation. *ATC to install two manual load break switches and one manual disconnect switch at the new tap point on line X-107 and 10 new structures and 8 foundations are planned. | WI | WI | 2023-06-01 | Other - Load Interconnection |  |  | American Transmission Co. LLC |  | Other |  | Load Growth | 2023-06-01 | 2023-06-01 | 138 | 0 | Proposed | 3220000
A in MTEP22 | C | West | ATC | 22988 | 2022-05-23 |  | Gaston Road SS, DIC, Additional Transformer | New DIC, additional transformer | WI | WI | 2024-12-31 | Load Interconnection |  |  | American Transmission Co. LLC |  | Other |  | Load Growth | 2024-12-31 | 2024-12-31 | 69 | 0 | Proposed | 3000000
A in MTEP22 | C | West | ATC | 22989 | 2022-05-23 |  | Columbus SS, DIC, Transformer Replacement | Columbus SS, new DIC, transformer replacement | WI | WI | 2024-06-01 | Load Interconnection |  |  | American Transmission Co. LLC |  | Other |  | Load Growth | 2024-06-01 | 2024-06-01 | 69 | 0 | Proposed | 8782156
A in MTEP22 | C | West | ATC | 23007 | 2022-05-23 |  | Cambria SS, DIC, New Substation | Distribution Interconnection, new substation | WI | WI | 2024-12-31 | Load Interconnection |  |  | American Transmission Co. LLC |  | Other |  | Load Growth | 2024-12-31 | 2024-12-31 | 69 | 0 | Proposed | 3000000
A in MTEP22 | C | West | ATC | 23008 | 2022-05-23 |  | WisDOT I-94 Stadium Group of Projects | WisDOT Road Move: ATC’s 138kV lines and the Park Hill substation have been identified as impacted by the roadway construction in all WisDOT alternatives and will require relocation between the end of Calvary Cemetery and the 28th Street Substation to maintain the transmission network and distribution interconnections. Final transmission line routing and substation site selection to be determined through project investigations and coordination. Asset Renewal Rebuild of Structures 4145-4149: Install structures, OPGW/static, and new conductors. Communications: Install fiber communications between 96th Street Substation to structure 4145 and from the new substation location for the WisDOT road move to Valley Substation. | WI | WI | 2026-12-31 | Relocation / Age, Condition and Performance |  |  | American Transmission Co. LLC |  | Other |  | Age and Condition | 2026-12-31 | 2026-12-31 | 138 | 0 | Proposed | 63700000
A in MTEP22 | C | West | ATC | 23520 | 2022-08-26 |  | Johnstown SS, DIC, New Substation | DIC, New Substation | WI | WI | 2024-05-01 | Other - Load Interconnection |  |  | American Transmission Co. LLC |  | Other |  | Load Growth | 2024-05-01 | 2024-05-01 | 69 | 0 | Proposed | 3000000
A in MTEP22 | C | West | ATC | 23531 | 2022-08-26 |  | Cottonwood - Summit Underground Fiber | This project will establish a fiber link between the Cottonwood to Summit substations, which will enhance communications resiliency by interconnecting into ATC’s larger substation fiber network infrastructure at Summit. | WI | WI | 2024-12-31 | Other - Communication |  |  | American Transmission Co. LLC |  | Other |  | Other Local Needs | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 3156228
A in MTEP22 | B | Central | AmerenIL | 20905 | 2021-09-17 | TP1442 | New Mulligan Solar (J1102) at Fogarty | Provide interconnection facilities for J1102 70 MW solar farm to connect at Fogarty. Reroute HOWL-FGTY-1417 to position H4 and install metering on position H2 for the customer to connect at. | IL | IL | 2021-12-15 | This project provides an interconnection point for J1102 to connect at to supply power they generate to MISO customers. |  |  | Ameren Services Company |  | GIP |  |  | 2021-12-01 | 2021-12-01 | 138 | 0 | M5_In Service | 500000
A in MTEP22 | B | Central | AmerenIL | 21005 | 2021-10-14 | TP1450 | New Ina 138 kV line breaker | Add a line breaker on the Benton NW terminal at Ina. | IL | IL | 2023-06-01 | Increased reliability. Adding this line breaker would eliminate a XFMR outage when there is a line outage on the Benton NW-Ina line. |  |  | Ameren Services Company |  | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 138 | 0 | Planned | 850000
A in MTEP22 | B | Central | AmerenIL | 21306 | 2022-07-15 | TP1453 | New Whitetail 138 kV Substation | Ameren would construct a new 138 kV substation ring bus configuration on the existing Ameren Monument-Macomb West-1646 138 kV line near structure 97. PPI would construct a 138 kV line to connect their Golden 138/69 kV step down station. This is in support of PPI Interconnection. | IL | IL | 2024-12-01 | Customer interconnection |  |  | Ameren Services Company |  | Other |  | Load Growth | 2024-12-01 | 2024-12-01 | 138 | 0 | Planned | 8000000
A in MTEP22 | B | Central | AmerenIL | 21326 | 2021-09-17 | TP1407 | New Duff 138 kV Substation | 3-position initial, 4 ultimate ringbus on the Ipava-Meredosia E-1568 138 kV line for PPI Indian Creek 138/69kV substation. This is in support of a PPI Interconnection. | IL | IL | 2023-12-01 | Customer interconnection |  |  | Ameren Services Company |  | Other |  | Load Growth | 2023-12-01 | 2023-12-01 | 138 | 0 | Planned | 8000000
A in MTEP22 | B | Central | AmerenIL | 21365 | 2021-10-14 | TP1448 | New Puro 138 kV Substation POI (J1453) | J1453 Moraine Sands Wind generator 188.3 MW Interconnection: Install Puro ring bus on Havana-Shockey 138 kV line | IL | IL | 2023-06-01 | Generator interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2023-06-01 | 2023-06-01 | 138 | 0 | Planned | 7200000
A in MTEP22 | B | Central | AmerenIL | 21385 | 2021-09-24 | TP5004 | Rebuild Austin-Taylorville South 138 kV line (1545) | Rebuild Austin-Taylorville South 138 kV line (1545) | IL | IL | 2023-12-01 | Aging infrastructure. Initial project to replace shield wire was changed to total rebuild due to condition of structures. |  |  | Ameren Services Company |  | Other |  | Age and Condition | 2023-12-01 | 2023-12-01 | 138 | 0 | Planned | 8900000
A in MTEP22 | B | Central | AmerenIL | 21386 | 2021-09-24 | TP5007 | Rebuild Ruby-Sidney 345 kV line (4560) | Rebuild Ruby-Sidney 345 kV line (4560) | IL | IL | 2023-12-01 | System repair and maintenance. Initial project to replace insulators was changed to partial rebuild due to condition of structures. |  |  | Ameren Services Company |  | Other |  | Age and Condition | 2023-12-01 | 2023-12-01 | 345 | 0 | Planned | 2200000
A in MTEP22 | B | Central | AmerenIL | 21405 | 2021-09-24 | TP5086 | Rebuild Mattoon East-Charleston NE 138 kV line | Rebuild this line due to the condition of the structures, will add OPGW as part of this. This is the Mattoon East to Charleston NE section of the KANW-MTE8-1 line. | IL | IL | 2023-06-01 | Age and condition. Maintains the reliability of the Transmission system. |  |  | Ameren Services Company |  | Other |  | Age and Condition | 2023-06-01 | 2023-06-01 | 138 | 0 | Planned | 3400000
A in MTEP22 | B | Central | AmerenIL | 21406 | 2021-09-24 | TP5106 | Rebuild Sparta Tap 138 kV radial line | Rebuild Sparta Tap on the Tibbs-Sparta-1723 138 kV line due to issues found during inspections. | IL | IL | 2023-12-01 | Age and condition. Maintain the reliability of the Transmission system. |  |  | Ameren Services Company |  | Other |  | Age and Condition | 2023-12-01 | 2023-12-01 | 138 | 0 | Planned | 2300000
A in MTEP22 | B | Central | AmerenIL | 21426 | 2021-09-24 | TP1417 | Reconductor S. Bloomington-W. Washington 138 kV lines (1334 & 1544) | Replace 3.5 miles and 3.48 miles of 477 KCMIL ACSR/T2 30/7 Hen 138 kV line conductor in SBLM-WWSH-1334 and in SBLM-WWSH-1544with a new line conductor having a minimum summer emergency rating of 2000 Amps, respectively. | IL | IL | 2022-12-01 | Customer load |  |  | Ameren Services Company |  | Other |  | Load Growth | 2022-12-01 | 2022-12-01 | 138 | 0 | Planned | 4200000
A in MTEP22 | C | Central | AmerenIL | 21428 | 2022-01-31 | TP1459 | Rebuild Tanner-Xenia 345 kV line | Rebuild the existing Newton-Xenia-1 345 kV line from Xenia-Str. 44. New conductor will be capable of 3000 A and 2 OPGW shield wires will be installed. | IL | IL | 2022-12-15 | Increased reliability. Age and condition. |  |  | Ameren Services Company |  | Other |  | Reliability | 2022-12-15 | 2022-12-15 | 345 | 0 | Planned | 9100000
A in MTEP22 | C | Central | AmerenIL | 21645 | 2022-01-12 | TP1460 | New Prairie Solar (J1139) Interconnection at Sidney 138kV | One 138 kV terminal in the Sidney Substation. The terminal will consist of all necessary terminal equipment to connect the J1139 leadline to the Sidney Substation 138 kV bus. | IL | IL | 2023-06-01 | Generator interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2023-06-01 | 2023-06-01 | 138 | 0 | Planned | 500000
A in MTEP22 | B | Central | AmerenIL | 21646 | 2021-09-24 | TP1461 | Rebuild Sullivan-Casey West 345 kV line | Rebuild the Sullivan-Casey West 345 kV line with conductors capable of 3000 amps Summer Emergency rating and two OPGWs. | IL | IL | 2023-12-01 | Increased reliability. Project upgrades the line to structures that meet Ameren's current loading requirements, hardening the circuit against storms and improving resiliency against cascade failure |  |  | Ameren Services Company |  | Other |  | Reliability | 2023-12-01 | 2023-12-01 | 345 | 0 | Planned | 36100000
A in MTEP22 | C | Central | AmerenIL | 21647 | 2021-09-17 | TP1462 | Rebuild Casey West-Kansas 345 kV line (4525) | Rebuild the Casey West-Kansas 345 kV line (4525) with conductors capable of 3000 amps Summer Emergency rating and two OPGWs. | IL | IL | 2024-12-01 | Project upgrades the line to structures that meet Ameren's current loading requirements, hardening the circuit against storms and improving resiliency against cascade failure |  |  | Ameren Services Company |  | Other |  | Age and Condition | 2024-12-01 | 2024-12-01 | 345 | 0 | Planned | 25200000
A in MTEP22 | B | Central | AmerenIL | 21970 | 2022-01-19 | TP1466 | Reconductor Kinmundy-Tanner 138 kV | Reconductor 27.4 miles Kinmundy-Tanner 138 kV line | IL | IL | 2026-06-01 | Increased reliability to meet LPC |  |  | Ameren Services Company |  | Other |  | Reliability | 2026-06-01 | 2026-06-01 | 138 | 0 | Planned | 10000000
A in MTEP22 | C | Central | AmerenIL | 22325 | 2022-01-12 | TP1473 | New Mogul 345 kV Ring Bus for J1464 | Construct a new 345 kV switching station in Sangamon, Macoupin & Morgan Counties, Illinois to provide a Point of Interconnection for the Generating Facility. The new 345kV Mogul switching station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Austin – Turner 345 kV transmission line and terminate the ends at two of the terminal positions. | IL | IL | 2023-10-31 | Generator interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2023-10-31 | 2023-10-31 | 345 | 0 | Planned | 10300000
A in MTEP22 | C | Central | AmerenIL | 22385 | 2022-01-12 | TP1478 | New Dion 345 kV Ring Bus for J1115 Greenswitch Wind | The Dion switching station will be a ring bus arrangement with three-line terminal positions and provisions for one additional future terminal position. The existing Latham-Oreana 345 kV transmission line will be cut. | IL | IL | 2024-06-01 | Generator Interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2024-06-01 | 2024-06-01 | 345 | 0 | Planned | 10500000
A in MTEP22 | C | Central | AmerenIL | 22405 | 2022-01-12 | TP1479 | Add J991 Monarch Solar at Xenia 345 kV | Add 345 kV terminal in the Xenia switching station for the J991 project. | IL | IL | 2023-06-01 | Generator Interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2023-06-01 | 2023-06-01 | 345 | 0 | Planned | 1000000
A in MTEP22 | C | Central | AmerenIL | 22407 | 2022-01-12 | TP1481 | Add J974 Fulton Wind at MapleRidge 345 kV | Add position to the existing Mapleridge 345 kV switching station for J974 interconnection facilities. | IL | IL | 2023-06-01 | Generator Interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2023-06-01 | 2023-06-01 | 345 | 0 | Planned | 2242000
A in MTEP22 | C | Central | AmerenIL | 22485 | 2022-01-12 | TP1485 | Add J1094 Tilden Solar at Prest 138 kV | Expand and convert the Prest switching station 138 kV bus from a 6-position ring to a 4-leg breaker and a half (BAAH) configuration to add J1094 Tilden Solar | IL | IL | 2024-01-01 | Generator Interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2024-01-01 | 2024-01-01 | 138 | 0 | Planned | 8520000
A in MTEP22 | C | Central | AmerenIL | 22566 | 2022-01-12 | TP1488 | New Morganfield 138 kV Ring Bus for J1096 Eldorado Solar | Construct a new 138 kV switching station in Saline County, Illinois to provide a Point of Interconnection for the Generating Facility. The new Morganfield 138 kV J1096 Interconnection Switching Station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Muddy-Norris City North 138 kV transmission line. | IL | IL | 2024-01-01 | Generator Interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2024-01-01 | 2024-01-01 | 138 | 0 | Planned | 6519000
A in MTEP22 | C | Central | AmerenMO | 18063 | 2022-08-17 | TP1350 | New Mt. Pleasant 345 kV substation | Placeholder | IA | IA | 2025-12-01 | Customer-Driver Request |  |  | Ameren Services Company |  | Other |  | Load Growth | 2025-12-01 | 2025-12-01 | 345 | 0 | Planned | 2600000
A in MTEP22 | B | Central | AmerenMO | 21931 | 2021-09-20 |  | New Crosstown 69/12 kV Substation | Crosstown 69/12kV Substation Build between Park Tap and Altenburg 69kV substation (Citizens project). | MO | MO | 2021-06-01 | Crosstown Substation is needed to help relieve loading on Altenburg, McBride, and Park Substations which are forecast to exceed their OA rating. |  |  | Wabash Valley Power Association, Inc. |  | Other |  | Reliability | 2021-06-01 | 2021-06-01 | 69 | 12 | M5_In Service | 800000
A in MTEP22 | B | Central | AmerenMO | 21948 | 2022-05-18 |  | Upgrade New Bourbon bus tie breaker (B40) | Replace B40 bus tie breaker. | MO | MO | 2022-12-31 | Replace B40 bus tie breaker that had several issues at New Bourbon. Had trouble while they were operating the breaker to put the station back in service after maintenance. |  |  | Wabash Valley Power Association, Inc. |  | Other |  | Age and Condition | 2022-05-31 | 2022-05-31 | 69 | 0 | Planned | 381780
A in MTEP22 | B | Central | AmerenMO | 21949 | 2022-05-18 |  | Rebuild T2B 34.5 kV line | Rebuild 34 kV line that feeds the Mosher B,C,&F plants and the Geneva switching station. This includes most of the switches in the line section. | MO | MO | 2024-03-31 | T2B 34.5 kV line old and in bad shape. |  |  | Wabash Valley Power Association, Inc. |  | Other |  | Age and Condition | 2024-03-31 | 2024-03-31 | 34.5 | 0 | Planned | 4558281
A in MTEP22 | B | Central | AmerenMO | 21967 | 2021-09-20 | TP1464 | New Dillon 138 kV Capacitor Bank (14 Mvar) | Add a 14 Mvar capacitor bank at Dillon with a separate breaker. The existing 28 Mvar bank will be reduced to 14 Mvar. | MO | MO | 2023-06-01 | This will ensure the entire bank isn't outaged for the one P14 event. This project will also reduce the voltage fluctuations caused by the existing 28 Mvar cap bank. |  |  | Ameren Services Company |  | BRP |  |  | 2023-06-01 | 2023-06-01 | 138 | 0 | Planned | 500000
A in MTEP22 | B | Central | AmerenMO | 21971 | 2022-01-26 | TP1467 | Upgrade Callaway 345 kV Substation | Add breakers on the high side of safeguard transformer A and B at Callaway 345 kV substation | MO | MO | 2023-06-01 | Generator stability |  |  | Ameren Services Company |  | BRP |  |  | 2023-06-01 | 2023-06-01 | 345 | 0 | Planned | 3000000
A in MTEP22 | C | Central | AmerenMO | 22365 | 2022-01-12 | TP1477 | New Adna 345 kV Ring Bus for J1107 Lutesville Solar | The Adna switching station will be a ring bus arrangement with three-line terminal positions and provisions for one additional future terminal position. The existing Kelso-Lutesville 345 kV transmission line will be cut. | MO | MO | 2023-11-01 | Generator Interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2023-11-01 | 2023-11-01 | 345 | 0 | Planned | 10837000
A in MTEP22 | C | Central | AmerenMO | 22406 | 2022-01-12 | TP1480 | Add J994 Guthrie Solar at Guthrie 161 kV | Add 161 kV terminal in the Guthrie substation for J994 project. | MO | MO | 2023-06-01 | Generator Interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2023-06-01 | 2023-06-01 | 161 | 0 | Planned | 1658000
A in MTEP22 | C | Central | AmerenMO | 22408 | 2022-01-12 | TP1482 | Add J987 Warren Solar at Montgomery 161 kV | Add 161 kV terminal in the Montgomery substation for the J987 | MO | MO | 2023-06-01 | Generator Interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2023-06-01 | 2023-06-01 | 345 | 161 | Planned | 2060000
A in MTEP22 | C | Central | AmerenMO | 22465 | 2022-01-12 | TP1484 | New Bullion 161 kV Ring Bus for J1087 Kelso Solar | Construct a new 161 kV switching station in Scott County, Missouri to provide a Point of Interconnection for the Generating Facility. The new 161 kV Bullion switching station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Kelso – Miner 161 kV transmission line. | MO | MO | 2024-03-31 | Generator Interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2024-03-31 | 2024-03-31 | 161 | 0 | Planned | 9189000
A in MTEP22 | C | Central | AmerenMO | 22527 | 2022-01-12 | TP1475 | New Harley 161 kV Ring Bus for J1268 Winfield Solar | Build a 161 kV three position ring bus along the Troy-Pike 161 kV transmission line in Lincoln County, Missouri. This is for Winfield Solar J1268. | MO | MO | 2023-06-01 | Generator Interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2023-06-01 | 2023-06-01 | 161 | 0 | Planned | 10652000
A in MTEP22 | C | Central | AmerenMO | 22529 | 2022-01-12 | TP1486 | New Vanduser 161 kV Ring Bus for J1034 Ringer Solar | Construct a new 161 kV switching station in Stoddard County, Missouri to provide a Point of Interconnection for the Generating Facility. The new Vanduser 161 kV J1034 Interconnection Switching Station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Morley – Stoddard 161 kV transmission line | MO | MO | 2024-06-01 | Generator Interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2024-06-01 | 2024-06-01 | 161 | 0 | Planned | 6730000
A in MTEP22 | C | Central | AmerenMO | 22546 | 2022-07-22 | TP1487 | New Rootbeer 345 kV Ring Bus for J976 Split Rail Solar | Construct a new 345 kV switching station in Warren County, Missouri to provide a Point of Interconnection for the Generating Facility. The new Rootbeer 345 kV J976 Interconnection Switching Station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Belleau – Montgomery 345 kV transmission line. | MO | MO | 2024-12-01 | Generator interconnection |  |  | Ameren Services Company |  | GIP |  |  | 2025-12-01 | 2025-12-01 | 345 | 0 | Planned | 10801000
A in MTEP22 | C | Central | AmerenMO | 22786 | 2022-08-29 | TP1492 | New Wildwood 345/138 kV Transformer No 2 | Upgrade 560 MVA TX to a 700 MVA 345/138 kV Transformer | MO | MO | 2024-06-01 | The larger 345/138kV transformer is needed for system reinforcement upon Rush Island Plant Retirement. |  |  | Ameren Services Company |  | GIP |  |  | 2024-06-01 | 2024-06-01 | 345 | 138 | Proposed | 17500000
A in MTEP22 | C | Central | AmerenMO | 22807 | 2022-08-25 | TP1494 | New Overton 161 kV Capacitor Bank | New 67 MVAR Capacitor at Overton 161 kV | MO | MO | 2024-04-01 | The 345 kV Capacitor Bank is needed for system reinforcement upon the Rush Island Plant Retirement. |  |  | Ameren Services Company |  | GIP |  |  | 2024-04-01 | 2024-04-01 | 161 | 0 | Proposed
A in MTEP22 | C | Central | AmerenMO | 22808 | 2022-08-25 | TP1495 | New Rush Island Area Statcoms | Add 250 MVAR Statcom at Bugle, Arnold, Mason and Highway N substations. | MO | MO |  | The Statcom is needed for system reinforcement due to the Rush Island Plant Retirement. |  |  | Ameren Services Company |  | GIP |  |  | 2024-12-01 | 2024-12-01 | 161 | 0 | Proposed | 120000000
A in MTEP22 | C | Central | BREC | 20766 | 2021-09-23 |  | New Easton Rd 69 kV line | Add 1 mile tap line to serve new distribution substation | KY | KY | 2022-02-01 | The distribution cooperative is constructing a new delivery point to serve member load. |  |  | Big Rivers Electric Corporation |  | Other |  | Load Growth | 2022-02-01 | 2022-02-01 | 69 | 0 | Proposed | 500000
A in MTEP22 | C | Central | BREC | 21685 | 2021-09-22 |  | New Pratt Paper Load Addition | Conversion of existing switching structure into a switching station and construction of a 8 mile radial transmission line to serve new industrial load. | KY | KY |  | Conversion of existing switching structure into a switching station and construction of a 8 mile radial transmission line to serve new industrial load. |  |  | Big Rivers Electric Corporation |  | Other |  | Load Growth | 2023-07-01 | 2023-07-01 | 161 | 0 | Proposed | 20200000
A in MTEP22 | C | Central | BREC | 22766 | 2022-08-10 |  | Replace McCracken-Shell Structure | Raise or replace existing line structures to provide necessary ground clearance. | KY | KY | 2022-10-01 | Existing structures are not tall enough to provide needed design clearance. |  |  | Big Rivers Electric Corporation |  | Other |  | Reliability | 2022-10-01 | 2022-10-01 | 69 | 0 | Proposed | 1500000
A in MTEP22 | C | South | CLECO | 20163 | 2021-11-17 |  | Many Area Transmission Expansion | Tap the existing Fisher to Mansfield Compressor 230 kV line 8.3 miles from Fisher. From the Tap point build two new new 2.8 mile 230 kV lines to a new substation (Belmont) tapped into the Pelican to Loring and Loring to Many 138 kV lines. At Belmont substation add a 230/138 kV 300 MVA Auto. | LA | LA | 2025-06-01 | In 2025 a P6 contingency on Many to Fisher 138 kV line followed by a contingency on Carroll to Red River 138 kV line causes an overload greater than 125 % on South Shreveport to Wallace lake 138 kV line. Also voltage violation exist for this contingency. Load shed is the only mitigation for this P6 contingency. With projected industrial load growth in this area this project has been modified to account for the additional load. The original alternative is in the Alternative notes. | Tap the existing Fisher to Mansfield Compressor 230 kV line 5.5 miles from Fisher near the Existing Many 138 kV substation. Build a new 2 mile 138 kV line from this new substation to Many 138 kV substation. At the new substation add a 230/138 kV 300 MVA Auto. | Revising the scope of the project for submittal to Target Appendix A in MTEP22 | Cleco Power LLC |  | BRP |  |  | 2025-06-01 | 2025-06-01 | 230 | 138 | Proposed | 38100000
A in MTEP22 | C | South | CLECO | 22205 | 2022-01-06 |  | Cole Substation | Tap the existing Cooper to Penton 230 kV line 2.4 miles from Cooper and build a new substation (Cole) | LA | LA | 2022-10-15 | This new substation is needed to serve a new industrial customer. |  |  | Cleco Power LLC |  | Other |  | Load Growth | 2023-03-27 | 2023-03-27 | 230 | 0 | Proposed | 18764954
A in MTEP22 | C | South | CLECO | 23327 | 2022-08-24 |  | Marthaville Substation | New load substation tapping the Fisher to Mansfield Compressor 230 kV line | LA | LA | 2023-04-23 | New industrial load |  | This project needs to expedited to meet the customer's in-service date | Cleco Power LLC |  | Other |  | Load Growth | 2023-04-23 | 2023-04-23 | 230 | 0 | Proposed | 15697000
A in MTEP22 | C | South | CLECO | 23328 | 2022-08-24 |  | Vernon Substation | Adding new load substation by tapping the Toledo to Leesville 138 kV line | LA | LA | 2023-04-23 | New industrial load |  | This project needs to be expedited to meet the in-service date of the customer | Cleco Power LLC |  | Other |  | Load Growth | 2023-04-23 | 2023-04-23 | 138 | 0 | Proposed | 13650000
A in MTEP22 | C | West | CMMPA | 21973 | 2021-09-15 |  | Blue Earth Light and Water- Rice Street Transformer Replacement | Blue Earth Light and Water has a Rice Street sub which carries a 10/14 MVA 69/12.47 kV Transformer. The transformer is showing signs of age as it is 28 years old and needs to be replaced because of potential load growth. | MN | MN | 2022-05-02 | The Rice street transformer is showing signs of age which is 28 years old and needs tp be replaced. Rice Street carries almost 60% of BELW load. |  |  | Central Minnesota Municipal Power Agency |  | Other |  | Age and Condition | 2022-05-02 | 2022-05-02 | 69 | 0 | Proposed | 1250000
A in MTEP22 | C | West | CMMPA | 21974 | 2021-09-15 |  | Blue Earth Light and Water- West Sub Transformer Replacement | Blue Earth Light and Water West Sub Transformer replacement. | MN | MN | 2022-05-02 | Blue Earth Light and Water has a West sub which carries a 10/14 MVA 69/12.47 kV Transformer. The transformer is showing signs of age as it is 32 years old and needs to be replaced because of potential load growth. |  |  | Central Minnesota Municipal Power Agency |  | Other |  | Age and Condition | 2022-05-02 | 2022-05-02 | 69 | 0 | Proposed | 1500000
A in MTEP22 | C | West | CMMPA | 21975 | 2022-05-17 |  | Blue Earth Light and Water- New Northeast 69/12.47 kV Sub | Build a new North East 69/12.47kV substation and self-supporting steel pole with 69kV 3-way switch. | MN | MN | 2023-01-16 | Following a PSS/E AC Contingency Calculation (ACCC) analysis of the Blue Earth Light & Water (BELW) transmission system, numerous voltage violations (< 0.93 per unit) were noted on BELW facilities as a result of a few different contingencies. The analysis included various load and generation forecasts, and these violations were noted in several years and seasons. The Rice St. and West 69/12.47kV substations do not have enough capacity to add additional load growth in the city. With a potential 3.5 MW approximately new load scheduled to come online, there is a need to build a new North East 69/12.47kV substation to accommodate load growth, load transfers, support transmission system voltage, and add reliability to the BELW transmission and distribution systems. The new substation would connect to the existing 69kV transmission system via a 3-way switch and would be designed to include room for future In/Out circuit breakers. |  |  | Central Minnesota Municipal Power Agency |  | Other |  | Reliability | 2023-01-16 | 2023-01-16 | 69 | 0 | Proposed | 4100000
A in MTEP22 | C | Central | DEI | 2125 | 2021-11-18 | 802J3045 | Upgrade Centerton 138/69kV Bk 1 | Upgrade/replace existing 75MVA 138/69kV bank with 150MVA bank | IN | IN |  | (N-1) A 69kv line outage from Bloomington to Martinsville S.E. Jct. causes an overload on the Centerton 138/69kv Bank (75MVA nameplate, hot spot 91.1MVA). The 138kv winding is 102% of the emergency or hot spot rating. | 2nd bank | Late submittal for MTEP22 - please manually update | Duke Energy Corporation |  | Other | Not Shared | Reliability | 2024-09-11 | 2024-09-11 | 138 | 69 | Proposed | 4010138
A in MTEP22 | C | Central | DEI | 22185 | 2021-11-18 | M200021 | New J1063 Hardy Hills Solar | J1063 - Hardy Hills Solar | IN | IN |  | J1063 - GIA |  |  | Duke Energy Corporation |  | GIP |  |  | 2023-02-20 | 2023-02-20 | 230 | 0.66 | Under Construction | 3617000
A in MTEP22 | C | Central | DEI | 22206 | 2021-11-18 | M210417 | Replace Dresser 138kV Breaker | Replace (5) over-dutied Dresser CBs: (13869-9, 13869-10, 138B3-1, 138B3-2, 138138) with higher interruption capacity (63 KIAC rating) | IN | IN |  | These CBs were identified in the 2021 short circuit study as being over-dutied during certain fault conditions. This is a NERC TPL 001-4 compliance requirement. | system reconfigurations to reduce fault current are significantly more expensive |  | Duke Energy Corporation |  | BRP |  |  | 2026-03-20 | 2026-03-20 | 138 | 0 | Proposed | 562153
A in MTEP22 | C | Central | DEI | 22207 | 2021-11-18 | M210418 | New WVPA Hendricks Belle Union 138/12kV Distribution Sub | New 138/12 kV - 22.4MVA Belle Union substation for Hendricks Power to be constructed by WVPA. Substation 138kV - 13867 source to be looped through with SCADA controlled switches. | IN | IN |  | WVPA distribution load growth | No alternative studied - WVPA project required to serve load. |  | Duke Energy Corporation |  | Other |  | Load Growth | 2023-12-31 | 2023-12-31 | 138 | 12 | Proposed | 1408403
A in MTEP22 | C | Central | DEI | 22208 | 2021-12-18 | M210521 | Rebuild Bedford to Mitchell Lehigh 138kV - 13822 Line | Bedford to Mitchell Lehigh 138kV - Rebuild 13822 line section with 954ACSR@120C; upgrade 1200A Wave trap at Bedford to 2000A; upgrade 954AL bus at Bedford to 1590AL | IN | IN |  | MTEP21 results show line overload for multiple Cat. P6 pairings; interim operating mitigation to reduce Gibson/Petersburg station gens by 500MWs; if necessary, load shed up to 40MWs from bus 249932 (proposed new load in MTEP19) | short term ratings with operating mitigations - could be delayed by future actual load levels at Mitchell Lehigh (below the currently planned 40MWs) |  | Duke Energy Corporation |  | BRP |  |  | 2027-06-01 | 2027-06-01 | 138 | 0 | Proposed | 17960000
A in MTEP22 | C | Central | DEI | 22209 | 2021-12-18 | M210528 | Upgrade Columbus 13830 Line Terminal | Columbus 13830 line terminal: upgrade 300CU bus to 954AL to increase facility rating to 178MVA (line conductor rating) ; P6 - 13828 + 13829 ckts; Relay loadability ok as-is | IN | IN |  | MTEP21 results show overload of the Columbus 13830 line terminal: P6 - 13828 + 13829 ckts | none considered - minor equipment upgrade |  | Duke Energy Corporation |  | BRP |  |  | 2027-06-01 | 2027-06-01 | 138 | 0 | Proposed | 500000
A in MTEP22 | C | Central | DEI | 22210 | 2021-11-18 | M180035 | Rebuild Collamer Jct to N.Manchester 69kV (6923) Line | Collamer Jct to N.Manchester 6923 (Pt2) Rebuild with 477ACSR@120C | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  | Duke Energy Corporation |  | Other |  | Reliability | 2023-05-19 | 2023-05-19 | 69 | 0 | Proposed | 7300000
A in MTEP22 | C | Central | DEI | 22211 | 2021-11-18 | M180276 | Rebuild and Reconfigure Huntington 138kV Sub | Huntington 138kV Sub rebuild and reconfigure: establish 4-position 138kV ring bus; replace (2)138/69/12 xfmrs with (2)50MVA 138/69 xfmrs and (1)22.4MVA 138/12 xfmr; establish 4-position 69kV ring bus | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  | Duke Energy Corporation |  | Other |  | Reliability | 2024-07-19 | 2024-07-19 | 138 | 69 | Proposed | 28444000
A in MTEP22 | C | Central | DEI | 22212 | 2022-05-04 | M170059 | Rebuild Morgantown to Samaria Jct 69kV Line | Rebuild 6949 Line from Morgantown to Samaria Jct; 3.63 miles; 954ACSR@120C | IN | IN |  | Transmission Planning identified contingency overload due to Load Growth; Contingency: Bloomington 230 to Needmore Jct. 6949 Line Outage | New 69kV lines and / or sources into the area are significantly more expensive. |  | Duke Energy Corporation |  | Other |  | Load Growth | 2023-05-01 | 2023-05-01 | 69 | 0 | Proposed | 2901158
A in MTEP22 | C | Central | DEI | 22213 | 2021-11-30 | M190306 | Replace Dresser 69kV - 6901 Tower | Dresser 69kV - 6901 Tower Replacements - Replace 1.25 miles of steel lattice towers - six total (802-1012 to 802-1007, including the Wabash River crossing) | IN | IN |  | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. | No alternative studied - this project improves reliability and is part of the TDSIC plan approved by IURC. |  | Duke Energy Corporation |  | Other |  | Reliability | 2023-07-28 | 2023-07-28 | 69 | 0 | Proposed | 4780000
A in MTEP22 | C | Central | DEI | 22226 | 2021-12-03 | M210351 | New Wabash River Station 345kV-230kV Substation | Wabash River Station 345kV-230kV Substation: (1) Add Sandford 345kV 3-CB ring bus in the 34513 Cayuga - Sugar Crk line; (2) build 5.5 mile 345kV - 34556 line to Wabash River Station; (3) add 345/230 xfmr(s) at Wabash River Station | IN | IN |  | Past MTEP results have shown multiple line and xfmr overloads for multiple categories of TPL contingencies that have been addressed using short term ratings and operating mitigations that are no longer deemed acceptable for the long term. This project would bring a 345kV source into Wabash River Station that would act as a balancing force to the Dresser 345kV source and dramatically reduce contingency flows through the Terre Haute area's 138kV and 230kV systems. | Incremental existing system upgrades were considered as the baseline. One alternative still under consideration is the use of 2 smaller parallel 345/230 xfmrs. |  | Duke Energy Corporation |  | BRP |  |  | 2026-10-22 | 2026-10-22 | 345 | 230 | Proposed | 50000000
A in MTEP22 | C | Central | DEI | 22227 | 2021-12-18 | M210523 | Staunton 230-138kV Xfmr Addition | Staunton sub: add a third parallel 230/138kV transformer | IN | IN |  | Past MTEP P6 OL of Staunton Bk1 or Bk2 flo 13861 Dresser to Staunton line coupled with the loss of one of the Staunton 230/138 banks - somewhat exacerbated by Wabash River 345/230 project. Interim operating mitigation: open circuit breaker 13801 at Cloverdale (open branch 249708,249731,1). | Incremental existing system upgrades were considered as the baseline: replacing/upgrading both 230/138kV transformers at Staunton |  | Duke Energy Corporation |  | BRP |  |  | 2026-12-31 | 2026-12-31 | 230 | 138 | Proposed | 6000000
A in MTEP22 | C | Central | DEI | 22230 | 2021-12-15 | M210313/M210371 | Upgrade Gibson 34509 Line Terminal | Gibson 345 Switchyard 34509 Line Terminal Upgrades: M210313 - (for Ameren Albion ring bus project) WT / Relays replacement; M210371 - replace (2)345kV CBs, free-standing CTs, and disconnect switches | IN | IN |  | M210313 - required for Ameren Albion ring bus project (100% reimbursable); M210371 - CBs, CTs, and Disconnect Switches identified for replacement by Asset Mgmt based on age and condition | No alternatives considered except continued and increasingly difficult maintenance and operation. |  | Duke Energy Corporation |  | Other |  | Age and Condition | 2023-05-01 | 2023-05-01 | 345 | 0 | Proposed | 2950051
A in MTEP22 | C | Central | DEI | 22245 | 2021-11-18 | M210314 | Improve 23008 Tipton W-Cammack Rd Line | Noblesville to Tipton West 23008 ckt: reinsulate and implement anti-gallop line conductor modifications | IN | IN |  | TDSIC 2.0 - The assets being addressed in this project fall under one or more of the system programs as outlined in the TDSIC Plan filed with and approved by the Indiana Utility Regulatory Commission. This line has been identified by Duke's R&I Planning group as having an unacceptable outage rate due to faulty insulators and galloping issues. | Complete line rebuild is too costly without an associated capacity need. |  | Duke Energy Corporation |  | Other |  | Reliability | 2026-11-30 | 2026-11-30 | 230 | 0 | Proposed | 4716099
A in MTEP22 | C | Central | DEI | 22246 | 2021-11-19 | M200364/M200365/M200367 | New IMPA Frankfort 300W 69/12kV Distribution Substation | IMPA Frankfort 300W 69/12kV Distribution Substation | IN | IN |  | Distribution load growth: wholesale obligation to serve load via IMPA for Frankfort Municipal | None considered by Duke - project is an IMPA proposal |  | Duke Energy Corporation |  | Other |  | Load Growth | 2023-06-01 | 2023-06-01 | 69 | 12 | Proposed | 5018000
A in MTEP22 | C | Central | DEI | 22265 | 2021-11-19 | DEI-2022-4 | Rebuild Purdue NW Tap to Cincinnati St. 138kV - 13820 Line | Rebuild the 13820 line from Purdue NW Tap to Cincinnati St. using 954 ACSR at 120 C | IN | IN |  | This project is being proposed as a replacement for project 20230 with an additional line section added to the scope and increased costs per the latest Eng'g estimates. With the new West Lafayette Airport sub getting placed in-service on the 13820 line between the Purdue Northwest Tap and West Lafayette Purdue subs, when there is a breaker failure that takes out bus 2 at Westwood, the line segments from the Purdue Northwest Tap to West Lafayette Airport to Purdue to Cincinnati St. are loaded to 99.7% or higher per the MTEP21 - 2023 sum peak _AA model. | short term ratings with operating mitigations; Change the 13806 and 13820 line terminals at Westwood, which moves the 13820 line to Bus 2 at Westwood and the 13806 line to Bus 1 at Westwood, but this does not help with N-1-1 contingencies | Increased Cost Estimates over project 20230 synopsis: The original planning estimate was on a typical per mile basis. As this project has progressed through development, Engineering has identified that with the larger conductor needed and the taller poles we will likely be installing mostly engineered poles on foundations. This has increased the price significantly, additionally it is likely that the majority of the route will need significant access and matting since it is cross country and a large portion is in a flood plain. We are carrying a significant amount for matting and access after reviewing similar projects that have recently completed. | Duke Energy Corporation |  | BRP |  |  | 2023-12-31 | 2025-12-31 | 138 | 0 | Proposed | 45000000
A in MTEP22 | C | Central | DEI | 22425 | 2021-12-14 | DEI-2022-5 | New West Lafayette Substation | West Lafayette New Customer: construct 345kV and 138kV facilities to serve new proposed industrial load of approximately 353MVA | IN | IN | 2024-12-31 | New Customer load of 300MW/186MVAR with capacity factor of 50% | Multiple alternatives were investigated due to the nature and size of the load. Major Alternative #1: Build a 345kV line from Dequine to the new customer substation and a new 345kV line from Westwood to the new customer substation. Major Alternative #2: Build a new 345kV substation just south of Dequine and take two 138kV lines from this new substation to the customer substation. Also rearrange the Dequine substation such that the two 345kV lines from Dequine to the new substation don’t share a common breaker at Dequine and eliminate the double circuit from Dequine to the new substation by putting the two 345 kV lines on separate right-of-way. This still leaves the TPL cat. P6 exposure of both 345kV lines into Westwood. |  | Duke Energy Corporation |  | Other |  | Load Growth | 2024-12-27 | 2025-01-01 | 345 | 138 | Proposed | 100000000
A in MTEP22 | C | West | DPC | 22531 | 2022-01-18 |  | Bell Center-Lancaster N6 Rebuild | This project is a rebuild of DPC's existing 69 kV line (N6) connecting the Bell Center and Lancaster transmission substations. The recommended plan is to rebuild 40.51 miles of new 69 kV transmission line on existing right-of-way with 477 ACSR conductor. The recommended plan will address the age and condition issues, constructing the line with new poles and new 477 ACSR conductor. | WI | WI |  | DPC’s transmission line in this area was constructed in 1948 and has age and condition issues. |  |  | Dairyland Power Cooperative |  | Other |  | Age and Condition | 2025-10-15 | 2025-10-15 | 69 | 0 | Proposed | 23877825.37
A in MTEP22 | C | South | Entergy-AR | 21565 | 2022-01-18 |  | Ward Breaker Additions | Install five (5) breakers, one of which will be a transfer breaker, at AECC's Ward 115kV Switching Station. | AR | AR | 2023-12-01 | Reliability issues with serving the Ward load. |  |  | Arkansas Electric Coopertive Corporation |  | Other |  | Reliability | 2023-12-01 | 2023-12-01 | 115 | 0 | Planned | 3000000
A in MTEP22 | C | South | Entergy-AR | 21805 | 2022-09-01 | 22-EAL-002 | 2023 EAL Asset Renewal Program | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. | AR | AR | 2023-12-31 | The program is needed to replace or repair aging or failing transmission assets across EAL's territory. |  |  | Entergy Arkansas |  | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 115 | 0 | M1_Final SPM or OOC | 28500000
A in MTEP22 | C | South | Entergy-AR | 21806 | 2021-09-21 | 22-EAL-003 | Junction City 115kV: Upgrade CT's | This project will upgrade the existing 600 amp CT's at Junction City to >1000 amps. | AR | AR |  | The CT's at Junction City 115kV is limiting the line section rating and is prohibiting the use of temperature adjusted ratings. This upgrade also mitigates a cascading event during a NERC TPL extreme event. |  |  | Entergy Arkansas |  | Other |  | Reliability | 2023-12-30 | 2023-12-30 | 115 | 0 | M1_Final SPM or OOC | 1415000
A in MTEP22 | C | South | Entergy-AR | 22530 | 2022-07-11 | 22-EAL-008 | Sandy Bayou 500/230kV: New substation | Construct a new 500/230kV substation to serve a new industrial customer. The substation will consist of a 4 breaker 500kV ring bus, two 500/230kV autotransformer banks (7 single-phase 250 MVA units that includes one spare), a two bay breaker and a half 230kV bus with two 230kV sources to the customer. This new substation will be cut into the existing Driver - Shelby 500kV transmission line. | AR | AR | 2024-06-01 | This project is needed to serve a new industrial customer locating in Mississippi county, AR near the Driver - Shelby 500kV transmission line. |  |  | Entergy Arkansas |  | Other |  | Load Growth | 2024-03-01 | 2024-03-01 | 500 | 230 | M1_Final SPM or OOC | 122000000
A in MTEP22 | C | South | Entergy-AR | 23154 | 2022-08-02 |  | Keo 500kV: Expansion for J1258 & J1415 | The KEO 500kV substation will be expanded to interconnect the J1258/J1415 gen-tie 500kV line. The Network Upgrades include a new 500 kV gas circuit breaker, two new 500 kV disconnect switches, relay panels, revising the station RTU configuration, wiring additions to the DFR, and telecommunication additions. | AR | AR | 2024-10-15 | The project is needed to interconnect GIA Projects J1258 and J1415. |  |  | Entergy Arkansas |  | GIP |  |  | 2024-10-15 | 2024-10-15 | 500 | 0 | Planned | 8888000
A in MTEP22 | C | South | Entergy-AR | 23267 | 2022-08-02 |  | Fountain Hill 115kV: J1281 Cut In Switching Station | Entergy will provide oversight for the construction of the transmission owners interconnection facilities and stand alone network upgrades associated with the interconnection of J1281 on the Crossett - Monticello East 115kV line. The Crossett North 115kV substation will have new line protection installed. The Monticello East 115kV substation will have new line protection installed alond with new CCVT's and a new breaker. | AR | AR | 2024-10-31 | This transmission cut in is needed to interconnect the 75 MW solar project (J1281) per the executed GIA. |  |  | Entergy Arkansas |  | GIP |  |  | 2024-10-31 | 2024-10-31 | 115 | 0 | Planned | 3796000
A in MTEP22 | C | South | Entergy-AR | 23326 | 2022-08-02 |  | Sunset 230kV: J1215 New Switching Station Cut-In | A new 230kV three breaker ring bus substation will be cut-in to the Woodward - Stuttgart Ricuskey 230kV transmission line. Remote end upgrades will be performed at Stuttgart Ricuskey and Woodward substations. Approximately 2.6 miles of OPGW fiber will be installed between Stuttgart Ricuskey and the new J1215 stations. 230kV Circuit breakers B8414 and B8406 will be replaced at Stuttgart Ricuskey. | AR | AR | 2025-02-15 | This new switching station and remote end upgrades are needed to interconnect J1215 as per the executed generator interconnection agreement. |  |  | Entergy Arkansas |  | GIP |  |  | 2025-02-15 | 2025-02-15 | 230 | 0 | Planned | 14695000
A in MTEP22 | B | South | Entergy-LA | 13910 | 2021-09-21 | 18-ELN-002 | Calhoun: New distribution substation | Construct a 230 kV distribution substation named Calhoun in western Ouachita parish near the town of Calhoun and construct a 230 kV transmission line from the new substation that terminates into the Cadeville substation. | LA | LA | 2026-06-01 | Area distribution load |  |  | Entergy |  | Other |  | Load Growth | 2026-06-01 | 2026-06-01 | 230 | 0 | Proposed | 56800000
A in MTEP22 | C | South | Entergy-LA | 21808 | 2022-09-01 | 22-ENO-001 | 2023 ENOL Asset Renewal Program | This project is for the ENOL Asset Renewal Program that will be executed in 2023. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. | LA | LA |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  | Entergy |  | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 230 | 69 | Proposed | 1900000
A in MTEP22 | C | South | Entergy-LA | 21809 | 2022-09-01 | 22-ELS-007 | 2023 ELL Asset Renewal Program | This project is for the ELL Asset Renewal Program that will be executed in 2023. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. | LA | LA |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  | Entergy |  | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 500 | 69 | Proposed | 55100000
A in MTEP22 | C | South | Entergy-LA | 21811 | 2021-09-09 | 22-ELF-001 | Richard 500-138 kV AT1 Relay Improvement SPOF | Ensure the Richard 500-138 kV autotransformer #1 has redundant high-speed protection with independent CT and PT windings. | LA | LA | 2023-06-01 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. P5 contingency SLG fault on the Richard 500 kV bus with non-redundant relay failure for the Richard 500/138 kV auto #1 protection has the potential to cause 600MW of generation to trip. |  |  | Entergy |  | BRP |  |  | 2024-12-31 | 2024-12-31 | 500 | 138 | Proposed | 10270000
A in MTEP22 | C | South | Entergy-LA | 21816 | 2022-01-18 | 22-ELB-001 | Drusilla to Jefferson 69 kV: Upgrade Switches | Upgrade switches 9716 and 9717 at Jefferson 69 kV station to 1200 Amps. Upgrade switch 4474 at East 69 kV station to 1200 Amps. Upgrade any remaining terminal equipment to achieve a rating of 1200 Amps on the Drusilla to Jefferson to East 69 kV path. | LA | LA | 2023-06-01 | Entergy’s Planning Guidelines. The P2.1 loss of Essen Tap to Tiger 69 kV will overload from Drusilla to Jefferson 69kV line. |  |  | Entergy |  | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 69 | 0 | Proposed | 2742000
A in MTEP22 | C | South | Entergy-LA | 21822 | 2021-09-09 | 22-ELC-001 | Hartburg to Rhodes 500 kV River Crossing Tower Replacement | Replace the existing structure with a new structure that will be installed further to the east to avoid future washing out. Access to the structure is especially difficult and will require extensive matting and/or the use of specialized marsh equipment. | LA | LA |  | The Sabine River Louisiana side crossing structure (Structure 133) for the Hartburg – Rhodes 500kV line is being washed out by the progression of the Sabine River eastward. |  |  | Entergy |  | Other |  | Age and Condition | 2023-08-31 | 2023-08-31 | 500 | 0 | Proposed | 5790000
A in MTEP22 | C | South | Entergy-LA | 21832 | 2021-09-27 | 19-ELB-001 | Dow Meter to Tiger 230 kV Re-Termination project | Re-terminate the Addis to Tiger and Dow Meter to Addis 230 kV lines to create the Dow Meter to Tiger 230 kV line, which will bypass the Addis 230 kV station. | LA | LA | 2023-06-01 | The 2018 MISO Deliverability study shows an overload on the Addis to Tiger 230 kV line for the P1.2 loss of the Dow Meter to Chenango 230 kV or the Richardson to Iberville 230 kV line in 2023. This project replaces project 15566, which was shown to be ineffective in mitigating deliverability constraints in the area. |  |  | Entergy |  | BRP |  |  | 2024-06-01 | 2024-06-01 | 230 | 0 | Proposed | 5700000
A in MTEP22 | C | South | Entergy-LA | 21835 | 2022-05-24 | 22-ELS-005 | Kaiser 230-115 kV Autotransformer | Install 300 MVA, 230/115kV Autotransformer to tie Kaiser 230 kV to Conquest 115 kV. Kaiser and Conquest stations are adjacent to each other. Remove Behrman to Pt Nickel 115 kV line from the model. This facility includes an under the Mississippi River section that has failed. The Kaiser Auto alleviates some of the potential radial concerns during outages with this line removed. | LA | LA |  | Enhanced Reliability. P6 Loss of Peters Road-Behrman 230kV and Munster-Oaks 230kV overloads Gretna-Behrman 115kV. This project also alleviates potential radial concerns and higher loadings for the P6 with the Behrman to Port Nickel 115 kV line removal. |  |  | Entergy |  | Other |  | Reliability | 2024-12-01 | 2024-12-01 | 230 | 115 | Proposed | 26320000
A in MTEP22 | C | South | Entergy-LA | 23147 | 2022-05-23 | 22-ELS-009 | J1219/J1257 115 kV station(Hickory) | Construct a 115 kV substation between the existing Amite and Chicken Farm 115 kV stations | LA | LA |  | This station is being constructed to accommodate the interconnection of a solar facility (J1219/1257) |  |  | Entergy |  | GIP |  |  | 2024-09-24 | 2024-09-24 | 115 | 0 | Proposed | 14390000
A in MTEP22 | C | South | Entergy-LA | 23308 | 2022-08-03 | 22-ELS-010 | J1246 Bayou Labutte 500 kV Interconnection | The Bayou Labutte 500kV substation will be expanded to interconnect the J1246 gen-tie 500kV line. The Network Upgrades include relocation of the Willow Glen 500 kV line position, new 500 kV gas circuit breaker, two new 500 kV disconnect switches, along with other additional station equipment and upgrades at Bayou Labutte. Also Included in the network upgrades for J1246 are the replacement of two 230 kV breakers at the Point Pleasant 230 kV station to 63 kA IPO breakers along with relay upgrades for the associated equipment. | LA | LA |  | The project is needed to interconnect GIA Project J1246. |  |  | Entergy |  | GIP |  |  | 2024-06-01 | 2025-04-09 | 500 | 0 | Proposed | 14344000
A in MTEP22 | C | South | Entergy-LA | 23330 | 2022-08-03 | 22-ELN-003 | Rilla 115 kV: Expand Station (J1239) | The Rilla 115 kV station will be expanded to interconnect J1239. | LA | LA |  | This project is needed to facilitate the interconnection of J1239 100 MW solar generating facility. |  |  | Entergy |  | GIP |  |  | 2024-10-15 | 2024-10-15 | 115 | 0 | Proposed | 7233000
A in MTEP22 | C | South | Entergy-LA | 23386 | 2022-09-01 | 22-ELS-011 | MPFCA J1281, J1294, J1458 Adams Creek 230 kV and Bogalusa 500-230 kV Upgrades | MPFCA J1281, J1294, J1458 Adams Creek 230 kV and Bogalusa 500-230 kV Upgrades. Replace breakers S4402/S4405 and switches at Adams Creek 230 kV with 4000 Amp equipment. Upgrade bus at Bogalusa 500-230 kV and install slipover current transformers on 230 kV bushings of existing 500-230 kV autotransformers. These upgrades will increase the rating of the circuit between the Adams Creek 230 kV station and the Bogalusa 500-230 kV station to 1281 MVA. | LA | LA |  | Identified by MISO as required for GIA J1281, J1294, J1458. |  |  | Entergy |  | GIP |  |  | 2024-04-04 | 2024-04-04 | 230 | 0 | Proposed | 3990000
A in MTEP22 | C | South | Entergy-LA | 23421 | 2022-08-10 | 22-ELB-005 | J1368/J1372 Interconnection: Ventress 230 kV Station | Construct a new Ventress 230 kV substation between the existing Fancy Point and Waterloo 230 kV stations. | LA | LA |  | This station is being constructed to accommodate the interconnection of a solar facility (J1368/1372) |  |  | Entergy |  | GIP |  |  | 2023-04-21 | 2023-04-21 | 230 | 0 | Proposed | 5354000
A in MTEP22 | B | South | Entergy-MS | 20063 | 2022-05-23 | 21-EML-019 | Choctaw - TVA French Camp 500 kV: Decommission Line | Decommission and demolish the existing Choctaw-TVA French Camp 500kV line that was recently acquired by Entergy in November of 2019 (~0.75mi). | MS | MS |  | Enhanced Reliability. The current TVA interconnection for the Choctaw power station creates some operational issues that would be removed if the interconnection was terminated. |  |  | Entergy Mississippi |  | Other |  | Reliability | 2024-12-15 | 2024-12-15 | 500 | 0 | Proposed | 500000
A in MTEP22 | B | South | Entergy-MS | 20064 | 2022-05-23 | 21-EML-020 | Choctaw - Wolf Creek 500 kV: Build New Line | Utilize ~0.1mi of existing Choctaw-French Camp 500kV line to tie into Wolf Creek (Choctaw – French Camp 500 kV decommissioned with a separate project). Convert Wolf Creek 500kV switching yard to 4 breaker ring bus to accommodate 2nd line. | MS | MS |  | Enhanced Reliability. Once the existing TVA interconnection is removed from the Choctaw switchyard, the plant will only have one tie to the BES through breaker CC80 into Wolf Creek 500 kV substation. Adding a second interconnection will prevent a single transmission outage from taking the Choctaw Power Station offline and enhance the operational flexibility for the plant. |  |  | Entergy Mississippi |  | Other |  | Reliability | 2024-12-15 | 2024-12-15 | 500 | 0 | Proposed | 7100000
A in MTEP22 | C | South | Entergy-MS | 21815 | 2022-09-01 | 22-EML-002 | 2023 EML Asset Renewal Program | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. | MS | MS |  | The AM renewal asset program is to address aging and failing transmission assets across EML's territory. |  |  | Entergy Mississippi |  | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 500 | 0 | Proposed | 56009600
A in MTEP22 | C | South | Entergy-MS | 22345 | 2022-07-21 |  | East Winstonville Delivery Point | Tap the Energy owned Delta SES - Shelby 115kV line with switching station and build a 115kV line to the new member East Winstonville delivery point. | MS | MS | 2024-07-01 | Member has requested a new load delivery point near Winstonville, MS. |  |  | South Mississippi Electric Power Association |  | Other |  | Load Growth | 2024-07-01 | 2024-07-01 | 115 | 0 | Planned | 1862800
A in MTEP22 | C | South | Entergy-MS | 23268 | 2022-07-25 | 22-EML-003 | Franklin - Ray Braswell 500 kV Upgrade - MPFCA | Multi-Party Facilities Construction Agreement for J1215, J1281, J1294, J1425, J1434, J1440, and J1458 to upgrade the Franklin 500 kV Substation: Replace four (4) 500 kV switches with motor operators, and one (1) 500 kV ground switch. | MS | MS |  | This network upgrade project is needed to facilitate ERIS/NRIS of J1215, J1281, J1294, J1425, J1434, J1440, and J1458 generating facilities. |  |  | Entergy Mississippi |  | GIP |  |  | 2023-12-19 | 2023-12-19 | 500 | 0 | Planned | 1739000
A in MTEP22 | C | South | Entergy-MS | 23387 | 2022-08-26 | 22-EML-004 | Gerald Andrus - Tinnin 230 kV Cut-in and Line Upgrade (J1458) | Generator Interconnection new Panther Burn 230 kV station on the Gerald Andrus - Tinnin 230 kV line and Network Upgrade rebuild of the Greenville - SE Greenville 115 kV line. | MS | MS |  | This project is needed for interconnection and ERIS/NRIS as part of the J1458 generator interconnection agreement for the 200 MW solar facility. The NRIS will be limited to 170 MW until the completion of all Network Upgrades and Affected System Upgrades. |  |  | Entergy Mississippi |  | GIP |  |  | 2024-03-13 | 2024-03-13 | 230 | 0 | Proposed | 10425000
A in MTEP22 | C | South | Entergy-MS | 23482 | 2022-08-26 | 22-EML-006 | Isola - Belzoni 115 kV Upgrade - MPFCA | MPFCA. Belzoni 115 kV Substation: Replace line terminal bus and insulators for the line terminal to Isola 115 kV to a new through-path rating of 106 MVA. | MS | MS |  | MPFCA upgrade project needed for GI projects J1294 and J1458. |  |  | Entergy Mississippi |  | GIP |  |  | 2023-11-10 | 2023-11-10 | 115 | 0 | Proposed | 406000
A in MTEP22 | C | South | Entergy-MS | 23518 | 2022-08-26 | 22-EML-007 | Tunica - Lula 115 kV Cut-in (J1440) | Generator Interconnection J1440 new Dundee 115 kV station cutting in on the Tunica - Lula 115 kV transmission line. Conditional on Ray Braswell - Franklin 500 kV MPFCA | MS | MS |  | Needed to facilitate the interconnection of J1440 150 MW generator interconnection project. |  |  | Entergy Mississippi |  | GIP |  |  | 2024-05-23 | 2024-05-23 | 115 | 0 | Proposed | 13560000
A in MTEP22 | C | South | Entergy-MS | 23519 | 2022-08-26 | 22-EML-008 | Indianola - Cleveland 115 kV Cut-in (J1294) | Generator Interconnection for J1294 GI on the Indianola - Cleveland 115 kV transmission line. This generation project is conditional on: Ray Braswell – Franklin 500 kV Terminal Equipment Upgrades (DPP 2019 Shared Network Upgrade – MPFCA executed) Isola – Belzoni 115 kV Upgrade (DPP 2019 Shared Network Upgrade – MPFCA executed) Bogalusa – Adams Creek 230 kV Upgrade (DPP 2019 Shared Network Upgrade – MPFCA executed) | MS | MS |  | Needed for J1294 99 MW generator interconnection. |  |  | Entergy Mississippi |  | GIP |  |  | 2024-05-23 | 2024-05-23 | 115 | 0 | Proposed | 3870000
A in MTEP22 | B | South | Entergy-TX | 15649 | 2021-09-10 | 19-ETI-004 | Texas 138 kV: New Distribution Station | Cut the Texas substation in and out of the Lewis Creek to Goree 138 kV line. | TX | TX |  | Distribution load growth. |  |  | Entergy |  | Other |  | Load Growth | 2025-12-01 | 2025-12-01 | 138 | 0 | Proposed | 69400000
A in MTEP22 | B | South | Entergy-TX | 18262 | 2021-09-10 | 20-ETI-001 | Tarkington to New Long John 138 kV: Rebuild Line | Rebuild Tarkington to New Long John (L870). | TX | TX | 2023-06-01 | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. This project replaces the Pony project. The P5 contingency loss of Porter 138 kV bus differential relaying plus a fault causes thermal overloads on the line in multiple sensitivity cases. Tarkington to New Long John 138 kV line also overloads for the loss of Porter to New Caney 138 kV line. |  |  | Entergy |  | BRP |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | Proposed | 18230000
A in MTEP22 | C | South | Entergy-TX | 21810 | 2022-09-01 | 22-ETI-007 | 2023 ETI Asset Renewal Program | This project is for the ETI Asset Renewal Program that will be executed in 2023. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. | TX | TX |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  | Entergy |  | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 500 | 69 | Proposed | 31600000
A in MTEP22 | C | South | Entergy-TX | 21841 | 2021-09-28 | 22-ETI-003 | Porter to Oak Ridge 138 kV Station Equipment Upgrade | Upgrade Line Bay Bus at Porter 138 kV to achieve a through path rating of 1766 A on the Porter to Oak Ridge 138 kV line. | TX | TX |  | The N-1-1 contingency involving the loss of the Conroe to Forest and Lewis Creek to Alden 138 kV lines could result in non-consequential load loss in the Woodlands area. |  |  | Entergy |  | Other |  | Reliability | 2023-12-01 | 2023-12-01 | 138 | 0 | Proposed | 459000
A in MTEP22 | C | South | Entergy-TX | 21843 | 2021-09-10 | 22-ETI-008 | Neches River Crossing Structure Mitigation | Mitigation includes: Replace coffers, de-water and excavate soils Perform structure foundation inspection(s), fortify/repair where possible Restore soils around structure foundations, fill coffers to grade | TX | TX |  | Neches River has eroded around the foundations at the base of the structures on Neches to Sabine 138 kV lines 5 and 172. |  |  | Entergy |  | Other |  | Age and Condition | 2025-06-01 | 2025-06-01 | 138 | 0 | Proposed | 28000000
A in MTEP22 | C | South | Entergy-TX | 21847 | 2021-09-10 | 22-ETI-009 | Galaxy: New 138 kV Distribution Station | Cut the Galaxy substation in and out of the Porter to Apollo 138 kV line. | TX | TX |  | Distribution load growth. |  |  | Entergy |  | Other |  | Load Growth | 2026-06-01 | 2026-06-01 | 138 | 0 | Proposed | 65900000
A in MTEP22 | C | South | Entergy-TX | 21850 | 2021-09-10 | 22-ETI-011 | District: New 138 kV Distribution Station | Cut the District substation in and out of the Crystal to Security 138 kV line. | TX | TX |  | Distribution load growth. |  |  | Entergy |  | Other |  | Load Growth | 2026-12-01 | 2026-12-01 | 138 | 0 | Proposed | 85200000
A in MTEP22 | C | South | Entergy-TX | 21851 | 2022-01-18 | 22-ETI-012 | Falcon: New 138 kV Distribution Station | Cut the Falcon substation in and out of the Luce Bayou to Tarkington 138 kV line. | TX | TX |  | Distribution load growth. |  |  | Entergy |  | Other |  | Load Growth | 2026-12-01 | 2026-12-01 | 138 | 0 | Proposed | 113800000
A in MTEP22 | C | South | Entergy-TX | 22125 | 2022-01-31 | 22-ETI-014 | R1003 Generator Interconnection at Sabine 230/138 kV Station (OCAPS) | This project is to perform the required upgrades to accommodate the interconnection at the existing Sabine 230/138 kV station identified in the GIA for R1003(OCAPS) | TX | TX |  | This project is to support the interconnection of generation interconnection project for R1003(OCAPS) at the Sabine 230/138 kV substation. |  |  | Entergy |  | GIP |  |  | 2025-03-01 | 2025-03-01 | 230 | 138 | Planned | 14762000
A in MTEP22 | C | South | Entergy-TX | 23209 | 2022-08-24 | 22-ETI-015 | Legend 230 kV New Customer Connection | Entergy is proposing to construct new 230 kV transmission facilities at the existing Legend 230 kV substation which will serve a new industrial customer in Port Arthur, TX. The proposed new facilities include installing two additional 230 kV breakers into the Legend substation and extending a 230 kV radial transmission line towards the customer’s site. | TX | TX |  | Entergy has received a request from a customer interested in adding new load to a new station on the transmission system. |  |  | Entergy |  | Other |  | Load Growth | 2023-01-31 | 2023-01-31 | 230 | 0 | Proposed | 4250000
A in MTEP22 | C | South | Entergy-TX | 23307 | 2022-08-24 | 22-ETI-016 | Flare Hill 230 kV New Customer Substation | Entergy has been notified that a customer is proposing to construct a new 230 kV substation called Flare Hill, which will serve an industrial customer’s new load in Port Arthur, TX. The substation will be cut in on the existing Port Acres to Southside circuit 1. | TX | TX |  | Entergy has received a request from a customer interested in adding new load to a new station on the transmission system. |  |  | Entergy |  | Other |  | Load Growth | 2023-04-30 | 2023-04-30 | 230 | 0 | Proposed | 980000
A in MTEP22 | C | West | GRE | 20666 | 2022-08-25 | 208760 | Litchfield - Litchfield Tap Double Circuit Rebuild | Rebuild ~2.5 miles of the Litchfield - Litchfield 69 kV tap line to double circuit. | MN | MN | 2026-12-31 | Reduce line exposure to the Cedar Mills, Atwater, Litchfield and Grove City substations. The double circuit line reduces the four terminal line to three for better relay coordination. The double circuit line bifurcates the Litchfield Tap – Grove City Tap 69 kV line, which would allow the Big Swan source to be available to serve the Litchfield Muni sub during contingencies on the Panther – Litchfield Muni 69 kV line. The double circuit configuration reduces line exposure to the Cedar Mills, Atwater, Litchfield and Grove City substations. |  |  | Great River Energy |  | Other |  | Reliability | 2026-12-31 | 2026-12-31 | 69 | 0 | Proposed | 2281569
A in MTEP22 | C | West | GRE | 20707 | 2022-05-19 | 209074 | Granite Falls - Willmar (WB) Line Upgrade | Upgrade the Granite Falls - Willmar (WB) line to 212 F by replacing 10 structures. | MN | MN | 2025-06-01 | Thermal violations caused by NERC Category P6 events in both 2026 Shoulder High Wind (wind dispatched at 83% of nameplate) and 2026 Spring Light Load (wind dispatched at 70% of nameplate) Sensitivity models. |  |  | Great River Energy |  | BRP |  |  | 2025-06-01 | 2025-06-01 | 230 | 0 | Proposed | 598979
A in MTEP22 | C | West | GRE | 20865 | 2022-08-25 | 207451 | Shamrock 69 kV Substation | Construct an in/out line to the Wright Hennepin Electric Association's Shamrock substation. The Shamrock substation is a rebuild of the nearby Corcoran substation. The load served at Corcoran will be gradually moved to the new Shamrock substation. | MN | MN | 2023-02-21 | Accommodate a second transformer in the near future (~2023). The existing Corcoran substation is locked with roads that are close to the substation and there is no room to accommodate expansions to meet fast growing electric demand in the area. |  |  | Great River Energy |  | Other |  | Load Growth | 2023-02-21 | 2023-02-21 | 69 | 0 | Proposed | 1709484.43
A in MTEP22 | C | West | GRE | 21065 | 2022-08-28 | 207408 | Big Swan 5N18 115 kV Breaker Addition | Add the Big Swan 5N18 breaker on the Crow River 115 kV line. | MN | MN | 2024-11-01 | Reduce over tripping for a fault on the Big Swan - Crow River 115 kV line. A fault on the Big Swan – Crow River 115 kV line trips the Big Swan 115/69 kV transformer causing low voltage problems in the 69 kV system. |  |  | Great River Energy |  | BRP |  |  | 2024-11-01 | 2024-11-01 | 115 | 0 | Proposed | 700000
A in MTEP22 | C | West | GRE | 21705 | 2022-05-19 | 207723 | Mud Lake - Benton County - Monticello Storm Structure Addition | Add 5 storm resistant structures to the Mud Lake - Benton County - Monticello 230 kV line. | MN | MN | 2022-12-01 | The storm structures will enhance system reliability by limiting the potential for full failure of all structures within a corridor. History has shown that H-frame structures are at risk of failure during certain weather events resulting in major damage along the corridor. Due to the risk in the number of miles being rebuilt, it was determined that adding storm structures would: • Reduce replacement cost of potentially greater miles of rebuild • Reduce outage time related to rebuilding the system resulting in shorter periods of potential market congestion • Reduce potential safety issues with less wire on the ground • Allowing for less time in getting needed materials within the supply chain |  |  | Great River Energy |  | Other |  | Reliability | 2022-12-01 | 2022-12-01 | 230 | 0 | Proposed | 1823350.49
A in MTEP22 | C | West | GRE | 21823 | 2022-05-20 | 208306 | Benson – Morris Storm Structures | Install storm structures in the Benson – Morris 115 kV line. | MN | MN | 2023-12-01 | The storm structures will enhance system reliability by limiting the potential for full failure of all structures within a corridor. History has shown that H-frame structures are at risk of failure during certain weather events resulting in major damage along the corridor. Due to the risk in the number of miles being rebuilt, it was determined that adding storm structures would: • Reduce replacement cost of potentially greater miles of rebuild • Reduce outage time related to rebuilding the system resulting in shorter periods of potential market congestion • Reduce potential safety issues with less wire on the ground • Allowing for less time in getting needed materials within the supply chain |  |  | Great River Energy |  | Other |  | Reliability | 2023-12-01 | 2023-12-01 | 230 | 0 | Proposed | 1277000
A in MTEP22 | C | West | GRE | 21824 | 2022-05-20 | 208309 | Riverton – Wing River Storm Structures | Install storm structures in the Riverton – Wing River 230 kV line. | MN | MN | 2023-12-01 | The storm structures will enhance system reliability by limiting the potential for full failure of all structures within a corridor. History has shown that H-frame structures are at risk of failure during certain weather events resulting in major damage along the corridor. Due to the risk in the number of miles being rebuilt, it was determined that adding storm structures would: • Reduce replacement cost of potentially greater miles of rebuild • Reduce outage time related to rebuilding the system resulting in shorter periods of potential market congestion • Reduce potential safety issues with less wire on the ground • Allowing for less time in getting needed materials within the supply chain |  |  | Great River Energy |  | Other |  | Reliability | 2023-12-01 | 2023-12-01 | 230 | 0 | Proposed | 658000
A in MTEP22 | C | West | GRE | 21825 | 2022-05-20 | 208307 | Cormorant – Pelican Rapids Storm Structures | Install storm structures in the Cormorant – Pelican Rapids 115 kV line. | MN | MN | 2024-06-28 | The storm structures will enhance system reliability by limiting the potential for full failure of all structures within a corridor. History has shown that H-frame structures are at risk of failure during certain weather events resulting in major damage along the corridor. Due to the risk in the number of miles being rebuilt, it was determined that adding storm structures would: • Reduce replacement cost of potentially greater miles of rebuild • Reduce outage time related to rebuilding the system resulting in shorter periods of potential market congestion • Reduce potential safety issues with less wire on the ground • Allowing for less time in getting needed materials within the supply chain |  |  | Great River Energy |  | Other |  | Reliability | 2024-06-28 | 2024-06-28 | 115 | 0 | Proposed | 651387
A in MTEP22 | C | West | GRE | 21826 | 2022-05-20 | 208308 | Bunker Lake - Elk River Storm Structures | Install storm structures in the Bunker Lake - Elk River 230 kV line. | MN | MN | 2024-06-28 | The storm structures will enhance system reliability by limiting the potential for full failure of all structures within a corridor. History has shown that H-frame structures are at risk of failure during certain weather events resulting in major damage along the corridor. Due to the risk in the number of miles being rebuilt, it was determined that adding storm structures would: • Reduce replacement cost of potentially greater miles of rebuild • Reduce outage time related to rebuilding the system resulting in shorter periods of potential market congestion • Reduce potential safety issues with less wire on the ground • Allowing for less time in getting needed materials within the supply chain |  |  | Great River Energy |  | Other |  | Reliability | 2024-06-28 | 2024-06-28 | 230 | 0 | Proposed | 596365
A in MTEP22 | C | West | GRE | 21829 | 2022-05-20 | 208734 | South Dayton 115 kV Substation | Construct the new Connexus Energy (CE) South Dayton 115 kV in-and-out distribution substation in the Xcel 5522 line. | MN | MN | 2023-09-01 | Connexus Energy’s distribution planning group has calculated the 5-year load projection for Connexus Energy substations in Hennepin County, starting with the South Dayton #1 bank being installed in 2023, as well as a projection of the Connexus Energy load south of the river at the end of the current City of Dayton planning time horizon. This is based on the Metro Council’s “2015 System Statement” for the City of Dayton dated 17 SEP 2015, and CE’s understanding of the City of Dayton area that lies within the Connexus Energy service area. Page 4 of this document shows a household count of 4,400 in 2040 vs. 2,200 in 2020, and most of this increase falls within the Connexus Energy service area. The City of Dayton “2040 Future Land Use Draft” shows Commercial, Mixed Use, and Business Park use within the Connexus Energy service further justifying the load projections. In addition, the City of Maple Grove shows that the Hennepin #4 feeder area adjacent to the substation serves commercial property, which has the potential to re-develop to higher load density as it sits on the Highway 610 corridor. Connexus Energy anticipates both the Hennepin and the South Dayton substations to have a strong potential to double their load over the time window between 2023 and 2040, bringing Connexus Energy’s south of the river load to 23 MW. Project Alternatives: Connexus Energy investigated adding a 2nd transformer at Hennepin Substation, but that substation is remote from the growth area and has severely restricted feeder routes, due to the Elm Creek Park Reserve, and cannot adequately serve the growth area. Connexus Energy studied additional river crossings from Energy Park or Daytonport Substations, but the distances are too long and expensive, and the process to construct additional Mississippi River crossings is very complex. The existing Energy Park Substation river crossing has recently been re-built, and it is dedicated to loads south of the river, but it has limited reach into the growth areas. Overall, the distance from source to load on CE’s 12.47 kV system requires a new delivery point situated in the heart of the load growth area |  |  | Great River Energy |  | Other |  | Load Growth | 2023-09-01 | 2023-09-01 | 115 | 0 | Proposed | 1485000
A in MTEP22 | C | West | GRE | 21830 | 2022-05-20 | 208527 | Shamineau Lake 115 kV Substation | Construct the new Crow Wing Power Shamineau Lake distribution substation. | MN | MN | 2022-11-21 | Crow Wing Power has served the southern Motley / Lincoln area from the Ward delivery point for a while and Crow Wing Power is noticing that it is becoming more difficult to maintain end of the line voltage for its customers. The Ward substation is in Todd-Wadena’s service territory and Crow Wing Power must go 6 miles before they enter their own service territory which makes the voltage issue even more challenging. Having a source closer to their load pocket and within their own service territory will lower the miles per feeder, lowering the exposure for each circuit resulting in better reliability. Additionally, the new source will be closer to the growing load pocket and end of the line voltage will be met. The addition of regulators and capacitor banks isn’t viable since the distribution system already has two sets of regulation. The regulators on the feeders from Ward have been working overtime to keep up with the 34.5kV voltage fluctuations. |  |  | Great River Energy |  | Other |  | Load Growth | 2022-11-21 | 2022-11-21 | 115 | 0 | Proposed | 792000
A in MTEP22 | C | West | GRE | 22025 | 2022-05-20 | 208426 | Parkwood 115 kV Ring Bus | Rebuild the 115 kV bus at Parkwood substation as a ring bus. | MN | MN | 2024-11-08 | 115 kV line faults cause a trip of a Parkwood 115/69 kV transformer. Parkwood 12WB2 breaker failure causes overload of the Bunker Lake-Village Ten 69 kV line under peak loading conditions. A Parkwood 115/69 kV transformer differential protection activation causes transfer tripping to the remote substations. For the Crooked Lake 115 kV line, this causes the loss of Connexus’ load service at Crooked Lake, which serves a major commercial development. Project Alternatives: Adding 115 kV line breakers. This option is feasible but is not as robust as a ring bus topology. A 115/69 kV transformer trip still will open a 115 kV line and a 12WB2 breaker failure event still trips out the entire 115 kV bus. Rebuilding the Bunker Lake-Village Ten 69 kV line (2.63 miles). This circuit is double circuited with the Blaine-Bunker Lake 230 kV line on steel structures. About 0.50 miles of structures have been replaced as part of past road move projects, but it is unknown if these could be reused. Also, about 0.75 miles of this circuit runs through a residential neighborhood, so access for rebuilding might be challenging. The option, while correcting a NERC Category P24 contingency overload, does not increase the robustness of the Parkwood 115 kV topology. Do nothing and accept the risk of the Parkwood 12WB2 stuck breaker contingency occurring. A P24 contingency is a more extreme contingency than a Category P1 contingency occurring. Should the contingency occur under high system loading conditions, however, the only recourse to alleviate the overload would be load shedding, likely several large commercial districts in Anoka County. This option does not increase the robustness of the Parkwood 115 kV topology. |  |  | Great River Energy |  | BRP |  |  | 2024-11-08 | 2024-11-08 | 115 | 0 | Proposed | 7620000
A in MTEP22 | C | West | GRE | 22026 | 2022-08-25 | 208453 | Deer River - Jessie Lake - Wirt Tap 69 kV Line Rebuild | Rebuild the Deer River - Jessie Lake - Wirt Tap 69 kV line. | MN | MN | 2025-09-30 | This line is being rebuilt due to age and condition concerns. Additional benefit is improvement of voltage drop and line losses due to lower impedance of the replacement conductor. |  |  | Great River Energy |  | Other |  | Age and Condition | 2025-09-30 | 2025-09-30 | 69 | 0 | Proposed | 20723354.36
A in MTEP22 | C | West | GRE | 22027 | 2022-08-24 | 209093 | Birch Lake - Pleasant Lake - Wabedo 69 kV Line Rebuild | Rebuild the Birch Lake - Pleasant Lake - Wabedo 69 kV line. | MN | MN | 2024-06-01 | Age and condition. For the loss of the Badoura - Tripp Lake 115 kV line, the voltages in the Blind Lake area go into violation. The existing line is 1/0 and 2/0 ACSR and is planned to be rebuilt with 795 ACSR to help the voltage profile of the Blind Lake area loads. |  |  | Great River Energy |  | BRP |  |  | 2024-06-01 | 2024-06-01 | 69 | 0 | Proposed | 14419044.49
A in MTEP22 | C | West | GRE | 22028 | 2022-05-20 | 208345 | Denham - Harry Maser 69 kV Line Rebuild | Rebuild the Denham - Harry Maser 69 kV line. | MN | MN | 2025-05-02 | Age and condition. For the loss of the Cromwell - Kettle River 69 kV line, there is a voltage violation at Sturgeon Lake but after rebuilding the existing line from 1/0 ACSR to 477 ACSR we will no longer have this voltage violation. |  |  | Great River Energy |  | BRP |  |  | 2025-05-02 | 2025-05-02 | 69 | 0 | Proposed | 5112000
A in MTEP22 | C | West | GRE | 22029 | 2022-08-24 | 208767 | Walden 115/41.6 kV LTC | Replace the existing Walden 115/41.6 kV transformer with an LTC transformer. | MN | MN | 2023-08-31 | This project is primarily needed to address low voltage concerns in the area. System planning studies with historical summer peak loads have shown that the Walden to Elbow Lake 41.6 kV system experiences marginal system intact voltage. The study also showed post contingent low voltage planning criteria violations in the Elbow Lake – Walden 41.6 kV system. The most critical contingencies for the area are the Morris to Morris OTP 115 kV line outage and Walden 115/41.6 kV transformer outage. For the loss of Morris to Morris OTP 115 kV line outage, all loads that are served from the Walden 115/41.6 kV transformer experience low voltage that are below GRE’s post contingent low voltage criteria of 0.92 per unit. Even though wide voltage swings are expected between different loading profiles throughout the year in the 41.6 kV system, historical voltage profile of the Walden 41.6 kV bus shows that the Walden 41.6 kV bus experiences high voltage problems that violates GRE’s high voltage criteria of 1.05 per unit. The Walden LTC transformer is required to regulate both the low voltage and high voltage concerns in the area. |  |  | Great River Energy |  | BRP |  |  | 2023-08-31 | 2023-08-31 | 115 | 0 | Proposed | 2500000
A in MTEP22 | C | West | GRE | 22030 | 2022-05-20 | 208722 | Rost 161/69 kV Substation and Lorain - Rost 69 kV Line | Construct the Rost 161/69 kV substation interconnection in the Heron Lake – Round Lake 69 kV transmission line. Construct approximately 9 miles of 69 kV transmission line from the Lorain substation to the Rost substation. Previously named Worthington Area Projects. | MN | MN | 2026-10-30 | Missouri River Energy Services (MRES), Great River Energy (GRE), and ITC Midwest (ITCM) performed a joint study of the Worthington area in southwestern Minnesota. Existing operational and reliability issues in this area have existed for some time. Various options have been considered for the Worthington load center, approximately 60 MW, and other loads that surround the area. At present, single contingency bus outages at Elk 161/69 kV substation cause the Worthington load to drop. In addition, there is a challenge to take maintenance outages on the 161 kV system from Split Rock to Lakefield Junction, some portions of the 69 kV system, and some portions of the neighboring 345 kV system due to voltage concerns across the area. Reconfiguration of the 69 kV system is a normal occurrence and puts area load at risk if an event were to occur in this temporary configuration. With the load growth occurring in Worthington for Worthington Public Utilities (WPU) over the next few years, the above issues are being exacerbated, and the proposal of a new substation in the Worthington area, prompted a deeper look into the area resulting in the following project need: Phase 1: Approximately 9 mile, 69-kV line from existing MRES Lorain breaker station to new Rost 69 kV breaker substation: Necessity: Establish alternative source beyond Elk to serve the Worthington load center Allow redundant 161/69 kV sources to be connected (Heron Lake and Elk) Lower reliability exposure to multiple 69 kV loads and wind farm connections on long 69 kV corridors Establish new relaying point to enhance relay settings with consideration for the wind farm sources and allow for future wind connections into the substation Benefits: Reduces the dependence of the Worthington load pocket on ITCM’s Elk Substation Increased operational flexibility for Worthington load for prior outages Additional 69-kV source to the Federated Rural Electric Association service territory including breaking up a highly exposed 69 kV line Enhanced relaying for line protection that consist of long distance 69 kV line with many radial taps and four wind farms, all without breaker protection Phase 2: Establish 161/69 kV at Rost with new 161 kV line from new ITC 161 KV Lakefield Corners breaker station Necessity: Low voltage - any outage on the 161-kV between Split Rock Substation (Xcel Energy) and Magnolia Substation leaves the system susceptible to low voltages for faults anywhere between Lakefield Junction and Elk 161-kV. Eliminate considerable operational concerns for prior-outage situation with a second event in the area. 161 kV prior outages of concern from Split Rock to Lakefield Junction including 161 kV substation on the corridor of Magnolia, Elk, Brewster, and Heron Lake. Reduce temporary operating guide and system reconfiguration due to voltage issues caused by a second contingency event. Eliminate significant risk of load loss within a broad area of southwestern Minnesota Benefits: New 161-kV source to the Worthington load pocket, via Rost 69 kV development allowing continued load expansion in the Worthington area Projects address voltage collapse and allows 69-kV system to remain in normal configuration during critical prior outages New Rost 161/69 kV source allows simplification of work at Heron Lake thus resulting in reduced cost at that substation. |  |  | Great River Energy |  | BRP |  |  | 2025-10-03 | 2026-10-30 | 161 | 69 | Proposed | 13368000
A in MTEP22 | C | West | GRE | 22445 | 2022-05-20 | 209056 | Cedar 115 kV Substation | DEA building new in/out distribution substation. GRE will need to double circuit tap into sub off of DA-DA line. GRE is also responsible for the highside structures and associated equipment. | MN | MN | 2023-06-01 | Cedar Substation – This is a new site located near the intersection of Cedar Ave and Lakeville Blvd. in Lakeville. DEA has talked to engineering and land rights at GRE about the feasibility as this now has passed city council and DEA is purchasing the land and would likely build out this site in 2023. Load growth within the city limits of Lakeville, between Dodd Boulevard, Flagstaff Avenue, and the area south of the existing Dodd Park substation, are forecasted to exceed the available capacity of neighboring Dodd Park, Vermillion River, and Ritter Park substations. Much of the developable land within Lakeville’s 2040 comprehensive plan is proposed as either low density or low/medium density residential housing. Area adjacent to Cedar Avenue, between County Road 50 and 190th Street West, is proposed to be developed as commercial, mixed use, and residential density at or above medium density housing units. The Cedar substation is required to supply new and existing members within both the Lakeville and Farmington city limits an adequate voltage supply during both normal system configurations. The new Cedar substation is also required to provide an adequate contingency supply to southern circuits of the Dodd Park substation, as well as northern and western feeders leaving the Vermillion River substation. Feeders are proposed to be constructed as part of the new Cedar substation as new loads continue to come into the area surrounding the site; specifically residential and mixed use to the north and largely commercial and industrial to the south of the substation location. |  |  | Great River Energy |  | Other |  | Load Growth | 2023-06-01 | 2023-06-01 | 115 | 0 | Proposed | 2773049.09
A in MTEP22 | C | West | GRE | 22528 | 2022-08-24 | 209073 | Matter 69 kV Substation | Install a manual load break 3-way load break 69kV/1200A switch on a steel pole and foundation on GRE’s DX (Crow River to Victor) line. Install adjacent grading structures if needed. Build HS DE to 115kV. | MN | MN | 2024-01-01 | Delano Municipal Utilities (DMU) desires to establish a distribution substation tapping GRE’s DX line to serve about 5 MW peak load and provide a backup service to its existing Delano Muni distribution substation. DMU will be responsible to install a metering package per GRE’s requirement to allow metering data transfer between DMU’s new substation and GRE. |  |  | Great River Energy |  | Other |  | Load Growth | 2024-01-01 | 2024-01-01 | 69 | 0 | Proposed | 402407
A in MTEP22 | C | Central | HE | 22628 | 2022-05-11 |  | New HE_Sleepy_Hollow 345/161 Sub | New 345kV ring bus station with 345/161kV transformation and 161 kV transmission line to new station (22646) | IN | IN | 2028-06-01 | Construct new 345kV ring bus station with 345/161 transformation between DEI Prescott and DEI Columbus. Construct new 161kV transmission line to new 161kV station between Decatur and Napoleon. Required to accommodate up to 400 MW load, and maintain N-2 reliability, at new Decatur-Napoleon 161kV station. |  |  | Hoosier Energy REC, Inc. |  | Other |  | Load Growth | 2028-06-01 | 2028-06-01 | 345 | 161 | Proposed | 38000000
A in MTEP22 | C | Central | HE | 22646 | 2022-04-06 |  | New Decatur-Napoleon 161KV Station | New 161 kV transmission station between Decatur and Napoleon | IN | IN | 2024-10-01 | New customer request interconnection to 161kV line. Construct new 161kV station about 1.5 miles south of Decatur station to accommodate interconnection. Initial load about 25 MW, growing up to 400 MW through 2032. |  |  | Hoosier Energy REC, Inc. |  | Other |  | Load Growth | 2024-10-01 | 2024-10-01 | 161 | 0 | Proposed | 26000000
A in MTEP22 | C | Central | HE | 22648 | 2022-05-16 |  | New HE_Prescott_161kV_Line | New 161kV line from DEI Prescott to new 161kV station | IN | IN | 2026-06-01 | Expand DEI Prescott ring-bus and construct new 345/161 substation. Construct 161kV line from Prescott to new Decatur-Napoleon Station (22646). Required to accommodate up to 400 MW load, and maintain N-2 reliability, at new Decatur-Napoleon 161kV station. |  |  | Hoosier Energy REC, Inc. |  | Other |  | Load Growth | 2026-06-01 | 2026-06-01 | 345 | 161 | Proposed | 45000000
A in MTEP22 | C | Central | HE | 22666 | 2022-05-16 |  | New HE_Batesville_161kV_Line | New 161kV line from DEI Batesville to new 161kV station (22646) | IN | IN | 2027-06-01 | Expand DEI Batesville ring-bus and construct new 345/161 substation. Construct new 161kV line from DEI Batesville to new 161kV station between Decatur and Napoleon. Required to accommodate up to 400 MW load, and maintain N-2 reliability, at new Decatur-Napoleon 161kV station. |  |  | Hoosier Energy REC, Inc. |  | Other |  | Load Growth | 2027-06-01 | 2027-06-01 | 345 | 161 | Proposed | 45000000
A in MTEP22 | C | Central | HE | 23266 | 2022-08-10 |  | New HE_AboutBit 115 MVA Load | Extend a new 69kV transmission line from an available bay position at Merom transmission station (Bus # 248774) to the new customer. The 69kV line will split at about 0.3 miles from Merom station, extending to two separate substations. Total estimated load is 115 MVA (20 MVA on substation 1 and 95 MVA on substation 2). | IN | IN | 2023-01-01 | Hoosier Energy has received a request from a customer to add 115 MVA load to the 69kV transmission system, about 1 mile south of Merom station. An agreement targeting an in-service date of January 2023 was reached between Hoosier Energy and the customer in June 2022. The project is to be constructed prior to the MTEP23 cycle. |  |  | Hoosier Energy REC, Inc. |  | Other |  | Load Growth | 2023-01-01 | 2023-01-01 | 69 | 0 | Proposed | 1200000
A in MTEP22 | C | Central | HMPL | 22228 | 2022-01-31 |  | Upgrades HMPL Transmission Due to I-69 DOT Project | Rerouting of HMPL 69kV transmission lines (HMPL Sub 6 to HMPL Sub 1, HMPL Sub 6 to (BREC) HMPL6 Tap, HMPL Sub 6 to HMPL Sub 3, and HMPL Sub 3 to (BREC) Wolf Hills Tap) due to I-69 KY DOT project. | KY | KY |  | HMPL needs to reroute its transmission lines due to the KY I-69 DOT project. |  |  | Henderson Municipal Power & Light |  | Other |  | Reliability | 2022-06-30 | 2022-06-30 | 69 | 0 | Planned | 3800000
A in MTEP22 | C | Central | IPL | 21836 | 2021-09-20 |  | Replace Sunnyside 345 kV and 138 kV Breakers | Replacement of three (3) 345 kV breaker #21, #22 & #23 and two (2) 138 kV breakers #1, & #3 | IN | IN | 2024-12-31 | Age and condition |  |  | Indianapolis Power & Light Company |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 345 | 0 | Proposed | 5100000
A in MTEP22 | C | Central | IPL | 21838 | 2021-09-20 |  | Replace Southwest 138 kV Breakers | Replacement of five (5) 138 kV breakers #4, #5, #3, #26, #27 | IN | IN |  | Age and Condition |  |  | Indianapolis Power & Light Company |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 138 | 0 | Planned | 4500000
A in MTEP22 | C | Central | IPL | 21839 | 2021-09-20 |  | Replace West 138 kV Breakers | Replacement of three (3) 138 kV breakers #1, #4, #7 | IN | IN |  | Age and Condition |  |  | Indianapolis Power & Light Company |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 138 | 0 | Planned | 2400000
A in MTEP22 | C | West | ITCM | 21828 | 2021-09-10 | Agency St Enclosure & Relays | Agency Street New Control Enclosure & Relay Replacements | The relays at Agency Street are approaching their 20 year end of life. ITC will install a new control enclosure with all new relays to provide ITC a separate control enclosure from IPL and minimize required outages and outage times for the relay replacements. All necessary outages should be coordinated with IPL. Also coordinate with IPL on location of new control building as this is an IPL owned site. | IA | IA | 2024-12-31 | The relays at Agency Street are approaching their 20 year end of life. |  |  | ITC Midwest |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 2090891
A in MTEP22 | C | West | ITCM | 21842 | 2021-09-22 | Jasper County Enclosure & Relay Replacements | Jasper County Control Enclosure and Relay Replacements | A new Control Enclosure is required at the Jasper County Substation due to age and condition. ITC will install a new Control Enclosure with all new relays. | IA | IA | 2024-12-30 | The existing control enclosure and relays are at the end of their respective lives and in need of replacement. |  |  | ITC Midwest |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 161 | 161 | Planned | 2486897
A in MTEP22 | C | West | ITCM | 21929 | 2022-08-22 | Forks SS & line | Forks Switching Station & Forks-Rost 161kV Circuit | As part of a joint study to serve load expansion in Worthington, MN, ITC will construct a 161kV circuit between new Forks switching station and GRE Rost substations. | MN | MN | 2026-12-31 | Part of a joint study to serve load expansion in Worthington, MN. MRES submitted a load addition on the Southeast side of the city of Worthington, MN. As part of this load addition study, GRE and ITC Midwest analyzed the existing operation and reliability concerns/violations. |  |  | ITC Midwest |  | BRP |  |  | 2026-12-31 | 2026-12-31 | 161 | 161 | Planned | 13456200
A in MTEP22 | C | West | ITCM | 21930 | 2021-09-14 | Millstream | Millstream 69kV Switching Station | ITC has been working with Amana Society on way to improve reliability to their substation, and ITC will be building a new 69 kV switching station called “Millstream” adjacent to the existing Amana Society substation to improve area transmission system reliability. | IA | IA | 2024-12-31 | ITC has been working with Amana Society on way to improve reliability to their substation, and ITC will be building a new 69 kV switching station called “Millstream” adjacent to the existing Amana Society substation to improve area transmission system reliability. |  |  | ITC Midwest |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 7748400
A in MTEP22 | C | West | ITCM | 21933 | 2021-10-01 | Fox Lake Relay, Bkr, SCADA | Fox Lake Relay, Breaker, & SCADA Replacements | ITC will replace all of its relays and SCADA equipment as well as remove the existing carrier equipment/wave trap at the Fox Lake substation. Circuit Breaker 736 will also be replaced at Fox Lake substation. | MN | IA | 2025-12-31 | Relays and SCADA equipment are near the end of their lifespan and will need replacement due to aging. Circuit breaker 736 will also need replacement due to aging condition. |  |  | ITC Midwest |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 161 | 161 | Planned | 2651016
A in MTEP22 | C | West | ITCM | 21935 | 2021-09-22 | Hayward Transformer Replacement | Hayward Transformer Replacement | ITC will replace the two 161/69kV transformers at Hayward Substation with a single 150 MVA 161/69kV unit. To make room for the new 161kV bus tie breaker. ITC will move the Glenworth – Hayward 161kV terminal to the opposite side of the Hayward – Murphy Creek 161kV terminal. | MN | MN | 2025-12-31 | At Hayward Substation there are two 75MVA 161/69kV transformers that are beginning to gas. Both units are over 50 years of age, and the DGA results show that the paper cellulose insulation is at the end of life. |  |  | ITC Midwest |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 161 | 69 | Planned | 6744271
A in MTEP22 | C | West | ITCM | 21936 | 2021-09-14 | Centerville Cooper Creek | Centerville Cooper Creek 69kV Interconnection | IPL will be building a new 69/25x12.5 kV substation named “Centerville Cooper Creek” adjacent to the existing Centerville North substation on the location of the old combustion turbines. This new substation will replace the existing IPL/ITC Centerville North Substation and accommodate future area load growth as well as IPL’s future conversion to 25 kV distribution. IPL will be installing two 12/20 MVA transformers at the new Centerville Cooper Creek substation. For the ITC owned portion of Centerville North, ITC will build a new 69 kV substation with two single boxes, two line breakers, and a bus tie breaker. Once the new Centerville Cooper Creek substation is in-service, the existing Centerville North substation will be retired. | IA | IA | 2025-12-31 | Load serving, future conversion and retirement of existing Centerville North substation. |  |  | ITC Midwest |  | Other |  | Load Growth | 2025-12-31 | 2026-06-30 | 69 | 69 | Planned | 3708274
A in MTEP22 | C | West | ITCM | 21937 | 2021-09-14 | Chariton North 69kV Interconnection | Chariton North 69kV Substation Interconnection | IPL will be building a new 69/26.2 kV Substation named Chariton North. IPL will be installing one 69/26.2 kV 20/33 MVA or 30/50 MVA transformer initially but is planning the substation to accommodate a second 69/26.2 kV 20/33 MVA or 30/50 MVA transformer when all the load is added. All the ITC 69 kV substation equipment will be capable of 1200A or greater. The 69 kV lines to the new substation will be T2-4/0 or larger and will be the standard 69 kV construction. | IA | IA | 2024-12-30 | Customer Interconnection |  |  | ITC Midwest |  | Other |  | Load Growth | 2024-12-30 | 2024-12-30 | 69 | 69 | Planned | 6836817
A in MTEP22 | C | West | ITCM | 21939 | 2021-09-14 | CR Hunter Field Expansion | Cedar Rapids Hunter Field Substation Expansion | IPL has notified ITC that it will be adding a 3rd 161x69/24.9 kV transformer at the Hunter Field Substation. ITC will need to add an additional breaker and bus to connect the new IPL transformer at Hunter Field. All new ITC equipment to be designed to 161 kV specs to allow future conversion of the substation to 161 kV operation. Substation will initially be operated at 69 kV. | IA | IA |  | Customer requested and system reliability. |  |  | ITC Midwest |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 1284996
A in MTEP22 | C | West | ITCM | 21940 | 2021-09-14 | Turkey River to Guttenburg | Turkey River to Guttenburg 69kV Rebuiild | The 9.04 mile Turkey River – Guttenberg 69 kV line is at the end of its useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Turkey River and Monona. | IA | IA | 2025-12-31 | Age & Condition, end of useful life. |  |  | ITC Midwest |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 69 | 69 | Planned | 10376400
A in MTEP22 | C | West | ITCM | 21941 | 2022-08-23 | Guttenburg to Grrnavillo | Guttenburg to Garnavillo 69kV Rebuild | The 11.23 mile Guttenberg - Garnavillo 69 kV line along with the 0.18 mile tap to Garnavillo are at the end of their useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Guttenberg and Monona. | IA | IA | 2028-12-31 | Age & Condition, end of useful life. |  |  | ITC Midwest |  | Other |  | Age and Condition | 2028-12-31 | 2028-12-31 | 69 | 69 | Planned | 14391600
A in MTEP22 | C | West | ITCM | 21942 | 2022-08-23 | Garnavillo to Elkader | Garnavillo to Elkader 69kV Rebuild | The 7.63 mile Garnavillo - Elkader 69 kV line is at the end of its useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Garnavillo and Elkader. | IA | IA | 2028-12-31 | Age & Condition, end of useful life. |  |  | ITC Midwest |  | Other |  | Age and Condition | 2028-12-31 | 2028-12-31 | 69 | 69 | Planned | 10012800
A in MTEP22 | C | West | ITCM | 21943 | 2021-09-14 | Rose Hollow Add 161kV Terminal | Rose Hollow Add 161kV Terminal for North Gate line | MidAmerican has notified ITC that they will be building a new 161 kV line from their exiting North Gate substation to the ITC Rose Hollow substation. Per the terms of the agreement with MidAmerican, ITC will need to install a new 161 kV terminal at Rose Hollow for the new line to North Gate. | IA | IA | 2024-12-31 | Customer requested |  |  | ITC Midwest |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 161 | 161 | Planned | 984000
A in MTEP22 | C | West | ITCM | 21946 | 2021-09-14 | Pelican-Triboji 69kV Rebuild | Pelican-Triboji 69kV Rebuild | Two sections of the Pelican-Triboji 69kV line are near end of life and in poor condition. The line between Pelican and structure 162 (~1.04 miles) and the line between Triboji and structure 72 (~4.45 miles) will be rebuilt to current 69kV standards. All new line should be rated 600A or higher. All necessary outages should be coordinated with IPL and CBPC. | IA | IA | 2023-12-31 | Two sections of the Pelican-Triboji 69kV line are near end of life and in poor condition. |  |  | ITC Midwest |  | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 69 | 69 | Planned | 6462000
A in MTEP22 | C | West | ITCM | 21976 | 2022-05-02 | Jasper to Laurel 161kV Line Rebuild | Jasper to Laurel 161kV Line Rebuild | ITC will rebuild approximately 10 miles of the Jasper to Laurel 161kV line. The 161kV line conductor will be capable of 1600A or greater. | IA | IA | 2027-12-30 | The existing control enclosure and relays are at the end of their respective lives and in need of replacement. |  |  | ITC Midwest |  | Other |  | Age and Condition | 2027-12-30 | 2027-12-30 | 161 | 161 | Planned | 18781720
A in MTEP22 | C | West | ITCM | 21977 | 2022-05-20 | J1050 TOIF | J1050 Generator Interconnection - TOIF | The Interconnection Customer, Great Pathfinder Wind, LLC, has proposed connection of a 225 MW wind powered generating facility to the Doud 161 kV bus. A breaker position in the Doud 161 kV ring bus will be added to accommodate the interconnection. TOIF cost to include dead end, line disconnect switch, arresters, PT’s, relay panel, and other associated equipment. The IC has requested ITCM to begin design under an E&P agreement to better accommodate their requested in service date while the MISO process is still ongoing. | IA | IA | 2022-08-22 | Customer requested - GIA |  |  | ITC Midwest |  | GIP |  |  | 2022-08-22 | 2022-08-22 | 161 | 161 | Under Construction | 403313
A in MTEP22 | C | West | ITCM | 21978 | 2021-09-15 | J1050 NU | J1050 Generator Interconnection - Network Upgrade | The Interconnection Customer, Great Pathfinder Wind, LLC, has proposed connection of a 225 MW wind powered generating facility to the Doud 161 kV bus. A breaker position in the Doud 161 kV ring bus will be added to accommodate the interconnection. Network Upgrade cost to include the new breaker position, switch and associated equipment. The IC has requested ITCM to begin design under an E&P agreement to better accommodate their requested in service date while the MISO process is still ongoing. | IA | IA | 2022-07-01 | Customer requested - GIA |  |  | ITC Midwest |  | GIP |  |  | 2022-08-22 | 2022-08-22 | 161 | 161 | Under Construction | 408428
A in MTEP22 | C | West | ITCM | 21980 | 2021-11-24 | ITC Midwest Asset Replacement Program 2025 | ITC Midwest Asset Replacement Program 2024 | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA,MN,IL | IA,MN,IL | 2024-12-31 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance have increased potential for misoperations and higher maintenance costs associated with their ongoing use. |  |  | ITC Midwest |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 345 | 69 | Planned | 37080000
A in MTEP22 | C | West | ITCM | 21982 | 2021-10-07 | S Dubuque 161/69kV Source & Bunker Hill 69kV Loop | Southern Dubuque 161/69kV Source & Bunker Hill 69kV Loop | ITC Midwest will construct a new 161/69kV substation on the south side of Dubuque. Then a new right of way 69 kV line ~2.65 miles to the existing Bunker Hill substation in the center of Dubuque. The new line will provide the 2nd 69kV line to the radial Bunker Hill 69kV sub. Alliant Energy will expand the Bunker Hill site to allow for a 2nd distribution transformer and ITC to have two 69 kV line breakers and a 69 kV bus tie breaker. The new ITC 161/69kV sub will be capable of two 150 MVA 161/69kV transformers (one initially). The 161kV will be constructed with the standard 161 kV ring convertible to breaker and 1/2 with just the single transformer and the two 161kV line taps initially. The 69kV will need to allow for a potential 2nd 150 MVA transformer and 69kV bus tie breaker, but will initially be just a single 69kV line to feed the Bunker Hill loop. | IA | IA | 2026-12-31 | Alliant Energy has requested that ITC provide a network feed for the radial Dubuque 8th Street-Bunker Hill 69 kV line. The Bunker Hill site is centrally located with all other transmission lines more or less bordering the edges of the city of Dubuque. The Bunker Hill substation can not serve existing distribution load during summer months and Alliant Energy must move several distributions feeders to other distribution sources. The new 69kV source will initially be just the new 69 kV loop to Bunker Hill, but will also be effective at serving future load along the Southwest Arterial, a recently completed 4 lane bypass connecting the major highways heading south and west from Dubuque. |  |  | ITC Midwest |  | Other |  | Load Growth | 2025-12-31 | 2025-12-31 | 161 | 69 | Planned | 19306266
A in MTEP22 | C | West | ITCM | 21987 | 2022-05-23 | J1181 GIA - TOIF | J1181 GIA - TOIF Lasalle 345 kV Switching Station | ITC is entering into a Generator Interconnection Agreement with Invenergy for the interconnection of project J1181, a 200 MW wind-powered generating facility to a new, 3 breaker, 3 terminal 345 kV “Lasalle” switching station along the Hazleton to Mitchell 345 kV line. Invenergy’s collector substation will be located in close proximity to the new Lasalle switching station. Invenergy has requested an October 31, 2022 in service date for the project. Under the terms of the GIA, Invenergy will transfer property for Lasalle 345 kV station to ITC, and Invenergy will also provide a topographical survey and soil borings for the ITC facilities. Lasalle switching station will be constructed with 3,000A capability. | IA | IA | 2023-08-31 | Customer requested - GIA |  |  | ITC Midwest |  | GIP |  |  | 2023-08-31 | 2023-08-31 | 345 | 345 | Planned | 892270
A in MTEP22 | C | West | ITCM | 21989 | 2022-04-07 | J1181 GIA - TO Funded 345 kV Network Upgrades | J1181 GIA - TO Funded 345 kV Network Upgrades | ITC is entering into a Generator Interconnection Agreement with Invenergy for the interconnection of project J1181, a 200 MW wind-powered generating facility to a new, 3 breaker, 3 terminal 345 kV “Lasalle” switching station along the Hazleton to Mitchell 345 kV line. Invenergy’s collector substation will be located in close proximity to the new Lasalle switching station. Invenergy has requested an October 31, 2022 in service date for the project. Under the terms of the GIA, Invenergy will transfer property for Lasalle 345 kV station to ITC, and Invenergy will also provide a topographical survey and soil borings for the ITC facilities. Lasalle switching station will be constructed with 3,000A capability. | IA | IA | 2023-08-31 | Customer requested - GIA |  |  | ITC Midwest |  | GIP |  |  | 2023-08-31 | 2023-08-31 | 345 | 345 | Planned | 12653333
A in MTEP22 | C | West | ITCM | 21991 | 2021-09-15 | J836 GIA - TOIF - Ledyard 345 kV | J836 GIA - TOIF - Ledyard 345 kV | 7-21-21: ITCM and Duke Energy have entered into a MISO Generator Interconnection Agreement. Initial sketch provided Design work for TOIF under an Engineering and Procurement Agreement. The work under the E&P Agreement included design of TOIF and Network Upgrades necessary for the expansion of Ledyard 345 kV to a 4-terminal, 4-breaker ring bus configuration. | IA | IA | 2022-07-01 | Customer requested - GIA |  |  | ITC Midwest |  | GIP |  |  | 2022-08-26 | 2022-08-26 | 345 | 345 | Under Construction | 1146492
A in MTEP22 | C | West | ITCM | 21992 | 2021-09-15 | J836 TO Funded GIA Network Upgrades | J836 TO Funded Generator Interconnection - Ledyard 345 kV | ITCM and Duke Energy have entered into a MISO Generator Interconnection Agreement for upgrade of Ledyard 345 kV switching station. The work under the Agreement will include design of TOIF and Network Upgrades necessary for the expansion of Ledyard 345 kV to a 4-terminal, 4-breaker ring bus configuration. Design work for TOIF and Network Upgrade commenced under an Engineering and Procurement Agreement, and the GIA provides for continuation and completion of the work at Ledyard. | IA | IA |  | Customer requested - GIA |  |  | ITC Midwest |  | GIP |  |  | 2022-07-01 | 2022-07-01 | 345 | 345 | Planned | 1814497
A in MTEP22 | C | West | ITCM | 21996 | 2021-09-15 | J1084 Generator Interconnection TOIF | J1084 Generator Interconnection TOIF | TOIF includes facilities and equipment at the 345 kV substation dedicated to the 345 kV radial line and Generating Facility | IA | IA | 2023-10-01 | Customer requested - GIA |  |  | ITC Midwest |  | GIP |  |  | 2023-10-01 | 2023-10-01 | 345 | 345 | Planned | 661704
A in MTEP22 | C | West | ITCM | 21997 | 2021-09-15 | J1084 Generator Interconnection Network Upgrades | J1084 Generator Interconnection Network Upgrades | Rock Creek 345 kV ring bus will be expanded with a 345 kV breaker and other necessary equipment to interconnect the new terminal for project J1084. | IA | IA | 2023-10-01 | Customer requested - GIA |  |  | ITC Midwest |  | GIP |  |  | 2023-10-01 | 2023-10-01 | 345 | 345 | Planned | 1294462
A in MTEP22 | C | West | ITCM | 21998 | 2022-08-24 | J1164 Generator Interconnection TOIF | J1164 Generator Interconnection TOIF | Magnolia 161 kV substation currently has no circuit breakers protecting the Magnolia to Elk 161 kV line and the Magnolia to Rock County 161 kV line. The Facilities Study for J1164 identified Network Upgrades and TOIF necessary for the interconnection of project J1164 to ITCM’s Magnolia 161 kV substation. Project J1164’s impact to the transmission system is currently being evaluated as part of the DPP 2018 April West Area Study, which has not been finalized pending results of an Affected System Study. | MN | MN | 2024-08-01 | To interconnect project J1164 to the ITC Midwest (“ITCM”) system at the interconnection customer’s requested point of interconnection, ITCM will upgrade Magnolia 161 kV substation to a 4 terminal ring bus configuration. The interconnection customer, MISO and ITCM entered into an Engineering and Procurement Agreement for initial design work for the Magnolia 161 kV expansion, and it is expected that a Generator Interconnection Agreement (“GIA”) will be entered into by the interconnection customer, MISO and ITCM soon. Network Upgrades and Transmission Owner Interconnection Facilities (“TOIF”) are expected to be constructed at Magnolia substation for project J1164, an 80 MW, solar-powered generating facility under a Generator Interconnection Agreement (“GIA”) as a condition of the project’s Interconnection Service. |  |  | ITC Midwest |  | GIP |  |  | 2024-08-01 | 2024-08-01 | 161 | 161 | Planned | 475538
A in MTEP22 | C | West | ITCM | 21999 | 2022-08-24 | J1164 Generator Interconnection Network Upgrades | J1164 Generator Interconnection Network Upgrades | Magnolia 161 kV substation currently has no circuit breakers protecting the Magnolia to Elk 161 kV line and the Magnolia to Rock County 161 kV line. The Facilities Study for J1164 identified Network Upgrades and TOIF necessary for the interconnection of project J1164 to ITCM’s Magnolia 161 kV substation. Project J1164’s impact to the transmission system is currently being evaluated as part of the DPP 2018 April West Area Study, which has not been finalized pending results of an Affected System Study. | MN | MN | 2024-08-01 | To interconnect project J1164 to the ITC Midwest (“ITCM”) system at the interconnection customer’s requested point of interconnection, ITCM will upgrade Magnolia 161 kV substation to a 4 terminal ring bus configuration. The interconnection customer, MISO and ITCM entered into an Engineering and Procurement Agreement for initial design work for the Magnolia 161 kV expansion, and it is expected that a Generator Interconnection Agreement (“GIA”) will be entered into by the interconnection customer, MISO and ITCM soon. Network Upgrades and Transmission Owner Interconnection Facilities (“TOIF”) are expected to be constructed at Magnolia substation for project J1164, an 80 MW, solar-powered generating facility under a Generator Interconnection Agreement (“GIA”) as a condition of the project’s Interconnection Service. |  |  | ITC Midwest |  | GIP |  |  | 2024-08-01 | 2024-08-01 | 161 | 69 | Planned | 8833588
A in MTEP22 | B | East | ITCT | 15875 | 2021-09-24 | ITC_19_028 | Kentucky - Luzon 120 kV Sag Remediation | Completely remove the sag limit on the Kentucky – Luzon 120 kV line. | MI | MI | 2024-06-01 | The Kentucky – Luzon 120 kV line is projected to be overloaded for several shutdown-plus-contingency that involve the loss of the Brownstown – Swan Creek 120 kV line. The identified overloaded equipment on this circuit is the sag limit. The thermal violations are found in peak and off peak conditions. |  | Issue identified in MISO’s MTEP21 independent analysis and ITC’s internal assessment. Gen. Redisp found: turn on one Fermi peaker (ENFPKR1-2) at 16 MW can be an acceptable mitigation | ITC Transmission |  | BRP |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Proposed | 500000
A in MTEP22 | B | East | ITCT | 17999 | 2021-09-17 |  | Re-conductor Corktown - Waterman 120 kV UG | The proposed solution is to re-conductor approximately 3.7 miles of the Corktown – Waterman 120 kV underground cable utilizing 5000 Kcmil underground cable. | MI | MI | 2026-06-01 | The Corktown – Waterman 120 kV underground cable is projected to marginally overload. |  | Issue identified in MISO’s MTEP21 independent analysis and ITC’s internal assessment. | ITC Transmission |  | BRP |  |  | 2024-06-01 | 2024-06-01 | 120 | 0 | Proposed | 7000000
A in MTEP22 | B | East | ITCT | 20182 | 2022-08-19 |  | Northeast 120kV 55 MVAR Reactor | Install a 120 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Northeast 120 kV bus. | MI | MI | 2024-12-31 | The Northeast, Mack, Warren, Stephens and various 120 kV buses on ITCT system has been experienced high voltages during light load conditions and Real-time Operations has challenging mitigating the issues. The Power Factor (PF) was modified in the planning models to reflect the PF seen in real-time operations. |  |  | ITC Transmission |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 120 | 0 | Proposed | 1320000
A in MTEP22 | B | East | ITCT | 20183 | 2022-08-19 |  | Stephens 345kV 55 MVAR Reactor | Install a 345 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Stephens 345kV bus. | MI | MI | 2023-12-31 | The Northeast, Mack, Warren, Stephens and various 120 kV buses on ITCT system has been experienced high voltages during light load conditions and Real-time Operations has challenging mitigating the issues. The Power Factor (PF) was modified in the planning models to reflect the PF seen in real-time operations. |  |  | ITC Transmission |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 230 | 0 | Proposed | 3500000
A in MTEP22 | B | East | ITCT | 20185 | 2022-08-19 |  | Warren 120kV 55 MVAR Reactor | Install a 120 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Warren 120kV bus. | MI | MI | 2023-12-31 | The Northeast, Mack, Warren, Stephens and various 120 kV buses on ITCT system has been experienced high voltages during light load conditions and Real-time Operations has challenging mitigating the issues. The Power Factor (PF) was modified in the planning models to reflect the PF seen in real-time operations. |  |  | ITC Transmission |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 120 | 0 | Proposed | 1700000
A in MTEP22 | B | East | ITCT | 20186 | 2022-08-19 |  | Mack 120kV 55 MVAR Reactor | Install a 120 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Mack 120kV bus. | MI | MI | 2024-12-31 | The Northeast, Mack, Warren, Stephens and various 120 kV buses on ITCT system has been experienced high voltages during light load conditions and Real-time Operations has challenging mitigating the issues. The Power Factor (PF) was modified in the planning models to reflect the PF seen in real-time operations. |  |  | ITC Transmission |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 120 | 0 | Proposed | 1700000
A in MTEP22 | C | East | ITCT | 20525 | 2021-09-17 |  | ITCT Line Relocation Blanket | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI | MI | 2022-12-31 | ITCT has transmission lines and underground cables in road right of way, without easement. The State of Michigan and local municipalities have road improvement projects which require ITCT to relocation portions of our transmission lines, often with a very short time to comply. This blanket is for smaller projects (each less than $1 million) with in service dates too soon to run through the normal MTEP process. |  |  | ITC Transmission |  | Other |  | Other Local Needs | 2022-12-31 | 2022-12-31 | 345 | 120 | Proposed | 2000000
A in MTEP22 | C | East | ITCT | 21166 | 2021-09-17 |  | Maple - J1062 Generator Interconnection | Build a new 345kV 3 breaker substation cut-in from the Lemoyne - Majestic 345kV circuit, and removal of terminal equipment at Majestic 345kV substation. | MI | MI | 2023-06-01 | J1062 is a 150 MW Solar Power Plant connecting to the ITCT Lemoyne - Majestic 345 kV circuit in the DPP-2018-APR Cycle. |  |  | ITC Transmission |  | GIP |  |  | 2023-06-01 | 2023-06-01 | 345 | 0 | Planned | 16434520
A in MTEP22 | C | East | ITCT | 21726 | 2022-05-04 | ITC_21_029 | Warren 120kV Pos JJ Station Equipment Upgrade | Replace station equipment at Warren to meet or exceed 528 MVA (2540 Amps) | MI | MI | 2026-06-01 | The station equipment at Warren Pos JJ is projected to be overloaded for P21 contingency during peak load condition. |  | Issue identified in MISO’s MTEP21 independent analysis and ITC’s internal assessment. | ITC Transmission |  | BRP |  |  | 2026-06-01 | 2026-06-01 | 120 | 0 | Proposed | 160000
A in MTEP22 | C | East | ITCT | 21745 | 2022-05-03 | ITC_21_031 | Cato - Waterman 120 kV Re-conductor | The Cato – Waterman 120 kV underground cable is projected to overload for P11 and P6 contingencies during peak load. The limiting elements on this circuit are the cable conductor. | MI | MI | 2026-06-01 | The proposed solution is to re-conductor approximately 4.43 miles utilizing 1600MM2 CU XLPE underground cable. |  | Issue identified in MISO’s MTEP21 independent analysis and ITC’s internal assessment. | ITC Transmission |  | BRP |  |  | 2026-06-01 | 2026-06-01 | 120 | 0 | Proposed | 15000000
A in MTEP22 | C | East | ITCT | 21958 | 2021-09-17 | ITC_19_003 | Augusta 2 120kV PTS Additions | Install 2 new 120 kV, 1-way, full-load-break 2,000 A GOAB switches near the Augusta 2 Tap. | MI | MI | 2024-12-31 | Installing pole-top switches, or replacing them as appropriate, at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. This significantly reduces service interruptions to the customers during planned maintenance work or restoration from the aftermath extreme weather events. Even if an automatic load throw-over (ATO) scheme is present at a station which is tapped off two circuits, that customer or distribution station can still benefit from having pole top switches installed at the tap points on those circuits because in the event of a double circuit tower (DCT) outage, an ATO will not be able to restore service to the customer if both circuits are on the same structure. Installing pole top switches on those circuits will enable us to still serve that customer even during that scenario by sectionalizing the circuit. If nothing is done, this will reduce our ability to sectionalize the circuits with tapped customers and may increase restoration time to the tapped stations in the event of an outage. |  |  | ITC Transmission |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 120 | 0 | Proposed | 1300000
A in MTEP22 | C | East | ITCT | 22013 | 2021-09-17 |  | ITCT Pole Top Switch Additions/Replacement Program 2023 | Install or replace an existing pole top switch with a new 120 kV, 1-way full-load-break pole top switch at tap points. | MI | MI | 2023-12-31 | The ITCT system has many 120 kV load interconnection taps that do not have pole-top switches installed on either one or both sides of the tap or have switches that are not operable. Without pole-top switches, this reduces the flexibility to isolate faults or planned outages of a section of the line (for repair work or maintenance purposes. As a consequence, all distribution or industrial load that is tapped and served from the line will be out of service along with it until the faulted section can be repaired. Since there are no switches installed at these junctions or the switches are not operable, it is impossible to sectionalize a faulted part of the circuit to restore power to customers while the crew is working on bringing that section of the line back in-service again. The transmission circuits are often long transmission lines which have more exposure to weather related forces (e.g. ice, snow, wind, extreme temperatures, and lightning strikes). |  |  | ITC Transmission |  | Other |  | Reliability | 2023-12-31 | 2023-12-31 | 138 | 0 | Proposed | 2400000
A in MTEP22 | C | East | ITCT | 22016 | 2021-09-17 |  | 2025 ITCT Customer Interconnections | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $1 Million that have an in service date within the year 2025 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $1 Million a separate project will be submitted for approval. | MI | MI | 2025-12-31 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. These projects are strictly in response to customer interconnection requests. They are not being proposed to address any specific ITCT system reliability concerns. |  |  | ITC Transmission |  | Other |  | Load Growth | 2025-12-31 | 2025-12-31 | 120 | 0 | Proposed | 2000000
A in MTEP22 | C | East | ITCT | 22017 | 2021-09-17 |  | 2024 ITCTransmission Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | MI | 2024-12-31 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. |  |  | ITC Transmission |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 345 | 120 | Proposed | 37140000
A in MTEP22 | C | West | MDU | 20946 | 2021-09-15 |  | Poplar2 115/60 kV | Build a Poplar Oil Field 115/60 kV sub and a 115 kV line from the Poplar Trans sub to the Poplar Oil Field sub to tie into the 60 kV system near MDU's Poplar Oil Field load. | MT | MT | 2023-12-31 | Load growth; extend 115 kV to Poplar Oil Field to support load growth on the 60 kV system and mitigate 60 kV voltage violations under Poplar 60 kV line-end outage contingency or loss of existing 115/60 kV transformer at Poplar. | 20945-Poplar 115/60 kV Substation |  | Montana-Dakota Utilities Company |  | Other |  | Load Growth | 2024-12-31 | 2024-12-31 | 115 | 60 | Proposed | 8525000
A in MTEP22 | C | West | MDU | 21889 | 2022-08-25 |  | Hettinger 115/69/41.6 | Rebuild Hettinger Substation 115/69/41.6 due to age and condition | ND | ND | 2024-12-31 | Age and condition |  | This replaces project 15788 | Montana-Dakota Utilities Company |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 115 | 0 | Proposed | 6500000
A in MTEP22 | C | West | MDU | 21894 | 2021-09-13 |  | Retire Tioga 1 | Retire Tioga 1, expand Tioga 2 to move the 60 kV lines from Tioga 1 to Tioga 2 along with a 115/60 kV transformer, move 115 kV lines position in station and add another 115 kV breaker. | ND | ND | 2022-12-31 | Retire old sub and expand a newer substation |  |  | Montana-Dakota Utilities Company |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 115 | 60 | Planned | 7050000
A in MTEP22 | C | West | MEC | 21871 | 2022-04-07 | T91NQ | Sub E East Moline 69 kV Upgrades | Replace aged equipment at Sub E East Moline. Project includes installing a new control building, replacing 69 kV oil circuit breakers, and replacing 69 kV cap-and-pin switches and insulators. | IL | IL | 2024-12-31 | Lifecyle management of older equipment |  |  | MidAmerican Energy Company |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 69 | 0 | Planned | 7000000
A in MTEP22 | C | West | MEC | 21872 | 2022-04-07 | T92AB | Sub E East Moline-Sub 37 69 kV OPGW Installation | Install OPGW on the Sub E East Moline-Sub 37 69 kV Line | IL | IL | 2024-12-31 | Fiber path needed for communication and protective relaying |  |  | MidAmerican Energy Company |  | Other |  | Other Local Needs | 2024-12-31 | 2024-12-31 | 69 | 0 | Planned | 1000000
A in MTEP22 | C | West | MEC | 21873 | 2021-09-13 | T92AC, T92AD | Sub 39-Sub 28 161 kV OPGW Installation | Install OPGW on the 161 kV line from Sub 39-Sub 28 | IL | IL | 2023-12-31 | Fiber path needed for communication and protective relaying |  |  | MidAmerican Energy Company |  | Other |  | Other Local Needs | 2021-12-31 | 2023-12-31 | 161 | 0 | Planned | 700000
A in MTEP22 | C | West | MEC | 21874 | 2022-05-27 |  | Sub 17 Expansion to Add 345-161 kV Transformer | Convert Sub 17 161 kV yard to a ring bus. Loop the Sub 49-Beaver Channel 161 kV line into Sub 17. Add a new short 345 kV line connecting Cordova and Sub 17 and a new 345-161 kV transformer at Sub 17. | IL | IL | 2024-07-01 | Local 161 kV bus voltages identified as being below planning criteria minimum for NERC TPL-001 Category P6 N-1-1 contingencies in the MTEP21 reliability assessment. |  |  | MidAmerican Energy Company |  | BRP | Not Shared |  | 2024-12-31 | 2024-12-31 | 345 | 161 | Planned | 23000000
A in MTEP22 | C | West | MEC | 21893 | 2021-09-15 |  | Neal North 161-69 kV Transformer Replacement | Replace Neal North 161-69 kV Transformer AC2 (83.3 MVA unit) which recently failed with a spare unit. Purchase a new 161-69 kV transformer at Neal North as a spare unit. | IA | IA | 2021-12-31 | The Neal North 161-69 kV Transformer AC2 (83.3 MVA unit) recently failed and is in the process of being replaced. The replacement transformer will be a spare 161-69 kV, 83.3 MVA unit with an load tap changer (LTC). The replacement of Neal North transformer with spare unit and purchase of new spare transformer will be completed by the end of this year. |  |  | MidAmerican Energy Company |  | Other |  | Reliability | 2021-09-30 | 2021-12-31 | 161 | 69 | Planned | 1600000
A in MTEP22 | C | West | MEC | 21895 | 2021-09-15 |  | Sycamore 161-69 kV Transformer Replacement | Replace the failed 161-69 kV transformer at Sycamore substation with a spare unit. Purchase a new 161-69 kV spare transformer at Sycamore substation. | IA | IA | 2022-09-30 | The 161-69 kV transformer at Sycamore substation failed recently and is in the process of being replaced. The transformer will be replaced with a spare unit of same size. A new 161-69 kV spare transformer will be purchased at Sycamore substation. |  |  | MidAmerican Energy Company |  | Other |  | Reliability | 2021-12-31 | 2022-09-30 | 161 | 69 | Planned | 3000000
A in MTEP22 | C | West | MEC | 21896 | 2021-09-13 |  | NE 94th Avenue 161-13.2 kV Substation | Construct NE 94th Ave 161-13.2 kV substation and taps | IA | IA | 2023-06-01 | Reliability improvement and serve load |  |  | MidAmerican Energy Company |  | Other |  | Load Growth | 2023-06-01 | 2023-06-01 | 161 | 13.2 | Planned | 6700000
A in MTEP22 | C | West | MEC | 21897 | 2021-09-13 |  | Berwick 161-13.2 kV Substation | Construct Berwick 161-13.2 kV substation and taps | IA | IA | 2025-06-01 | To serve growing load. |  |  | MidAmerican Energy Company |  | Other |  | Load Growth | 2025-06-01 | 2025-06-01 | 161 | 13.2 | Planned | 6700000
A in MTEP22 | C | West | MEC | 21898 | 2021-09-13 |  | Increase Bus Withstand Capabiities | At Raun 161 kV, Neal North 161 kV, CBEC 161 kV, Sycamore 161 kV and Sycamore 69 kV, replace insulators, install new bus supports and/or replace bus to increase bus withstand capabilities | IA | IA | 2023-12-01 | Fault current can exceed existing bus capabillities. |  |  | MidAmerican Energy Company |  | Other |  | Reliability | 2023-12-01 | 2024-12-01 | 161 | 69 | Planned | 6500000
A in MTEP22 | C | West | MEC | 21901 | 2021-09-13 |  | Raun Substation: 345 kV Switch Replacements | Replace 10 switches due to condition | IA | IA | 2022-12-01 | Reliability improvement |  |  | MidAmerican Energy Company |  | Other |  | Age and Condition | 2022-12-01 | 2022-12-01 | 345 | 0 | Planned | 900000
A in MTEP22 | C | West | MEC | 21902 | 2022-01-26 |  | Anthon Substation | Construct a new 69-12.47 kV distribution substation and associated 69 kV line work. | IA | IA | 2023-12-01 | Serve load |  |  | MidAmerican Energy Company |  | Other |  | Load Growth | 2023-12-01 | 2023-12-01 | 69 | 0 | Proposed | 1500000
A in MTEP22 | C | West | MEC | 21904 | 2022-01-26 |  | Sioux Center Substation | Construct a new 69-12.47 kV distribution substation and associated 69 kV line work. | IA | IA | 2023-12-01 | Serve load |  |  | MidAmerican Energy Company |  | Other |  | Load Growth | 2023-12-01 | 2023-12-01 | 69 | 0 | Proposed | 600000
A in MTEP22 | C | West | MEC | 21906 | 2021-09-13 |  | Sheldon-Boyden 69 kV Line Uprate | Replace structures and jumpers on Sheldon-Boyden 69 kV line to increase line rating | IA | IA | 2022-12-01 | Reliability improvement |  |  | MidAmerican Energy Company |  | Other |  | Age and Condition | 2022-12-01 | 2022-12-01 | 69 | 0 | Planned | 600000
A in MTEP22 | C | West | MEC | 21907 | 2022-01-26 |  | Replace structures on Templeton-Audubon North-Exira 69 kV line to increase line rating | Replace terminal equipment at Audubon North and replace structures on Templeton-Audubon North-Exira 69 kV line to increase the line rating | IA | IA | 2023-06-01 | Reliability improvement |  |  | MidAmerican Energy Company |  | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 69 | 0 | Proposed | 1650000
A in MTEP22 | C | West | MEC | 21908 | 2022-05-26 |  | Carroll County-Auburn-Sherwood 69 kV Line Rebuild & Terminal Upgrades | Rebuild 69 kV lines from Carroll County to Auburn and Auburn to Sherwood and replace line structures. | IA | IA | 2024-12-31 | Several line structure issues have been found during annual inspection. Also this facility gets congested occasionally. The project will fix the issues in line structures and will relive the congestion as well. |  |  | MidAmerican Energy Company |  | Other |  | Age and Condition | 2024-12-01 | 2024-12-01 | 69 | 0 | Planned | 7700000
A in MTEP22 | C | West | MEC | 21909 | 2021-09-13 |  | Sac City Switching Station & Rebuild of Sac County-Odebolt-Schaller 69 kV Line | Construct new Sac City switching station to interconnect two MidAmerican 69 kV lines and one Corn Belt 69 kV line | IA | IA | 2024-12-01 | Low voltage can occur for loss of Sac County 161-69 kV Transformer |  |  | MidAmerican Energy Company |  | BRP |  |  | 2024-12-01 | 2024-12-01 | 69 | 0 | Planned | 20000000
A in MTEP22 | C | West | MEC | 21910 | 2021-09-14 |  | Hills 345 kV Equipment Replacements | Replace 345 kV Breakers and switches at Hills substation due to condition and operational issues. Replace relaying on two Hills lines and remote ends. The project will be completed in conjunction with MTEP Project 20121 | IA | IA | 2022-12-31 | Reliability improvement |  |  | MidAmerican Energy Company |  | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 345 | 0 | Planned | 5400000
A in MTEP22 | C | West | MEC | 21911 | 2022-01-26 |  | IC Enron Substation: 161 kV Line Switch Additions | Add line switches at IC Enron Substation. | IA | IA | 2022-12-31 | Reliability Improvement |  |  | MidAmerican Energy Company |  | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 161 | 0 | Planned | 300000
A in MTEP22 | C | West | MEC | 21912 | 2021-09-13 |  | Substation J 161 kV Capacitor Bank Replacement | Replace 161 kV Capacitor due to condition and operational failures. | IA | IA | 2022-12-31 | Reliability improvement |  |  | MidAmerican Energy Company |  | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 161 | 0 | Planned | 500000
A in MTEP22 | C | West | MEC | 21913 | 2021-09-13 |  | Northgate Substation: Ring bus expansion and 161 kV tie line to ITCM’s Rose Hollow Substation | Expand Northgate Substation to a ring bus configuration and build 161 kV tie line from Northgate Substation to ITCM owned Rose Hollow Substation | IA | IA |  | Reliability improvement |  |  | MidAmerican Energy Company |  | Other |  | Reliability | 2024-12-01 | 2024-12-01 | 161 | 0 | Planned | 3500000
A in MTEP22 | C | West | MEC | 21914 | 2022-06-23 |  | Butler 161-69 kV Transformer | Install 161-69 kV, 125 MVA Transformer at Butler Substation to accommodate a networked 69 kV system between MidAmerican’s Butler, New Hartford and Shell Rock Substations and Corn Belt’s Donald Feldman Switching Station. MTEP21. The project also include upgrading 34.5 kV lines from Butler to New Hartford and New Hartford to Shell Rock to 69 kV lines. | IA | IA | 2024-12-01 | Satisfy MidAmerican's 69 kV n-1-1 voltage reliability criteria |  |  | MidAmerican Energy Company |  | BRP |  |  | 2024-12-01 | 2024-12-01 | 161 | 69 | Planned | 25700000
A in MTEP22 | C | West | MEC | 22305 | 2021-12-01 |  | Lakefield Jct to Obrien 345 kV Line Structure Replacements | The project will replace some line structure on MidAmerican owned part of Lakefield to Obrien 345 kV line. This project will increase the line rating of MidAmerican portion of Lakefield to Obrien 345 kV. | IA | IA |  | The Lakefield to Obrien 345 kV line congestion was studied as part of MidAmerican's local stakeholder planning process using PROMOD models. The project show good benefits to MidAmerican LBA. |  |  | MidAmerican Energy Company |  | Other |  | Other Local Needs | 2022-12-31 | 2022-12-31 | 345 | 0 | Planned | 2200000
A in MTEP22 | C | West | MEC | 22746 | 2022-05-23 |  | Overland Trail to Fallow Avenue 345 kV line structure replacements | Replace five line structures on Overland Trail to Fallow avenue 345 kV line. | IA | IA | 2022-12-31 | These structures were damaged due to storm and will be replaced by the end of year 2022. |  |  | MidAmerican Energy Company |  | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 345 | 0 | Planned | 1250000
A in MTEP22 | C | West | MEC | 22747 | 2022-05-23 |  | Interstate Containment Structures Installation Blanket | Based on recent experience from storms and its effects on transportation, installation of containment structures on either side of heavily traveled interstate and similar highway crossings is planned. The structures will reduce the likelihood of failure. If a severe storm occurs, the containment structures will reduce cascading and enable faster cleanup of the highway because the conductor can be cut free as it will not be under high tension. | IA | IA | 2022-12-31 | The wood H-frame or monopole structures will be replaced with steel structures. New structures are planned at two 345 kV crossings, three 161 kV crossing, and five 69 kV crossings. |  |  | MidAmerican Energy Company |  | Other |  | Other Local Needs | 2022-12-31 | 2022-12-31 | 345 | 0 | Planned | 13000000
A in MTEP22 | C | West | MEC | 23366 | 2022-08-24 |  | Powell Creek 161-13 kV Substation | Construct a new Powell Creek 161-13 kV distribution substation tapping the Buena Vista-Sac County 161 kV line. | IA | IA | 2024-01-02 | Serve new customer load |  |  | MidAmerican Energy Company |  | Other |  | Load Growth | 2024-01-02 | 2024-01-02 | 161 | 13 | Proposed | 5500000
A in MTEP22 | C | West | MEC | 23480 | 2022-08-24 |  | Substation 18: Replace Failed 161/69 kV Transformer 1 | Replace transformer that was failed in May 2022. Purchase replacement spare transformer for the unit being replaced at Sub. 18 | IA | IA | 2023-12-31 | Replace failed transformer at Sub. 18 |  |  | MidAmerican Energy Company |  | Other |  | Age and Condition | 2022-09-30 | 2023-12-31 | 161 | 69 | Planned | 3400000
A in MTEP22 | C | West | MEC | 23516 | 2022-08-24 | H01DE, T92NP | Enterprise Way South Substation | Construct new 161-13.2 kV distribution substation bisecting the existing Sub 56-Enterprise Way 161 kV line. | IA | IA | 2024-09-01 | Serve new customer load |  |  | MidAmerican Energy Company |  | Other |  | Load Growth | 2024-09-01 | 2024-09-01 | 161 | 0 | Proposed | 3500000
A in MTEP22 | B | East | METC | 15910 | 2021-09-29 | METC_18_072 | Marquette - Bingham 138 kV Rebuild | Rebuild 18.76 miles of the Marquette – Bingham circuit using 954 ACSR conductor with double-circuit steel structures. | MI | MI | 2025-12-31 | The Marquette – Bingham 138 kV Rebuild project is being re-submitted to MTEP22 due to the age and condition of the circuit. This project was first submitted to MTEP19 and was recommended to Appendix B by MISO. Based on the latest METC circuit rating data (updated in March 2020), this line is the 17th worst performing circuit (top 20 worst circuits) on the system. The Marquette – Bingham 138 kV line outages effect three (3) major customers: Ventra (American Bumper Sub), MWC (formerly Glanbia, Technical Drive Sub Ckt #1) and Proliant (Technical Drive Ckt #2). The sentiment of these customers is that they feel there are frequent outages. The Technical Drive substation customers have experienced two major outages since the sub was built in early 2020. |  | MISO did not see the need for this project in MTEP19 assessment. | METC |  | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 138 | 0 | Proposed | 27600000
A in MTEP22 | C | East | METC | 20906 | 2022-04-11 |  | Styx - J984 Generator Interconnection | Build a new 345kV three breaker ring bus station and cut-in the Murphy - Nelson Road 345kV line. Remote relay upgrades at Murphy 345kV and Nelson Road 345kV substations, as well as jumper work at Slate 345kV substation. | MI | MI | 2023-01-31 | J984 is a 200MW Wind Power Plant in the DPP-2018-April Cycle connecting to the METC Murphy - Nelson Road 345 kV circuit. |  |  | METC |  | GIP |  |  | 2023-01-31 | 2023-01-31 | 345 | 0 | Planned | 15319904
A in MTEP22 | C | East | METC | 20965 | 2021-09-17 |  | METC Line Relocation Blanket | Relocation portions of transmission lines located in public right of way at the government entity's mandate. | MI | MI | 2022-12-31 | ITCT has transmission lines and underground cables in road right of way, without easement. The State of Michigan and local municipalities have road improvement projects which require ITCT to relocation portions of our transmission lines, often with a very short time to comply. This blanket is for smaller projects (each less than $1 million) with in service dates too soon to run through the normal MTEP process. |  |  | METC |  | Other |  | Other Local Needs | 2022-12-31 | 2022-12-31 | 345 | 138 | Proposed | 2000000
A in MTEP22 | C | East | METC | 21145 | 2022-01-11 |  | J996 Generator Interconnection | Build a new 138 kV, 3 breaker ring switching station cut in from the METC Beecher - Morocco 138 kV circuit. | MI | MI | 2023-03-31 | J996 is a 80 MW Solar Power Plant that requested to interconnect to the METC Beecher - Morocco 138 kV circuit in the DPP-2018-APRIL cycle |  |  | METC |  | GIP |  |  | 2023-03-31 | 2023-03-31 | 138 | 0 | M3_Long Lead Materials | 6618732
A in MTEP22 | C | East | METC | 21146 | 2021-09-17 |  | J1172 Generator Interconnection | Build a new 138 kV, 3 breaker ring switching station cut in from the METC Dort - Garfield 138 kV circuit. | MI | MI | 2023-11-15 | J1172 is a 50 MW Solar Power Plant that requested to interconnect to the METC Dort - Garfield 138 kV circuit in the DPP-2018-APRIL cycle. |  |  | METC |  | GIP |  |  | 2023-11-15 | 2023-11-15 | 138 | 0 | M3_Long Lead Materials | 10889470
A in MTEP22 | C | East | METC | 21185 | 2021-09-17 |  | Muskrat - J1043 Generator Interconnection | Build a new three breaker ring bus station and cut-in the Vergennes - Nelson Road 345kV line. Install remote relay upgrades at Vergennes 345kV and Nelson Road 345kV substations. | MI | MI | 2024-05-31 | J1043 is a Wind farm capable of 374.4 MW of generation in the DPP-2018-April cycle connecting to the METC Vergennes - Nelson Road 345kV circuit |  |  | METC |  | GIP |  |  | 2024-05-31 | 2024-05-31 | 345 | 0 | M2a_Pre-Project Approval | 9585454
A in MTEP22 | C | East | METC | 21445 | 2021-09-17 |  | Donaldson Creek - White Lake 138 kV Rebuild (J1071) | Rebuild approximately 18.43 miles of the 336 ACSR conductor utilizing 954 ACSR on standard 138 kV double circuit structures with OPGW. Upgrade 336 ACSR Line Drop and 336 ACSR Bus at White Lake Position 188, as well as the 336 ACSR line drop at Donaldson Creek position BM11 to meet or exceed the summer emergency rating of the new conductor. | MI | MI | 2024-06-01 | The MISO East 2019 DPP cycle determined that the Donaldson Creek - White Lake 138kV line is limited by the 336 ACSR conductor as a result of the J1071 generation interconnection. |  |  | METC |  | GIP |  |  | 2024-06-01 | 2024-06-01 | 138 | 0 | M3_Long Lead Materials | 30142027
A in MTEP22 | C | East | METC | 21446 | 2021-09-17 |  | J1071 Generator Interconnection | Install 138kV breaker at position 13W8. Install 138kV disconnect switches at positions 13W8 & 13M6. | MI | MI |  | J1071 is a 100 MW Solar Power Plant that requested to interconnect to the METC Donaldson Creek 138kV substation in the DPP-2018-APRIL cycle. |  |  | METC |  | GIP |  |  | 2023-12-31 | 2023-12-31 | 138 | 0 | M3_Long Lead Materials | 1159555
A in MTEP22 | C | East | METC | 21485 | 2022-05-17 |  | Lawndale - Murphy 138kV Sag Remediation | The proposed solution is to remove sag limits on the Lawndale to Murphy 138 kV line to conductor limit. | MI | MI | 2025-12-31 | Lawndale to Murphy 138 kV line is projected to be overloaded for P1, P2, P3, P6, and P7 contingencies in peak and off-peak scenarios. This consequently causes the Lawndale to Murphy 138kV line section to exceed its summer emergency limit. The overloaded equipment identified on this circuit is the overhead conductor, 795 ACSR 26/7. |  | MISO's MTEP21 independent analysis identified issue on Lawndale [256193] – Murphy [256499] Ckt 1. | METC |  | BRP |  |  | 2025-12-31 | 2025-12-31 | 138 | 0 | Proposed | 931000
A in MTEP22 | C | East | METC | 21505 | 2021-09-22 |  | Houghton Lake Interconnection | Create a three-breaker ring bus switching station. Install three 138kV breakers, buswork, and associated disconnects. Loop in the METC Bard Rd - Higgins 138kV circuit to the new switching station. Connect CE Houghton Lake Substation to new switching station. | MI | MI | 2025-06-01 | Consumers Energy has provided notification for a new 138kV substation to be located approximately 12.5 miles west of the METC Bard Rd - Higgins point of interconnection. Houghton Lake station will serve 13.5 MW and 7.9 MVAR of load transferred from the CE Houghton Heights Substation. The new switching station is needed to service the new CE substation. |  |  | METC |  | Other |  | Load Growth | 2025-06-01 | 2025-06-01 | 138 | 0 | M2a_Pre-Project Approval | 6161060
A in MTEP22 | C | East | METC | 21706 | 2022-04-11 |  | Mill Creek Interconnection | Install tap pole and two 1-way switches to facilitate the Mill Creek tap on the Mcgulpin-Riggsville line. | MI | MI | 2023-06-30 | WPSC has provided a formal interconnection request for transmission service tapped from the Mcgulpin - Riggsville 138kV line. WPSC will construct Mill Creek substation as a 138/13.08 kV distribution station with a single transformer and high-side protection. Mill Creek station will serve 1.62 MW and 0.7 MVAR of new load and 1.39 MW of transferred load from the WPSC Cheboygan Station. |  |  | METC |  | Other |  | Load Growth | 2023-06-30 | 2023-06-30 | 138 | 0 | M2a_Pre-Project Approval | 1822800
A in MTEP22 | C | East | METC | 21890 | 2022-03-01 | METC_21_067 | Gallagher - Ogemaw 138 kV Sag Remediation | Remediate sag on the 336 ACSR conductor on the Gallagher to Ogemaw 138 kV circuit up to at least 60 MVA summer emergency rating. | MI | MI | 2026-06-01 | The Gallagher - Ogemaw 138 kV circuit is projected to be overloaded for P2, P5, and P6 contingencies during peak load conditions. The identified overloaded equipment on this circuit is the sag limit on the Gallagher – Ogemaw 138 kV sections. |  |  | METC |  | BRP |  |  | 2026-06-01 | 2026-06-01 | 138 | 0 | Proposed | 660000
A in MTEP22 | C | East | METC | 21945 | 2022-05-10 |  | Parr Road-Whiting 138kV Rebuild | Rebuild approximately 12 miles from Parr Rd - Tangent (J875 Generator Interconnection) and approximately 28.6 miles from Raisin Tap - Whiting on 138kV future double circuit steel poles with 1431 ACSR conductor with OPGW (coordinating with J875 Generator Interconnection project). | MI | MI | 2025-05-15 | The METC system relies heavily on both wood poles and steel lattice towers, many of which are 70 years of age or older. METC transmission structures may experience increasing failure rates that could degrade reliability on the system. Maintenance, partial rebuild, or complete rebuild activities need to be undertaken on aging circuits throughout the system in order to maintain acceptable levels of system reliability. ITC performed an analysis in 2020 to assess the METC and ITCT circuits based on 4 main factors: recent outage history, current maintenance needs, age and type of structures and circuit importance. The objective of the analysis was to assist ITC staff in identifying circuits that should be considered for rebuilding. While there is not a specific criteria used to determine when these assets reach their end of life, utilizing the factors described above helps to prioritize replacement of aging infrastructure across the ITC systems. Based on that criteria, the Parr Rd - Whiting 138kV line is being recommended for a full rebuild. Currently based on the 2020 analysis, this line is in the top 10 worst performance circuit on the ITC systems. Upon further investigation, approximately 80% of this circuit is found to be structurally overloaded. This can lead to reduced life expectancy, more frequent maintenance, and pose an elevated safety risk particularly during reactive maintenance and system restoration. Additionally, this compromised design renders the circuit inflexible for marginal improvements and limited preventative maintenance. METC is recommending this circuit be rebuilt in order to maintain acceptable levels of system performance and to improve system reliability. Most poles are expected to reach their maximum life span in the next 5-10 years. Furthermore, approximately 80% of the circuit is found to be structurally overloaded. |  |  | METC |  | Other |  | Reliability | 2025-05-15 | 2025-05-15 | 138 | 0 | Proposed | 53580500
A in MTEP22 | C | East | METC | 21947 | 2021-09-29 | METC_19_004 | Roedel Road 138 kV PTS Replacements | The proposed solution is to replace 3185 and 3198 pole top switches with 2 new 138kV, 1-way, full-load-break 2,000 A GOAB switch near the Roedel Road Tap. | MI | MI | 2024-12-31 | Installing pole-top switches, or replacing them as appropriate, at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. This significantly reduces service interruptions to the customers during planned maintenance work or restoration from the aftermath extreme weather events. Even if an automatic load throw-over (ATO) scheme is present at a station which is tapped off two circuits, that customer or distribution station can still benefit from having pole top switches installed at the tap points on those circuits because in the event of a double circuit tower (DCT) outage, an ATO will not be able to restore service to the customer if both circuits are on the same structure. Installing pole top switches on those circuits will enable us to still serve that customer even during that scenario by sectionalizing the circuit. If nothing is done, this will reduce our ability to sectionalize the circuits with tapped customers and may increase restoration time to the tapped stations in the event of an outage. |  |  | METC |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 1200000
A in MTEP22 | C | East | METC | 21952 | 2021-09-17 | METC_21_013 | Dutton 138 kV PTS Replacements | Replace 3004, 3017 and 3493 pole top switches with 3 new 138kV, 1-way, full-load-break 2,000 A GOAB switch near the Dutton Tap. | MI | MI | 2024-12-31 | Installing pole-top switches, or replacing them as appropriate, at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. This significantly reduces service interruptions to the customers during planned maintenance work or restoration from the aftermath extreme weather events. |  |  | METC |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 1700000
A in MTEP22 | C | East | METC | 21984 | 2021-09-21 |  | METC Pole Top Switch Additions/Replacement Program 2023 | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. | MI | MI | 2023-12-31 | The METC system has many 138 kV load interconnection taps that do not have pole-top switches installed on either one or both sides of the tap or have switches that are not operable. Without pole-top switches, this reduces the flexibility to isolate faults or planned outages of a section of the line (for repair work or maintenance purposes. As a consequence, all distribution or industrial load that is tapped and served from the line will be out of service along with it until the faulted section can be repaired. Since there are no switches installed at these junctions or the switches are not operable, it is impossible to sectionalize a faulted part of the circuit to restore power to customers while the crew is working on bringing that section of the line back in-service again. The transmission circuits are often long transmission lines which have more exposure to weather related forces (e.g. ice, snow, wind, extreme temperatures, and lightning strikes). |  |  | METC |  | Other |  | Reliability | 2023-12-31 | 2023-12-31 | 138 | 0 | Proposed | 2400000
A in MTEP22 | C | East | METC | 21990 | 2021-09-17 | METC_21_062 | Cut Iosco – Karn into Twining 138 kV | Cut the Iosco – Karn 138 kV circuit into the Twining 138 kV substation. This will require expand the Twining 138 kV substation and constructing approximately 0.15 miles of new right of way to bring the line into the substation. | MI | MI | 2026-06-01 | This project aims to increase reliability and address operational issues in Northern Michigan. The Iosco – Karn 138 kV circuit is 82 mile long and can only be safely removed from service during off peak times. Taking Iosco – Karn out of service can only be performed outside of summer months due to area voltages and overloads on the CE 46kV system. Splitting this line in half would reduce the number of required outages to perform maintenance. If at any time the line is lost for any reason during the summer, METC is in an extreme rush to return the line to service. Splitting this circuit in half would provide operational flexibility and increase reliability. The Twining substation also struggles with taking outages during the summer peak load. This project would provide more connections at the station for operational flexibility when taking outages. |  |  | METC |  | Other |  | Reliability | 2026-06-01 | 2026-06-01 | 138 | 0 | Proposed | 4100000
A in MTEP22 | C | East | METC | 21993 | 2021-09-17 |  | METC Pole Top Switch Additions/Replacement Program 2024 | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. | MI | MI | 2024-12-31 | The METC system has many 138 kV load interconnection taps that do not have pole-top switches installed on either one or both sides of the tap or have switches that are not operable. Without pole-top switches, this reduces the flexibility to isolate faults or planned outages of a section of the line (for repair work or maintenance purposes. As a consequence, all distribution or industrial load that is tapped and served from the line will be out of service along with it until the faulted section can be repaired. Since there are no switches installed at these junctions or the switches are not operable, it is impossible to sectionalize a faulted part of the circuit to restore power to customers while the crew is working on bringing that section of the line back in-service again. The transmission circuits are often long transmission lines which have more exposure to weather related forces (e.g. ice, snow, wind, extreme temperatures, and lightning strikes). |  |  | METC |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 2400000
A in MTEP22 | C | East | METC | 21995 | 2021-09-17 |  | 2025 METC Customer Interconnections | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $1 Million that have an in service date within the year 2025 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $1 Million a separate project will be submitted for approval | MI | MI | 2025-12-31 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. These projects are strictly in response to customer interconnection requests. They are not being proposed to address any specific ITCT system reliability concerns. |  |  | METC |  | Other |  | Load Growth | 2025-12-31 | 2025-12-31 | 138 | 0 | Proposed | 2000000
A in MTEP22 | C | East | METC | 22000 | 2021-09-17 |  | 2024 METC Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | MI | 2024-12-31 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. |  |  | METC |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 39400000
A in MTEP22 | C | East | METC | 22001 | 2021-09-17 |  | Westwood 138 kV Interconnection | Install a 138 kV breaker and associated equipment at Plum station to accommodate Wolverine’s interconnection request. | MI | MI | 2024-12-31 | Wolverine Power Cooperative requests for a new 138 kV interconnection to METC’s Plum station. |  |  | METC |  | Other |  | Load Growth | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 3700000
A in MTEP22 | C | East | METC | 22020 | 2021-09-17 |  | Leoni – Parr Rd 138kV Rebuild | Rebuild approximately 19 miles from Leoni to Parr Rd utilizing 1431 ACSR on standard 138 kV double circuit steel poles with OPGW. | MI | MI | 2025-12-31 | The majority (approximately 80%) of the Leoni - Parr Rd 138 kV circuit contains structures that are 70 years of age and have reached their end of life. Approximately 20% of those structures is tagged for replacement. The most recent inspection determined that several structures were marked “urgent” for replacements (needed ASAP or within 2 years) due to the amount of internal decay found. Furthermore, an investigation on the conditions of the structures determined that over 65% of the circuit contains structures that are structurally overloaded. Structures that are overloaded can lead to reduce life expectancy, more frequent maintenance, and pose an elevated safety risk particularly during reactive maintenance and system restoration. Additionally, this compromised design renders the circuit inflexible for marginal improvements and limited preventative maintenance. Therefore, METC recommends that this circuit be rebuilt to maintain acceptable levels of system reliability and performance. |  |  | METC |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 138 | 0 | Proposed | 32630000
A in MTEP22 | C | East | METC | 22021 | 2021-09-17 |  | Chopin – Dupont – White Lake 138kV Rebuild | Rebuild approximately 21 miles of the Chopin – Dupont – White Lake 138 kV Circuit from around structure 003F410 to Dupont utilizing 954 ACSR conductor on standard 138 kV double circuit structures with OPGW and relocate Cobb - White Lake and Dupont White Lake lines to the other side of the new 138 kV standard structures utilizing 954 ACSR conductor. | MI | MI | 2025-12-31 | Cobb – Dupont – White Lake 138 kV Approximately 70% of the structures on the Cobb – Dupont – White Lake 138 kV circuit consists of wood pole structures from its original construction of 1962 and is at or approaching its end of life. About 35% of these structures are slated to be replaced. Furthermore, as much as 67% of the structures in this circuit were identified to be structurally overloaded. Cobb – White Lake 138 kV Approximately 90% of the structures on the Cobb – White Lake 138 kV circuit consists of wood pole structures from its original construction of 1953 and is at or approaching its end of life. About 34% of these structures are slated to be replaced. Furthermore, as much as 87% of the structures in this circuit were identified to be structurally overloaded Structures that are overloaded can lead to reduce life expectancy, more frequent maintenance, and pose an elevated safety risk particularly during reactive maintenance and system restoration. Additionally, this compromised design renders the circuit inflexible for marginal improvements and limited preventative maintenance. Furthermore, many of the structures between the two circuits are in extremely poor conditions (See example pictures in the “Other Project Justification” section below). Therefore, METC recommends that these circuits be rebuilt in order to maintain acceptable levels of system reliability and performance. Since extensive replacements are necessary on both circuits, METC determined the best path forward is to rebuild one circuit with double circuit structures and place the other circuit on the empty side. |  |  | METC |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 138 | 0 | Proposed | 39018000
A in MTEP22 | C | East | METC | 22586 | 2022-08-19 |  | Buskirk - New CE Interconnection | METC to construct a new 138 kV switching station, Buskirk, with three 138 kV breakers in a ring-bus configuration, expandable for a fourth line exit, and cut the Buck Creek-Hazelwood 138 kV line in. | MI | MI | 2024-12-31 | Consumers Energy requested to interconnect a new 138/46 kV bulk power substation (Buskirk), proposed to be located adjacent to the existing Titus Lake substation. Consumers Energy plans to retire and decommission Wayland 138/46 kV bulk power substation once Buskirk is energized. |  |  | METC |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 7800000
A in MTEP22 | C | East | METC | 22627 | 2022-08-11 | METC_21_086 | Day - New WPSC Interconnection | Tap the Deja Jct. – Derby Jct. section of Eureka – Vestaburg 138kV line, approximately 2.5 miles West of Deja Tap. Transmission tap will be ~ 4 miles long. Install tap pole at the tap location, install two new 138 kV, 1-way, full-load-break 2000 A. | MI | MI | 2024-06-01 | WPSC interconnection request for transmission service tapped from the Deja Jct. – Derby Jct. section of Eureka – Vestaburg 138kV line. WPSC will construct Day substation as a distribution station with a single transformer and associated high-side protection. Wolverine has submitted the following MTEP project into the portal database for the WPSC owned portion of facilities: Day Interconnection – MTEP21 Target A, project #21665 |  |  | METC |  | Other |  | Load Growth | 2024-06-01 | 2024-06-01 | 138 | 0 | Proposed | 1132000
A in MTEP22 | C | East | METC | 23246 | 2022-08-10 | METC_22_032 | CE - Riverbend Tap (Saginaw River - Twining 138 kV) | Install a tap pole and two 1-way, 2000 Amp switches near structure #229 on the Saginaw River-Twining 138 kV line to connect Consumer Energy’s new Riverbend substation. | MI | MI | 2023-12-31 | Consumers Energy requested to tap METC's Saginaw-Twining 138 kV line to connect its new Riverbend substation. The new Riverbend substation will serve 4.25 MW load, 1.35 MW of it is being transferred from the existing Bessinger substation (46kV). |  |  | METC |  | Other |  | Load Growth | 2023-12-31 | 2023-12-31 | 138 | 0 | M2a_Pre-Project Approval | 1160000
A in MTEP22 | B | West | MP | 17868 | 2021-09-03 | Duluth Loop 115 kV Project | Duluth Loop 115 kV Project | Construct new 115 kV lines: Hilltop - Haines Road 115 kV and Haines Road - Ridgeview 115 kV Combine existing Arrowhead - Haines Road 115 kV and Haines Road - Swan Lake 115 kV lines to create Arrowhead - Swan Lake 115 kV Line Expand Ridgeview Substation to a ring bus which will allow 2 additional transmission line connections Add 115 kV line entrance at Hilltop and add a breaker at Haines Road | MN | MN | 2026-12-31 | Voltage collapse for loss of connection to Arrowhead Substation, thermal overloads on Arrowhead - Colbyville 115 kV for loss of Arrowhead - Haines Road 115 kV and vice versa |  |  | Minnesota Power (Allete, Inc.) |  | BRP |  |  | 2026-12-31 | 2026-12-31 | 115 | 0 | Proposed | 46900000
A in MTEP22 | B | West | MP | 18058 | 2021-09-03 |  | Square Butte - Arrowhead HVDC Line Hardening | Structure replacements to improve HVDC line resiliency and restorability at critical locations, including transportation and infrastructure crossings. | ND | MN | 2025-12-31 | Resiliency |  |  | Minnesota Power (Allete, Inc.) |  | Other |  | Reliability | 2023-12-31 | 2027-12-31 | 250 | 0 | Proposed | 14000000
A in MTEP22 | C | West | MP | 20074 | 2022-04-05 | Two Islands Switching Station | Two Islands 115 kV Project | Construction of new 115 kV switching station near the existing Tac Harbor Substation. Route North Shore-Tac Harbor and Mesaba Junction-Tac Harbor Ckt #1 & Ckt #2 into the new switching station. One capacitor bank will be added to the switching station and it will connect to a new GRE 115/69 kV Two Islands Substation | MN | MN | 2024-12-31 | Safety, expandability, and outage constraint concerns with the existing Tac Harbor substation design. |  |  | Minnesota Power (Allete, Inc.) |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 115 | 0 | Proposed | 14100000
A in MTEP22 | C | West | MP | 20077 | 2022-01-19 | Hilltop 230 kV Reliability Project | Hilltop 230 kV Reliability Project | Upgrade Hilltop 1TR to 373 MVA base 230/115 kV transformer. Add 230 kV breaker to high side of transformer. Disconnect Hilltop Tap from 3-Terminal 230 kV line and extend this tap 0.7 Miles to a new line entrance at Arrowhead 230 kV. | MN | MN | 2024-12-31 | Additional transformation capacity needed at Hilltop. Breaking up the existing 3-terminal 230 kV line connected to Hilltop will resolve existing relaying and reliability concerns. |  |  | Minnesota Power (Allete, Inc.) |  | BRP |  | Reliability | 2024-12-31 | 2024-12-31 | 230 | 115 | Proposed | 13100000
A in MTEP22 | C | West | MP | 21605 | 2022-09-11 | 25 Line Phase 2 | Hibbing Transmission Exits | Rebuild two 115 kV lines coming into Hibbing Substation on double circuit structures and realign entrances to coordinate with Hibbing Substation Modernization Project (MTEP #18064) | MN | MN | 2025-12-31 | Asset renewal - age & condition - non-standard framing of existing 115 kV lines. Also, a need to realign at the substation exits in response to relocations within the substation itself. |  |  | Minnesota Power (Allete, Inc.) |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 115 | 0 | Proposed | 2000000
A in MTEP22 | C | West | MP | 21606 | 2022-08-24 |  | West Cohasset Project | Add new 115-23 kV transformer at existing Boswell SES substation and rename substation | MN | MN | 2024-12-31 | New customer load interconnection to 23 kV system |  |  | Minnesota Power (Allete, Inc.) |  | Other |  | Load Growth | 2024-12-31 | 2024-12-31 | 115 | 23 | Proposed | 500000
A in MTEP22 | C | West | MP | 21608 | 2022-04-04 | 105 & 106 Line Upgrade | 105 & 106 Line Upgrade | Rebuild and upgrade the two short parallel Blackberry - Iron Range 230 kV Lines | MN | MN | 2024-12-31 | Increased capacity |  |  | Minnesota Power (Allete, Inc.) |  | BRP |  | Reliability | 2024-12-31 | 2024-12-31 | 230 | 0 | Proposed | 1500000
A in MTEP22 | C | West | MP | 21686 | 2022-09-15 | Mesaba Junction 137 Line Extension | Mesaba Junction 137 Line Extension | Add breaker and transmission line entrance to Mesaba Junction Switching Station. Extend existing Embarrass - Babbitt 115 kV Line to switching station and establish a normal open between the Babbitt Tap and the Argo Tap | MN | MN | 2025-03-31 | Provides redundancy to an industrial load pocket that requires near-constant availability. Improves reliability by providing to independent sources to the Babbitt area. Enables asset renewal by allowing the existing Embarrass-Babbitt 115kV Line to be taken out of service and improved. |  |  | Minnesota Power (Allete, Inc.) |  | BRP |  |  | 2024-12-31 | 2025-03-31 | 115 | 0 | Planned | 9000000
A in MTEP22 | C | West | MP | 21763 | 2021-09-03 | North Shore Transformer | North Shore Transformer Addition | Add 115/14 kV transformer to existing North Shore Switching Station. Relocate 13K cap bank to make room for transformer | MN | MN | 2023-12-31 | Age & condition - project enables retirement of the existing Silver Bay Hillside Substation |  |  | Minnesota Power (Allete, Inc.) |  | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 115 | 0 | Planned | 250000
A in MTEP22 | C | West | MP | 21766 | 2022-09-11 | 126 Line Asset Renewal | 126 Line Asset Renewal | Replace transmission line structural components on Little Fork - I.Falls 115 kV Line, replace Little Fork 126L breaker, and replace relay panels on both ends of 126 Line | MN | MN | 2025-03-31 | Age & condition |  |  | Minnesota Power (Allete, Inc.) |  | Other |  | Age and Condition | 2023-12-31 | 2025-03-31 | 115 | 0 | Proposed | 900000
A in MTEP22 | C | East | MPPA | 21761 | 2022-05-26 |  | Zeeland Riley Transformer Addition | Install a second 138/69 kV Transformer at Riley Substation | MI | MI | 2022-09-30 | With the voltage conversion of the Wolverine transmission system to 138kV, there should be a focus on maintaining sufficient backup capacity in the 138kV:69kV connection. With the loss of one of the two 138kV:69kV transformers in the 2021 projected load scenario, internal generation would be needed to maintain load levels below rated capacity for the remaining transformer. An additional 83.3MVA 138kV:69kV transformer installed at Riley Substation would provide sufficient capacity for an N-1 contingency through 2035 load projections. |  | Zeeland Board of Public Works, a Member of Michigan Public Power Agency, expects 34 MWs of load growth from new industrial customers over the next 10-12 years. Zeeland has had studies performed on their system that identify a need for a 2nd 138/69 kV transformer at their Riley substation in order to provide sufficient capacity for an N-1 contingency. | Michigan Public Power Agency |  | Other |  | Load Growth | 2022-09-30 | 2022-09-30 | 138 | 69 | Planned | 1465000
A in MTEP22 | C | West | MRES | 21938 | 2021-09-14 |  | Worthington Sub 2 Breaker | A breaker will be added to Worthington Public Utilities(WPU) Sub #2. The breaker will protect for a fault between Sub #2 and Elk. | MN | MN | 2023-04-01 | The normally open line between WPU Sub #1 and Sub #2 as a result of the MTEP 20608 Worthington Substation project. A breaker will be added to minimize load exposure to a single fault. |  |  | Missouri River Energy Services (MRET) |  | Other |  | Reliability | 2023-04-01 | 2023-04-01 | 69 | 0 | Planned | 375000
A in MTEP22 | C | West | MRES | 23346 | 2022-08-24 |  | Hutchinson Substation | This project will add a second 115/69 kV transformer to the existing City of Hutchinson MN, Hutchinson Substation. The project will also rebuild the Hutchinson 115 kV into a four position ring bus. | MN | MN | 2025-12-31 | There are existing operational concerns in the area that require generation to be ran system intact. The City of Hutchinson expects a large expansion of existing customer load over the next couple of years, which will exacerbate the operational concern. |  |  | Missouri River Energy Services (MRET) |  | Other |  | Load Growth | 2025-12-31 | 2025-12-31 | 115 | 69 | Proposed | 8000000
A in MTEP22 | C | Central | NIPS | 21167 | 2021-09-21 |  | New Menges Ditch 138/69 kV Substation | New 138/69kV Substation source from AEP's E. Elkhart substation. | IN | IN | 2025-12-31 | New 69kV source needed in the Bristol area. |  |  | Northern Indiana Public Service Company |  | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 138 | 69 | Proposed | 42368620
A in MTEP22 | C | Central | NIPS | 21168 | 2022-01-21 |  | New Hiple to Northport 138kV Line | New Hiple to Northport 138kV line | IN | IN | 2024-12-31 | Support to East 69kV Network. Relieves overload of 6990 seen in system outage studies. |  |  | Northern Indiana Public Service Company |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 27527004
A in MTEP22 | C | Central | NIPS | 21867 | 2021-09-17 |  | Rebuild Marktown 138 kV Substation | Rebuild Marktown 138kV Substation | IN | IN | 2024-12-31 | Age & Condition |  |  | Northern Indiana Public Service Company |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 138 | 0 | Planned | 30190251
A in MTEP22 | C | Central | NIPS | 21870 | 2021-09-24 |  | Rebuild S.Chalmers -Oakdale 69 kV_Circuit 6972 | Rebuild circuit 6972, South Chalmers to Oakdale substations | IN | IN | 2022-12-31 | Age & Condition |  |  | Northern Indiana Public Service Company |  | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 69 | 0 | Planned | 4917926
A in MTEP22 | C | Central | NIPS | 21875 | 2021-09-24 |  | Rebuild Lagrange 69 kV line-Circuit 6980 | Rebuild 3.4 miles of circuit 6980 | IN | IN |  | Age and Condition |  |  | Northern Indiana Public Service Company |  | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 69 | 0 | Planned | 3014269
A in MTEP22 | C | Central | NIPS | 21876 | 2021-09-20 |  | Upgrade Transmission Substation - 2022 Program | Transmission Age & Condition Projects | IN | IN |  | Age & Condition |  |  | Northern Indiana Public Service Company |  | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 345 | 69 | Planned | 26223459
A in MTEP22 | C | Central | NIPS | 21878 | 2021-09-17 |  | Upgrade transmission lines - 2022 program | Rebuilds/upgrades 69 kV and up line based on age and condition, including structures, conductor, switches and communication upgrades (fiber) | IN | IN |  | Age & Condition |  |  | Northern Indiana Public Service Company |  | Other |  | Age and Condition | 2022-12-31 | 2022-12-31 | 138 | 34 | Planned | 36772890
A in MTEP22 | C | Central | NIPS | 21879 | 2021-09-17 |  | Upgrade Transmission Substation - 2023 Program | Upgrades/replacements 69 kV and up Substation based on age and condition, including but not limited to switches, breakers, transformers, and protection and communication equipment. | IN | IN |  | Age & Condition |  |  | Northern Indiana Public Service Company |  | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 345 | 34 | Planned | 42330170
A in MTEP22 | C | Central | NIPS | 21880 | 2021-09-17 |  | Upgrade transmission lines - 2023 program | Rebuilds/upgrades 69 kV and up line based on age and condition, including structures, conductor, switches and communication upgrades (fiber) | IN | IN |  | Age and Condition |  |  | Northern Indiana Public Service Company |  | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 345 | 34 | Planned | 19261989
A in MTEP22 | C | Central | NIPS | 21881 | 2021-09-17 |  | Upgrade Transmission Substation - 2024 Program | Upgrades/replacements 69 kV and up Substation based on age and condition, including but not limited to switches, breakers, transformers, and protection and communication equipment. | IN | IN |  | Age & Condition |  |  | Northern Indiana Public Service Company |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 345 | 34 | Planned | 32711473
A in MTEP22 | C | Central | NIPS | 21882 | 2021-09-17 |  | Upgrade transmission lines - 2024 program | Rebuilds/upgrades 69 kV and up line based on age and condition, including structures, conductor, switches and communication upgrades (fiber) | IN | IN |  | Age & Condition |  |  | Northern Indiana Public Service Company |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 345 | 34 | Planned | 31312504
A in MTEP22 | C | Central | NIPS | 21883 | 2021-09-17 |  | Upgrade Transmission Substation - 2025 Program | Upgrades/replacements 69 kV and up Substation based on age and condition, including but not limited to switches, breakers, transformers, and protection and communication equipment. | IN | IN |  | age & condition |  |  | Northern Indiana Public Service Company |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 345 | 34 | Planned | 26977092
A in MTEP22 | C | Central | NIPS | 21884 | 2021-09-17 |  | Upgrade transmission lines - 2025 program | Rebuilds/upgrades 69 kV and up line based on age and condition, including structures, conductor, switches and communication upgrades (fiber) | IN | IN |  | Age & Condition |  |  | Northern Indiana Public Service Company |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 345 | 34 | Planned | 30216017
A in MTEP22 | C | Central | NIPS | 21885 | 2021-09-17 |  | Upgrade Transmission Substation - 2026 Program | Upgrades/replacements 69 kV and up Substation based on age and condition, including but not limited to switches, breakers, transformers, protection and communication equipment. | IN | IN |  | Age & Condition |  |  | Northern Indiana Public Service Company |  | Other |  | Age and Condition | 2026-12-31 | 2026-12-31 | 345 | 34 | Planned | 54852316
A in MTEP22 | C | Central | NIPS | 21886 | 2021-09-17 |  | Upgrade transmission lines - 2026 program | Rebuilds/upgrades 69 kV and up lines based on age and condition, including structures, conductor, switches and communication upgrades (fiber). | IN | IN |  | Age & Condition |  |  | Northern Indiana Public Service Company |  | Other |  | Age and Condition | 2026-12-31 | 2026-12-31 | 345 | 34 | Planned | 68286845
A in MTEP22 | B | Central | NIPS | 21950 | 2021-09-20 |  | New Timmons 69/12 kV substation | Build the new Timmons 69/12 kV 14.4 MVA sub. | IN | IN | 2023-12-31 | Build new substation to serve member load |  |  | Wabash Valley Power Association, Inc. |  | Other |  | Load Growth | 2023-12-31 | 2023-12-31 | 69 | 12 | Planned | 5301167
A in MTEP22 | C | Central | NIPS | 21954 | 2022-05-18 |  | New Rosebud 69/12kV Sub | Building new Rosebud 69/12 substation to feed load normally fed from existing Parr substation. | IN | IN | 2023-12-31 | Transfer of load from Old substation |  |  | Wabash Valley Power Association, Inc. |  | Other |  | Load Growth | 2022-11-29 | 2022-11-29 | 69 | 12 | Planned | 4947000
A in MTEP22 | C | Central | NIPS | 21955 | 2022-05-18 |  | Upgrade Fair Oaks 2nd bank 138/69/12 kV transformer | Add second 138/69/12kV 22.4MVA transformer to Fair Oaks substation to handle new load in area | IN | IN | 2024-10-17 | Add second 138/69/12kV 22.4MVA transformer to Fair Oaks substation to handle new load in area |  |  | Wabash Valley Power Association, Inc. |  | Other |  | Load Growth | 2024-10-17 | 2024-10-17 | 69 | 12 | Proposed | 4176754
A in MTEP22 | C | Central | NIPS | 21956 | 2021-09-17 |  | New Yellow River 69 kV Sub | Build a new 69kv/12.5 kV 14.4 MVA substation near the Knox Industrial Park. Install 13 MVAR cap bank. Build 0.5 miles of 69 kV to new sub. | IN | IN | 2022-06-01 | New Ind park load |  |  | Wabash Valley Power Association, Inc. |  | Other |  | Load Growth | 2023-12-31 | 2023-12-31 | 69 | 12 | Planned | 5255244
A in MTEP22 | C | Central | NIPS | 21957 | 2021-09-24 |  | Upgrade Oregon 69 kV Sub | Replace existing 7 MVA substation transformer at the KVREMC owned Oregon Substation to a 14 MVA. Add a backup transmission line for Oregon Substation and tap the nearby 69105 (0.25mi). New ATO scheme to be installed on KVL property on transmission line poles and to be owned by WVPA. | IN | IN | 2023-12-31 | Substation needs to supply new load in area. |  |  | Wabash Valley Power Association, Inc. |  | Other |  | Load Growth | 2023-12-31 | 2023-12-31 | 69 | 12 | Planned | 1338591
A in MTEP22 | C | Central | NIPS | 21959 | 2021-09-24 |  | Upgrade Moody 69 kV sub | Purchase the Moody Substation from NIPSCO and replace the transformer (14.4MVA from Fair Oaks), regulators, fuses, and jumpers. Add oil containment around a new foundation. | IN | IN | 2022-09-01 | Substation needed upgrade. Old and needed larger transformer |  |  | Wabash Valley Power Association, Inc. |  | Other |  | Age and Condition | 2022-09-01 | 2022-09-01 | 69 | 12 | Proposed | 1500000
A in MTEP22 | C | Central | NIPS | 21961 | 2021-09-17 |  | New Marco 69/12 kV substation | Build new Marco substation near the existing NIPS Argos substation. 69/12kV 14.4MVA Xfmr, design for 4 ckts used initially. Will replace Marshall MP. Add external control Hut for Fiber connections (Rochester Fiber). Build short tap from Nipsco 6968 to new sub | IN | IN | 2022-12-30 | Backup of existing load and added load. |  |  | Wabash Valley Power Association, Inc. |  | Other |  | Load Growth | 2022-12-30 | 2022-12-30 | 69 | 12 | Planned | 4947000
A in MTEP22 | C | Central | NIPS | 21962 | 2021-09-17 |  | New Berthaville 69/12 kV sub | New Berthaville substation needed south of Goodland for new dairy farm and added load near Newton office. 14.4 MVA transformer, 4 distr exits, 69kV with manual switch to Nipsco 6964 line. | IN | IN | 2022-09-30 | New Berthaville substation needed south of Goodland for new dairy farm and added load in area. |  |  | Wabash Valley Power Association, Inc. |  | Other |  | Load Growth | 2022-09-30 | 2022-09-30 | 69 | 12 | Under Construction | 4200000
A in MTEP22 | C | Central | NIPS | 21964 | 2021-09-17 |  | Upgrade Colfax 138/69/12 kV substation | Add 2nd transformer to Colfax substation. 138/69/12kV 22.4MVA transformer. Substation work to make space for new transformer. | IN | IN | 2023-11-30 | Added load in area |  |  | Wabash Valley Power Association, Inc. |  | Other |  | Load Growth | 2023-11-30 | 2023-11-30 | 69 | 12 | Proposed | 5000000
A in MTEP22 | C | Central | NIPS | 21965 | 2021-09-17 |  | Upgrade Otter sub eqmnt | Otter substation in Steuben has an inoperable switch and transrupter that need replaced. Replacing switch with a load break manual switch and replacing the transrupter with a S&C Circuit Switcher. | IN | IN | 2022-10-01 | Old equipment |  |  | Wabash Valley Power Association, Inc. |  | Other |  | Age and Condition | 2023-07-31 | 2023-07-31 | 69 | 12 | Planned | 872640
A in MTEP22 | C | Central | NIPS | 22630 | 2022-03-01 |  | J1067 Network Upgrades | Network upgrades necessary to connect J1067 to interconnect at NIPSCO's Reynolds to Burr Oak 345kV line | IN | IN | 2023-10-20 | Network upgrades necessary to connect J1067 to interconnect at NIPSCO's Reynolds to Burr Oak 345kV line |  |  | Northern Indiana Public Service Company |  | GIP |  |  | 2023-10-20 | 2023-10-20 | 345 | 0 | Planned | 23632643
A in MTEP22 | C | Central | NIPS | 22649 | 2022-03-01 |  | J968 J1069 Network Upgrades | New 345kV breaker in Bay 6 at Reynolds substation to accommodate new lead line into northern position, plus all associated equipment | IN | IN |  | Network upgrades necessary for J968 and J1069 to connect to NIPSCO's Reynolds 345kV substation |  |  | Northern Indiana Public Service Company |  | GIP |  |  | 2023-04-30 | 2023-04-30 | 345 | 0 | Planned | 2204486
A in MTEP22 | C | West | OTP | 20385 | 2021-10-28 |  | OTP Buffalo to Alice 115 kV Rebuild | Rebuild 7 miles of 115 kV line due to poor performance. | ND | ND | 2024-11-01 | Rebuild 7 miles of 115 kV line due to poor performance. |  | 10-14-2021 Project Manager reported that Phase A of this project will begin this month October, 2021. | Otter Tail Power Company |  | Other |  | Reliability | 2024-11-01 | 2024-11-01 | 115 | 0 | M4_Pre-Construction | 2000000
A in MTEP22 | B | West | OTP | 20565 | 2022-09-02 |  | Forman 230/115 kV uprate | Increase the capacity of the the Forman 230/115 kV transformer and the Forman - Forman WAPA 115 kV line. | ND | ND |  | A Market Participant has requested that these facilities capacity be increased. |  |  | Otter Tail Power Company |  | MPFP |  |  | 2024-10-09 | 2024-10-09 | 230 | 115 | Proposed | 6162000
A in MTEP22 | C | West | OTP | 21427 | 2022-06-02 | OTP | OTP Max Water Treatment Plant 41.6 kV | Project Description: This project will consist of: 1. Add one 41.6 kV circuit breaker at Max. | ND | ND | 2022-08-31 | A new water treatment plant is interconnecting to OTP's system in Max, ND. This new load addition is driving the need for transmission upgrades in the Max, ND and Parshall, ND 41.6 kV areas. |  |  | Otter Tail Power Company |  | Other |  | Load Growth | 2022-08-31 | 2022-08-31 | 41.6 | 0 | Planned | 350000
A in MTEP22 | C | West | OTP | 22606 | 2022-09-13 |  | OTP Jamestown, ND Load Addition | OTP has a new customer requesting to be served in Jamestown, ND. The customer facility will have a demand of 100 MWs. OTP will serve the new customer from the 41.6 kV tertiaries of both the existing Jamestown 345/115/41.6 kV transformers. The load will be split 50/50 between each of the transformers. OTP will install a new 115/41.6 kV 24 MVA transformer at the Jamestown 345 kV substation. The 115 kV bus will be expanded to allow for the new 115/41.6 kV transformer. The existing 41.6 kV load will be moved to be served off the new 115/41.6 kV 24 MVA transformer. | ND | ND | 2022-02-01 | The new 115/41.6 kV transformer will serve the existing 41.6 kV load, allowing additional capacity on the 41.6 kV tertiaries of the Jamestown 345/115/41.6 kV transformers to serve the new customer. |  |  | Otter Tail Power Company |  | Other |  | Load Growth | 2023-11-01 | 2023-11-01 | 115 | 41.6 | Planned | 2268000
A in MTEP22 | C | West | OTP | 23148 | 2022-09-02 |  | OTP Fergus Falls & Canby Area MPFPs | OTP has been requested by a Market Participant (Market Participant Funded Project - MPFP) to increase the capacity of the following Facilities: 1. Canby - Granite Falls 115 kV 2. Hoot Lake - Fergus Falls 115 kV 3. Hoot Lake - Fergus Falls SE 115 kV The Market Participant has requested an in-service date of 1/1/2023. | MN | MN |  | A Market Participant has requested that the capacity of the facilities below be increased: 1. Canby - Granite Falls 115 kV 2. Hoot Lake - Fergus Falls 115 kV 3. Hoot Lake - Fergus Falls SE 115 kV |  |  | Otter Tail Power Company |  | MPFP |  |  | 2023-06-30 | 2023-08-30 | 115 | 0 | Proposed | 1705000
A in MTEP22 | B | Central | PPI | 19945 | 2021-09-17 |  | New Topeka-Bishop 69 kV Line | New Topeka--Bishop 69 kV line (~8-mile) w/ 556 MCM in MEC | IL | IL | 2025-12-31 | Provide alternative feeds to Topeka and Bishop substations. Part of 69 kV path from Forest City to Grand Island, |  |  | Prairie Power, Inc. |  | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 69 | 0 | Planned | 5120000
A in MTEP22 | B | Central | PPI | 19950 | 2021-10-19 |  | New St. David-Wee-Ma-Tuk-Canton 69 kV line | New St. David-Wee-Ma-Tuk-Canton 69 kV line (10.4-mile) in Spoon River Electric Cooperative | IL | IL | 2023-12-31 | Provide alternative feeds to St. David, Wee-Ma-Tuk, and Canton substations |  |  | Prairie Power, Inc. |  | Other |  | Reliability | 2023-12-31 | 2023-12-31 | 69 | 0 | Planned | 5596000
A in MTEP22 | B | Central | PPI | 19952 | 2021-09-17 |  | Rebuild Walkerville-Eldred 69 kV line | Rebuild Rebuild Walkerville-Eldred 69 kV line (7.3-mile) in Illinois Electric Cooperative | IL | IL | 2024-12-31 | Age and Condition. Replace 4/0 line built in 1967 with 336.4 MCM ASCR conductor |  |  | Prairie Power, Inc. |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 69 | 0 | Planned | 3942000
A in MTEP22 | B | Central | PPI | 21746 | 2021-09-17 |  | New Bluff Hall-E. Hannibal 69 kV line | New Bluff Hall-E. Hannibal 69 kV line (~9-mile) 69 kV Line | IL | IL | 2022-12-31 | Provide backup feed to E. Hannibal and Barry substations. |  |  | Prairie Power, Inc. |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 4184000
A in MTEP22 | B | Central | PPI | 21747 | 2021-09-17 |  | New Barry 69 kV Substation | New Barry 69 kV Transmission Substation near Barry, IL. Terminals to Bluff Hall, Liberty, Pittsfield, and Barry Distribution substation. | IL | IL | 2022-12-31 | Provide service to new load (Cannibis facility) at Barry Distribution substation. |  |  | Prairie Power, Inc. |  | Other |  | Load Growth | 2022-12-31 | 2022-12-31 | 69 | 69 | Under Construction | 1600000
A in MTEP22 | B | Central | PPI | 21748 | 2021-09-28 |  | Rebuild Barry-E. Hannibal Tap 69 kV line to double circuit | Rebuild Barry-Old E. Hannibal Tap 69 kV line to double circuit. Split the Pittsfield to Liberty 69 kV line into a Pittsfield to Barry circuit and a Liberty to Barry circuit. Incudes new 0.3 mile line from Barry toward E Hannibal tap. Rebuilding only a portion of E Hannibal tap to Barry North and South. | IL | IL | 2022-12-31 | Provide network service to Barry substation. |  |  | Prairie Power, Inc. |  | Other |  | Load Growth | 2022-12-31 | 2022-12-31 | 69 | 0 | Under Construction | 3762000
A in MTEP22 | B | Central | PPI | 21749 | 2021-09-17 |  | New Trailblazer 69 kV Substation | New Trailblazer 69 kV breaker substation near Marblehead, IL. | IL | IL | 2022-12-31 | Trailblazer Breaker Station will sectionalize 69 kV lines to St, Anthony, Liberty and Barry. |  |  | Prairie Power, Inc. |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 2935000
A in MTEP22 | B | Central | PPI | 21750 | 2021-09-27 |  | New Rock Creek 69 kV Substation | New Rock Creek 69 kV breaker station near Ursa substation in Adams Electric Cooperative. Breaker station will have terminals looking towards Elvaston, Golden, and Payson. | IL | IL | 2025-12-31 | Sectionalize three terminal line to Ursa, Big Neck, and Burton. |  |  | Prairie Power, Inc. |  | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 69 | 69 | Planned | 2935000
A in MTEP22 | B | Central | PPI | 21751 | 2021-09-17 |  | New Panther 138/69 kV Substation | New Panther 138/69 kV substation near Pana, IL in Shelby Electric Cooperative. | IL | IL | 2025-12-31 | Provide backup for ISHI 138/69 kV substation. Allow for networking of several Shelby Electric Cooperative substations including Pana, Herrick and ISHI. Allow for upgrading of 34.5 kV system in area to 69 kV. |  |  | Prairie Power, Inc. |  | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 138 | 69 | Planned | 8425000
A in MTEP22 | B | Central | PPI | 21752 | 2021-09-17 |  | New Panther-Pana Tap 69 kV line | New Panther-Pana Tap 69 kV line (~2.5-mile) in Shelby Electric Cooperative | IL | IL | 2025-12-31 | Provide new feed for Shelby Electric Cooperative's Pana distribution substation, including conversion from 34.5 kV to 69 kV. Part of line connecting Panther to ISHI. |  |  | Prairie Power, Inc. |  | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 69 | 69 | Planned | 2250000
A in MTEP22 | B | Central | PPI | 21753 | 2021-09-17 |  | New Pana Tap-Lakewood 69 kV line | New Pana Tap-Lakewood 69 kV line (~12-mile) in Shelby Electric Cooperative | IL | IL | 2025-12-31 | Provide new feed to Lakewood and Herrick substations in Shelby Electric Cooperative including conversion from 34.5 kV to 69 kV. Part of line connecting Panther to ISHI. |  |  | Prairie Power, Inc. |  | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 69 | 69 | Planned | 7680000
A in MTEP22 | B | Central | PPI | 21754 | 2021-09-24 |  | New ISHI-Herrick 69 kV line | New ISHI-Herrick 69 kV line (~9.7-mile) in Shelby Electric Cooperative. This is part of the line from Panther to ISHI. | IL | IL | 2025-12-31 | Provide new feed for Herrick substation including conversion from 34.5 kV to 69 kV. This line is part of the line from Panther to ISHI substations. |  |  | Prairie Power, Inc. |  | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 69 | 0 | Planned | 5474000
A in MTEP22 | B | Central | PPI | 21755 | 2021-09-28 |  | Rebuild Hadley Breaker-Barry 69 kV line | Rebuild portion of Hadley Breaker-E. Hannibal Tap 69 kV line (0.54-mile) in Illinois Electric Cooperative. | IL | IL | 2025-12-31 | Age and condition. Replace 4/0 line built in 1967 with 336.4 ACSR line. |  |  | Prairie Power, Inc. |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 69 | 69 | Planned | 270000
A in MTEP22 | B | Central | PPI | 21756 | 2021-09-17 |  | Rebuild Hadley Breaker-Hadley 69 kV line | Rebuild Hadley Breaker-Hadley 69 kV line (1.61-mile) in Illinois Electric Cooperative | IL | IL | 2025-12-31 | Age and condition. Replace 4/0 ACSR line built in 1967 with 336.4 ACSR line, |  |  | Prairie Power, Inc. |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 69 | 69 | Planned | 805000
A in MTEP22 | C | Central | PPI | 21757 | 2021-09-28 |  | Rebuild Barry-Liberty 69 kV line | Rebuild portion of Barry-Liberty 69 kV line (6.35-mile) between Illinois Electric Cooperative and Adams Electric Cooperative. | IL | IL | 2023-12-31 | Age and condition. Replace 4/0 line built in 1967 with 336.4 MCM ACSR line. |  |  | Prairie Power, Inc. |  | Other |  | Age and Condition | 2023-12-31 | 2023-12-31 | 69 | 69 | Planned | 3175000
A in MTEP22 | B | Central | PPI | 21758 | 2021-09-17 |  | Rebuild Kampsville-Kampsville River Crossing 69 kV line | Rebuild Kampsville-Kampsville River Crossing 69 kV line (0.7-mile) in Illinois Electric Cooperative | IL | IL | 2025-12-31 | Age and condition. Replace 4/0 line originally built in 1949 with 336.4 MCM ACSR conductor. |  |  | Prairie Power, Inc. |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 69 | 69 | Planned | 350000
A in MTEP22 | B | Central | PPI | 21760 | 2021-09-17 |  | New Rushville 69 kV Substation | New 69 kV Rushville breaker substation in Adams Electric Cooperative. Terminals will look to Golden and Liberty. | IL | IL | 2024-12-31 | Sectionalize the line between Golden and Liberty which will contain five substations on the Adams East Loop: Camden, Rushville, Mt. Sterling, Sugar Grove and Kellerville. |  |  | Prairie Power, Inc. |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 2935000
A in MTEP22 | B | Central | PPI | 21788 | 2021-09-17 |  | Rebuild Andrew-Barclay 69 kV line | Rebuild Andrew-Barclay 69 kV line (~7.5-mile) in Menard Electric Cooperative. Replace 4/0 ACSR line built in 1964 with 556.5 MCM ACSR conductor. | IL | IL | 2024-12-31 | Age and condition. Upgrade rating of East Lanesville to Andrew path to accommodate CWLP imports. |  |  | Prairie Power, Inc. |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 3755000
A in MTEP22 | B | Central | PPI | 21789 | 2021-09-25 |  | Rebuild Lanesville-Barclay 69 kV Line | Rebuild ~11.5-mile Lanesville to Barclay 69 kV line in Menard Electric Cooperative. Replace 4/0 ACSR line built in 1964 with 556.5 MCM ACSR conductor. | IL | IL | 2025-12-31 | Age and condition. Increase rating of East Lanesville to Andrew path to accommodate CWLP imports. |  |  | Prairie Power, Inc. |  | Other |  | Age and Condition | 2025-12-31 | 2025-12-31 | 69 | 69 | Planned | 5745000
A in MTEP22 | B | Central | PPI | 21791 | 2021-09-17 |  | Rebuild E. Lanesville-Lanesville 69 kV line | Rebuild E. Lanesville-Lanesville 69 kV line (~0.9-mile) in Menard Electric Cooperative. Replace 336.4 MCM ACSR line built in 1981 with 556.5 MCM ACSR conductor. | IL | IL | 2024-12-31 | Upgrade rating of East Lanesville to Andrew path to improve CWLP import capability. |  |  | Prairie Power, Inc. |  | Other |  | Reliability | 2024-12-31 | 2024-12-31 | 69 | 69 | Planned | 450000
A in MTEP22 | B | Central | PPI | 21792 | 2021-09-17 |  | Rebuild Fancy Creek-Andrew 69 kV line | Rebuild Fancy Creek-Andrew 69 kV line (~4.5-mile) in Menard Electric Cooperative. Replace 336.4 MCM ACSR line built in 1969 with 556.5 MCM ACSR conductor. | IL | IL | 2026-12-31 | Age and condition. Upgrade Fancy Creek to Andrew path to accommodate CWLP imports. |  |  | Prairie Power, Inc. |  | Other |  | Age and Condition | 2026-12-31 | 2026-12-31 | 69 | 69 | Planned | 2250000
A in MTEP22 | B | Central | PPI | 21793 | 2021-09-17 |  | New Forest City-Bishop 69 kV line | New Forest City-Bishop 69 kV line (~2-mile) in Menard Electric Cooperative. | IL | IL | 2025-12-31 | Provide alternative feed to Bishop substation. Part of Forest City to Grand Island 69 kV path. |  |  | Prairie Power, Inc. |  | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 69 | 0 | Planned | 1415000
A in MTEP22 | B | Central | PPI | 21794 | 2022-02-16 |  | New Forest City 138/69 kV Substation | New 138/69 kV substation near Forest City, IL in Menard Electric Cooperative. This substation will connect to the Ameren Havana to Cincinnati 138 kV line at Winnebago on the high side and to the Menard Electric Cooperative Forest City to Bishop 69 kV line on the low side with an 84 MVA transformer, | IL | IL | 2025-12-31 | Backup Grand Island transformer for Menard Electric Cooperative, Provide alternative feed to Ameren's Mason City 138 kV substation for P6 loss of Havana - Cane 138 kV and Quiver - Mason City 138 kV. |  |  | Prairie Power, Inc. |  | BRP |  |  | 2025-12-31 | 2025-12-31 | 138 | 69 | Planned | 7725000
A in MTEP22 | B | Central | PPI | 21795 | 2021-09-24 |  | New Middletown 69 kV Substation | New 69 kV breaker substation near Middletown, IL in Menard Electric Cooperative. Substation will have terminals looking to Fancy Creek, Grand Island, Forest City, and Middletown Distribution substation. | IL | IL | 2025-12-31 | Sectionalize 69 kV lines Middletown - Fancy Creek, Middletown - Grand Island, and Middletown - Forest City. |  |  | Prairie Power, Inc. |  | Other |  | Reliability | 2025-12-31 | 2025-12-31 | 69 | 69 | Planned | 2107000
A in MTEP22 | C | Central | SIGE | 22002 | 2021-09-17 | 22SIGE01 | Francisco Gen Interconnection (J1074) | Francisco Substation modifications needed for the interconnection of Queue project J1074 | IN | IN | 2022-12-15 | Needed to interconnect generation customer for Queue project J1074 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | GIP |  |  | 2022-12-15 | 2022-12-15 | 138 | 0 | Planned | 1805104
A in MTEP22 | C | Central | SIGE | 22004 | 2021-09-17 | 22SIGE02 | Replace Southwind 69/12 kV T2 transformer | Replace 69/12 kV distribution transformer T2 at the Southwind substation | IN | IN | 2023-06-01 | Increase distribution capacity at substation |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 69 | 12 | Planned | 2000000
A in MTEP22 | C | Central | SIGE | 22005 | 2021-09-17 | 22SIGE03 | Replace Duff 345/138 kV substation 345 kV breakers | Replace two 345 kV breakers (#s 3200 and 3300) at the Duff 345/138 kV substation | IN | IN | 2023-06-01 | Increase the rating on the Duff - Francisco 345 kV transmission line |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 345 | 0 | Planned | 1500000
A in MTEP22 | C | Central | SIGE | 22006 | 2021-09-17 | 22SIGE04 | New Anderson Road 69/12 kV Substation | Build new 69/12 kV distribution substation | IN | IN | 2023-06-01 | Address load growth |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | Other |  | Load Growth | 2023-06-01 | 2023-06-01 | 69 | 12 | Planned | 8500000
A in MTEP22 | C | Central | SIGE | 22007 | 2021-09-17 | 22SIGE05 | Rebuid Warrick North 138 kV switching station | Expand Warrick North 138 kV switching station from ring bus to breaker and a half to allow for new terminal for large industrial customer. | IN | IN | 2023-07-01 | Create new terminal for transmission line to large industrial customer. |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | Other |  | Load Growth | 2023-07-01 | 2023-07-01 | 138 | 0 | Planned | 3500000
A in MTEP22 | C | Central | SIGE | 22008 | 2021-09-17 | 22SIGE06 | New Kaiser Aluminum 138 kV Sub | Build new 138 kV substation for new large industrial customer. | IN | IN | 2023-07-01 | New customer |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | Other |  | Load Growth | 2023-07-01 | 2023-07-01 | 138 | 15 | Planned | 12000000
A in MTEP22 | C | Central | SIGE | 22009 | 2021-09-17 | 22SIGE07 | New Midwest Fertilizer 138 kV Sub | Build new 138 kV substation on existing 138 kV line for large industrial customer | IN | IN | 2023-12-01 | New customer |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | Other |  | Load Growth | 2023-12-01 | 2023-12-01 | 138 | 12 | Planned | 8000000
A in MTEP22 | C | Central | SIGE | 22010 | 2021-09-17 | 22SIGE08 | Scott Gen Interconnection (J856) | New 138 kV terminal at existing Scott 138/69 kV substation to facilitate generation interconnection Queue project J856 | IN | IN | 2023-10-01 | Generation interconnection project |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | GIP |  |  | 2023-10-01 | 2023-10-01 | 138 | 0 | Planned | 1552504
A in MTEP22 | C | Central | SIGE | 22011 | 2021-09-17 | 22SIGE09 | New Warrick N. - Kaiser 138 kV Line | New 138 kV line from existing Warrick North 138 kV switching station to new Kaiser 138 kV substation to serve large industrial customer. | IN | IN | 2023-07-01 | New customer |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | Other |  | Load Growth | 2023-07-01 | 2023-07-01 | 138 | 0 | Planned | 2300000
A in MTEP22 | B | East | WPSC | 15652 | 2021-08-19 |  | Rebuild Atlanta to Gaylord 138kV | Rebuild 22 miles to Wolverine's 138 kV standard | MI | MI | 2024-12-31 | Condition Based - Replace aging infrastructure. • Built in 1978, current age 44 years • 5 Condemned poles, 144 Damaged poles, 133 Good poles • 53% of poles in need of replacement |  |  | Wolverine Power Supply Cooperative, Inc. |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 138 | 0 | Proposed | 16500000
A in MTEP22 | C | East | WPSC | 21425 | 2022-04-14 |  | Mills Creek Interconnection | Add .9 Miles Transmission and 138kV BUS to accommodate load interconnection. | MI | MI | 2023-06-29 | New interconnection/Load growth |  |  | Wolverine Power Supply Cooperative, Inc. |  | Other |  | Load Growth | 2022-12-31 | 2022-12-31 | 138 | 0 | Proposed | 1000000
A in MTEP22 | B | East | WPSC | 21665 | 2022-08-16 |  | Day Interconnection | New ROW and line for interconnection | MI | MI | 2024-06-01 | Interconnection Request |  |  | Wolverine Power Supply Cooperative, Inc. |  | Other |  | Load Growth | 2024-06-01 | 2024-06-01 | 138 | 0 | Proposed | 3500000
A in MTEP22 | C | East | WPSC | 21785 | 2021-09-17 |  | Grawn Station Protection System Update | Replace obsolete electromechanical relays that require replacement by modern digital relays. | MI | MI | 2024-12-31 | Protection system is obsolete and requires updated electronics. |  |  | Wolverine Power Supply Cooperative, Inc. |  | Other |  | Age and Condition | 2024-12-31 | 2024-12-31 | 69 | 0 | Proposed | 1500000
A in MTEP22 | C | East | WPSC | 21787 | 2021-09-17 |  | Westwood 138kV Interconnection | The Westwood Transmission station was fully rebuilt in 2009 and can accommodate the addition of a new 138kV/69kV power transformer. This project includes adding the power transformer, bus equipment, and protection systems, to accommodate the addition of a 138kV line terminal. | MI | MI | 2024-12-31 | Mitigate potential overloads seen on the Alba Transformer and allow for the retirement of the Alba Station. Address age and condition based issues seen at Alba station due to its age in excess of 60 years. Eliminate the three terminal protection scheme between Alba, Van Tyle, and Stoever. |  |  | Wolverine Power Supply Cooperative, Inc. |  | Other |  | Age and Condition | 2024-12-31 | 2025-12-31 | 138 | 69 | Proposed | 18000000
A in MTEP22 | C | West | XEL | 20505 | 2022-05-18 |  | Blue Earth-South Bend Area Upgrades | Rebuild approx. 30 miles of 161 kV line and upgrade South Bend TR6 to a 336 MVA transformer. | MN | MN | 2025-03-31 | Address Thermal violations in multiple sensitivity cases. |  |  | Northern States Power (Xcel Energy) |  | BRP |  |  | 2025-04-15 | 2025-04-15 | 161 | 115 | Proposed | 40000000
A in MTEP22 | C | West | XEL | 21285 | 2021-09-15 |  | Elm Creek TR10 | Install second 345/115 kV transformer at Elm Creek sub Route SHC-CNC #1 345 kV Line Into Elm Creek Sub Add 50 MVAR reactor to existing TR9. | MN | MN | 2023-06-01 | Additional load serving capability in the area Removes need to shed load under contingency Eliminates need for line rebuilds in the area, which would otherwise be required. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Reliability | 2023-06-01 | 2023-06-01 | 345 | 115 | Planned | 9750000
A in MTEP22 | C | West | XEL | 21833 | 2021-09-10 |  | Mallard Facility Rebuild | Joint NSP - Central Power facility rebuild. NSP substation grading and fencing, 3 new box structures, control and wiring modifications to accommodate Central Power equipment moves | ND | ND | 2023-05-15 | Central Power has failing 43.8kV control circuits and 115-43.8kV facilities approaching end of life. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Age and Condition | 2023-05-15 | 2023-05-15 | 115 | 0 | Planned | 2340000
A in MTEP22 | C | West | XEL | 21834 | 2022-05-23 |  | Boyd Sub Removal | Retire end of life Boyd sub and install two 5 MVAR capacitor banks at nearby Bateman sub. | WI | WI | 2023-06-13 | Project is required to keep the system within NSP Planning Criteria limits. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Reliability | 2022-06-01 | 2023-06-12 | 69 | 0 | Planned | 500000
A in MTEP22 | C | West | XEL | 21845 | 2021-09-10 |  | NSPM Metro Steel Pole Replacement | Address painted poles concerns between Riverside Sub and Main Street Sub. Approximately 4-mile of triple circuit structure(35-structures) to be either replaced, painted or a combination of replace/paint | MN | MN | 2024-12-15 | The existing structures were installed in the 1980’s and are experiencing paint peeling & steel deterioration |  |  | Northern States Power (Xcel Energy) |  | Other |  | Age and Condition | 2024-12-15 | 2024-12-15 | 115 | 0 | Planned | 20000000
A in MTEP22 | C | West | XEL | 21846 | 2021-09-10 |  | Hyland Lake TR1 and TR2 Upgrade | Upgrade TR1 and TR2 to 115/13.8 kV 70 MVA transformers at Hyland Lake Substation. Install high-side line breaker. Install new feeder bay. | MN | MN | 2022-10-15 | HYL TR1 and TR2 have load at risk under contingency. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Reliability | 2022-10-15 | 2022-10-15 | 115 | 13.8 | Planned | 6670000
A in MTEP22 | C | West | XEL | 21848 | 2022-05-25 |  | Willmar 230/115kV Interconnection | Build new dead-end structure to re-terminate the 0823 line to a southern position at the Willmar sub to accommodate GRE's substation reconfiguration | MN | MN | 2022-07-09 | Projected needed to address multiple N-2 low voltage and thermal violations in the area. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Reliability | 2022-07-09 | 2022-07-09 | 115 | 0 | Planned | 800000
A in MTEP22 | C | West | XEL | 21853 | 2021-09-10 |  | North Fork Sub Expansion | Retire the Flambeau breaker station and will add MOD’s to the switches at North Fork substation | WI | WI | 2023-12-01 | This project is needed to retire a substation at the ends of its life, consolidate assets at one substation and to remove old EEE equipment from the old Energy Supply building on site while keeping customer reliability high. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Reliability | 2023-12-01 | 2023-12-01 | 34.5 | 0 | Planned | 1500000
A in MTEP22 | C | West | XEL | 21866 | 2022-05-24 |  | Sleepy Eye Cap Bank Retirement | This cap bank is no longer needed to support the area and will be retired to prevent unnecessary maintenance costs on the system. | MN | MN | 2023-06-01 | A retirement project is needed to reduce unnecessary maintenance costs. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Other Local Needs | 2023-06-01 | 2023-06-01 | 69 | 0 | Planned | 100000
A in MTEP22 | C | West | XEL | 21868 | 2022-05-24 |  | Canistota Junction Cap Bank Retirement | This cap bank is no longer needed to support the area and will be retired to prevent unnecessary maintenance costs on the system. | MN | MN | 2023-06-01 | A retirement project is needed to reduce unnecessary maintenance costs. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Other Local Needs | 2023-06-01 | 2023-06-01 | 69 | 0 | Planned | 100000
A in MTEP22 | C | West | XEL | 21869 | 2022-05-23 |  | BRI CHB 34.5kV Cap Bank Retirement | Retire 34.5kV cap banks at Buffalo Ridge/Chanarambe feeders BRI311, BRI312, and CHB341. | MN | MN | 2023-06-01 | A retirement project is needed to reduce unnecessary maintenance costs. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Other Local Needs | 2023-06-01 | 2023-06-01 | 34.5 | 0 | Planned | 250000
A in MTEP22 | C | West | XEL | 21877 | 2021-09-13 |  | Coon Creek Substation 345kV Breaker Additions | Install three 345kV circuit breakers at the Coon Creek (CNC) substation to provide a better isolation between the Main Bus 1 & 2 to the line 1 & 2. | MN | MN | 2023-12-31 | Three breakers needed to isolate the SHC-CNC “Line 1” and “Line 3” from the 345kV Main Bus 1 and 2, which will prevent loss of large portions of substation during existing breaker trip. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Reliability | 2023-12-31 | 2023-12-31 | 345 | 0 | Planned | 2700000
A in MTEP22 | C | West | XEL | 21887 | 2021-09-13 |  | Rogers Lake Breaker Addition | Install two breakers at Rogers Lake to separate Airport – Rogers Lake 115 kV line and Rogers Lake TR2 | MN | MN | 2022-02-01 | Eliminate single breaker failure and eliminate distribution exposure by terminating the line and TR2 into individual positions in the breaker and a half scheme at RLK. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Reliability | 2022-02-01 | 2022-02-01 | 115 | 0 | Planned | 1860000
A in MTEP22 | C | West | XEL | 21888 | 2021-09-13 |  | Line 0761 Rebuild | Wreck-out 19.7 miles of existing 69kV on line 0761 rebuild to current 69kV Standards | MN | MN | 2022-12-15 | Rebuilding line for age and condition. Built in 1960, refurbished in 2011. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Age and Condition | 2022-12-15 | 2022-12-15 | 69 | 0 | Planned | 8500000
A in MTEP22 | C | West | XEL | 21891 | 2021-09-13 |  | Line 0726 Rebuild | NSM 0726-69kV Line Major line rebuild from Pipestone to Tracy Switching Station. | MN | MN | 2024-12-21 | Rebuilding line for age and condition |  |  | Northern States Power (Xcel Energy) |  | Other |  | Age and Condition | 2024-12-21 | 2024-12-21 | 69 | 0 | Planned | 17150000
A in MTEP22 | C | West | XEL | 21892 | 2021-09-13 |  | West Shakopee Interconnection | City of Shakopee T-L Interconnection Request. In-and-out off NSP’s Scott County - Dean Lake 115kV transmission line. Joint substation, NSP will own the high side. | MN | MN | 2023-06-01 | Needed to accommodate the rapidly developing load growth along the western edge of the City of Shakopee’s territory. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Load Growth | 2023-06-01 | 2023-06-01 | 115 | 0 | Planned | 3000000
A in MTEP22 | C | West | XEL | 22629 | 2022-09-15 |  | Wheaton Sub Tie | Project will tie Wheaton generation bus 1 to bus 2, effectively moving TR3 to the same bus as TR1 and TR2. | WI | WI | 2023-06-01 | This project will allow for operational flexibility between the two Wheaton buses. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Other Local Needs | 2023-06-01 | 2023-06-01 | 161 | 0 | Planned | 1500000
A in MTEP22 | C | West | XEL | 22686 | 2022-05-16 |  | Briggs Road - Lacrosse Upgrade | Reconductor of Briggs Road - Mayfair - LaCrosse line for age and condition. Upgrade to larger size to remediate N-1-1 thermal overloads. | WI | WI | 2023-05-15 | Line being reconductored for age and condition. Upgrading to large conductor to remediate N-1-1 overloads. |  |  | Northern States Power (Xcel Energy) |  | BRP |  |  | 2023-05-15 | 2023-05-15 | 161 | 0 | Planned | 4000000
A in MTEP22 | C | West | XEL | 23452 | 2022-09-08 |  | Brookings - Lyon, Hampton - Helena 2nd 345kV Circuits | Install second 345 kV circuit between the Brookings County and Lyon County substations. Install second 345 kV circuit between the Hampton Corner and Helena substations. Perform substation upgrades associated with installation of line. | MN | MN | 2025-09-01 | Adds second circuit that eliminates current system conditions that impede deliverability of existing resources to demand centers in primarily off-peak periods of high renewable production which results in a reduction of available generation capacity at times of higher than average maintenance and construction outages. |  |  | Northern States Power (Xcel Energy) |  | Other |  | Reliability | 2025-09-01 | 2025-09-01 | 345 | 0 | Proposed | 48700000

## Facilities MTEP22
Target Appendix | App ABC | Planning Region | Geographic Location by TO Member System | PrjID | Prj Rec Date | Owner PrjID | Facility ID | Record Date | Facility Type | Expected ISD | From Sub | To Sub | Ckt | Max kV | Min kV | Facility Rating | Description | Map Grid | State | Miles Upgrade | Miles New | Plan Status | Estimated Cost | Estimate Type | Gen Int Upgrade Type | Est. Year Dollars | Comments | Emerg. Rating | Submitting Comp. | TSR Cond Upg | Cost Shared | Postage Stamp
A in MTEP22 | B | West | ATC | 16766 | 2021-09-15 |  | 26620 | 2022-08-24 | SUBmisc | 2026-06-30 | Various Sites |  |  | 345 | 69 |  | Small capital project and asset renewal. |  | WI,MI |  |  | Proposed | 34925540 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | B | West | ATC | 16767 | 2022-09-02 |  | 26621 | 2022-08-24 | COM | 2026-06-30 | Various Sites |  |  | 0 |  |  | Communications Reliability Program |  | WI,MI |  |  | Proposed | 19593713 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | B | West | ATC | 16768 | 2021-09-15 |  | 26622 | 2022-08-24 | LNup | 2026-06-30 | Various Lines |  |  | 345 | 69 |  | Line Clearance Mitigation Program |  | WI,MI |  |  | Proposed | 3935020 |  |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | B | West | ATC | 16769 | 2021-09-15 |  | 26623 | 2022-08-24 | SUBmisc | 2025-01-01 | Various Sites |  |  | 345 | 69 |  | Physical Security Program |  | WI,MI |  |  | Proposed | 1859619 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | B | West | ATC | 16770 | 2021-09-15 |  | 26624 | 2022-08-24 | SUB | 2026-06-30 | Various Sites |  |  | 345 | 69 |  | Load Interconnection Program |  | WI,MI |  |  | Proposed | 18045914 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | B | West | ATC | 18046 | 2021-09-15 |  | 24826 | 2021-01-15 | LNrb | 2025-12-31 | Darlington | Rock Branch | Y-109 | 69 |  |  | Line Rebuild |  | WI |  |  | Proposed | 16700000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | B | West | ATC | 18047 | 2021-09-15 |  | 24827 | 2021-09-13 | LNrb | 2026-12-31 | South Beaver Dam | Horicon | Y-134 | 69 |  |  | Line Rebuild |  | WI |  |  | Proposed | 20100000 | Scoping |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | B | West | ATC | 18049 | 2022-08-23 |  | 24829 | 2022-08-23 | LNup | 2025-12-01 | 9 Mile SW STA | Portage |  | 69 |  |  | Re-insulation |  | MI |  |  | Proposed | 5400000 | Scoping |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 19525 | 2022-01-18 | PR08542 | 25500 | 2022-01-18 | SUB | 2025-12-01 | Saratoga SS |  |  | 138 | 69 |  | Asset Renewal |  | WI |  |  | Proposed | 8200000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 19962 | 2021-09-15 | PR08804, F5957 | 25646 | 2021-05-19 | LNrb | 2025-12-31 | Nelson Dewey | Bloomington | Y-184 | 69 |  |  | Line Rebuild |  | WI |  |  | Proposed | 16300000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 19966 | 2022-08-24 |  | 25971 | 2022-08-24 | IND | 2025-12-31 | Munising Area |  |  | 138 |  |  | Reactive Power Project |  | MI |  |  | Proposed | 10000000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 20805 | 2022-01-18 |  | 26100 | 2021-05-18 | SUB | 2024-12-31 | Kitty Hawk SS |  |  | 345 | 138 |  | This project will add a 500-MVA, 345-138 kV transformer at the Kitty Hawk substation and a 138 kV line between the Kitty Hawk and Town Line Road substations |  | WI |  |  | Proposed | 37100000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 20805 | 2022-01-18 |  | 26222 | 2021-05-18 | LINE | 2024-12-31 | Kittyhawk SS | Townline Rd |  | 138 |  |  | •Construct a temporary bypass for lines X-95 and X-39 around the Kittyhawk expansion area |  | WI |  |  | Proposed | 373000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 20805 | 2022-01-18 |  | 26221 | 2021-05-18 | BUS | 2024-12-21 | Rock River SS |  |  | 138 |  |  | •Reconductor bus 2 which consists of 3 138kV box structures |  | WI |  |  | Proposed | 408000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 20805 | 2022-01-18 |  | 26220 | 2021-05-18 | SUB | 2024-12-24 | Townline Rd |  |  | 138 |  |  | •Utilize existing 138kV open position at Townline Rd •Install new takeoff structure, switches, breaker, bus VTs, relay panels •See Townline Rd summary page for full scope |  | WI |  |  | Proposed | 1800000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 20805 | 2022-01-18 |  | 26219 | 2021-05-18 | LN | 2024-12-31 | Kittyhawk SS | Townline Road |  | 138 |  |  | •New 0.44 mile 138kV line from Kittyhawk to Townline Rd •Modify X-95 & X-39 138kV structures to enter Kittyhawk |  | WI |  |  | Proposed | 2320000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 20805 | 2022-01-18 |  | 26218 | 2021-05-18 | SUBmisc | 2024-12-31 | Remote End Grounding | Various Sites |  | 138 | 69 |  | •Upgrade grounding at 8 remote sites due to increased fault current •Townline Rd, Riverside, Rock River, Kittyhawk, West Riverside RAT, West Riverside, BOC Gasses, Marine |  | WI |  |  | Proposed | 2520000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 20805 | 2022-01-18 |  | 26217 | 2021-05-18 | LNrb | 2024-12-31 | Rock River SS | Marine | X-23 | 138 |  |  | •1.77 miles of X-23 needs to be reconductored. Due to the existing wood pole sizes and structure configuration, it is assumed all poles in the section need to be rebuilt. •Rebuild 0.5 miles of Y-72 to double circuit it with X-23 due to Rock River crossing and marsh terrain |  | WI |  |  | Proposed | 5200000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21286 | 2022-05-23 |  | 26229 | 2021-05-26 | TX | 2023-12-31 | Rocky Run SS |  |  | 345 | 115 |  | Replace #1 transformer. |  | WI |  |  | Proposed | 5408000 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21345 | 2021-09-13 |  | 26237 | 2022-04-20 | LNrb | 2025-12-31 | National SS | Presque Isle SW YD | 446 | 138 |  |  | Re-insulate & OPGW |  | MI |  |  | Proposed | 8300000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21346 | 2021-09-13 |  | 26238 | 2021-06-15 | LNrb | 2024-12-31 | Ontonagon | Victoria Hy |  | 69 |  |  | Re-insulate |  | MI |  |  | Proposed | 4750000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21347 | 2021-09-13 |  | 26239 | 2021-08-02 | LNrb | 2025-06-30 | Huiskamp | Ruskin | 6937 | 69 |  |  | Partial Rebuild |  | MI |  |  | Proposed | 7900000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21348 | 2022-01-19 |  | 26240 | 2022-01-19 | LNrb | 2024-04-01 | Tower Dr | Pulliam |  | 69 |  |  | Partial Rebuild |  | WI |  |  | Proposed | 4100000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21627 | 2021-09-13 |  | 26305 | 2021-08-09 | SUB | 2025-12-31 | North Lake SS |  |  | 138 | 69 |  | Power Transformer Asset Renewal |  | MI |  |  | Proposed | 4221065 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21628 | 2021-09-13 |  | 26306 | 2021-09-13 | SUB | 2025-12-31 | Rockdale SS |  |  | 345 | 138 |  | Control House & Relay Asset Renewal |  | WI |  |  | Proposed | 2900000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21628 | 2021-09-13 |  | 26307 | 2021-09-13 | SUB | 2025-12-31 | Christina SS |  |  | 138 |  |  | Control House & Relay Asset Renewal |  | WI |  |  | Proposed | 2900000 |  |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21629 | 2021-09-13 |  | 26308 | 2021-09-13 | SUB | 2025-12-31 | Oak Creek SS |  |  | 230 | 138 |  | Control Building & Relay Asset Renewal |  | WI |  |  | Proposed | 10450000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21629 | 2021-09-13 |  | 26309 | 2021-09-13 | SUB | 2025-12-31 | Racine SS |  |  | 345 | 138 |  | Control Building & Relay Asset Renewal |  | WI |  |  | Proposed | 10450000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21648 | 2021-09-21 |  | 26313 | 2021-09-09 | SUB | 2023-03-27 | Comet SS |  |  | 138 |  |  | Network Upgrades |  | WI |  |  | Proposed | 5730660 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21648 | 2021-09-21 |  | 26315 | 2022-08-24 | LINE | 2023-03-27 | Nelson Dewey SS | Ebenezer SS | X-16 | 138 |  |  | Loop into New SS |  | WI |  |  | Proposed | 710798 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21648 | 2021-09-21 |  | 26314 | 2021-09-09 | INT | 2023-03-27 | Comet SS |  |  | 138 |  |  | Interconnection Facilities |  | WI |  |  | Proposed | 252140 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21812 | 2022-01-19 |  | 26388 | 2021-09-09 | SUB | 2023-01-26 | Wautoma SS |  |  | 138 | 69 |  | Network Upgrades |  | WI |  |  | Proposed | 2019572 |  |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21812 | 2022-01-19 |  | 26390 | 2021-09-09 | INT | 2023-01-26 | Wautoma SS |  |  | 138 |  |  | Interconnection Facilities |  | WI |  |  | Proposed | 627686 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21812 | 2022-01-19 |  | 26389 | 2021-09-09 | LINE | 2023-01-26 | Green Lake SS | Wautoma SS | X-10 | 138 |  |  | Reroute into SS (X-10) |  | WI |  |  | Proposed | 599409 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21813 | 2022-08-24 |  | 26391 | 2022-08-24 | SUB | 2023-06-06 | North Beaver Dam SS |  |  | 138 | 69 |  | Substation Modifications |  | WI |  |  | Proposed | 366697 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21813 | 2022-08-24 |  | 26392 | 2022-08-24 | INT | 2023-06-06 | North Beaver Dam SS |  |  | 138 | 69 |  | Interconnection Facilities |  | WI |  |  | Proposed | 664689 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21814 | 2022-01-19 |  | 26393 | 2022-01-19 | SUBmisc | 2023-12-31 | Chaffee Creek SS |  |  | 69 |  |  | Grounding Improvements |  | WI |  |  | Proposed | 220000 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21814 | 2022-01-19 |  | 26400 | 2022-01-19 | LINE | 2023-12-31 | Wautoma SS | Port Edwards SS | X-11 | 138 |  |  | X-11 Uprate |  | WI |  |  | Proposed | 519783 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21814 | 2022-01-19 |  | 26399 | 2022-01-19 | SUB | 2023-12-31 | Wautoma SS |  |  | 138 | 69 |  | Transformer Replacement |  | WI |  |  | Proposed | 4738573 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21814 | 2022-01-19 |  | 26398 | 2022-01-19 | SUBmisc | 2023-12-31 | Wautoma SS |  |  | 138 | 69 |  | Grounding Improvements |  | WI |  |  | Proposed | 220000 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21814 | 2022-01-19 |  | 26397 | 2022-01-19 | SUBmisc | 2023-12-31 | Saratoga SS |  |  | 138 | 69 |  | Grounding Improvements |  | WI |  |  | Proposed | 672154 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21814 | 2022-01-19 |  | 26396 | 2022-01-19 | SUBmisc | 2023-12-31 | Sand Lake SS |  |  | 138 |  |  | Grounding Improvements |  | WI |  |  | Proposed | 220000 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21814 | 2022-01-19 |  | 26395 | 2022-01-19 | SUBmisc | 2023-12-31 | Hollywood SS |  |  | 69 |  |  | Grounding Improvements |  | WI |  |  | Proposed | 696730 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21814 | 2022-01-19 |  | 26394 | 2022-01-19 | SUBmisc | 2023-12-31 | Hancock SS |  |  | 69 |  |  | Grounding Improvements |  | WI |  |  | Proposed | 220000 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21899 | 2022-01-19 |  | 26489 | 2021-09-13 | LNrb | 2025-06-30 | Port Washington SS | Saukville SS |  | 138 |  |  | Port Washington – Saukville 138 kV (X-132/X-133) partial rebuild |  | WI |  |  | Proposed | 7000000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21915 | 2022-01-19 |  | 26523 | 2022-01-18 | SUB | 2025-12-31 | Fitzgerald SS |  |  | 345 | 138 |  | Transformer Replacement |  | WI |  |  | Proposed | 7897437 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21916 | 2021-09-13 |  | 26524 | 2021-09-13 | LNrb | 2026-12-31 | Browntown SS | South Monroe SS | Y-155 | 69 |  |  | Rebuild |  | WI |  |  | Proposed | 10300000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21917 | 2022-01-18 |  | 26525 | 2022-04-18 | SUB | 2025-12-31 | West Marinette SS |  |  | 138 | 69 |  | Transformer and Breaker Asset Renewal |  | WI |  |  | Proposed | 8962353 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21918 | 2022-01-31 |  | 26526 | 2022-08-24 | LNrb | 2027-12-31 | Pine River SS | Mich Limestone Load Dock | 6906 | 69 |  |  | Pine River - Mich Limestone Loading Dock 69 kV (ESE_6906), Rebuild |  | MI |  |  | Proposed | 31100000 | Planning |  | 2027 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21923 | 2022-01-19 |  | 26531 | 2021-09-15 | SUB | 2025-12-31 | Everett GIS SS |  |  | 138 |  |  | Everett GIS Asset Renewal |  | WI |  |  | Proposed | 16968398 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21925 | 2022-01-19 |  | 26533 | 2022-01-19 | SUB | 2025-09-01 | Plymouth #5 SS |  |  | 138 |  |  | Plymouth #5 - New DIC |  | WI |  |  | Proposed | 21500000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 21926 | 2022-08-24 |  | 26648 | 2021-09-15 | LNrb | 2025-12-31 | Norwich SS | Harbor SS |  | 138 |  |  | Norwich - Harbor 138kV, (893K11), underground line replacement |  | WI |  |  | Proposed | 37000000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22045 | 2021-11-04 |  | 26693 | 2021-09-24 | SUBmisc | 2022-12-31 | Spring Green SS |  |  | 138 |  |  | Grounding improvements |  | WI |  |  | Proposed | 220000 | Planning |  | 2022 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22046 | 2021-11-04 | PR08822 | 26694 | 2022-07-15 | INT | 2022-04-06 | Sheepskin SS |  |  | 138 |  |  | Interconnection Facilities |  | WI |  |  | M5_In Service | 417856 | Planning |  | 2022 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22046 | 2021-11-04 | PR08822 | 26696 | 2022-08-24 | SUBmisc | 2022-04-06 | Sheepskin SS |  |  | 138 |  |  | Network Upgrades |  | WI |  |  | M5_In Service | 491605 | Planning |  | 2022 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22046 | 2021-11-04 | PR08822 | 26695 | 2022-07-15 | SUB | 2022-05-11 | Sheepskin SS |  |  | 138 |  |  | Ground Grid |  | WI |  |  | M5_In Service | 220000 | Planning |  | 2022 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22047 | 2021-11-04 |  | 26697 | 2021-09-24 | LNrb | 2023-05-15 | Crawfish River SS | Jefferson SS | 6654 | 138 |  |  | Line rebuild |  | WI |  |  | Proposed | 1090475 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22047 | 2021-11-04 |  | 26698 | 2021-09-24 | LNrb | 2023-05-15 | Concord SS | Crawfish River SS | 9043 | 138 |  |  | Line rebuild |  | WI |  |  | Proposed | 1253209 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22048 | 2021-11-04 |  | 26700 | 2021-09-24 | SUBmisc | 2023-12-31 | Roeder SS |  |  | 138 |  |  | Ground grid improvements. |  | WI |  |  | Proposed | 220000 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22049 | 2021-11-04 |  | 26701 | 2021-09-24 | RLY | 2023-08-15 | Kewaunee SS |  |  | 345 |  |  | protective relay |  | WI |  |  | Proposed | 155000 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22085 | 2021-11-04 |  | 26706 | 2021-10-07 | SUBmisc | 2023-12-31 | North Beaver Dam |  |  | 138 | 69 |  | Ground Grid Analysis |  | WI |  |  | Proposed | 550000 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22105 | 2022-01-19 |  | 26720 | 2021-10-29 | SUB | 2023-09-15 | North Lake Geneva SS |  |  | 138 |  |  | Network Upgrades |  | WI |  |  | Proposed | 750098 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22105 | 2022-01-19 |  | 26722 | 2021-10-29 | INT | 2023-09-15 | North Lake Geneva SS |  |  | 138 |  |  | Interconnection Facilities |  | WI |  |  | Proposed | 627259 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22105 | 2022-01-19 |  | 26721 | 2021-10-29 | SUBmisc | 2023-09-15 | North Lake Geneva SS |  |  | 138 |  |  | Ground Grid Upgrades |  | WI |  |  | Proposed | 30000 | GIA |  |  |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22145 | 2022-01-19 | PR08781, F6068, F6070 | 26723 | 2022-08-24 | INT | 2022-07-20 | Holland SS |  |  | 138 |  |  | Interconnection Facilities |  | WI |  |  | M5_In Service | 651073 | GIA |  | 2022 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22145 | 2022-01-19 | PR08781, F6068, F6070 | 26731 | 2022-08-24 | RLY | 2022-07-20 | Forest Junction SS |  |  | 138 |  |  | Relay Panel Replacement |  | WI |  |  | M5_In Service | 445440 | GIA |  | 2022 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22145 | 2022-01-19 | PR08781, F6068, F6070 | 26730 | 2022-08-24 | RLY | 2022-07-20 | Howards Grove SS |  |  | 138 |  |  | Relay Panel Replacement |  | WI |  |  | M5_In Service | 632054 | GIA |  | 2022 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22145 | 2022-01-19 | PR08781, F6068, F6070 | 26729 | 2022-08-24 | RLY | 2022-07-20 | Plymouth SS |  |  | 138 |  |  | Relay Panel Replacements |  | WI |  |  | M5_In Service | 643548 | Planning |  | 2022 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22145 | 2022-01-19 | PR08781, F6068, F6070 | 26728 | 2022-08-24 | RLY | 2022-07-20 | Saukville SS |  |  | 345 | 138 |  | Relay Panel Replacements |  | WI |  |  | M5_In Service | 444947 | GIA |  | 2022 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22145 | 2022-01-19 | PR08781, F6068, F6070 | 26727 | 2022-08-24 | SUB | 2022-07-20 | Holland SS |  |  | 138 |  |  | Network Upgrades |  | WI |  |  | M5_In Service | 4745045 | GIA |  | 2022 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22145 | 2022-01-19 | PR08781, F6068, F6070 | 26726 | 2022-08-24 | SUBmisc | 2022-06-01 | Howards Grove SS |  |  | 138 |  |  | Ground Grid Upgrades |  | WI |  |  | Withdrawn | 220000 | GIA |  | 2022 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22145 | 2022-01-19 | PR08781, F6068, F6070 | 26725 | 2022-07-15 | SUBmisc | 2022-06-14 | Plymouth SS |  |  | 138 |  |  | Ground Grid Upgrades |  | WI |  |  | M5_In Service | 550000 | GIA |  | 2022 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22145 | 2022-01-19 | PR08781, F6068, F6070 | 26724 | 2022-08-24 | SUBmisc | 2022-06-01 | Holland SS |  |  | 138 |  |  | Ground Grid Upgrades |  | WI |  |  | Withdrawn | 110000 | GIA |  | 2022 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22146 | 2022-01-19 | PR08819, F6104, F6105 | 26732 | 2021-10-29 | INT | 2023-01-26 | Butternut SS |  |  | 138 |  |  | Interconnection Facilities |  | WI |  |  | Proposed | 819868 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22146 | 2022-01-19 | PR08819, F6104, F6105 | 26737 | 2021-10-29 | SUBmisc | 2023-01-26 | Butternut SS |  |  | 138 |  |  | Ground Grid Upgrades |  | WI |  |  | Proposed | 550000 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22146 | 2022-01-19 | PR08819, F6104, F6105 | 26736 | 2021-10-29 | SUB | 2023-01-26 | Forward Energy Center SS |  |  | 138 |  |  | Network Upgrades |  | WI |  |  | Proposed | 482308 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22146 | 2022-01-19 | PR08819, F6104, F6105 | 26735 | 2021-10-29 | SUB | 2023-01-26 | Auburn SS |  |  | 138 |  |  | Network Upgrades |  | WI |  |  | Proposed | 145578 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22146 | 2022-01-19 | PR08819, F6104, F6105 | 26734 | 2021-10-29 | SUB | 2023-01-26 | South Fond du Lac SS |  |  | 345 | 138 |  | Network Upgrades |  | WI |  |  | Proposed | 399270 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22146 | 2022-01-19 | PR08819, F6104, F6105 | 26733 | 2021-10-29 | SUB | 2023-01-26 | Butternut SS |  |  | 138 |  |  | Network Upgrades |  | WI |  |  | Proposed | 1521698 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22225 | 2022-01-19 |  | 26742 | 2021-11-09 | LNup | 2023-11-01 | Burlington | Sugar Creek | 6541 | 138 |  |  | Line Uprate |  | WI |  |  | Proposed | 4365163 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22986 | 2022-08-03 |  | 26869 | 2022-05-23 | CAP | 2024-12-31 | Vinburn SS |  |  | 69 |  |  | Add capacitor bank |  | WI |  |  | Proposed | 3620000 | Engineering |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22987 | 2022-05-23 | PR08815, F6122 | 26870 | 2022-05-23 | Dist | 2023-06-01 | Northview SS |  |  | 138 |  |  | New ~0.6mi 138kV tap off line X-107 to connect Alliant’s newly proposed Northview Substation. |  | WI |  |  | Proposed | 3220000 | Engineering |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22988 | 2022-05-23 |  | 26882 | 2022-05-23 | SUB | 2024-12-31 | Gaston Rd |  |  | 69 |  |  | Additional Transformer |  | WI |  |  | Proposed | 3000000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 22989 | 2022-05-23 |  | 26883 | 2022-08-24 | SUB | 2024-06-01 | Columbus SS |  |  | 69 |  |  | Transformer Replacement |  | WI |  |  | Proposed | 8782156 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 23007 | 2022-05-23 |  | 26881 | 2022-05-23 | SUB | 2024-12-31 | Cambria SS |  |  | 69 |  |  | New Substation, load interconnection |  | WI |  |  | Proposed | 3000000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 23008 | 2022-05-23 |  | 26894 | 2022-05-23 | LNrl | 2026-12-31 | WisDOT Relocation (Reimbursable) |  |  | 138 |  |  | WisDOT I-94 E/W Road Move: Conflict and relocation of ATC existing facilities |  | WI |  |  | Proposed | 51400000 | Budgetary |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 23008 | 2022-05-23 |  | 26897 | 2022-05-23 | COM | 2026-12-31 | 96th Street | Valley |  | 138 |  |  | Communication Infrastructure Improvement |  | WI |  |  | Proposed | 1400000 | Budgetary |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 23008 | 2022-05-23 |  | 26896 | 2022-05-23 | LNrb | 2026-12-31 | Asset Renewal of Structures 4145-4149 |  |  | 138 |  |  | Rebuild lines adjacent and concurrent to WisDOT Road Move due to age and condition |  | WI |  |  | Proposed | 10900000 | Budgetary |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 23520 | 2022-08-26 |  | 27305 | 2022-08-26 | Dist | 2024-05-01 | Johnstown SS |  |  | 69 |  |  | New Substation |  | WI |  |  | Proposed | 3000000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | C | West | ATC | 23531 | 2022-08-26 |  | 27303 | 2022-08-26 | COM | 2024-12-31 | Cottonwood | Summit |  | 138 |  |  | install underground fiber |  | WI |  |  | Proposed | 3156228 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP22 | B | Central | AmerenIL | 20905 | 2021-09-17 | TP1442 | 26110 | 2022-04-11 | INT | 2021-12-01 | Fogarty |  |  | 138 |  |  | This project provides an interconnection point for J1102 to connect at to supply power they generate to MISO customers. |  | IL |  |  | M5_In Service | 500000 | Budgetary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenIL | 21005 | 2021-10-14 | TP1450 | 26124 | 2021-10-14 | CB | 2023-06-01 | Ina |  |  | 138 |  |  | Add a line breaker on the Benton NW terminal at Ina. |  | IL |  |  | Planned | 850000 | Budgetary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenIL | 21306 | 2022-07-15 | TP1453 | 26232 | 2022-07-15 | SwSta | 2024-12-01 | Monument | Macomb West |  | 138 |  |  | Ameren would construct a new 138 kV substation in ring bus configuration on the existing Ameren Monument-Macomb West-1646 138 kV line near structure 97 |  | IL |  |  | Planned | 8000000 | Budgetary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenIL | 21326 | 2021-09-17 | TP1407 | 26236 | 2021-09-21 | SwSta | 2023-12-01 | Ipava | Meredosia E |  | 138 |  |  | 3-position initial, 4 ultimate ringbus on the Ipava-Meredosia E-1568 138 kV line for PPI Indian Creek 138/69kV substation |  | IL |  |  | Planned | 8000000 | Budgetary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenIL | 21365 | 2021-10-14 | TP1448 | 26241 | 2021-10-14 | SwSta | 2023-06-01 | Havana | Shockey |  | 138 |  |  | Puro Ring Bus for J1453 |  | IL |  |  | Planned | 7200000 | Budgetary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenIL | 21365 | 2021-10-14 | TP1448 | 26242 | 2021-10-14 | INT | 2023-06-01 | Puro |  |  | 138 |  |  | Puro ring bus for J1453 |  | IL |  |  | Planned | [6 empty] | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenIL | 21385 | 2021-09-24 | TP5004 | 26249 | 2021-07-14 | LNrb | 2023-12-01 | Austin | Taylorville South |  | 138 |  |  | Rebuild Austin-Taylorville South-1545 |  | IL |  |  | Planned | 8900000 | Budgetary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenIL | 21386 | 2021-09-24 | TP5007 | 26250 | 2022-01-13 | LNrb | 2023-12-01 | Ruby | Sidney |  | 345 |  |  | Ruby-Sidney-4560 345 kV rebuild from structures 5-18 |  | IL |  |  | Planned | 2200000 | Budgetary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenIL | 21405 | 2021-09-24 | TP5086 | 26252 | 2022-01-24 | LNrb | 2023-06-01 | Mattoon East | Charleston NE |  | 138 |  |  | Rebuild this line due to the condition of the structures, will add OPGW as part of this. This is the Mattoon East to Charleston NE section of the line. |  | IL |  |  | Planned | 3400000 | Budgetary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenIL | 21406 | 2021-09-24 | TP5106 | 26253 | 2022-01-24 | LNrb | 2023-12-01 | Sparta | Tibbs |  | 138 |  |  | Repair issues found during inspections |  | IL |  |  | Planned | 2300000 | Budgetary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenIL | 21426 | 2021-09-24 | TP1417 | 26257 | 2021-10-14 | LNrc | 2022-12-01 | South Bloomington | West Washington | 1334 | 138 |  |  | Replace 3.5 miles of 477 KCMIL ACSR/T2 30/7 Hen 138 kV line conductor in SBLM-WWSH-1334 with new line conductor having a minimum summer emergency rating of 2000 Amps |  | IL |  |  | Planned | 3600000 | Budgetary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenIL | 21426 | 2021-09-24 | TP1417 | 26258 | 2021-10-14 | LNrc | 2022-12-01 | South Bloomington | West Washington | 1544 | 138 |  |  | Replace 3.48 miles of 477 KCMIL ACSR/T2 30/7 Hen 138 kV line conductor in SBLM-WWSH-1544 with new line conductor having a minimum summer emergency rating of 2000 Amps |  | IL |  |  | Planned | 600000 | Budgetary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenIL | 21428 | 2022-01-31 | TP1459 | 26259 | 2022-08-24 | LNrb | 2022-12-15 | Tanner | Xenia |  | 345 |  |  | Rebuild the existing Newton-Xenia-1 345 kV line from Xenia-Str. 44. New conductor will be capable of 3000 A and 2 OPGW shield wires will be installed. |  | IL |  |  | Planned | 9100000 | Budgetary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenIL | 21645 | 2022-01-12 | TP1460 | 26310 | 2022-01-19 | INT | 2023-06-01 | Sidney |  |  | 138 |  |  | One 138 kV terminal in the Sidney Substation. The terminal will consist of all necessary terminal equipment to connect the J1139 leadline to the Sidney Substation 138 kV bus. |  | IL |  |  | Planned | 500000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenIL | 21646 | 2021-09-24 | TP1461 | 26311 | 2022-07-15 | LNrb | 2023-12-01 | Sullivan | Casey West |  | 345 |  |  | Project upgrades the line to structures that meet Ameren's current loading requirements, hardening the circuit against storms and improving resiliency against cascade failure |  | IL |  |  | Planned | 36100000 | Engineering |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenIL | 21647 | 2021-09-17 | TP1462 | 26312 | 2021-10-14 | LNrb | 2024-12-01 | Casey West | Kansas |  | 345 |  |  | Rebuild the Casey West-Kansas-4525 345 kV line with conductors capable of 3000 amps Summer Emergency rating and two OPGWs. |  | IL |  |  | Planned | 25200000 | Engineering |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenIL | 21970 | 2022-01-19 | TP1466 | 26598 | 2022-01-24 | LNrc | 2026-06-01 | Kinmundy | Tanner |  | 138 |  |  | Reconductor 27.4 miles Kinmundy-Tanner 138 kV line |  | IL |  |  | Planned | 10000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenIL | 22325 | 2022-01-12 | TP1473 | 26773 | 2022-01-19 | SwSta | 2023-10-31 | Mogul |  |  | 345 |  |  | Construct a new 345 kV switching station in Sangamon, Macoupin & Morgan Counties, Illinois to provide a Point of Interconnection for the Generating Facility. The new 345kV Mogul switching station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Austin – Turner 345 kV transmission line and terminate the ends at two of the terminal positions. |  | IL |  |  | Planned | 10300000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenIL | 22385 | 2022-01-12 | TP1478 | 26778 | 2022-01-19 | SwSta | 2024-06-01 | Dion |  |  | 345 |  |  | The Dion switching station will be a ring bus arrangement with three-line terminal positions and provisions for one additional future terminal position. The existing Latham-Oreana 345 kV transmission line will be cut. |  | IL |  |  | Planned | 10500000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenIL | 22405 | 2022-01-12 | TP1479 | 26779 | 2022-01-19 | TEQ | 2023-06-01 | Xenia |  |  | 345 |  |  | Add 345 kV terminal in the Xenia switching station for the J991 project. |  | IL |  |  | Planned | 1000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenIL | 22407 | 2022-01-12 | TP1481 | 26781 | 2022-08-11 | TEQ | 2023-06-01 | Mapleridge |  |  | 345 |  |  | Add position to the existing Mapleridge 345 kV switching station for J974 interconnection facilities. |  | IL |  |  | Planned | 2242000 | Engineering |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenIL | 22485 | 2022-01-12 | TP1485 | 26793 | 2022-08-11 | SwSta | 2024-01-01 | Prest |  |  | 138 |  |  | Expand and convert the Prest switching station 138 kV bus from a 6-position ring to a 4-leg breaker and a half (BAAH) configuration |  | IL |  |  | Planned | 8520000 | Engineering Preliminary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenIL | 22566 | 2022-01-12 | TP1488 | 26798 | 2022-08-11 | SwSta | 2024-01-01 | Morganfield |  |  | 138 |  |  | Construct a new 138 kV switching station in Saline County, Illinois to provide a Point of Interconnection for the Generating Facility. The new Morganfield 138 kV J1096 Interconnection Switching Station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Muddy-Norris City North 138 kV transmission line. |  | IL |  |  | Planned | 6519000 | Facility Study |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenMO | 18063 | 2022-08-17 | TP1350 | 24847 | 2022-09-14 | SUB | 2025-12-01 | Maywood | Sub T |  | 345 | 0 |  | Placeholder |  | IA |  |  | Planned | 2600000 | Budgetary |  |  | Construct three breaker, 345 kV substation west of Mt. Pleasant, Iowa, along the Maywood-Sub T Transmission Line. Install 345/69 kV step-down transformer and construct 69 kV networked loop to interconnect MPMU's distribution substations |  | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenMO | 21931 | 2021-09-20 |  | 26541 | 2022-05-19 | SUB | 2021-06-01 | Crosstown |  |  | 69 | 12 |  | Crosstown Substation is needed to help relieve loading on Altenburg, McBride, and Park Substations which are forecast to exceed their OA rating. |  | MO |  |  | M5_In Service | 800000 | Engineering |  |  |  |  | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP22 | B | Central | AmerenMO | 21948 | 2022-05-18 |  | 26568 | 2022-05-18 | SUB | 2022-05-31 | New Bourbon |  |  | 69 |  |  | Replace B40 bus tie breaker that had several issues at New Bourbon. Had trouble while they were operating the breaker to put the station back in service after maintenance. |  | MO |  |  | Planned | 381780 | Planning |  |  |  |  | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP22 | B | Central | AmerenMO | 21949 | 2022-05-18 |  | 26569 | 2022-05-19 | LNrb | 2024-03-31 | Carron |  |  | 34.5 |  | 19MVA | Rebuild 34kV line that feeds the Mosher B,C,&F plants and the Geneva switching station. This includes most of the switches in the line section. |  | MO | 3.1 |  | Planned | 4558281 | Engineering |  |  |  | 19MVA | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP22 | B | Central | AmerenMO | 21967 | 2021-09-20 | TP1464 | 26590 | 2022-01-19 | CAP | 2023-06-01 | Dillon |  |  | 138 |  |  | Add Dillon 14 MVAR Cap Bank |  | MO |  |  | Planned | 500000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | B | Central | AmerenMO | 21971 | 2022-01-26 | TP1467 | 26599 | 2021-09-21 | CB | 2023-06-01 | Callaway |  |  | 345 |  |  | Add circuit breakers to high side of safeguard transformers A and B |  | MO |  |  | Planned | 3000000 | Budgetary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenMO | 22365 | 2022-01-12 | TP1477 | 26777 | 2022-08-11 | SwSta | 2023-11-01 | Adna |  |  | 345 |  |  | The Adna switching station will be a ring bus arrangement with three-line terminal positions and provisions for one additional future terminal position. The existing Kelso-Lutesville 345 kV transmission line will be cut. |  | MO |  |  | Planned | 10837000 | Facility Study |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenMO | 22406 | 2022-01-12 | TP1480 | 26780 | 2022-08-11 | TEQ | 2023-06-01 | Guthrie |  |  | 161 |  |  | Add 161 kV terminal in the Guthrie substation for J994 project. |  | MO |  |  | Planned | 1658000 | Facility Study |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenMO | 22408 | 2022-01-12 | TP1482 | 26782 | 2022-08-11 | TEQ | 2023-06-01 | Montgomery |  |  | 345 | 161 |  | Add 161 kV terminal in the Montgomery substation for the J987 |  | MO |  |  | Planned | 2060000 | GIA |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenMO | 22465 | 2022-01-12 | TP1484 | 26790 | 2022-08-11 | SwSta | 2024-03-31 | Bullion |  |  | 161 |  |  | Construct a new 161 kV switching station in Scott County, Missouri to provide a Point of Interconnection for the Generating Facility. The new 161 kV Bullion switching station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Kelso – Miner 161 kV transmission line. |  | MO |  |  | Planned | 9189000 | GIA |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenMO | 22527 | 2022-01-12 | TP1475 | 26794 | 2022-08-11 | SwSta | 2023-06-01 | Harley 161 kV |  |  | 161 |  |  | Build a 161 kV three position ring bus along the Troy-Pike 161 kV transmission line in Lincoln County, Missouri. |  | MO |  |  | Planned | 10652000 | GIA |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenMO | 22529 | 2022-01-12 | TP1486 | 26796 | 2022-08-11 | SwSta | 2024-06-01 | Vanduser |  |  | 161 |  |  | Construct a new 161 kV switching station in Stoddard County, Missouri to provide a Point of Interconnection for the Generating Facility. The new Vanduser 161 kV J1034 Interconnection Switching Station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Morley – Stoddard 161 kV transmission line |  | MO |  |  | Planned | 6730000 | GIA |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenMO | 22546 | 2022-07-22 | TP1487 | 26797 | 2022-08-11 | SwSta | 2025-12-01 | Rootbeer |  |  | 345 |  |  | Construct a new 345 kV switching station in Warren County, Missouri to provide a Point of Interconnection for the Generating Facility. The new Rootbeer 345 kV J976 Interconnection Switching Station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Belleau – Montgomery 345 kV transmission line. |  | MO |  |  | Planned | 10801000 | GIA |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenMO | 22786 | 2022-08-29 | TP1492 | 26934 | 2022-08-25 | TX | 2024-06-01 | Wildwood |  |  | 345 | 138 |  | Upgrade 560 MVA to 700 MVA Transformer |  | MO |  |  | Proposed | 17500000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenMO | 22807 | 2022-08-25 | TP1494 | 26936 | 2022-08-25 | CAP | 2024-04-01 | Overton |  |  | 161 |  |  | New 67 MVAR Capacitor at Overton 161 kV |  | MO |  |  | Proposed | [6 empty] | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenMO | 22808 | 2022-08-25 | TP1495 | 26937 | 2022-09-01 | SVC | 2024-12-01 | Arnold |  |  | 138 |  |  | Add 250 MVAR Capacitor at Arnold |  | MO |  |  | Proposed | 30000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenMO | 22808 | 2022-08-25 | TP1495 | 27073 | 2022-09-01 | SVC | 2024-12-01 | Bugle |  |  | 138 |  |  | 250 MVAR STATCOM at Bugle |  | MO |  |  | Proposed | 30000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenMO | 22808 | 2022-08-25 | TP1495 | 26939 | 2022-09-01 | SVC | 2024-12-01 | Highway N |  |  | 161 |  |  | add 250 MVAR Statcom at highway N |  | MO |  |  | Proposed | 30000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | AmerenMO | 22808 | 2022-08-25 | TP1495 | 26938 | 2022-09-01 | SVC | 2024-12-01 | Mason |  |  | 138 |  |  | Add 250 MVA STATCOM at Mason |  | MO |  |  | Proposed | 30000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP22 | C | Central | BREC | 20766 | 2021-09-23 |  | 26083 | 2021-01-13 | LN | 2022-02-01 | Easton Tap | Easton Road | 1 | 69 |  |  | New 1.0 mile 69 kV tap with 336 ACSR |  | KY |  | 1 | Proposed | 500000 | Budgetary |  |  |  |  | Big Rivers Electric Corporation | N | N | N
A in MTEP22 | C | Central | BREC | 21685 | 2021-09-22 |  | 26328 | 2021-08-25 | SwSta | 2023-07-01 | HMPL 4 Tap |  |  | 161 |  |  | Convert present HMPL 4 Tap switching site in to a full switching station. |  | KY |  |  | Proposed | 6070000 | Budgetary |  |  |  |  | Big Rivers Electric Corporation | N | N | N
A in MTEP22 | C | Central | BREC | 21685 | 2021-09-22 |  | 26331 | 2021-08-25 | LN | 2023-07-01 | HMPL 4 Tap | HPM |  | 161 |  |  | New 161 kV line to serve industrial customer. |  | KY |  |  | Proposed | 9375000 | Budgetary |  |  |  |  | Big Rivers Electric Corporation | N | N | N
A in MTEP22 | C | Central | BREC | 21685 | 2021-09-22 |  | 26329 | 2021-08-25 | SUB | 2023-07-01 | HPM |  |  | 161 |  |  | Substation at load site. |  | KY |  |  | Proposed | 4755000 | Budgetary |  |  |  |  | Big Rivers Electric Corporation | N | N | N
A in MTEP22 | C | Central | BREC | 22766 | 2022-08-10 |  | 26828 | 2022-08-24 | LNup | 2022-10-01 | McCracken | Shell/Ragland | 1 | 69 |  |  | Raise or replace existing line structures to provide necessary ground clearance. |  | KY |  |  | Proposed | 1500000 | Engineering |  |  |  |  | Big Rivers Electric Corporation | N | N | N
A in MTEP22 | C | South | CLECO | 20163 | 2021-11-17 |  | 25882 | 2021-11-08 | SUB | 2025-06-01 | Mansfield Compressor | Fisher | 1 | 230 | 138 |  | Tap the Existing Mansfield Compressor to Fisher 230 kV line at this new substation 8.3 miles from Fisher. Extend both lines 2.8 miles to a new substation Belmont. This substation would tie into the existing Pelican to Loring and Loring to Many 138 kV lines. This substation will have a 3 breaker 230 kV ring and a 5 terminal breaker and a half 138 kV substation connected by a 300 MVA 230/138 kV Auto |  | LA |  |  | Proposed | 19100000 | Planning Preliminary |  |  |  |  | Cleco Power LLC | N | N | N
A in MTEP22 | C | South | CLECO | 20163 | 2021-11-17 |  | 25884 | 2021-11-08 | TX | 2025-06-01 | Belmont (New Sub) |  |  | 230 | 138 |  | Add a 300 MVA 230/138 kV Autotransformer at the new substation |  | LA |  |  | Proposed | 6000000 | Planning Preliminary |  |  |  |  | Cleco Power LLC | N | N | N
A in MTEP22 | C | South | CLECO | 20163 | 2021-11-17 |  | 25883 | 2021-11-08 | LN | 2025-06-01 | Belmont (New Sub) | Many | 1 | 230 |  |  | Build two new 2.8 mile 230 kV lines from the line tap to Belmont Substation. |  | LA |  | 5.6 | Proposed | 13000000 | Planning Preliminary |  |  |  |  | Cleco Power LLC | N | N | N
A in MTEP22 | C | South | CLECO | 22205 | 2022-01-06 |  | 26741 | 2022-07-05 | SUB | 2023-03-27 | Cooper | Penton | 1 | 230 |  |  | Tap Cooper to Penton 2.4 miles from Cooper substation for a new Substation (Cole) |  | LA |  |  | Proposed | 18764954 | Pre-Construction |  |  |  |  | Cleco Power LLC | N | N | N
A in MTEP22 | C | South | CLECO | 23327 | 2022-08-24 |  | 27020 | 2022-09-13 | SUB | 2023-04-23 | Mansfield Compressor | Fisher | 1 | 230 |  |  | New industrial load substation tapping Mansfield Compressor to Fisher 230 kV line |  | LA |  | 0.8 | Proposed | 15697000 | Engineering Preliminary |  |  |  |  | Cleco Power LLC | N | N | N
A in MTEP22 | C | South | CLECO | 23328 | 2022-08-24 |  | 27021 | 2022-09-13 | SUB | 2023-04-23 | Toledo Bend | Leesville | 1 | 138 |  |  | New industrial load substation tapping Toledo Bend to Leesville 138 kV line |  | LA |  | 1.5 | Proposed | 13650000 | Engineering Preliminary |  |  |  |  | Cleco Power LLC | N | N | N
A in MTEP22 | C | West | CMMPA | 21973 | 2021-09-15 |  | 26601 | 2022-01-18 | TX | 2022-05-02 | Rice Street |  |  | 69 |  |  | Blue Earth Light and Water Rice Street |  | MN |  |  | Proposed | 1250000 | [5 empty] | Central Minnesota Municipal Power Agency | N | N | N
A in MTEP22 | C | West | CMMPA | 21974 | 2021-09-15 |  | 26602 | 2022-01-18 | TX | 2022-05-02 | West |  |  | 69 |  |  | West Sub 69/12.47kV transformer |  | MN |  |  | Proposed | 1500000 | [5 empty] | Central Minnesota Municipal Power Agency | N | N | N
A in MTEP22 | C | West | CMMPA | 21975 | 2022-05-17 |  | 26603 | 2022-09-12 | SUB | 2023-01-16 | Blue Earth AE(ITC) |  |  | 69 |  |  | New Northeast Sub |  | MN |  |  | Proposed | 4100000 | Budgetary |  |  |  |  | Central Minnesota Municipal Power Agency | N | N | N
A in MTEP22 | C | Central | DEI | 2125 | 2021-11-18 | 802J3045 | 2910 | 2021-11-10 | TX | 2024-09-11 | Centerton | transformer | 1 | 138 | 69 | 168 | Upgrade/replace existing 75MVA 138/69kV bank with 150MVA bank |  | IN |  |  | Proposed | 4010138 | Engineering w/AFUDC |  | 2021 | Target A for MTEP22 - late submittal Deferred by Transmission Planning due to lower growth rate projections and development of operating procedures. | 175 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22185 | 2021-11-18 | M200021 | 26739 | 2022-09-13 | GEN | 2023-02-20 | J1063 Hardy Hills Solar |  |  | 230 | 0.66 | 195 | J1063 Hardy Hills Solar (IPL/AES) 230kV POI switching station and 195MW generating station |  | IN |  |  | Under Construction | 3617000 | Engineering w/AFUDC |  | 2021 | DEI cost estimate is lower than normal due to GO self-building the 230kV switching station POI | 195 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22206 | 2021-11-18 | M210417 | 26748 | 2021-11-13 | CB | 2026-03-20 | Dresser |  |  | 138 |  |  | Replace (5) Dresser CBs: 13869-9, 13869-10, 138B3-1, 138B3-2, 138138 were identified in the 2021 short circuit study as being over-dutied during certain fault conditions. This is a NERC TPL 001-4 compliance requirement to replace the following breakers with higher interruption capacity (63 KIAC rating). |  | IN |  |  | Proposed | 562153 | Engineering Preliminary |  | 2021 |  |  | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22207 | 2021-11-18 | M210418 | 26749 | 2021-11-13 | Dist | 2023-12-31 | 138 | 12 |  | 138 | 12 |  | New 138/12 kV - 22.4MVA Belle Union substation for Hendricks Power to be constructed by WVPA. Substation 138kV - 13867 source to be looped through with SCADA controlled switches. |  | IN |  |  | Proposed | 1408403 | Planning Preliminary |  | 2021 |  |  | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22208 | 2021-12-18 | M210521 | 26754 | 2021-12-18 | LNrb | 2027-06-01 | Bedford | Mitchell Lehigh | 1 | 138 |  | 301 | Bedford to Mitchell Lehigh 138kV - Rebuild 13822 line section with 954ACSR@120C; upgrade 1200A Wave trap at Bedford to 2000A; upgrade 954AL bus at Bedford to 1590AL |  | IN | 8.73 |  | Proposed | 17960000 | Planning Preliminary |  | 2021 |  | 301 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22209 | 2021-12-18 | M210528 | 26755 | 2021-12-18 | LNup | 2027-06-01 | Columbus | Seymour | 1 | 138 |  | 178 | Columbus 13830 line terminal: upgrade 300CU bus to 954AL to increase facility rating to 178MVA (line conductor rating) |  | IN |  |  | Proposed | 500000 | Planning Preliminary |  | 2021 |  | 178 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22210 | 2021-11-18 | M180035 | 26756 | 2021-11-15 | LNrb | 2023-05-19 | Collamer Jct | North Manchester |  | 69 |  | 99 | Collamer Jct to N. Manchester 6923 (Pt2) Rebuild with 477ACSR@120C |  | IN | 6.9 |  | Proposed | 7300000 | Engineering Preliminary |  | 2021 |  | 99 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22211 | 2021-11-18 | M180276 | 26757 | 2022-09-13 | SUB | 2024-07-19 | Huntington 138 |  |  | 138 | 69 | 60 | Huntington 138kV Sub rebuild and reconfigure: establish 4-position 138kV ring bus; replace (2)138/69/12 xfmrs with (2)50MVA 138/69 xfmrs and (1)22.4MVA 138/12 xfmr; establish 4-position 69kV ring bus |  | IN |  |  | Proposed | 28444000 | Engineering Preliminary |  | 2021 |  | 65 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22212 | 2022-05-04 | M170059 | 26758 | 2021-11-16 | LNrb | 2023-05-01 | Morgantown | Samaria Jct |  | 69 |  | 150 | Rebuild 6949 Line from Morgantown to Samaria Jct; 3.63 miles; 954ACSR@120C |  | IN | 3.63 |  | Proposed | 2901158 | Engineering Preliminary |  | 2021 | less than 5 miles - no MOD will be submitted for MTEP22 - update will be posted once in service | 150 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22213 | 2021-11-30 | M190306 | 26759 | 2021-11-16 | LNup | 2023-07-28 | Dresser |  |  | 69 |  |  | Dresser 69kV - 6901 Tower Replacements - Replace 1.25 miles of steel lattice towers - six total (802-1012 to 802-1007, including the Wabash River crossing) |  | IN | 1.25 |  | Proposed | 4780000 | Engineering Preliminary |  | 2021 |  |  | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22226 | 2021-12-03 | M210351 | 26750 | 2021-11-15 | SwSta | 2026-10-22 | Sandford 345 |  |  | 345 |  |  | Sandford 345kV substation: Add 3-CB ring bus in the 34513 Cayuga - Sugar Crk line; approximately 6 miles from Sugar Creek. |  | IN |  |  | Proposed | 11000000 | Planning Preliminary |  | 2021 |  |  | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22226 | 2021-12-03 | M210351 | 26752 | 2021-11-15 | SUB | 2026-10-22 | Wabash River 345/230 |  |  | 345 | 230 | 666 | Wabash River Station 345kV-230kV Substation: establish new 345 yard and bus and add 500MVA 345/230 xfmr to tie into existing 230kV bus |  | IN |  |  | Proposed | 17000000 | Planning Preliminary |  | 2021 |  | 682 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22226 | 2021-12-03 | M210351 | 26751 | 2021-11-15 | LN | 2026-10-22 | Sandford 345 | Wabash River 345 |  | 345 |  | 1508 | Build 5.5 mile 345kV - 34556 line from Sandford 345 to existing Wabash River Station |  | IN |  | 5.5 | Proposed | 22000000 | Planning Preliminary |  | 2021 |  | 1508 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22227 | 2021-12-18 | M210523 | 26753 | 2021-12-18 | TX | 2026-12-31 | Staunton | 230/138 xfmr | 3 | 230 | 138 | 177 | Staunton sub - add a third parallel 230/138kV transformer |  | IN |  |  | Proposed | 6000000 | Planning Preliminary |  | 2021 |  | 181 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22230 | 2021-12-15 | M210313/M210371 | 26765 | 2022-07-11 | CB | 2023-05-01 | Gibson Gen Sta |  |  | 345 |  |  | Gibson 345 Switchyard 34509 Line Terminal Upgrades: M210313: WT replace and relays M210371: replace (2)345kV CBs 34509 / 34509-G3 along with associated free-standing CTs and disconnect switches (34509 Line Disconnect, 34509-G3 Disconnect) |  | IN |  |  | Proposed | 2950051 | Engineering Preliminary |  | 2021 |  |  | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22245 | 2021-11-18 | M210314 | 26747 | 2022-07-11 | LNup | 2026-11-30 | Tipton West | Cammack Rd SS |  | 230 |  |  | 23008 Tipton W-Cammack Rd: Insulator Replacement and anti-gallop line conductor modifications |  | IN |  |  | Proposed | 4716099 | Engineering w/AFUDC |  | 2021 |  |  | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22246 | 2021-11-19 | M200364/M200365/M200367 | 26764 | 2022-07-11 | Dist | 2023-06-01 | IMPA Frankfort 300W |  |  | 69 | 12 | 150 | IMPA Frankfort 300W 69/12kV Distribution Substation in the 69196 ckt.; between Frankfort 230 and West Side; loop through design; New load initial estimate of 5.1MW |  | IN |  | 0.5 | Proposed | 5018000 | Engineering Preliminary |  | 2021 |  | 150 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22265 | 2021-11-19 | DEI-2022-4 | 26766 | 2021-11-19 | LNrb | 2025-12-31 | Purdue | Laf. Cincinnati St. | 1 | 138 |  | 301 | Rebuild the 13820 line using 954ACSR@120C: (part 3) Purdue to Cincinnati St. (1.29 miles) |  | IN | 1.29 |  | Proposed | 6750000 | Engineering Preliminary |  | 2021 |  | 301 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22265 | 2021-11-19 | DEI-2022-4 | 26768 | 2021-11-19 | LNrb | 2024-12-31 | Airport Rd | Purdue | 1 | 138 |  | 301 | Rebuild the 13820 line using 954ACSR@120C (some existing 954 in circuit): (part 2) 12/31/24 (guesstimate) new Airport Rd sub to Purdue (5.59 miles) |  | IN | 5.59 |  | Proposed | 29250000 | Engineering Preliminary |  | 2021 |  | 301 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22265 | 2021-11-19 | DEI-2022-4 | 26767 | 2021-11-19 | LNrb | 2023-12-31 | Purdue NW Tap | Airport Rd | 1 | 138 |  | 301 | Rebuild the 13820 line using 954ACSR@120C (some existing 954 in circuit): (part 1) PU NW tap to new Airport Rd sub (1.76 miles) |  | IN | 1.76 |  | Proposed | 9000000 | Engineering Preliminary |  | 2021 |  | 301 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22425 | 2021-12-14 | DEI-2022-5 | 26783 | 2021-12-08 | SUB | 2024-12-27 | Westwood |  |  | 345 |  |  | Westwood 345kV Sub Expansion: 11 - 345kV breakers configured in breaker and 1/2 scheme |  | IN |  |  | Proposed | 30000000 | Planning Preliminary |  | 2021 |  |  | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22425 | 2021-12-14 | DEI-2022-5 | 26788 | 2021-12-08 | SUB | 2025-01-01 | Westwood |  | 4 | 345 | 138 | 498 | Westwood 345/138kV Bk4 |  | IN |  |  | Proposed | 5000000 | Planning Preliminary |  | 2021 |  | 516 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22425 | 2021-12-14 | DEI-2022-5 | 26787 | 2021-12-08 | LN | 2024-12-31 | Westwood | New Customer Sub | 2 | 138 |  | 480 | Westwood to New Customer 138kV line (second source) |  | IN |  | 4 | Proposed | 10000000 | Planning Preliminary |  | 2021 |  | 480 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22425 | 2021-12-14 | DEI-2022-5 | 26786 | 2021-12-08 | LN | 2024-12-30 | Westwood | New Customer Sub | 1 | 138 |  | 480 | Westwood to New Customer 138kV line and New Customer substation (load) |  | IN |  | 4 | Proposed | 15000000 | Planning Preliminary |  | 2021 |  | 480 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22425 | 2021-12-14 | DEI-2022-5 | 26785 | 2021-12-09 | SUB | 2024-12-29 | Westwood |  |  | 345 | 138 | 498 | Westwood 345/138kV Bk3 and new customer dedicated 138kV ring bus with normally open 138kV breaker connection to existing 138kV bus 1 or 2 |  | IN |  |  | Proposed | 25000000 | Planning Preliminary |  | 2021 |  | 516 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | Central | DEI | 22425 | 2021-12-14 | DEI-2022-5 | 26784 | 2021-12-08 | LN | 2024-12-28 | AEP Dequine | Westwood | 3 | 345 |  | 1025 | AEP Dequine to Westwood 345kV line (on new right of way) including 345kV breaker addition at AEP Dequine (CB A2 position proposed) |  | IN |  | 2 | Proposed | 15000000 | Planning Preliminary |  | 2021 |  | 1217 | Duke Energy Corporation | N | N | N
A in MTEP22 | C | West | DPC | 22531 | 2022-01-18 |  | 26801 | 2022-09-07 | LNrb | 2025-10-15 | Bell Center | Lancaster |  | 69 |  |  | 40.51 Mile Rebuild to 477 ACSR on existing ROW |  | WI | 40.51 | 0 | Proposed | 23877825.37 | Planning |  | 2022 |  |  | Dairyland Power Cooperative | N | N | N
A in MTEP22 | C | South | Entergy-AR | 21565 | 2022-01-18 |  | 26977 | 2022-08-24 | SwSta | 2023-12-01 | AECC Ward 115kV |  |  | 115 |  |  | Building our station to add five (5) breakers, associated relaying, communication equipment, and some bus upgrades |  | AR |  |  | Planned | 3000000 | Engineering Preliminary |  |  |  |  | Arkansas Electric Coopertive Corporation | N | N | N
A in MTEP22 | C | South | Entergy-AR | 21805 | 2022-09-01 | 22-EAL-002 | 26373 | 2022-08-03 | TEQ | 2023-12-31 | Woodward |  |  | 115 |  |  | Replace aging and failed equipment across EAL territory. |  | AR |  |  | M1_Final SPM or OOC | 28500000 | Planning |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP22 | C | South | Entergy-AR | 21806 | 2021-09-21 | 22-EAL-003 | 26374 | 2022-08-03 | TEQ | 2023-12-30 | Junction City |  |  | 115 |  |  | Replace CT's at Junction City with higher rated equipment |  | AR |  |  | M1_Final SPM or OOC | 1415000 | Planning |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP22 | C | South | Entergy-AR | 22530 | 2022-07-11 | 22-EAL-008 | 26799 | 2022-09-14 | SUB | 2024-03-01 | Sandy Bayou |  |  | 500 | 230 |  | A new 500/230kV substation. |  | AR |  |  | M1_Final SPM or OOC | 122000000 | Pre-Construction |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP22 | C | South | Entergy-AR | 23154 | 2022-08-02 |  | 26997 | 2022-08-24 | INT | 2024-10-15 | Keo 500kV |  |  | 500 |  |  | New interconnection for J1258 and J1415 at Keo 500kV |  | AR |  |  | Planned | 8888000 | GIA |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP22 | C | South | Entergy-AR | 23267 | 2022-08-02 |  | 27022 | 2022-08-24 | INT | 2024-10-31 | Fountain Hill 115kV |  |  | 115 |  |  | New cut-in for a 115kV substation to interconnect J1281. |  | AR |  |  | Planned | 3796000 | GIA |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP22 | C | South | Entergy-AR | 23326 | 2022-08-02 |  | 27015 | 2022-08-24 | INT | 2025-02-15 | Sunset |  |  | 230 |  |  | New 230kV switching station for J1215 interconnection |  | AR |  |  | Planned | 14695000 | GIA |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP22 | B | South | Entergy-LA | 13910 | 2021-09-21 | 18-ELN-002 | 22996 | 2021-09-09 | Dist | 2026-06-01 | Calhoun |  |  | 230 |  |  | 230 kV distribution substation |  | LA |  |  | Proposed | 56800000 | Planning |  |  |  |  | Entergy | N | N | N
A in MTEP22 | B | South | Entergy-LA | 13910 | 2021-09-21 | 18-ELN-002 | 22997 | 2021-09-21 | LN | 2026-06-01 | Cadeville | Calhoun | 1 | 230 |  | 519 | Construct approximately 10 miles of 230 kV transmission line from the new substation that terminates into the Cadeville substation. |  | LA |  | 10 | Proposed | [5 empty] | 519 | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 21808 | 2022-09-01 | 22-ENO-001 | 26376 | 2022-01-11 | TEQ | 2023-12-31 | Multiple |  |  | 230 | 69 |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  | LA |  |  | Proposed | 1900000 | Planning |  |  |  |  | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 21809 | 2022-09-01 | 22-ELS-007 | 26377 | 2022-07-14 | TEQ | 2023-12-31 | Multiple |  |  | 500 | 69 |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  | LA |  |  | Proposed | 55100000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 21811 | 2021-09-09 | 22-ELF-001 | 26379 | 2022-05-20 | RLY | 2024-12-31 | Richard |  |  | 500 | 138 |  | Ensure the Richard 500/138 kV auto #1 has redundant high-speed protection with independent CT and PT windings. |  | LA |  |  | Proposed | 10270000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 21816 | 2022-01-18 | 22-ELB-001 | 26402 | 2022-07-15 | TEQ | 2023-06-01 | Jefferson | East |  | 69 |  |  | Entergy’s Planning Guidelines. The P2.1 loss of Essen Tap to Tiger 69 kV will overload from Drusilla to Jefferson 69kV line. |  | LA |  |  | Proposed | 2742000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 21822 | 2021-09-09 | 22-ELC-001 | 26408 | 2022-01-11 | LNup | 2023-08-31 | Hartburg | Rhodes |  | 500 |  |  | Replace the existing structure with a new structure that will be installed further to the east to avoid future washing out. Access to the structure is especially difficult and will require extensive matting and/or the use of specialized marsh equipment. |  | LA |  |  | Proposed | 5790000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 21832 | 2021-09-27 | 19-ELB-001 | 26420 | 2022-07-15 | LN | 2024-06-01 | Dow Meter | Tiger |  | 230 |  |  | Re-terminate the Addis to Tiger and Dow Meter to Addis 230 kV lines to create the Dow Meter to Tiger 230 kV line, which will bypass the Addis 230 kV station. |  | LA |  |  | Proposed | 5700000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 21835 | 2022-05-24 | 22-ELS-005 | 26423 | 2022-07-15 | TX | 2024-12-01 | Kaiser | Conquest |  | 230 | 115 |  | Install 300 MVA, 230/115kV Autotransformer to tie Kaiser 230 kV to Conquest 115 kV. Kaiser and Conquest stations are adjacent to each other. |  | LA |  |  | Proposed | 26320000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 21835 | 2022-05-24 | 22-ELS-005 | 26978 | 2022-05-24 | Remove | 2024-12-01 | Behrman | Port Nickel |  | 115 |  |  | Remove Behrman to Port Nickel 115 kV line from model. |  | LA |  |  | Proposed | [6 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 21835 | 2022-05-24 | 22-ELS-005 | 26976 | 2022-05-24 | BUS | 2024-12-01 | Conquest |  |  | 115 |  |  | Work to be done at the Conquest 115 kV station to accommodate the interconnection |  | LA |  |  | Planned | [6 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 23147 | 2022-05-23 | 22-ELS-009 | 26971 | 2022-08-24 | INT | 2024-09-24 | Amite | Chicken Farm |  | 115 |  |  | Construct 115 kV station for a solar interconnection customer between Amite and Chicken Farm 115 kV stations. |  | LA |  |  | Proposed | 14390000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 23308 | 2022-08-03 | 22-ELS-010 | 27017 | 2022-08-24 | INT | 2024-06-01 | Bayou Labutte |  |  | 500 |  |  | Upgrades and expansion needed for the interconnection of J1246 |  | LA |  |  | Proposed | 11244000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 23308 | 2022-08-03 | 22-ELS-010 | 27018 | 2022-08-24 | CB | 2025-04-09 | Point Pleasant |  |  | 230 |  |  | Replace two 230 kV breakers and associated relay equipment. |  | LA |  |  | Proposed | 3100000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 23330 | 2022-08-03 | 22-ELN-003 | 27023 | 2022-08-24 | INT | 2024-10-15 | Rilla |  |  | 115 |  |  | Interconnection at Rilla switching station for J1239 generation interconnection. |  | LA |  |  | Proposed | 7233000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 23386 | 2022-09-01 | 22-ELS-011 | 27028 | 2022-07-25 | CB | 2024-04-04 | Adams Creek |  |  | 230 |  |  | Replace breakers S4402/S4405 and switches. |  | LA |  |  | Proposed | 3990000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 23386 | 2022-09-01 | 22-ELS-011 | 27029 | 2022-07-25 | BUS | 2024-04-04 | Bogalusa |  |  | 230 |  |  | Upgrade bus and CTs |  | LA |  |  | Proposed | [6 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-LA | 23421 | 2022-08-10 | 22-ELB-005 | 27069 | 2022-08-24 | INT | 2023-04-21 | Ventress |  |  | 230 |  |  | Construct Ventress 230 kV station between Fancy Point and Waterloo. |  | LA |  |  | Proposed | 5354000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | B | South | Entergy-MS | 20063 | 2022-05-23 | 21-EML-019 | 25766 | 2022-08-24 | LINE | 2024-12-15 | Choctaw | TVA French Camp |  | 500 |  |  | Decommission and demolish the existing Choctaw-TVA French Camp 500kV line that was recently acquired by Entergy in November of 2019 (~0.75mi). |  | MS |  |  | Proposed | 500000 | [5 empty] | Entergy Mississippi | N | N | N
A in MTEP22 | B | South | Entergy-MS | 20064 | 2022-05-23 | 21-EML-020 | 25767 | 2022-08-24 | LN | 2024-12-15 | Choctaw | Wolf Creek |  | 500 |  |  | Utilize ~0.1mi of existing Choctaw-French Camp 500kV line to tie into Wolf Creek (Choctaw – French Camp 500 kV decommissioned with a separate project). Convert Wolf Creek 500kV switching yard to 4 breaker ring bus to accommodate 2nd line. |  | MS |  |  | Proposed | 7100000 | [5 empty] | Entergy Mississippi | N | N | N
A in MTEP22 | C | South | Entergy-MS | 21815 | 2022-09-01 | 22-EML-002 | 26401 | 2022-07-15 | TEQ | 2023-12-31 | Franklin |  |  | 500 |  |  | The AM renewal asset program is to address aging and failing transmission assets across EAL's territory. |  | MS |  |  | Proposed | 56009600 | [5 empty] | Entergy Mississippi | N | N | N
A in MTEP22 | C | South | Entergy-MS | 22345 | 2022-07-21 |  | 26774 | 2022-07-21 | SwSta | 2024-07-01 | East Winstonville |  |  | 115 |  |  | Tap the Energy owned Delta SES - Shelby 115kV line with switching station. |  | MS |  |  | Planned | 925000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP22 | C | South | Entergy-MS | 22345 | 2022-07-21 |  | 26805 | 2022-07-21 | COM | 2024-07-01 | East Winstonville |  |  | 115 |  |  | Install communication equipment for metering and motor operated switching. |  | MS |  |  | Planned | 60000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP22 | C | South | Entergy-MS | 22345 | 2022-07-21 |  | 26775 | 2022-07-21 | LN | 2024-07-01 | East Winstonville |  |  | 115 |  |  | Tap the Energy owned Delta SES - Shelby 115kV line with switching station and build a 115kV line to the new member East Winstonville delivery point. |  | MS |  |  | Planned | 877800 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP22 | C | South | Entergy-MS | 23268 | 2022-07-25 | 22-EML-003 | 27024 | 2022-08-24 | TEQ | 2023-12-19 | Franklin |  |  | 500 |  |  | Replace four (4) 500 kV switches with motor operators, and one (1) 500 kV ground switch at the Franklin 500 kV substation. |  | MS |  |  | Planned | 1739000 | [5 empty] | Entergy Mississippi | N | N | N
A in MTEP22 | C | South | Entergy-MS | 23387 | 2022-08-26 | 22-EML-004 | 27031 | 2022-08-24 | INT | 2024-03-13 | 336858 | 337040 | 1 | 230 |  |  | POI on Gerald Andrus - Tinnin 230 kV line |  | MS |  |  | Proposed | 4516000 | [5 empty] | Entergy Mississippi | N | N | N
A in MTEP22 | C | South | Entergy-MS | 23387 | 2022-08-26 | 22-EML-004 | 27032 | 2022-08-24 | LNrb | 2024-03-13 | 337044 | 337045 | 1 | 115 |  |  | Network Upgrade Line Rebuild on Greenville - SE Greenville 115 kV line |  | MS |  |  | Proposed | 5909000 |  |  | 2021 |  |  | Entergy Mississippi | N | N | N
A in MTEP22 | C | South | Entergy-MS | 23482 | 2022-08-26 | 22-EML-006 | 27297 | 2022-08-26 | TEQ | 2023-11-10 | Belzoni |  |  | 115 |  |  | Replace line terminal bus and insulators at Belzoni for the line terminal to Isola 115 kV. |  | MS |  |  | Proposed | 406000 | [5 empty] | Entergy Mississippi | N | N | N
A in MTEP22 | C | South | Entergy-MS | 23518 | 2022-08-26 | 22-EML-007 | 27298 | 2022-08-26 | INT | 2024-05-23 | Tunica | Lula |  | 115 |  |  | J1440 generator interconnection on the Tunica – Lula 115 kV transmission line. |  | MS |  |  | Proposed | 13560000 | [5 empty] | Entergy Mississippi | N | N | N
A in MTEP22 | C | South | Entergy-MS | 23519 | 2022-08-26 | 22-EML-008 | 27299 | 2022-08-26 | INT | 2024-05-23 | Indianola | Cleveland |  | 115 |  |  | J1294 generator interconnection on Indianola - Cleveland 115 kV transmission line. |  | MS |  |  | Proposed | 3870000 | [5 empty] | Entergy Mississippi | N | N | N
A in MTEP22 | B | South | Entergy-TX | 15649 | 2021-09-10 | 19-ETI-004 | 23655 | 2022-07-15 | Dist | 2025-12-01 | Texas |  |  | 138 |  |  | Construct a new 138 kV distribution station |  | TX |  |  | Proposed | 69400000 | Planning |  |  |  |  | Entergy | N | N | N
A in MTEP22 | B | South | Entergy-TX | 15649 | 2021-09-10 | 19-ETI-004 | 23657 | 2021-07-14 | LN | 2025-12-01 | Cut in | Texas |  | 138 |  |  | 230 kV cut in to the Texas Station |  | TX |  |  | Proposed | [6 empty] | Entergy | N | N | N
A in MTEP22 | B | South | Entergy-TX | 15649 | 2021-09-10 | 19-ETI-004 | 23656 | 2021-07-14 | Dist | 2025-12-01 | Texas |  |  | 138 |  |  | Construct a 138 kV station on the Lewis Creek to Goree kV line. |  | TX |  |  | Proposed |  | Planning |  |  |  |  | Entergy | N | N | N
A in MTEP22 | B | South | Entergy-TX | 18262 | 2021-09-10 | 20-ETI-001 | 25098 | 2022-07-15 | LNrb | 2024-06-01 | Tarkington | New Long John |  | 138 |  |  | Rebuild the Tarkington to New Long John 138 kV line. |  | TX | 9 |  | Proposed | 18230000 | Planning |  |  |  |  | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-TX | 21810 | 2022-09-01 | 22-ETI-007 | 26378 | 2022-07-14 | TEQ | 2023-12-31 | Multiple |  |  | 500 | 69 |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  | TX |  |  | Proposed | 31600000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-TX | 21841 | 2021-09-28 | 22-ETI-003 | 26431 | 2022-07-15 | TEQ | 2023-12-01 | Porter | Oak Ridge |  | 138 |  |  | Upgrade Line Bay Bus at Porter to achieve a through path rating of 1766 A on the Porter to Oak Ridge 138 kV line |  | TX |  |  | Proposed | 459000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-TX | 21843 | 2021-09-10 | 22-ETI-008 | 26433 | 2022-07-15 | LNup | 2025-06-01 | Neches | Sabine |  | 138 |  |  | Replace coffers, de-water and excavate soils Perform structure foundation inspection(s), fortify/repair where possible Restore soils around structure foundations, fill coffers to grade |  | TX |  |  | Proposed | 28000000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-TX | 21847 | 2021-09-10 | 22-ETI-009 | 26436 | 2022-07-15 | Dist | 2026-06-01 | Galaxy |  |  | 138 |  |  | Cut the Galaxy substation in and out of the Porter to Apollo 138 kV line. |  | TX |  |  | Proposed | 65900000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-TX | 21850 | 2021-09-10 | 22-ETI-011 | 26441 | 2022-07-15 | Dist | 2026-12-01 | District |  |  | 138 |  |  | Cut the District substation in and out of the Crystal to Security 138 kV line. |  | TX |  |  | Proposed | 85200000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-TX | 21851 | 2022-01-18 | 22-ETI-012 | 26442 | 2022-08-31 | Dist | 2026-12-01 | Falcon |  |  | 138 |  |  | Cut the Falcon substation in and out of the Luce Bayou to Tarkington 138 kV line. |  | TX |  |  | Proposed | 113800000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-TX | 22125 | 2022-01-31 | 22-ETI-014 | 26708 | 2022-08-24 | INT | 2025-03-01 | Sabine |  |  | 230 | 138 |  | Interconnection for R1003 |  | TX |  |  | Planned | 14762000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-TX | 23209 | 2022-08-24 | 22-ETI-015 | 26995 | 2022-08-24 | SUB | 2023-01-31 | Legend |  |  | 230 |  |  | The proposed new facilities include installing two additional 230 kV breakers into the Legend substation and extending a 230 kV radial transmission line towards the customer’s site. |  | TX |  |  | Proposed | 4250000 | [5 empty] | Entergy | N | N | N
A in MTEP22 | C | South | Entergy-TX | 23307 | 2022-08-24 | 22-ETI-016 | 27016 | 2022-08-24 | SUB | 2023-04-30 | Port Acres | Southside | 1 | 230 |  |  | The new Flare Hill 230 kV substation will be cut in on the existing customer owned Port Acres to Southside 230 kV circuit 1. |  | TX |  |  | Proposed | 980000 |  |  |  | Cost is Entergy's portion to be reimbursed by customer. Customer has chosen to construct substation. |  | Entergy | N | N | N
A in MTEP22 | C | West | GRE | 20666 | 2022-08-25 | 208760 | 26064 | 2022-08-25 | LNrb | 2026-12-31 | Litchfield | Litchfield Tap | 1 | 69 |  |  | Rebuild the Litchfield to Litchfield Tap as a double circuit line. |  | MN | 2.45 |  | Proposed | 2281569 | Planning |  | 2020 |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 20707 | 2022-05-19 | 209074 | 26070 | 2022-05-19 | LNup | 2025-06-01 | Granite Falls | Willmar | 1 | 230 |  |  | Upgrade the Granite Falls - Willmar (WB) line to 212 F by replacing 10 structures. |  | MN | 17.7 |  | Proposed | 598979 | Planning |  | 2020 |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 20865 | 2022-08-25 | 207451 | 26106 | 2022-08-25 | TAP | 2023-02-21 | Shamrock |  |  | 69 |  |  | Construct an in/out line to the Wright Hennepin Electric Association's Shamrock substation. |  | MN |  |  | Proposed | 1709484.43 | Planning |  | 2021 |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 21065 | 2022-08-28 | 207408 | 26136 | 2022-08-28 | CB | 2024-11-01 | Big Swan |  |  | 115 |  |  | Add Big Swan 5N18 115 kV breaker on the Crow River 115 kV line. |  | MN |  |  | Proposed | 700000 | Planning |  | 2021 |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 21705 | 2022-05-19 | 207723 | 26330 | 2022-05-19 | LNup | 2022-12-01 | Benton County | Mud Lake | 1 | 230 |  |  | Install storm resistant structures. |  | MN |  |  | Proposed | 1473350.49 | Planning Preliminary |  | 2021 |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 21705 | 2022-05-19 | 207723 | 26332 | 2021-08-25 | LNup | 2022-12-01 | Benton County | Monticello | 1 | 230 |  |  | Install storm resistant structures. |  | MN |  |  | Proposed | 350000 | Planning Preliminary |  | 2021 |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 21823 | 2022-05-20 | 208306 | 26409 | 2022-05-20 | LNup | 2023-12-01 | Benson | Morris | 1 | 230 |  |  | Install storm structures in the Benson – Morris 115 kV line. |  | MN |  |  | Proposed | 1277000 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 21824 | 2022-05-20 | 208309 | 26410 | 2022-05-20 | LNup | 2023-12-01 | Riverton | Wing River | 1 | 230 |  |  | Install storm structures in the Riverton – Wing River 230 kV line. |  | MN |  |  | Proposed | 658000 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 21825 | 2022-05-20 | 208307 | 26411 | 2022-05-20 | LNup | 2024-06-28 | Cormorant | Pelican Rapids | 1 | 115 |  |  | Install storm structures in the Cormorant – Pelican Rapids 115 kV line. |  | MN |  |  | Proposed | 651387 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 21826 | 2022-05-20 | 208308 | 26412 | 2022-05-20 | LNup | 2024-06-28 | Bunker Lake | Elk River | 1 | 230 |  |  | Install storm structures in the Bunker Lake - Elk River 230 kV line. |  | MN |  |  | Proposed | 596365 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 21829 | 2022-05-20 | 208734 | 26413 | 2022-05-20 | Dist | 2023-09-01 | South Dayton |  |  | 115 |  |  | Construct the new Connexus Energy (CE) South Dayton 115 kV in-and-out distribution substation in the Xcel 5522 line. |  | MN |  |  | Proposed | 1485000 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 21830 | 2022-05-20 | 208527 | 26415 | 2022-03-11 | Dist | 2022-11-21 | Shamineau Lake |  |  | 115 |  |  | Construct the new Crow Wing Power Shamineau Lake distribution substation. |  | MN |  | 0.1 | Proposed | 792000 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 22025 | 2022-05-20 | 208426 | 26686 | 2022-05-20 | BUS | 2024-11-08 | Parkwood |  |  | 115 |  |  | Rebuild the 115 kV bus at Parkwood substation as a ring bus. |  | MN |  |  | Proposed | 7620000 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 22026 | 2022-08-25 | 208453 | 26687 | 2022-08-25 | LNrb | 2025-09-30 | Deer River | Wirt Tap | 1 | 69 |  |  | Rebuild the Deer River - Jessie Lake - Wirt Tap 69 kV line. |  | MN | 26.52 |  | Proposed | 20723354.36 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 22027 | 2022-08-24 | 209093 | 26688 | 2022-05-20 | LNrb | 2024-06-01 | Birch Lake | Wabedo | 1 | 69 |  |  | Rebuild the Birch Lake - Pleasant Lake - Wabedo 69 kV line. |  | MN | 12.46 |  | Proposed | 14419044.49 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 22028 | 2022-05-20 | 208345 | 26689 | 2022-05-20 | LNrb | 2025-05-02 | Denham | Harry Maser | 1 | 69 |  |  | Rebuild the Denham - Harry Maser 69 kV line. |  | MN | 8.3 |  | Proposed | 5112000 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 22029 | 2022-08-24 | 208767 | 26690 | 2022-08-25 | TX | 2023-08-31 | Walden |  |  | 115 |  |  | Replace the existing Walden 115/41.6 kV transformer with an LTC transformer. |  | MN |  |  | Proposed | 2500000 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 22030 | 2022-05-20 | 208722 | 26691 | 2022-05-20 | SUB | 2026-10-30 | Rost |  |  | 161 | 69 |  | Build the Rost 161/69 kV substation |  | MN |  |  | Proposed | 7977841 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 22030 | 2022-05-20 | 208722 | 26692 | 2022-05-20 | LN | 2025-10-03 | Lorain | Rost | 1 | 69 |  |  | Construct a new 69 kV line from Lorain substation to the Rost substation. |  | MN |  | 9 | Proposed | 5390159 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 22445 | 2022-05-20 | 209056 | 26789 | 2022-05-20 | Dist | 2023-06-01 | Cedar |  |  | 115 |  |  | DEA building new in/out distribution substation. GRE will need to double circuit tap into sub off of DA-DA line. GRE is also responsible for the highside structures and associated equipment. |  | MN |  | 0.1 | Proposed | 2773049.09 | Planning Preliminary |  | 2021 |  |  | Great River Energy | N | N | N
A in MTEP22 | C | West | GRE | 22528 | 2022-08-24 | 209073 | 26795 | 2022-05-20 | Dist | 2024-01-01 | Matter |  |  | 69 |  |  | Install a manual load break 3-way load break 69kV/1200A switch on a steel pole and foundation on GRE’s DX (Crow River to Victor) line. Install adjacent grading structures if needed. Build HS DE to 115kV. |  | MN |  |  | Proposed | 402407 | Planning Preliminary |  | 2021 |  |  | Great River Energy | N | N | N
A in MTEP22 | C | Central | HE | 22628 | 2022-05-11 |  | 26815 | 2022-08-24 | SwSta | 2028-06-01 | New Sleepy Hollow |  |  | 345 |  |  | New 345 transmission ring bus located about 6 miles south of DEI Prescott staiton, near 39°24'34.71"N, 85°43'34.61"W. |  | IN |  |  | Proposed | 9000000 | Planning Preliminary |  |  |  |  | Hoosier Energy REC, Inc. | N | N | N
A in MTEP22 | C | Central | HE | 22628 | 2022-05-11 |  | 26817 | 2022-08-24 | TX | 2028-06-01 | New Sleepy Hollow |  |  | 345 | 161 |  | 345/161kV, 400 MVA nameplate transformer at new Sleepy Hollow station |  | IN |  |  | Proposed | 3000000 | Planning Preliminary |  |  |  |  | Hoosier Energy REC, Inc. | N | N | N
A in MTEP22 | C | Central | HE | 22628 | 2022-05-11 |  | 26816 | 2022-08-24 | LN | 2028-06-01 | New Sleepy Hollow | New Decatur-Napoleon (ID 22646) |  | 161 |  |  | New 18 mile 161kV transmission line from Sleepy Hollow Station to New Decatur-Napoleon (ID 22646) |  | IN |  |  | Proposed | 26000000 | Planning Preliminary |  |  |  |  | Hoosier Energy REC, Inc. | N | N | N
A in MTEP22 | C | Central | HE | 22646 | 2022-04-06 |  | 26808 | 2022-08-24 | SwSta | 2024-10-01 | Decatur | Napoleon |  | 161 |  |  | Construct 161kV breaker-and-a-half station about 1.5 miles south of Decatur Station. Located between Decatur and Napoleon Stations. |  | IN |  |  | Proposed | 26000000 | Planning Preliminary |  |  |  |  | Hoosier Energy REC, Inc. | N | N | N
A in MTEP22 | C | Central | HE | 22648 | 2022-05-16 |  | 26812 | 2022-08-24 | LN | 2026-06-01 | DEI Prescott | HE New 161 Decatur-Napoleon |  | 161 |  |  | New 161kV transmission line from DEI Prescott to the new HE Decatur-Napoleon station (about 13.5 miles) |  | IN |  | 13.5 | Proposed | 34000000 | Planning Preliminary |  |  |  |  | Hoosier Energy REC, Inc. | N | N | N
A in MTEP22 | C | Central | HE | 22648 | 2022-05-16 |  | 26814 | 2022-08-24 | SUB | 2026-06-01 | DEI Prescott |  |  | 345 | 161 |  | New 345/161kV substation |  | IN |  |  | Proposed | 5000000 | Planning Preliminary |  |  |  |  | Hoosier Energy REC, Inc. | N | N | N
A in MTEP22 | C | Central | HE | 22648 | 2022-05-16 |  | 26813 | 2022-08-24 | SwSta | 2026-06-01 | DEI Prescott |  |  | 345 |  |  | Expand DEI Prescott 345kV to ring bus station |  | IN |  |  | Proposed | 6000000 | Planning Preliminary |  |  |  |  | Hoosier Energy REC, Inc. | N | N | N
A in MTEP22 | C | Central | HE | 22666 | 2022-05-16 |  | 26809 | 2022-08-24 | LN | 2027-06-01 | DEI Batesville | New Decatur-Napoleon (ID 22646) |  | 161 |  |  | Construct new 161kV line from DEI Batesville to New Decatur-Napoleon (ID 22646), about 18 miles |  | IN |  | 18 | Proposed | 34000000 | [5 empty] | Hoosier Energy REC, Inc. | N | N | N
A in MTEP22 | C | Central | HE | 22666 | 2022-05-16 |  | 26811 | 2022-08-24 | SwSta | 2027-06-01 | DEI Batesville |  |  | 345 |  |  | Expand DEI Batesville 345kV station to ring bus |  | IN |  |  | Proposed | 6000000 | [5 empty] | Hoosier Energy REC, Inc. | N | N | N
A in MTEP22 | C | Central | HE | 22666 | 2022-05-16 |  | 26810 | 2022-08-24 | SUB | 2027-06-01 | DEI Batesville |  |  | 345 | 161 |  | New 345/161 kV transformer at DEI Batesville 345 station and bus-work for connection |  | IN |  |  | Proposed | 5000000 | [5 empty] | Hoosier Energy REC, Inc. | N | N | N
A in MTEP22 | C | Central | HE | 23266 | 2022-08-10 |  | 27000 | 2022-08-24 | LN | 2023-01-01 | Merom 69kV | AboutBit (new customer-owned) |  | 69 |  |  | Extend a new 69kV transmission line from an available bay position at Merom transmission station (Bus # 248774) to the new customer. The 69kV line will split at about 0.3 miles from Merom station, extending to two separate substations. |  | IN |  | 0.8 | Proposed | 1200000 | Planning |  | 2022 |  |  | Hoosier Energy REC, Inc. | N | N | N
A in MTEP22 | C | Central | HMPL | 22228 | 2022-01-31 |  | 26760 | 2022-08-24 | LNrl | 2022-06-30 | HMPL SUB 1 | HMPL SUB 6 |  | 69 |  |  | Rebuild - The Line will shorten by approximately 1,700 ft. |  | KY |  |  | Planned | 800000 | Planning |  |  |  |  | Henderson Municipal Power & Light | N | N | N
A in MTEP22 | C | Central | HMPL | 22228 | 2022-01-31 |  | 26763 | 2022-08-24 | LNrl | 2022-06-30 | HMPL SUB 3 | (BREC) Wolf Hills Tap |  | 69 |  |  | Rebuild - The line will lengthen approximately 300 ft. |  | KY |  |  | Planned | 950000 | Planning |  |  |  |  | Henderson Municipal Power & Light | N | N | N
A in MTEP22 | C | Central | HMPL | 22228 | 2022-01-31 |  | 26762 | 2022-08-24 | LNrl | 2022-06-30 | HMPL SUB 6 | HMPL SUB 3 | 1 | 69 |  |  | Rebuild - The line will shorten by approximately 350 ft. |  | KY |  |  | Planned | 650000 | Planning |  |  |  |  | Henderson Municipal Power & Light | N | N | N
A in MTEP22 | C | Central | HMPL | 22228 | 2022-01-31 |  | 26761 | 2022-08-24 | LNrl | 2022-06-30 | HMPL SUB 6 | (BREC) HMPL6 Tap | 1 | 69 |  |  | Rebuild - The line will lengthen by approximately 2,100 ft. |  | KY |  |  | Planned | 1400000 | Planning |  |  |  |  | Henderson Municipal Power & Light | N | N | N
A in MTEP22 | C | Central | IPL | 21836 | 2021-09-20 |  | 26425 | 2021-09-10 | CB | 2024-12-31 | Sunnyside |  |  | 345 |  |  | #21,#22,#23 |  | IN |  |  | Planned | 3500000 | Planning |  |  |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP22 | C | Central | IPL | 21836 | 2021-09-20 |  | 26427 | 2021-09-10 | CB | 2024-12-31 | Sunnyside |  |  | 138 |  |  | #1,#3 |  | IN |  |  | Proposed | 1600000 | Planning |  |  |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP22 | C | Central | IPL | 21838 | 2021-09-20 |  | 26428 | 2021-09-10 | CB | 2024-12-31 | Southwest |  |  | 138 |  |  | Replacement of five (5) 138 kV breakers #4, #5, #3, #26, #27 |  | IN |  |  | Planned | 4500000 | Planning |  |  |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP22 | C | Central | IPL | 21839 | 2021-09-20 |  | 26429 | 2021-09-10 | CB | 2024-12-31 | West |  |  | 138 |  |  | Replacement of three (3) 138 kV breakers #1, #4, #7 |  | IN |  |  | Planned | 2400000 | Planning |  |  |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP22 | C | West | ITCM | 21828 | 2021-09-10 | Agency St Enclosure & Relays | 26414 | 2021-09-10 | RLY | 2024-12-31 | Agency Street | Substation |  | 69 | 69 |  | The relays at Agency Street are approaching their 20 year end of life. ITC will install a new control enclosure with all new relays to provide ITC a separate control enclosure from IPL and minimize required outages and outage times for the relay replacements. All necessary outages should be coordinated with IPL. Also coordinate with IPL on location of new control building as this is an IPL owned site. |  | IA |  |  | Planned | 2090891 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21842 | 2021-09-22 | Jasper County Enclosure & Relay Replacements | 26432 | 2021-09-10 | RLY | 2024-12-31 | Jasper County | Substation |  | 161 | 161 |  | A new Control Enclosure is required at the Jasper County Substation due to age and condition. ITC will install a new Control Enclosure with all new relays. |  | IA |  |  | Planned | 2486897 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21929 | 2022-08-22 | Forks SS & line | 26535 | 2022-08-22 | SUB | 2026-12-31 | Forks | Switch Station |  | 161 | 161 |  | ITC Midwest will construct a three position 161kV ring bus substation named Forks on the Dickinson County – Lakefield Junction circuit. |  | MN |  |  | Planned | 5353800 | Engineering |  | 2021 | Originally submitted as "Lakefield Corners". |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21929 | 2022-08-22 | Forks SS & line | 27301 | 2022-08-24 | LN | 2026-12-31 | Dickinson Coutny | Lakefireld | 1 | 161 | 161 |  | Line taps for the new Forks 161kV Switch Station on the Dickinson County-Lakefield 161kV line. |  | MN |  |  | Planned | 0 | Engineering Preliminary |  |  |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21929 | 2022-08-22 | Forks SS & line | 26536 | 2022-08-22 | LN | 2026-12-31 | Forks | Rost | 1 | 161 | 161 |  | ITC Midwest will construct a ~6.5mi 161kV circuit between the new Forks – Rost substations using T2-636 ACSR. |  | MN |  | 6.5 | Planned | 8102400 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21930 | 2021-09-14 | Millstream | 26538 | 2021-09-14 | SwSta | 2024-12-31 | Millstream | Switch Station |  | 69 | 69 |  | Construct new Millstream Switching Station |  | IA |  |  | Planned | 5700000 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21930 | 2021-09-14 | Millstream | 26540 | 2021-09-14 | LNup | 2024-12-31 | Millstream | Homestead |  | 69 | 69 |  | Install OPGW between Millstream and location of future Homestead Switching Station. |  | IA |  |  | Planned | 1300800 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21930 | 2021-09-14 | Millstream | 26539 | 2021-09-14 | LN | 2024-12-31 | Millstream | Line Taps |  | 69 | 69 |  | Construct new line taps for Millstream switching station and remove existing PTS 1084, 1085, and 1087. |  | IA |  |  | Planned | 747600 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21933 | 2021-10-01 | Fox Lake Relay, Bkr, SCADA | 26542 | 2021-09-14 | CB | 2025-12-31 | Fox Lake | Substation |  | 161 | 161 |  | Upgrade all relaying and replace breaker 736. Remove wavetrap on Fox Lake to Lakefield 161 kV line. |  | IA |  |  | Planned | 2447934 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21933 | 2021-10-01 | Fox Lake Relay, Bkr, SCADA | 26544 | 2021-09-14 | RLY | 2025-12-31 | Lakefield Junction | Substation | 1 | 161 | 161 |  | Remove wavetrap and upgrade relaying on Fox Lake to Lakefield 161 kV line. |  | MN |  |  | Planned | 203082 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21935 | 2021-09-22 | Hayward Transformer Replacement | 26548 | 2021-12-17 | SUB | 2025-12-31 | Hayward | Substation |  | 161 | 69 | 150 MVA | Replace the existing transformers with a single 150 MVA unit |  | MN |  |  | Planned | 6024271 | Engineering |  | 2021 |  | 150 MVA | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21935 | 2021-09-22 | Hayward Transformer Replacement | 26549 | 2021-09-14 | LN | 2025-12-31 | Glenworth | Hayward | 1 | 161 | 161 |  | Reterminate the Glenworth - Hayward circuit into the terminal at Hayward |  | MN |  |  | Planned | 720000 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21936 | 2021-09-14 | Centerville Cooper Creek | 26550 | 2021-10-22 | SUB | 2025-12-31 | Centerville Cooper Creek | Substation |  | 69 | 69 |  | Construct new Centerville Cooper Creek Substation |  | IA |  |  | Planned | 2884631 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21936 | 2021-09-14 | Centerville Cooper Creek | 26553 | 2021-10-22 | SUB | 2026-06-30 | Centerville North | Substation |  | 69 | 69 |  | Retire Centerville North substation |  | IA |  |  | Planned | 533243 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21936 | 2021-09-14 | Centerville Cooper Creek | 26552 | 2021-09-14 | LN | 2025-12-31 | Centerville North | Centerville South | 1 | 69 | 69 |  | Terminate Centerville North - Centerville South Line into new Cooper Creek Substation |  | IA |  |  | Planned | 156000 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21936 | 2021-09-14 | Centerville Cooper Creek | 26551 | 2021-09-14 | LN | 2025-12-31 | Centerville North | Bridgeport North | 1 | 69 | 69 |  | Terminate Bridgeport - Centerville North Line into new Cooper Creek Substation |  | IA |  |  | Planned | 134400 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21937 | 2021-09-14 | Chariton North 69kV Interconnection | 26554 | 2021-10-22 | SUB | 2024-12-30 | Chariton North | Substation |  | 69 | 69 |  | New 69 kV Substation Chariton North. |  | IA |  |  | Planned | 4128417 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21937 | 2021-09-14 | Chariton North 69kV Interconnection | 26556 | 2021-10-22 | LN | 2024-12-30 | Lucas County | Woodburn Jct | 1 | 69 | 69 |  | New 69 kV line taps tapping the Lucas County to Woodburn Junction 69 kV line to the new Chariton North Substation |  | IA |  |  | Planned | 482400 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21937 | 2021-09-14 | Chariton North 69kV Interconnection | 26555 | 2021-10-22 | LN | 2024-12-30 | Court | Lucas County | 1 | 69 | 69 |  | New Double Circuit line tapping the Lucas County to Court 69 kV line to the new Chariton North Substation. |  | IA |  |  | Planned | 2226000 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21939 | 2021-09-14 | CR Hunter Field Expansion | 26557 | 2021-09-14 | SUB | 2024-12-31 | Cedar Rapids Hunter Field | Substation |  | 69 | 69 |  | IPL has notified ITC that it will be adding a 3rd 161x69/24.9 kV transformer at the Hunter Field Substation. ITC will need to add an additional breaker and bus to connect the new IPL transformer at Hunter Field. All new ITC equipment to be designed to 161 kV specs to allow future conversion of the substation to 161 kV operation. Substation will initially be operated at 69 kV. |  | IA |  |  | Planned | 1284996 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21940 | 2021-09-14 | Turkey River to Guttenburg | 26558 | 2021-09-14 | LNrb | 2025-12-31 | Turkey River | Guttenburg | 1 | 69 | 69 |  | The 9.04 mile Turkey River – Guttenberg 69 kV line is at the end of its useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Turkey River and Monona. |  | IA | 9.04 |  | Planned | 10376400 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21941 | 2022-08-23 | Guttenburg to Grrnavillo | 26559 | 2022-08-23 | LNrb | 2028-12-31 | Guttenburg | Garnavillo | 1 | 69 | 69 |  | The 11.23 mile Guttenberg - Garnavillo 69 kV line along with the 0.18 mile tap to Garnavillo are at the end of their useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Guttenberg and Monona. |  | IA | 11.23 |  | Planned | 14391600 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21942 | 2022-08-23 | Garnavillo to Elkader | 26560 | 2022-08-23 | LNrb | 2028-12-31 | Garnavillo | Elkader | 1 | 69 | 69 |  | The 7.63 mile Garnavillo - Elkader 69 kV line is at the end of its useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Garnavillo and Elkader. |  | IA | 7.63 |  | Planned | 10012800 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21943 | 2021-09-14 | Rose Hollow Add 161kV Terminal | 26562 | 2021-12-17 | TEQ | 2024-12-31 | Rose Hollow | Substation |  | 161 | 161 |  | MidAmerican has notified ITC that they will be building a new 161 kV line from their exiting North Gate substation to the ITC Rose Hollow substation. Per the terms of the agreement with MidAmerican, ITC will need to install a new 161 kV terminal at Rose Hollow for the new line to North Gate. |  | IA |  |  | Planned | 984000 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21946 | 2021-09-14 | Pelican-Triboji 69kV Rebuild | 26565 | 2021-09-14 | LNrb | 2023-12-31 | Pelican | West Okoboji | 1 | 69 | 69 |  | Rebuild the line between Pelican and structure 162 (~1.04 miles). |  | IA | 1.04 |  | Planned | 1422000 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21946 | 2021-09-14 | Pelican-Triboji 69kV Rebuild | 26566 | 2021-09-14 | LNrb | 2023-12-31 | Tirboji | West Okoboji | 1 | 69 | 69 |  | Rebuild the line between Triboji and structure 72 (~4.45 miles). |  | IA | 4.45 |  | Planned | 5040000 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21976 | 2022-05-02 | Jasper to Laurel 161kV Line Rebuild | 26606 | 2022-05-02 | LNrb | 2027-12-30 | Jasper | Laurel |  | 161 | 161 |  | ITC will rebuild approximately 10 miles of the Jasper to Laurel 161kV line. The 161kV line conductor will be capable of 1600A or greater. |  | IA | 10 |  | Planned | 18420000 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21976 | 2022-05-02 | Jasper to Laurel 161kV Line Rebuild | 26608 | 2022-05-02 | SUBmisc | 2027-12-30 | Laurel | Substation |  | 161 | 161 |  | Laurel Substation work to accommodate the addition of OPGW |  | IA |  |  | Planned | 180860 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21976 | 2022-05-02 | Jasper to Laurel 161kV Line Rebuild | 26607 | 2022-05-02 | SUBmisc | 2027-12-30 | Jasper County | Substation |  | 161 | 161 |  | Substation work to accommodate OPGW between Jasper County and Laurel |  | IA |  |  | Planned | 180860 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21977 | 2022-05-20 | J1050 TOIF | 26610 | 2022-08-24 | BUS | 2022-08-22 | Doud | Substation |  | 161 | 161 |  | A breaker position in the Doud 161 kV ring bus will be added to accommodate the interconnection. TOIF will be equipment dedicated to connecting the J1050 generating facility. TOIF cost to include dead end, line disconnect switch, arresters, PT’s, relay panel, and other associated equipment. |  | IA |  |  | Under Construction | 403313 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21978 | 2021-09-15 | J1050 NU | 26609 | 2022-08-24 | CB | 2022-08-22 | Doud | Substation |  | 161 | 161 |  | Add a breaker position in the Doud 161 kV ring bus. Network Upgrade cost to include the new breaker position, switch and associated equipment. |  | IA |  |  | Under Construction | 408428 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21980 | 2021-11-24 | ITC Midwest Asset Replacement Program 2025 | 26612 | 2022-08-25 | LN | 2024-12-31 | ITCM Asset Blanket for 2024 | Throughout system |  | 345 | 69 |  | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. |  | IA,MN,IL |  |  | Planned | 37080000 | Engineering Preliminary |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21982 | 2021-10-07 | S Dubuque 161/69kV Source & Bunker Hill 69kV Loop | 26615 | 2021-12-17 | SUB | 2025-12-31 | Dubuque North Cascade Rd | Substation |  | 161 | 69 | 150 MVA | ITC Midwest will construct a new three position 161kV Ring (convertable to Bkr and 1/2) with a new 161/69kV 150 MVA to a single 69kV line terminal initially to Bunker Hill and looping to Dubuque 8th Street. |  | IA |  |  | Planned | 10741866 | Engineering |  | 2021 |  | 150 MVA | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21982 | 2021-10-07 | S Dubuque 161/69kV Source & Bunker Hill 69kV Loop | 26743 | 2021-12-17 | LN | 2025-12-31 | Dubuque 8th Street | Bunker Hill | 1 | 69 | 69 |  | Line tap modifications for Bunker Hills expansion. |  | IA |  |  | Planned | 0 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21982 | 2021-10-07 | S Dubuque 161/69kV Source & Bunker Hill 69kV Loop | 26619 | 2021-12-17 | SUB | 2025-12-31 | Dubuque 8th Street | Substation |  | 69 | 69 |  | Upgrade 69kV terminal limits to above line conductor rating of T2-477 ACSR. |  | IA |  |  | Planned | 198000 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21982 | 2021-10-07 | S Dubuque 161/69kV Source & Bunker Hill 69kV Loop | 26618 | 2021-12-17 | SUB | 2025-12-31 | Bunker Hill | Substation |  | 69 | 69 |  | Alliant will expand the Bunker Hill sub if necessary to allow for ITC to install 2 69kV line breakers and a 69kV bus tie breaker to allow for the 2nd Alliant 69/distribution transformer. |  | IA |  |  | Planned | 3051600 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21982 | 2021-10-07 | S Dubuque 161/69kV Source & Bunker Hill 69kV Loop | 26617 | 2021-12-17 | LN | 2025-12-31 | Dubuque North Cascade Rd | Bunker Hill | 1 | 69 | 69 |  | New 69kv line from the new North Cascade Rd Substation to Bunker Hill (~2.6 miles) |  | IA |  |  | Planned | 4279200 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21982 | 2021-10-07 | S Dubuque 161/69kV Source & Bunker Hill 69kV Loop | 26616 | 2021-12-17 | LN | 2025-12-31 | Salem | Julian | 1 | 161 | 161 |  | New 161kV line taps for the new 161/69kV substation. |  | IA |  |  | Planned | 1035600 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21987 | 2022-05-23 | J1181 GIA - TOIF | 26630 | 2022-05-23 | SUB | 2023-08-31 | Lasalle | Substation |  | 345 | 345 |  | The work order will capture costs associated with TOIF at Lasalle switching station dedicated to the generating facilities. TOIF will include, dead-end, PTs, relay panel for gen-tie line, line disconnect switch and other facilities at the switching station dedicated to the gen-tie line and generating facility. The interconnection customer will fund the cost of the TOIF without refund and will be responsible for ongoing maintenance costs and replacement cost of facilities |  | IA |  |  | Planned | 892270 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21989 | 2022-04-07 | J1181 GIA - TO Funded 345 kV Network Upgrades | 26633 | 2022-04-07 | SUB | 2023-08-31 | Lasalle | Switch Station |  | 345 | 345 |  | The work order is for costs associated with the construction of a new 3 terminal, 3 breaker Lasalle 345 kV switching station. The work will be funded by ITCM, and ITCM will recover 90% of the cost of the work under a Facilities Service Agreement with the Interconnection Customer. The remaining 10% of the cost will be recovered under Attachment GG. |  | IA |  |  | Planned | 9628085 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21989 | 2022-04-07 | J1181 GIA - TO Funded 345 kV Network Upgrades | 26636 | 2022-04-07 | SUBmisc | 2023-08-31 | Hazleton | Substation |  | 345 | 345 |  | The work order is to capture costs associated with installation of dual power line carrier and relaying at Hazleton for the new Lasalle 345 kV switching station. ITC will fund the estimated cost of the facilities, and ITC will recover 90% of the cost of the Network Upgrade from the interconnection customer under a Facilities Service Agreement, with the interconnection customer providing security to backstop ITC funding. The remaining 10% of the cost of the Network Upgrade will be recovered by ITCM under ITCM’s regionally shared Attachment GG rates |  | IA |  |  | Planned | 335868 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21989 | 2022-04-07 | J1181 GIA - TO Funded 345 kV Network Upgrades | 26635 | 2022-04-07 | SUBmisc | 2023-08-31 | Mitchell County | Substation |  | 345 | 345 |  | he work order is to capture costs associated with installation of dual power line carrier and relaying at Mitchell Co for the new Lasalle 345 kV switching station. This upgrade will not be needed if a fiber link is installed between Lasalle and Mitchell Co. The fiber installation is a separate project under a separate CM Sketch. o ITC will fund the estimated cost of the facilities, and ITC will recover 90% of the cost of the Network Upgrade from the interconnection customer under a Facilities Service Agreement, with the interconnection customer providing security to backstop ITC funding. The remaining 10% of the cost of the Network Upgrade will be recovered by ITCM under ITCM’s regionally shared Attachment GG rates |  | IA |  |  | Planned | 289380 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21989 | 2022-04-07 | J1181 GIA - TO Funded 345 kV Network Upgrades | 26634 | 2022-04-07 | LN | 2023-08-31 | Mitchell County | Hazleton | 1 | 345 | 345 |  | he work order is for costs associated with tapping the Mitchell-Hazleton 345 kV line for the new Lasalle switching station. The work will be funded by ITCM, and ITCM will recover 90% of the cost of the work under a Facilities Service Agreement with the Interconnection Customer. The remaining 10% of the cost will be recovered under Attachment GG. |  | IA |  |  | Planned | 2400000 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21991 | 2021-09-15 | J836 GIA - TOIF - Ledyard 345 kV | 26642 | 2022-08-24 | SUB | 2022-08-26 | Ledyard | Substation |  | 345 | 345 |  | This work order covers the TOIF work under the GIA. The interconnection customer will fund and be responsible for costs associate with the TOIF work. TOIF includes the work on facilities dedicated to the J836 generating facility terminal including a dead-end, switch, relay panel, VTs and other equipment. The GIA replaces the E&P Agreement. |  | IA |  |  | Under Construction | 1146492 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21992 | 2021-09-15 | J836 TO Funded GIA Network Upgrades | 26639 | 2021-09-15 | SUB | 2022-07-01 | Ledyard | Substation |  | 345 | 345 |  | The GIA provides for ITCM to fund the cost of the 345 kV Ledyard Bus Expansion Network Upgrade work, and the interconnection customer, Duke Energy, will backstop ITC work with security for 90% of the cost of the Network Upgrade. The GIA further requires ITCM, Duke Energy and MISO to enter into a Facilities Service Agreement that will allow ITCM a return on and return of 90% of the cost of the network upgrade. The remaining 10% of the cost of the Network Upgrade will be recovered by ITCM under regionally cost shared Attachment GG rates. The Network Upgrade project work that began under the E&P agreement will continue and be completed under the GIA. |  | IA |  |  | Planned | 1814497 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21996 | 2021-09-15 | J1084 Generator Interconnection TOIF | 26645 | 2021-09-15 | SUB | 2023-10-01 | Rock Creek | Substation |  | 345 | 345 |  | TOIF includes facilities and equipment at the 345 kV substation dedicated to the 345 kV radial line and Generating Facility |  | IA |  |  | Planned | 661704 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21997 | 2021-09-15 | J1084 Generator Interconnection Network Upgrades | 26646 | 2021-09-15 | SUB | 2023-10-01 | Rock Creek | Substation |  | 345 | 345 |  | Rock Creek 345 kV ring bus will be expanded with a 345 kV breaker and other necessary equipment to interconnect the new terminal for project J1084. |  | IA |  |  | Planned | 1294462 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21998 | 2022-08-24 | J1164 Generator Interconnection TOIF | 26674 | 2022-08-24 | SUB | 2024-08-01 | Magnolia | Substation |  | 161 | 161 |  | Magnolia 161 kV substation currently has no circuit breakers protecting the Magnolia to Elk 161 kV line and the Magnolia to Rock County 161 kV line. The Facilities Study for J1164 identified Network Upgrades and TOIF necessary for the interconnection of project J1164 to ITCM’s Magnolia 161 kV substation. Project J1164’s impact to the transmission system is currently being evaluated as part of the DPP 2018 April West Area Study, which has not been finalized pending results of an Affected System Study. |  | MN |  |  | Planned | 475538 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21999 | 2022-08-24 | J1164 Generator Interconnection Network Upgrades | 26675 | 2022-08-24 | SUB | 2024-08-01 | Magnolia | Substation |  | 161 | 161 |  | Rebuild of Magnolia 161 kV substation as a 4-terminal, 4 breaker, ring-bus substation |  | MN |  |  | Planned | 6770308 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21999 | 2022-08-24 | J1164 Generator Interconnection Network Upgrades | 26678 | 2022-08-24 | LN | 2024-08-01 | Rock County | Magnolia | 1 | 161 | 161 |  | The Magnolia - Rock County 161 kV line will be relocated to a new terminal at the reconstructed Magnolia 161 kV ring-bus |  | MN |  |  | Planned | 730080 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21999 | 2022-08-24 | J1164 Generator Interconnection Network Upgrades | 26677 | 2022-08-24 | LN | 2024-08-01 | Elk | Magnolia | 1 | 161 | 161 |  | The Magnolia-Elk 161 kV line will be relocated to a new terminal at the reconstructed Magnolia 161 kV ring-bus |  | MN |  |  | Planned | 775200 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | C | West | ITCM | 21999 | 2022-08-24 | J1164 Generator Interconnection Network Upgrades | 26676 | 2022-08-24 | LN | 2024-08-01 | Sibley | Magnolia | 1 | 69 | 69 |  | The Sibley to Magnolia 69 kV line will be relocated to allow for expansion of facilities at Magnolia |  | MN |  |  | Planned | 558000 | Engineering |  | 2021 |  |  | ITC Midwest | N | N | N
A in MTEP22 | B | East | ITCT | 15875 | 2021-09-24 | ITC_19_028 | 23968 | 2021-09-24 | LNup | 2024-06-01 | Kentucky | Luzon | 1 | 120 |  |  | Completely remove the sag limit on the Kentucky – Luzon 120 kV line. |  | MI |  |  | Proposed | 500000 | Engineering |  |  |  |  | ITC Transmission | N | N | N
A in MTEP22 | B | East | ITCT | 17999 | 2021-09-17 |  | 24771 | 2020-01-08 | LNrc | 2024-06-01 | Corktown | Waterman | 1 | 120 |  |  | The proposed solution is to re-conductor approximately 3.7 miles utilizing 3200 Kcmil underground cable. |  | MI | 3.7 |  | Proposed | 7000000 | Engineering |  | 2020 |  |  | ITC Transmission | N | N | N
A in MTEP22 | B | East | ITCT | 20182 | 2022-08-19 |  | 25943 | 2022-06-07 | IND | 2024-12-31 | Northeast |  |  | 120 |  |  | Install a 120 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Northeast 120kV bus. |  | MI |  |  | Proposed | 1320000 | Engineering |  |  |  |  | ITC Transmission | N | N | N
A in MTEP22 | B | East | ITCT | 20183 | 2022-08-19 |  | 25945 | 2022-06-07 | IND | 2024-12-31 | Stephens |  |  | 230 |  |  | Install a 230 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Staphens 230kV bus. |  | MI |  |  | Proposed | 3500000 | Engineering |  |  |  |  | ITC Transmission | N | N | N
A in MTEP22 | B | East | ITCT | 20185 | 2022-08-19 |  | 25947 | 2022-06-07 | IND | 2024-12-31 | Warren |  |  | 120 |  |  | Install a 120 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Warren 120kV bus. |  | MI |  |  | Proposed | 1700000 | Engineering |  |  |  |  | ITC Transmission | N | N | N
A in MTEP22 | B | East | ITCT | 20186 | 2022-08-19 |  | 25948 | 2022-06-07 | IND | 2024-12-31 | Mack |  |  | 120 |  |  | Install a 120 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Mack 120kV bus. |  | MI |  |  | Proposed | 1700000 | Engineering |  |  |  |  | ITC Transmission | N | N | N
A in MTEP22 | C | East | ITCT | 20525 | 2021-09-17 |  | 26120 | 2021-09-17 | LNrl | 2022-12-31 | blanket |  |  | 345 | 120 |  | blanket relocation project for relocations less than $1 million each |  | MI |  |  | Proposed | 2000000 | Planning |  |  |  |  | ITC Transmission | N | N | N
A in MTEP22 | C | East | ITCT | 21166 | 2021-09-17 |  | 26160 | 2021-09-17 | SUB | 2023-06-01 | Maple (J1062) |  |  | 345 |  |  | Build the J1062 Interconnection station as a breaker and half station with three breakers in a ring bus configuration. |  | MI |  |  | Planned | 10908064 |  |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP22 | C | East | ITCT | 21166 | 2021-09-17 |  | 26162 | 2021-09-17 | TEQ | 2023-06-01 | Majestic |  |  | 345 |  |  | Remove Majestic pos. AI wave trap. |  | MI |  |  | Planned | 252456 |  |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP22 | C | East | ITCT | 21166 | 2021-09-17 |  | 26161 | 2021-09-17 | LINE | 2023-06-01 | Majestic | Lemoyne | 1 | 345 |  |  | Extend the Lemoyne - Majestic 345kV line to loop in the station. |  | MI |  |  | Planned | 5274000 |  |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP22 | C | East | ITCT | 21726 | 2022-05-04 | ITC_21_029 | 26336 | 2022-03-10 | SUBmisc | 2026-06-01 | Warren |  |  | 120 |  |  | Replace station equipment at Warren to meet or exceed 528 MVA (2540 Amps) |  | MI |  |  | Proposed | 160000 | Engineering |  | 2021 |  |  | ITC Transmission | N | N | N
A in MTEP22 | C | East | ITCT | 21745 | 2022-05-03 | ITC_21_031 | 26337 | 2021-09-21 | LNrc | 2026-06-01 | Cato | Waterman | 1 | 120 |  |  | Re-conductor approximately 4.43 miles utilizing 1600MM2 CU XLPE underground cable. |  | MI | 4.43 |  | Proposed | 15000000 | Engineering |  | 2021 |  |  | ITC Transmission | N | N | N
A in MTEP22 | C | East | ITCT | 21958 | 2021-09-17 | ITC_19_003 | 26578 | 2021-09-17 | TAP | 2024-12-31 | Augusta |  |  | 120 |  |  | Install 2 new 120 kV, 1-way, full-load-break 2,000 A GOAB switches near the Augusta 2 Tap. |  | MI |  |  | Proposed | 1300000 | Engineering |  | 2021 |  |  | ITC Transmission | N | N | N
A in MTEP22 | C | East | ITCT | 22013 | 2021-09-17 |  | 26661 | 2021-10-11 | TAP | 2023-12-31 | ITCT 120 kV Lines |  |  | 138 |  |  | Install or replace an existing pole top switch with a new 120 kV, 1-way full-load-break pole top switch at tap points. |  | MI |  |  | Proposed | 2400000 | Budgetary |  | 2021 |  |  | ITC Transmission | N | N | N
A in MTEP22 | C | East | ITCT | 22016 | 2021-09-17 |  | 26663 | 2021-09-17 | SUB | 2025-12-31 | ITCT Facilities |  |  | 120 |  |  | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $1 Million that have an in service date within the year 2025 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $1 Million a separate project will be submitted for approval. |  | MI |  |  | Proposed | 2000000 | Budgetary |  | 2021 |  |  | ITC Transmission | N | N | N
A in MTEP22 | C | East | ITCT | 22017 | 2021-09-17 |  | 26665 | 2021-09-17 | SUB | 2024-12-31 | ITCT Facilities |  |  | 345 | 120 |  | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. |  | MI |  |  | Proposed | 37140000 | Budgetary |  | 2021 |  |  | ITC Transmission | N | N | N
A in MTEP22 | C | West | MDU | 20946 | 2021-09-15 |  | 26118 | 2022-09-08 | LN | 2024-12-31 | Poplar Trans | Poplar Oil Field | 1 | 115 |  |  | Build a new Poplar Trans-Poplar Oil Field 115 kV line |  | MT |  | 10 | Proposed | 1350000 | Planning |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP22 | C | West | MDU | 20946 | 2021-09-15 |  | 27407 | 2022-09-08 | SUB | 2024-12-31 | Poplar |  |  | 115 | 60 |  | Bay addition for new line to Poplar 2 |  | MT |  |  | Planned | 1450000 | Planning |  | 2022 |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP22 | C | West | MDU | 20946 | 2021-09-15 |  | 26119 | 2022-09-08 | SUB | 2024-12-31 | Poplar Oil Field |  |  | 115 | 60 |  | Build a new Poplar Oil Field 115/60 kV sub |  | MT |  |  | Proposed | 5725000 | Planning |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP22 | C | West | MDU | 21889 | 2022-08-25 |  | 26475 | 2021-09-24 | SUB | 2024-12-31 | Hettinger |  |  | 115 |  |  | Age and condition to replace existing 115/69/41.6 kV facilities |  | ND |  |  | Proposed | 6500000 | Planning |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP22 | C | West | MDU | 21894 | 2021-09-13 |  | 26484 | 2022-08-25 | SUB | 2024-12-31 | Tioga 2 |  |  | 115 | 60 |  | Add 2-115 kV breaker, re-terminate 115 kV lines, add 115/60 kV transformer and breakers and move 60 kV lines from Tioga 1 |  | ND |  |  | Planned | 5200000 | Planning |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP22 | C | West | MDU | 21894 | 2021-09-13 |  | 26702 | 2022-04-11 | LN | 2024-12-31 | Tioga 2 | Ray | 2 | 60 |  |  | A second circuit from Tioga 2 towards Ray sub |  | ND |  |  | Planned | 1500000 | Planning |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP22 | C | West | MDU | 21894 | 2021-09-13 |  | 26518 | 2022-04-11 | LN | 2024-12-31 | Tioga 2 | Ray |  | 115 |  |  | With retirement of Tioga 1 tying the 115 kV line together from Ray to Tioga 2 |  | ND |  | 0 | Planned | 75000 | Planning |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP22 | C | West | MDU | 21894 | 2021-09-13 |  | 26511 | 2022-04-11 | LN | 2024-12-31 | Tioga 2 | Ray |  | 60 |  |  | Re-terminate 60 kV line from retired Tioga 1 to Tioga 2 |  | ND |  | 2.5 | Planned | 175000 | Planning |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP22 | C | West | MDU | 21894 | 2021-09-13 |  | 26506 | 2022-04-11 | LN | 2024-12-31 | Tioga 2 | Battleview |  | 60 |  |  | Re-terminate 60 kV line from retire Tioga 1 to Tioga 2 |  | ND |  | 0.06 | Planned | 100000 | Planning |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP22 | C | West | MEC | 21871 | 2022-04-07 | T91NQ | 26452 | 2022-04-07 | SUB | 2024-12-31 | Sub E East Moline |  |  | 69 |  |  | Replace aged equipment at Sub E East Moline. Project includes installing a new control building, replacing 69 kV oil circuit breakers, and replacing 69 kV cap-and-pin switches and insulators. |  | IL |  |  | Planned | 7000000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21872 | 2022-04-07 | T92AB | 26453 | 2022-04-07 | COM | 2024-12-31 | Sub E East Moline | Sub 37 |  | 69 |  |  | Install OPGW on the Sub E East Moline-Sub 37 69 kV Line |  | IL |  |  | Planned | 1000000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21873 | 2021-09-13 | T92AC, T92AD | 26454 | 2021-09-13 | COM | 2021-12-31 | Sub 39 | Sub 31 Tap |  | 161 |  |  | Install OPGW on the Sub 39-Sub 31 Tap 161 kV line |  | IL |  |  | Planned | 500000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21873 | 2021-09-13 | T92AC, T92AD | 26455 | 2021-09-13 | COM | 2023-12-31 | Sub 31 Tap | Sub 28 |  | 161 |  |  | Install OPGW on the Sub 31 Tap-Sub 28 161 kV line |  | IL |  |  | Planned | 200000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21874 | 2022-05-27 |  | 26457 | 2022-05-27 | SUB | 2024-12-31 | Sub 17 |  |  | 345 | 161 |  | Convert the Sub 17 161 kV yard to a ring bus. Install new 345-161 kV transformer. |  | IL |  |  | Planned | 15000000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21874 | 2022-05-27 |  | 26461 | 2022-05-27 | TAP | 2024-12-31 | Sub 49 | Beaver Channel | 1 | 161 |  | 266 | Install new line taps to loop the Sub 49-Beaver Channel 161 kV line into Sub 17. |  | IL |  |  | Planned | 1600000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21874 | 2022-05-27 |  | 26460 | 2022-05-27 | TAP | 2024-12-31 | Sub 17 | Sub 28 | 1 | 161 |  | 277 | Reterminate the Sub 17-Sub 28 161 kV line at a new terminal at Sub 17 to accommodate Sub 17 161 kV yard conversion to a ring bus. Install OPGW between Sub 17 and Sub 28 during the same construction outage. |  | IL |  |  | Planned | 1600000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21874 | 2022-05-27 |  | 26459 | 2022-05-27 | LN | 2024-12-31 | Cordova | Sub 17 | 1 | 345 |  | 1740 | Install a new 345 kV line connecting Cordova and Sub 17. |  | IL |  | 0.2 | Planned | 1800000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21874 | 2022-05-27 |  | 26458 | 2022-05-27 | SUB | 2024-12-31 | Cordova |  |  | 345 |  |  | Expand the Cordova 345 kV ring bus to add one new 345 kV line terminal for the new 345 kV line between Cordova and Sub 17. |  | IL |  |  | Planned | 3000000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21893 | 2021-09-15 |  | 26480 | 2021-09-13 | TX | 2021-09-30 | Neal North |  |  | 161 | 69 |  | Remove the failed 161-69 kV transformer at Neal North and replace it with a spare unit. |  | IA |  |  | Planned | 500000 | Planning |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21893 | 2021-09-15 |  | 26481 | 2021-09-13 | TX | 2021-12-31 | Neal North |  |  | 161 | 69 |  | Purchase a new 161-69 kV spare transformer. |  | IA |  |  | Planned | 1100000 | Planning |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21895 | 2021-09-15 |  | 26482 | 2021-09-14 | TX | 2021-12-31 | Sycamore |  |  | 161 | 69 |  | Removed failed transformer and replace it with a spare unit |  | IA |  |  | Planned | 1500000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21895 | 2021-09-15 |  | 26483 | 2021-09-14 | TX | 2022-09-30 | Sycamore |  |  | 161 | 69 |  | Purchase a new 161-69 kV spare unit at Sycamore. |  | IA |  |  | Planned | 1500000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21896 | 2021-09-13 |  | 26485 | 2021-09-13 | SUB | 2023-06-01 | NE 94th Ave Substation |  |  | 161 | 13.2 |  | Construct new 161-13.8 kV substation |  | IA |  |  | Planned | 5300000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21896 | 2021-09-13 |  | 26486 | 2021-09-13 | TAP | 2023-06-01 | NE 54th Ave | Bondurant |  | 161 |  |  | Construct 161 kV line taps |  | IA |  |  | Planned | 1400000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21897 | 2021-09-13 |  | 26487 | 2021-09-13 | SUB | 2025-06-01 | Berwick |  |  | 161 | 13.2 |  | Construct new 161-13.8 kV substation |  | IA |  |  | Planned | 5300000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21897 | 2021-09-13 |  | 26488 | 2021-09-13 | TAP | 2025-06-01 | Delaware | 34th Ave NW |  | 161 |  |  | Construct 161 kV line taps |  | IA |  |  | Planned | 1400000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21898 | 2021-09-13 |  | 26491 | 2021-09-13 | BUS | 2023-12-01 | CBEC |  |  | 161 |  |  | Replace insulators, install new bus supports and/or replace bus to increase bus withstand capabilities |  | IA |  |  | Planned | 1000000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21898 | 2021-09-13 |  | 26494 | 2021-09-13 | BUS | 2024-12-01 | Sycamore |  |  | 161 | 69 |  | Replace insulators, install new bus supports and/or replace bus to increase bus withstand capabilities. |  | IA |  |  | Planned | 4500000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21898 | 2021-09-13 |  | 26493 | 2021-09-13 | BUS | 2023-12-01 | Neal North |  |  | 161 |  |  | Replace insulators, install new bus supports and/or replace bus to increase bus withstand capabilities. |  | IA |  |  | Planned | 300000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21898 | 2021-09-13 |  | 26492 | 2021-09-13 | BUS | 2023-12-01 | Raun |  |  | 161 |  |  | Replace insulators, install new bus supports and/or replace bus to increase bus withstand capabilities |  | IA |  |  | Planned | 700000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21901 | 2021-09-13 |  | 26495 | 2021-09-13 | TEQ | 2022-12-01 | Raun |  |  | 345 |  |  | Replace switches due to condition |  | IA |  |  | Planned | 900000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21902 | 2022-01-26 |  | 26497 | 2022-01-26 | TAP | 2023-12-01 | Anthon |  |  | 69 |  |  | Install 69 kV line taps into new substation to serve customer load or to improve system reliability. |  | IA |  |  | Proposed | 1500000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21904 | 2022-01-26 |  | 26499 | 2022-01-26 | TAP | 2023-12-01 | Sioux Center |  |  | 69 |  |  | Install 69 kV line taps into new substation to serve customer load or to improve system reliability. |  | IA |  |  | Proposed | 600000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21906 | 2021-09-13 |  | 26500 | 2021-09-14 | LNup | 2022-12-01 | Sheldon | Boyden | 1 | 69 |  |  | Replace structures and jumpers on Sheldon-Boyden 69 kV line to increase line rating |  | IA |  |  | Planned | 600000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21907 | 2022-01-26 |  | 26502 | 2021-09-13 | LNup | 2023-06-01 | Templeton | Audubon North | 1 | 69 |  |  | Replace structures on Templeton-Audubon North 69 kV line to increase rating |  | IA |  |  | Proposed | 500000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21907 | 2022-01-26 |  | 26504 | 2021-09-13 | TEQ | 2023-06-01 | Audoban North |  |  | 69 |  |  | Replace terminal equipment and relaying at Audubon North |  | IA |  |  | Planned | 400000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21907 | 2022-01-26 |  | 26503 | 2021-09-14 | LNup | 2023-06-01 | Exira | Audubon North | 1 | 69 |  |  | Replace structures on Audubon North-Exira 69 kV line to increase rating |  | IA |  |  | Planned | 750000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21908 | 2022-05-26 |  | 26505 | 2022-05-26 | LNrb | 2024-12-01 | Carroll County | Auburn |  | 69 |  |  | Rebuild the Carroll County-Auburn 69 kV line |  | IA |  |  | Planned | 2500000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21908 | 2022-05-26 |  | 26996 | 2022-05-26 | LNrb | 2024-12-01 | Auburn | Sherwood | 1 | 69 |  |  | Rebuild Auburn to Sherwood 69 kV line. |  | IA |  |  | Planned | 4700000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21908 | 2022-05-26 |  | 26507 | 2022-05-23 | TEQ | 2024-12-01 | Auburn |  |  | 69 |  |  | Replace limiting terminal equipment (jumpers and switches) at Auburn Substation |  | IA |  |  | Planned | 500000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21909 | 2021-09-13 |  | 26508 | 2021-09-13 | SwSta | 2024-12-01 | Sac City |  |  | 69 |  |  | Construct a new switching station to interconnect two MidAmerican 69 kV lines and one Corn Belt 69 kV line |  | IA |  |  | Planned | 6000000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21909 | 2021-09-13 |  | 26512 | 2021-09-13 | LNrb | 2024-12-01 | Schaller | Odebolt | 1 | 69 |  |  | Rebuild and reconductor the Schaller-Odebolt 69 kV line |  | IA |  |  | Planned | 10000000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21909 | 2021-09-13 |  | 26510 | 2021-09-14 | LNrb | 2024-12-01 | Sac County | Schaller | 1 | 69 |  |  | Rebuild and reconductor the Sac County-Schaller 69 kV line |  | IA |  |  | Planned | 3000000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21909 | 2021-09-13 |  | 26509 | 2021-09-13 | TAP | 2024-12-01 | Sac City |  |  | 69 |  |  | Construct line taps into Sac City Switching Station |  | IA |  |  | Planned | 1000000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21910 | 2021-09-14 |  | 26513 | 2021-09-13 | SUB | 2022-12-31 | Hills |  |  | 345 |  |  | Replace 345 kV Breakers, Switches, and relaying equipment at Hills Substation |  | IA |  |  | Planned | 4500000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21910 | 2021-09-14 |  | 26516 | 2021-09-13 | TEQ | 2022-12-31 | Louisa |  |  | 345 |  |  | Replace 345 kV relaying on the Hills-Sub T Haskins - Louisa terminal and Hills - Walcott - Louisa terminals at Louisa |  | IA |  |  | Planned | 300000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21910 | 2021-09-14 |  | 26515 | 2021-09-13 | TEQ | 2022-12-31 | Walcott |  |  | 345 |  |  | Replace 345 kV relaying on Hills-Walcott - Louisa terminal at Walcott |  | IA |  |  | Planned | 300000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21910 | 2021-09-14 |  | 26514 | 2021-09-13 | TEQ | 2022-12-31 | Sub T Haskins |  |  | 345 |  |  | Replace 345 kV relaying on Hills-Sub T Haskins - Louisa terminal at Sub T Haskins |  | IA |  |  | Planned | 300000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21911 | 2022-01-26 |  | 26517 | 2021-09-13 | SUBmisc | 2022-12-31 | IC Enron |  |  | 161 |  |  | Add two line switches at IC Enron |  | IA |  |  | Planned | 300000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21912 | 2021-09-13 |  | 26519 | 2021-09-13 | CAP | 2022-12-31 | Substation J |  |  | 161 |  |  | Replace 161 kV Capacitor at Sub J |  | IA |  |  | Planned | 500000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21913 | 2021-09-13 |  | 26520 | 2021-09-13 | LN | 2024-12-01 | Northgate | Rose Hollow | 1 | 161 |  |  | Construct 161 kV line from Northgate to Rose Hollow |  | IA |  |  | Planned | 2000000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21913 | 2021-09-13 |  | 26521 | 2021-09-13 | TEQ | 2024-12-01 | Northgate |  |  | 161 |  |  | Expand existing Northgate bus to a ring bus to accommodate new line terminal |  | IA |  |  | Planned | 1500000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21914 | 2022-06-23 |  | 26522 | 2022-06-23 | SUB | 2024-12-01 | Butler |  |  | 161 | 69 |  | Install 161-69 kV, 125 MVA Transformer and associated 161 kV and 69 kV circuit breakers for transformer and 69 kV line |  | IA |  |  | Planned | 4500000 | Budgetary |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21914 | 2022-06-23 |  | 27124 | 2022-08-10 | LNcnv | 2024-12-01 | Donald Feldman | Shell Rock | 1 | 69 |  |  | Convert 34.5 kV line from Donald Feldman to Shell Rock to 69 kV line |  | IA |  |  | Planned | 3200000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21914 | 2022-06-23 |  | 27123 | 2022-08-10 | LNcnv | 2024-12-01 | New Hartford | Shell Rock | 1 | 69 |  |  | Convert 34.5 kV line from New Hartford to Shell Rock to 69 kV line. |  | IA |  |  | Planned | 10000000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 21914 | 2022-06-23 |  | 26852 | 2022-08-10 | LNcnv | 2024-12-01 | Butler | New Hartford | 1 | 69 |  |  | Convert 34 kV line from Butler to New Hartford to 69 kV |  | IA |  |  | Planned | 8000000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 22305 | 2021-12-01 |  | 26772 | 2022-01-17 | LNup | 2022-12-31 | Lakefield Jct | Obrien | 1 | 345 |  |  | Replace line structures to increase line ratings on MidAmerican owned portion of Lakefield to Obrien 345 kV line. MidAmerican owns the line from Obrien to Lakefield Jct and ITC owns the remaining line from Lakefield Jct to Lakefield generating station. |  | IA |  |  | Planned | 2200000 | Planning |  | 2021 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 22746 | 2022-05-23 |  | 26827 | 2022-05-23 | LNup | 2022-12-31 | Overland Trail | Fallow | 1 | 345 |  |  | Replace five line structures on Overland Trail to Fallow Avenue 345 kV line. |  | IA |  |  | Planned | 1250000 | Engineering |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 22747 | 2022-05-23 |  | 26829 | 2022-03-01 | LNup | 2022-12-31 | Sycamore | Bondurant | 1 | 345 |  |  | The wood H-frame or monopole structures will be replaced with steel structures. |  | IA |  |  | Planned | 2500000 | Engineering |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 22747 | 2022-05-23 |  | 26838 | 2022-03-01 | LNup | 2022-12-31 | 2nd & Broadway | Sycamore | 1 | 69 |  |  | The wood H-frame or monopole structures will be replaced with steel structures. |  | IA |  |  | Planned | 1000000 | Engineering |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 22747 | 2022-05-23 |  | 26837 | 2022-03-01 | LNup | 2022-12-31 | Sycamore | 50th & Aurora | 1 | 69 |  |  | The wood H-frame or monopole structures will be replaced with steel structures. |  | IA |  |  | Planned | 1000000 | Engineering |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 22747 | 2022-05-23 |  | 26836 | 2022-03-01 | LNup | 2022-12-31 | 86th & University | Ashawa | 1 | 69 |  |  | The wood H-frame or monopole structures will be replaced with steel structures. |  | IA |  |  | Planned | 1000000 | Engineering |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 22747 | 2022-05-23 |  | 26835 | 2022-03-01 | LNup | 2022-12-31 | 38th & Franklin | 28th & Rock Island | 1 | 69 |  |  | The wood H-frame or monopole structures will be replaced with steel structures. |  | IA |  |  | Planned | 1000000 | Engineering |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 22747 | 2022-05-23 |  | 26834 | 2022-03-01 | LNup | 2022-12-31 | 59th & Tonka Tap | 73rd & Buffalo | 1 | 69 |  |  | The wood H-frame or monopole structures will be replaced with steel structures. |  | IA |  |  | Planned | 1000000 | Engineering |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 22747 | 2022-05-23 |  | 26833 | 2022-03-01 | LNup | 2022-12-31 | Delaware | 34th Avenue NW | 1 | 161 |  |  | The wood H-frame or monopole structures will be replaced with steel structures. |  | IA |  |  | Planned | 1000000 | Engineering |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 22747 | 2022-05-23 |  | 26832 | 2022-03-01 | LNup | 2022-12-31 | Sycamore | Forest&Vermont | 1 | 161 |  |  | The wood H-frame or monopole structures will be replaced with steel structures. |  | IA |  |  | Planned | 1000000 | Engineering |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 22747 | 2022-05-23 |  | 26831 | 2022-05-23 | LNup | 2022-12-31 | Ashawa | 109th & Clark | 1 | 161 |  |  | The wood H-frame or monopole structures will be replaced with steel structures. |  | IA |  |  | Planned | 1000000 | Engineering |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 22747 | 2022-05-23 |  | 26830 | 2022-05-23 | LNup | 2022-12-31 | Bondurant | Montezuma | 1 | 345 |  |  | The wood H-frame or monopole structures will be replaced with steel structures. |  | IA |  |  | Planned | 2500000 | Engineering |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 23366 | 2022-08-24 |  | 27026 | 2022-08-24 | SUB | 2024-01-02 | Powell Creek |  |  | 161 | 13 |  | Construct a new Powell Creek 161-13 kV distribution substation tapping the Buena Vista-Sac County 161 kV line. |  | IA |  |  | Planned | 3500000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 23366 | 2022-08-24 |  | 27027 | 2022-08-24 | TAP | 2024-01-02 | Powell Creek |  |  | 161 |  |  | Power Creek substation is tapped on Buena Vista to Sac County 161 kV line |  | IA |  |  | Proposed | 2000000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 23480 | 2022-08-24 |  | 27291 | 2022-08-24 | TX | 2022-09-30 | Sub. 18 |  |  | 161 | 69 |  | Installation of replacement transformer at Sub. 18 |  | IA |  |  | Planned | 1400000 | Engineering |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 23480 | 2022-08-24 |  | 27292 | 2022-08-24 | TX | 2023-12-31 | Sub. 18 |  |  | 161 | 69 |  | Purchase a new spare transformer at Sub. 18 |  | IA |  |  | Planned | 2000000 | Engineering |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 23516 | 2022-08-24 | H01DE, T92NP | 27289 | 2022-08-24 | SUB | 2024-09-01 | Enterprise Way South |  |  | 161 |  |  | Construct new 161-13.2 kV distribution substation |  | IA |  |  | Proposed | 3000000 | Budgetary |  | 2022 | Transmission costs only |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | C | West | MEC | 23516 | 2022-08-24 | H01DE, T92NP | 27290 | 2022-08-24 | TAP | 2024-09-01 | Sub 56 | Enterprise Way | 1 | 161 |  |  | Install in-and-out line taps to loop the existing Sub 56-Enterprise Way 161 kV line into the new Enterprise Way South substation. |  | IA |  |  | Proposed | 500000 | Budgetary |  |  |  |  | MidAmerican Energy Company | N | N | N
A in MTEP22 | B | East | METC | 15910 | 2021-09-29 | METC_18_072 | 24018 | 2022-05-25 | LNrb | 2025-12-31 | Marquette | Bingham | 1 | 138 |  |  | Rebuild 18.76 miles of the Marquette – Bingham circuit using 954 ACSR conductor with single circuit steel structures. |  | MI | 18.76 |  | Proposed | 27450000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | B | East | METC | 15910 | 2021-09-29 | METC_18_072 | 26989 | 2022-05-25 | TEQ | 2025-12-31 | Bingham |  |  | 138 |  |  | Complete all work necessary to connect OPGW at position WM8 at Bingham 138 kV station. |  | MI |  |  | Proposed | 80000 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP22 | B | East | METC | 15910 | 2021-09-29 | METC_18_072 | 26988 | 2022-05-25 | TEQ | 2025-12-31 | Marquette | Bingham |  | 138 |  |  | Complete all work necessary to connect Technical Drive MOAB 3105 back to Bingham station. |  | MI |  |  | Proposed | 70000 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 20906 | 2022-04-11 |  | 26111 | 2022-04-11 | SUB | 2023-01-31 | Styx (J984) |  |  | 345 |  |  | Install a new 345kV 3 Breaker ring station laid out in a breaker and a half configuration. |  | MI |  |  | Planned | 11526200 | [5 empty] | METC | N | N | N
A in MTEP22 | C | East | METC | 20906 | 2022-04-11 |  | 26115 | 2022-04-11 | TEQ | 2023-01-31 | Slate |  |  | 345 |  |  | Fiber jumper work at Slate station. |  | MI |  |  | Planned | 21060 | [5 empty] | METC | N | N | N
A in MTEP22 | C | East | METC | 20906 | 2022-04-11 |  | 26114 | 2022-04-11 | SUBmisc | 2023-01-31 | Murphy |  |  | 345 |  |  | Upgrade Murphy FH26 Relay |  | MI |  |  | Planned | 169122 | [5 empty] | METC | N | N | N
A in MTEP22 | C | East | METC | 20906 | 2022-04-11 |  | 26113 | 2022-04-11 | SUBmisc | 2023-01-31 | Nelson Road |  |  | 345 |  |  | Upgrade Relay at Nelson Rd Position FH28 |  | MI |  |  | Planned | 169122 | [5 empty] | METC | N | N | N
A in MTEP22 | C | East | METC | 20906 | 2022-04-11 |  | 26112 | 2022-04-11 | LINE | 2023-01-31 | Murphy | Nelson Road | 1 | 345 |  |  | Loop the Murphy - Nelson Road 345kV circuit into the new J984 Interconnection station. |  | MI |  |  | Planned | 3434400 | [5 empty] | METC | N | N | N
A in MTEP22 | C | East | METC | 20965 | 2021-09-17 |  | 26121 | 2021-02-22 | LNrl | 2022-12-31 | blanket |  |  | 345 | 138 |  | Relocation portions of transmission lines located in public right of way at the government entity’s mandate. |  | MI |  |  | Proposed | 2000000 | Planning |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21145 | 2022-01-11 |  | 26150 | 2022-01-11 | SwSta | 2023-03-31 | Pixley |  |  | 138 |  |  | Install a new 138 kV station with 3-138kV 40KAIC breakers and associated disconnects in a ring bus configuration. |  | MI |  |  | M3_Long Lead Materials | 5697000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21145 | 2022-01-11 |  | 26152 | 2022-01-11 | SUBmisc | 2023-03-31 | Beecher |  |  | 138 |  |  | Replace existing SCADA router at Beecher and update telecom. |  | MI |  |  | M3_Long Lead Materials | 78132 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21145 | 2022-01-11 |  | 26151 | 2022-01-11 | LINE | 2023-03-31 | Beecher | Morocco |  | 138 |  |  | Loop the Beecher - Morocco 138kV circuit into the new METC Pixley 138kV station. |  | MI |  |  | M3_Long Lead Materials | 843600 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21146 | 2021-09-17 |  | 26153 | 2021-04-23 | SwSta | 2023-11-15 | Morningside |  |  | 138 |  |  | Install a new 138 kV station with 3-138kV 40KAIC breakers and associated disconnects in a ring bus configuration. |  | MI |  |  | M3_Long Lead Materials | 6088870 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21146 | 2021-09-17 |  | 26157 | 2021-04-23 | COM | 2023-11-15 | Dort | Garfield |  | 138 |  |  | Install underground fiber communication between Morningside and Dort, Install underground fiber communication between Morningside and Garfield. |  | MI |  |  | M3_Long Lead Materials | 3580800 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21146 | 2021-09-17 |  | 26156 | 2021-04-23 | SUBmisc | 2023-11-15 | Garfield |  |  | 138 |  |  | Upgrade position 477 relaying. Remove position 477 wave trap and line tuner. |  | MI |  |  | M3_Long Lead Materials | 235500 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21146 | 2021-09-17 |  | 26155 | 2021-04-23 | SUBmisc | 2023-11-15 | Dort |  |  | 138 |  |  | Upgrade position 488 relaying. Remove position 488 wave trap and line tuner. |  | MI |  |  | M3_Long Lead Materials | 235500 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21146 | 2021-09-17 |  | 26154 | 2021-04-23 | LINE | 2023-11-15 | Dort | Garfield |  | 138 |  |  | Loop the Dort - Garfield 138kV circuit into the new METC 138kV Morningside station. |  | MI |  |  | M3_Long Lead Materials | 748800 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21185 | 2021-09-17 |  | 26176 | 2021-07-07 | SUB | 2024-05-31 | Muskrat (J1043) |  |  | 345 |  |  | Construct J1043 Station (Muskrat) as a ring bus station with three 40kA breakers. |  | MI |  |  | M2a_Pre-Project Approval | 7596934 |  |  | 2024 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21185 | 2021-09-17 |  | 26179 | 2021-07-07 | SUBmisc | 2024-05-31 | Nelson Road |  |  | 345 |  |  | Remove wavetrap and tuners and upgrade RH26 relaying. |  | MI |  |  | M2a_Pre-Project Approval | 175260 |  |  | 2024 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21185 | 2021-09-17 |  | 26178 | 2021-07-07 | SUBmisc | 2024-05-31 | Vergennes |  |  | 345 |  |  | Remove wave traps and tuners and upgrade relaying. |  | MI |  |  | M2a_Pre-Project Approval | 175260 |  |  | 2024 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21185 | 2021-09-17 |  | 26177 | 2021-07-07 | LINE | 2024-05-31 | Vergennes | Nelson Road | 1 | 345 |  |  | Extend the Vergennes - Nelson Road 345kV 0.1 miles to loop in the J1043 345kv station. |  | MI |  |  | M2a_Pre-Project Approval | 1638000 |  |  | 2024 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21445 | 2021-09-17 |  | 26271 | 2021-07-13 | LNrb | 2024-06-01 | Donaldson Creek | White Lake |  | 138 |  |  | Rebuild approximately 18.43 miles of the 336 ACSR conductor utilizing 954 ACSR on standard 138 kV double circuit structures with OPGW. |  | MI | 18.43 |  | M3_Long Lead Materials | 29581200 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21445 | 2021-09-17 |  | 26273 | 2021-07-13 | SUBmisc | 2024-06-01 | White Lake |  |  | 138 |  |  | Replace 188 Line Drop and Bus, Install OPGW |  | MI |  |  | M3_Long Lead Materials | 446857 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21445 | 2021-09-17 |  | 26272 | 2021-07-13 | SUBmisc | 2024-06-01 | Donaldson Creek |  |  | 138 |  |  | Replace BM11 Line Drop, Install OPGW |  | MI |  |  | M3_Long Lead Materials | 113970 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21446 | 2021-09-17 |  | 26274 | 2021-07-13 | SUB | 2023-12-31 | Donaldson Creek |  |  | 138 |  |  | Install 138kV breaker at position 13W8. Install 138kV disconnect switches at positions 13W8 & 13M6. |  | MI |  |  | M3_Long Lead Materials | 1159555 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21485 | 2022-05-17 |  | 26281 | 2021-07-21 | LNup | 2025-12-31 | Lawndale | Murphy | 1 | 138 |  |  | Remove the sag limit on the Lawndale to Murphy 138 kV line to conductor limit |  | MI |  |  | Proposed | 931000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21505 | 2021-09-22 |  | 26282 | 2022-07-11 | SwSta | 2025-06-01 | New Station - Name TBD |  |  | 138 |  |  | Install a new 138 kV station with 3-138kV 40KAIC breakers and associated disconnects in a ring bus configuration. |  | MI |  |  | M2a_Pre-Project Approval | 5093060 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21505 | 2021-09-22 |  | 26283 | 2022-07-11 | LN | 2025-06-01 | Bard | Higgins |  | 138 |  |  | Loop the Bard Rd - Higgins 138kV circuit into the new METC 138kV switching station. |  | MI |  | 0.2 | M2a_Pre-Project Approval | 1068000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21706 | 2022-04-11 |  | 26333 | 2022-04-11 | TAP | 2023-06-30 | Mcgulpin | Riggsville |  | 138 |  |  | Install tap pole and two 1-way switches to facilitate the Mill Creek tap on the Mcgulpin-Riggsville line. |  | MI |  |  | M2a_Pre-Project Approval | 1822800 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21890 | 2022-03-01 | METC_21_067 | 26476 | 2022-03-01 | LNup | 2026-06-01 | Gallagher | Ogemaw | 1 | 138 |  |  | Remediate sag on the 336 ACSR conductor on the Gallagher to Ogemaw 138 kV circuit up to at least 60 MVA summer emergency rating. |  | MI |  |  | Proposed | 660000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21945 | 2022-05-10 |  | 26563 | 2022-05-10 | LNrb | 2025-05-15 | Parr Road | Tangent |  | 138 |  |  | Rebuild approximately 12 miles from Parr Rd - Tangent (J875 Generator Interconnection) on 138kV future double circuit steel poles with 1431 ACSR conductor with OPGW. |  | MI | 12 |  | Proposed | 16000000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21945 | 2022-05-10 |  | 26746 | 2022-05-10 | SUBmisc | 2025-05-15 | Whiting |  |  | 138 |  |  | Equipment Connection |  | MI |  |  | Proposed | 162000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21945 | 2022-05-10 |  | 26745 | 2022-05-10 | SUBmisc | 2025-05-15 | Tangent |  |  | 138 |  |  | Equipment Connection |  | MI |  |  | Proposed | 188000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21945 | 2022-05-10 |  | 26744 | 2022-05-10 | SUBmisc | 2025-05-15 | Parr Road |  |  | 138 |  |  | Equipment Connection |  | MI |  |  | Proposed | 230500 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21945 | 2022-05-10 |  | 26564 | 2022-05-10 | LNrb | 2025-05-15 | Raisin Tap | Whiting |  | 138 |  |  | Rebuild approximately 28.6 miles from Raisin Tap - Whiting section of the Tangent - Whiting 138kV line on 138kV future double circuit steel poles with 1431 ACSR conductor with OPGW. |  | MI | 28.6 |  | Proposed | 37000000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21947 | 2021-09-29 | METC_19_004 | 26567 | 2021-09-14 | TAP | 2024-12-31 | Roedel Road |  |  | 138 |  |  | Replace 3185 and 3198 pole top switches with 2 new 138kV, 1-way, full-load-break 2,000 A GOAB switch near the Roedel Road Tap. |  | MI |  |  | Proposed | 1200000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21952 | 2021-09-17 | METC_21_013 | 26571 | 2021-09-14 | TAP | 2024-12-31 | Dutton |  |  | 138 |  |  | Replace 3004, 3017 and 3493 pole top switches with 3 new 138kV, 1-way, full-load-break 2,000 A GOAB switch near the Dutton Tap. |  | MI |  |  | Proposed | 1700000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21984 | 2021-09-21 |  | 26631 | 2021-10-11 | TAP | 2023-12-31 | METC 138 kV Lines |  |  | 138 |  |  | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. |  | MI |  |  | Proposed | 2400000 | Budgetary |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21990 | 2021-09-17 | METC_21_062 | 26637 | 2021-09-15 | SUB | 2026-06-01 | Twining |  |  | 138 |  |  | Extend the main bus, install a sectional breaker, and install two additional line terminals and all associated equipment at Twinging 138 kV. |  | MI |  |  | Proposed | 2850000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21990 | 2021-09-17 | METC_21_062 | 26638 | 2021-09-15 | LN | 2026-06-01 | Iosco | Karn | 1 | 138 |  |  | Cut the Iosco – Karn 138 kV circuit into Twining substation. Build approximately 0.15 miles of new right-of-way from the Iosco – Karn 138 kV circuit into the Twining 138 kV substation, using 954 ACSR conductor on both sides of double-circuit 138 kV structures. |  | MI |  |  | Proposed | 1250000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21993 | 2021-09-17 |  | 26640 | 2021-10-11 | TAP | 2024-12-31 | METC 138 kV Lines |  |  | 138 |  |  | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. |  | MI |  |  | Proposed | 2400000 | Budgetary |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 21995 | 2021-09-17 |  | 26643 | 2021-09-15 | SUBmisc | 2025-12-31 | METC Facilities |  |  | 138 |  |  | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $1 Million that have an in service date within the year 2025 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $1 Million a separate project will be submitted for approval. |  | MI |  |  | Proposed | 2000000 | Budgetary |  | 2025 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22000 | 2021-09-17 |  | 26647 | 2021-09-15 | SUB | 2024-12-31 | METC Facilities |  |  | 138 |  |  | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. |  | MI |  |  | Proposed | 39400000 | Budgetary |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22001 | 2021-09-17 |  | 26649 | 2022-01-28 | SUB | 2024-12-31 | Plum |  |  | 138 |  |  | Install a 138 kV breaker and associated equipment at Plum station to accommodate Wolverine’s interconnection request. |  | MI |  |  | Proposed | 1130000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22001 | 2021-09-17 |  | 26800 | 2022-05-05 | LINE | 2024-12-31 | Plum | Westwood | 1 | 138 |  |  | Install dead-end structure outside Plum substation and string 954 ACSR conductor from this new structure into the new frame. |  | MI |  | 0.05 | Proposed | 2570000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22020 | 2021-09-17 |  | 26668 | 2022-04-29 | LNrb | 2025-12-31 | Leoni | Parr Road | 1 | 138 |  |  | Rebuild approximately 19 miles from Leoni to Parr Rd utilizing 1431 ACSR on standard 138 kV double circuit steel poles with OPGW. |  | MI |  | 18.65 | Proposed | 26230000 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22020 | 2021-09-17 |  | 26947 | 2022-04-29 | LNrc | 2025-12-31 | Lark | Leoni | 1 | 138 |  |  | Utilize 1431 ACSR conductor and OPWG on the Northeast side of the double-circuit structures to relocate Lark – Washtenaw – Leoni 138 kV circuit to the same structures as the Leoni – Parr Road 138 kV circuit from Leoni until Parr Road. Decommission the existing 138 kV structures of the Lark – Washtenaw – Leoni 138 kV circuit from Leoni – Parr Road. |  | MI | 18.65 |  | Proposed | 6015000 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22020 | 2021-09-17 |  | 26946 | 2022-04-29 | TEQ | 2025-12-31 | Parr Road |  |  | 138 |  |  | Upgrade Terminal Equipment at Parr Road 138 kV substation. |  | MI |  |  | Proposed | 180000 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22020 | 2021-09-17 |  | 26945 | 2022-04-29 | TEQ | 2025-12-31 | Leoni |  |  | 138 |  |  | Upgrade Terminal Equipment at Leoni 138 kV substation. |  | MI |  |  | Proposed | 205000 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22021 | 2021-09-17 |  | 26669 | 2021-09-15 | LNrb | 2025-12-31 | Chopin | White Lake | 1 | 138 |  |  | Rebuild section from Chopin to White Lake from the line to Dupont utilizing 954 ACSR conductor on standard 138 kV double circuit structures with OPGW and relocate Cobb - White Lake (Benston) line to the other side of the new 138 kV standard structures utilizing 954 ACSR conductor. |  | MI |  |  | Proposed | 28050000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22021 | 2021-09-17 |  | 26673 | 2021-09-15 | LNrb | 2025-12-31 | Cobb | Dupont | 1 | 138 |  |  | Remove the old structures on the Cobb-Dupont-White Lake and the Cobb-White (Benston) circuits |  | MI |  |  | Proposed | 2310000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22021 | 2021-09-17 |  | 26672 | 2021-09-15 | LNrb | 2025-12-31 | White Lake | Dupont | 1 | 138 |  |  | Rebuild section from White Lake to Dupont utilizing 954 ACSR conductor on standard 138 kV double circuit structures with OPGW and relocate the line from Dupont back up to White Lake (to the east) to the other side of the new 138 kV structures utilizing 954 ACSR conductor. |  | MI |  |  | Proposed | 8475000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22021 | 2021-09-17 |  | 26671 | 2021-09-15 | TEQ | 2025-12-31 | Chopin |  |  | 138 |  |  | Upgrade Terminal Equipment |  | MI |  |  | Proposed | 76000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22021 | 2021-09-17 |  | 26670 | 2021-09-15 | TEQ | 2025-12-31 | White Lake |  |  | 138 |  |  | Upgrade Terminal Equipment |  | MI |  |  | Proposed | 107000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22586 | 2022-08-19 |  | 26803 | 2022-04-22 | SwSta | 2024-12-31 | Buskirk |  |  | 138 |  |  | Construct a new 138 kV station with three 138 kV breakers in a ring bus configuration, expandable for a fourth line exit. The new station would be located near the existing Titus Lake bulk power substation. |  | MI |  |  | Proposed | 5100000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22586 | 2022-08-19 |  | 26804 | 2022-04-22 | TAP | 2024-12-31 | Buck Creek | Hazelwood | 1 | 138 |  |  | Cut the Buck Creek–Hazelwood (formerly Beals Road–Hazelwood) 138 kV line into the new 138 kV station. The cut-in would be between structures #008Q158 and #008Q159ABSW, near Titus Lake bulk power substation. |  | MI |  |  | Proposed | 2700000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 22627 | 2022-08-11 | METC_21_086 | 26807 | 2022-01-31 | TAP | 2024-06-01 | Day Tap |  |  | 138 |  |  | Tap the Deja Jct. – Derby Jct. section of Eureka – Vestaburg 138kV line, approximately 2.5 miles West of Deja Tap. Transmission tap will be ~ 4 miles long. Install tap pole at the tap location, install two new 138 kV, 1-way, full-load-break 2000 A. |  | MI |  |  | Proposed | 1132000 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP22 | C | East | METC | 23246 | 2022-08-10 | METC_22_032 | 26999 | 2022-08-24 | TAP | 2023-12-31 | Saginaw River | Twining | 1 | 138 |  |  | Install a tap pole and two 1-way switches near structure #229 on the Saginaw River-Twining 138 kV line to connect Consumer Energy’s new Riverbend substation. The new Riverbend substation will serve 4.25 MW load, 1.35 MW of it is being transferred from the existing Bessinger substation (46kV). |  | MI |  |  | M2a_Pre-Project Approval | 1160000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP22 | B | West | MP | 17868 | 2021-09-03 | Duluth Loop 115 kV Project | 25389 | 2021-09-15 | SUB | 2026-12-31 | Hilltop |  |  | 115 |  |  | Hilltop 115 kV line entrance addition, 115 kV circuit breaker and panel replacements |  | MN |  |  | Proposed | 1300000 | Engineering Preliminary |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | B | West | MP | 17868 | 2021-09-03 | Duluth Loop 115 kV Project | 26611 | 2021-09-15 | LNrb | 2026-12-31 | Swan Lake Road | Ridgeview |  | 115 |  | 182 SUM/214 WTR | Rebuild and reconductor existing Swan Lake Road - Ridgeview 115 kV |  | MN | 2.9 |  | Proposed | 1900000 | Engineering Preliminary |  | 2021 |  | 200 SUM/235 WTR | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | B | West | MP | 17868 | 2021-09-03 | Duluth Loop 115 kV Project | 25396 | 2020-09-14 | LINE | 2026-12-31 | Arrowhead | Haines Road & Colbyville |  | 115 |  |  | Uncrossing of existing Arrowhead - Haines Road 115 kV & Arrowhead - Colbyville 115 kV & replacement of associated line panels |  | MN |  |  | Withdrawn_Error | 0 | Planning Preliminary |  | 2020 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | B | West | MP | 17868 | 2021-09-03 | Duluth Loop 115 kV Project | 25395 | 2021-09-15 | SUB | 2026-12-31 | Ridgeview |  |  | 115 |  |  | Expand Ridgeview to a 5 position ring bus, replace a 115/14 kV transformer |  | MN |  |  | Proposed | 9900000 | Engineering Preliminary |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | B | West | MP | 17868 | 2021-09-03 | Duluth Loop 115 kV Project | 25394 | 2020-09-14 | LNup | 2026-12-31 | Haines Road | Swan Lake |  | 115 |  | 182 SUM/214 WTR | Upgrade existing 636 ACSR between Haines Road and Swan Lake from 75C to 100C operating temperature |  | MN |  | 9.08 | Withdrawn_Error | 0 | Planning Preliminary |  | 2020 |  | 200 SUM/235 WTR | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | B | West | MP | 17868 | 2021-09-03 | Duluth Loop 115 kV Project | 25393 | 2021-09-15 | LN | 2026-12-31 | Haines Road | Ridgeview |  | 115 |  | 182 SUM/214 WTR | New 115 kV transmission line alongside existing transmission corridor |  | MN |  | 4.2 | Proposed | 4300000 | Engineering Preliminary |  | 2021 |  | 200 SUM/235 WTR | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | B | West | MP | 17868 | 2021-09-03 | Duluth Loop 115 kV Project | 25392 | 2021-09-15 | LNrb | 2026-12-31 | Arrowhead | Swan Lake |  | 115 |  | 182 SUM/214 WTR | Uncross existing Arrowhead - Haines Road 115 kV & Arrowhead - Colbyville 115 kV. Merge reconfigured Arrowhead - Haines Road 115 kV & Haines Road - Swan Lake 115 kV Lines to create Arrowhead - Swan Lake 115 kV Line. Reconductor existing 115 kV line between Haines Road and Swan Lake. Rebuild significant portion of existing 115 kV line due to corridor constraints. |  | MN | 7.5 |  | Proposed | 10100000 | Engineering Preliminary |  | 2021 |  | 200 SUM/235 WTR | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | B | West | MP | 17868 | 2021-09-03 | Duluth Loop 115 kV Project | 25391 | 2021-09-15 | SUB | 2026-12-31 | Haines Road |  |  | 115 |  |  | Haines Road breaker addition and panel replacements |  | MN |  |  | Proposed | 400000 | Engineering Preliminary |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | B | West | MP | 17868 | 2021-09-03 | Duluth Loop 115 kV Project | 25390 | 2021-09-15 | LN | 2026-12-31 | Hilltop | Haines Road |  | 115 |  | 182 SUM/214 WTR | New 115 kV transmission line alongside existing transmission corridor, portion double circuit with existing line |  | MN | 3.3 | 6.8 | Proposed | 19000000 | Engineering Preliminary |  | 2021 |  | 200 SUM/235 WTR | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | B | West | MP | 18058 | 2021-09-03 |  | 24925 | 2021-10-04 | HVDC | 2023-12-31 | Arrowhead | Center (Block 1) |  | 250 |  |  | HVDC transmission line targeted structure replacements, Year 1 |  | ND |  |  | Proposed | 3000000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | B | West | MP | 18058 | 2021-09-03 |  | 26298 | 2021-10-04 | HVDC | 2027-12-31 | Arrowhead | Ground Electrode |  | 250 |  |  | Replace existing ground electrode from Arrowhead converter station |  | MN |  |  | Proposed | 2000000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | B | West | MP | 18058 | 2021-09-03 |  | 26297 | 2021-10-04 | HVDC | 2026-12-31 | Arrowhead | Center (Block 4) |  | 250 |  |  | HVDC transmission line targeted structure replacements, Year 1 |  | MN |  |  | Proposed | 3000000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | B | West | MP | 18058 | 2021-09-03 |  | 26296 | 2021-10-04 | HVDC | 2025-12-31 | Arrowhead | Center (Block 3) |  | 250 |  |  | HVDC transmission line targeted structure replacements, Year 3 |  | MN |  |  | Proposed | 3000000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | B | West | MP | 18058 | 2021-09-03 |  | 24926 | 2021-10-04 | HVDC | 2024-12-31 | Arrowhead | Center (Block 2) |  | 250 |  |  | HVDC transmission line targeted structure replacements, Year 2 |  | ND |  |  | Proposed | 3000000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 20074 | 2022-04-05 | Two Islands Switching Station | 25773 | 2022-04-05 | SwSta | 2024-12-31 | Two Islands Switching Station |  |  | 115 |  |  | Construct a new 115 kV switching station |  | MN |  |  | Proposed | 12600000 | Engineering Preliminary |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 20074 | 2022-04-05 | Two Islands Switching Station | 26243 | 2022-04-05 | LN | 2024-12-31 | Two Islands | Line Entrances |  | 115 |  |  | Interconnections to existing 1, 2, and 128 Line. New exits to 177 Line (Tac Harbor), 178 & 179 Line (GRE) |  | MN |  | 1 | Proposed | 1500000 | Engineering Preliminary |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 20077 | 2022-01-19 | Hilltop 230 kV Reliability Project | 25783 | 2021-09-15 | LINE | 2024-12-31 | Arrowhead 230 kV | Hilltop 230 kV |  | 230 |  | 470/551 | Sectionalize existing Iron Range-Arrowhead-Hilltop 230 kV Line by extending the Hilltop Tap 0.7 Miles to a new line entrance at Arrowhead 230 kV. Upgrade Hilltop 230 kV Tap from 55C to 100C. Replace existing polymer insulators and OPGW. |  | MN | 7 | 0.7 | Proposed | 7000000 | Engineering Preliminary |  | 2021 |  | 518/606 | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 20077 | 2022-01-19 | Hilltop 230 kV Reliability Project | 25789 | 2021-09-15 | TX | 2024-12-31 | Hilltop 230 kV | Hilltop 115 kV |  | 230 | 115 | 373 | Replace existing 187 MVA 230/115 kV transformer at Hilltop with a 373 MVA base transformer. Add 230 kV circuit breaker to high side of Hilltop transformer and replace low side transformer breaker. Replace low side transformer switch and some jumpers due to increased transformation capacity |  | MN |  |  | Proposed | 4800000 | Engineering Preliminary |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 20077 | 2022-01-19 | Hilltop 230 kV Reliability Project | 25788 | 2020-09-14 | TEQ | 2024-12-31 | Hilltop 230 kV |  |  | 115 |  |  | Replace low side transformer switch and some jumpers due to increased transformation capacity |  | MN |  |  | Withdrawn_Error | 0 | Planning Preliminary |  | 2020 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 20077 | 2022-01-19 | Hilltop 230 kV Reliability Project | 25787 | 2020-09-14 | CB | 2024-12-31 | Hilltop |  |  | 230 | 115 |  | Add 230 kV circuit breaker to high side of Hilltop transformer and replace low side transformer breaker. |  | MN |  |  | Withdrawn_Error | 0 | Planning Preliminary |  | 2020 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 20077 | 2022-01-19 | Hilltop 230 kV Reliability Project | 25786 | 2021-09-15 | CB | 2024-12-31 | Arrowhead 230 kV |  |  | 230 |  |  | New 230 kV line entrance at Arrowhead 230 kV substation for extending Hilltop 230 kV Tap to Arrowhead |  | MN |  |  | Proposed | 1300000 | Engineering Preliminary |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 20077 | 2022-01-19 | Hilltop 230 kV Reliability Project | 25785 | 2020-09-14 | LNup | 2024-12-31 | Hilltop 230 kV | 98L Tap |  | 230 |  | 470/551 | Upgrade Hilltop 230 kV Tap from 55C to 100C. |  | MN | 7 |  | Withdrawn_Error | 0 | Planning Preliminary |  | 2020 |  | 518/606 | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 21605 | 2022-09-11 | 25 Line Phase 2 | 26292 | 2022-09-11 | LNrb | 2025-12-31 | Hibbing | Virginia |  | 115 |  |  | Rebuild a segment of Hibbing - Virginia 25 Line near Hibbing Substation |  | MN | 2.5 |  | Proposed | 1000000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 21605 | 2022-09-11 | 25 Line Phase 2 | 26293 | 2022-09-11 | LNrb | 2025-12-31 | Hibbing | 44 Line Tap |  | 115 |  |  | Rebuild Hibbing - 44 Line tap on double circuits with 25 Line |  | MN | 2.5 |  | Proposed | 1000000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 21606 | 2022-08-24 |  | 26294 | 2022-09-11 | SUB | 2024-12-31 | West Cohasset |  |  | 115 | 23 |  | Add 115 kV breaker for distribution transformer |  | MN |  |  | Proposed | 500000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 21608 | 2022-04-04 | 105 & 106 Line Upgrade | 26299 | 2021-08-06 | LNrb | 2024-12-31 | Blackberry | Iron Range | 1 | 230 |  |  | "105 Line" - rebuild transmission line with larger conductor |  | MN |  |  | Proposed | 500000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 21608 | 2022-04-04 | 105 & 106 Line Upgrade | 26301 | 2021-09-15 | TEQ | 2024-12-31 | Blackberry |  |  | 230 |  |  | Replace limiting terminal equipment at Blackberry Substation, including 12 230 kV switches |  | MN |  |  | Proposed | 500000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 21608 | 2022-04-04 | 105 & 106 Line Upgrade | 26300 | 2021-08-06 | LNrb | 2024-12-31 | Blackberry | Iron Range | 2 | 230 |  |  | "106 Line" - rebuild with larger conductor |  | MN |  |  | Proposed | 500000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 21686 | 2022-09-15 | Mesaba Junction 137 Line Extension | 26326 | 2022-09-13 | LN | 2025-03-31 | Mesaba Junction | Babbitt |  | 115 |  | 239/239 | Extend existing Embarrass - Babbitt 115 kV Line miles to new Mesaba Junction Switching Station |  | MN |  | 8 | Planned | 8000000 | Planning Preliminary |  | 2021 |  | 263/263 | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 21686 | 2022-09-15 | Mesaba Junction 137 Line Extension | 26327 | 2022-09-13 | SwSta | 2024-12-31 | Mesaba Junction |  |  | 115 |  | 239/239 | Add breaker and transmission line entrance to Mesaba Junction Switching Station |  | MN |  |  | Planned | 1000000 | Planning Preliminary |  | 2021 |  | 263/263 | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 21763 | 2021-09-03 | North Shore Transformer | 26705 | 2021-10-06 | SUB | 2022-12-31 | North Shore |  |  | 115 |  |  | Relocate existing capacitor bank to a new bus position, including new breaker |  | MN |  |  | Planned | 250000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 21766 | 2022-09-11 | 126 Line Asset Renewal | 26356 | 2022-09-11 | LNup | 2025-03-31 | Little Fork | International Falls |  | 115 |  |  | Asset renewal upgrades to 126 Line |  | MN |  |  | Proposed | 410000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 21766 | 2022-09-11 | 126 Line Asset Renewal | 26358 | 2022-09-11 | RLY | 2023-12-31 | Little Fork | International Falls |  | 115 |  |  | Replace line panels on both ends |  | MN |  |  | Proposed | 245000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MP | 21766 | 2022-09-11 | 126 Line Asset Renewal | 26357 | 2022-09-11 | CB | 2023-12-31 | Little Fork |  |  | 115 |  |  | Replace Little Fork 126L breaker |  | MN |  |  | Proposed | 245000 | Planning |  | 2021 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP22 | C | West | MPC | 21225 | 2021-05-11 |  | 26196 | 2021-05-11 | BUS | 2021-10-01 | 657755 |  |  | 230 |  |  | New 230 kV rung with 2 CBs |  | ND |  |  | Planned | [6 empty] | Minnkota Power Cooperative | N | N | N
A in MTEP22 | C | East | MPPA | 21761 | 2022-05-26 |  | 26354 | 2022-05-26 | TX | 2022-09-30 | Riley | Blendon |  | 138 | 69 | 83.3 | 50/66.7/83.3MVA 138:69kV transformer |  | MI |  |  | Planned | 1465000 |  |  | 2022 |  |  | Michigan Public Power Agency | N | N | N
A in MTEP22 | C | West | MRES | 21938 | 2021-09-14 |  | 26561 | 2021-09-14 | SUB | 2023-04-01 | 630085 | 630064 |  | 69 |  |  | WPU Sub #2 |  | MN |  |  | Planned | 375000 | Budgetary |  |  |  |  | Missouri River Energy Services (MRET) | N | N | N
A in MTEP22 | C | West | MRES | 23346 | 2022-08-24 |  | 27025 | 2022-08-24 | SUB | 2025-12-31 | 658279 |  |  | 115 | 69 |  | This project will add a second 115/69 kV transformer to the existing City of Hutchinson MN, Hutchinson Substation. The project will also rebuild the Hutchinson 115 kV into a four position ring bus. |  | MN |  |  | Proposed | 8000000 | Planning |  |  |  |  | Missouri River Energy Services (MRET) | N | N | N
A in MTEP22 | C | Central | NIPS | 21167 | 2021-09-21 |  | 26163 | 2021-04-27 | LN | 2025-12-31 | E.Elkart (AEP) | Menges Ditch | 1 | 138 |  |  | 2 New 138kV Circuits from E.Elkhart to Menges Ditch. (3) 69kV lines |  | IN |  | 18 | Proposed | 17544253 | Planning |  | 2021 | Cost includes 69kV line additions |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21167 | 2021-09-21 |  | 26164 | 2021-04-27 | SUB | 2025-12-31 | Menges Ditch |  |  | 138 | 69 |  | New 138/69kV substation |  | IN |  |  | Proposed | 24824367 | Planning |  |  |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21168 | 2022-01-21 |  | 26165 | 2021-04-27 | LN | 2024-12-31 | Hiple | Northport | 1 | 138 |  |  | New 10.2 mile 138kV line |  | IN |  | 10.2 | Proposed | 14699093 | Planning |  | 2021 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21168 | 2022-01-21 |  | 26166 | 2021-04-27 | TEQ | 2024-12-31 | Hiple | NOrthport |  | 138 |  |  | Hiple and Northport upgrades to accommodate 138kV line |  | IN |  |  | Proposed | 12827911 | Planning |  | 2021 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21867 | 2021-09-17 |  | 26449 | 2021-09-13 | BUS | 2024-12-31 | Marktown |  |  | 138 |  |  | Replace existing substation |  | IN |  |  | Planned | 30190251 | Engineering Preliminary |  | 2021 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21870 | 2021-09-24 |  | 26456 | 2021-09-13 | LNrb | 2022-12-31 | S. Chalmers | Oakdale |  | 69 |  |  | Rebuild 3 miles of line. Includes Relay upgrade |  | IN | 3 |  | Planned | 4917926 | Engineering Preliminary |  | 2021 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21875 | 2021-09-24 |  | 26462 | 2021-09-13 | LNrb | 2023-12-31 | Lagrange | Angola |  | 69 |  |  | Partial rebuild of line |  | IN |  |  | Planned | 3014269 | Engineering Preliminary |  |  |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21876 | 2021-09-20 |  | 26463 | 2021-09-13 | SUB | 2022-12-31 | VARIOUS |  |  | 345 | 69 |  | 69kv and up Substation replacements/upgrades based on age and condition, including but not limited to switches, breakers, transformers, and protection and communication equipment. |  | IN |  |  | Planned | 26223459 | Engineering Preliminary |  | 2021 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21878 | 2021-09-17 |  | 26464 | 2021-09-13 | LINE | 2022-12-31 | Various |  |  | 138 | 34 |  | 69kv and up line rebuilds/upgrades based on age and condition, including structures, conductor, switches and communication upgrades(fiber) |  | IN |  |  | Planned | 36772890 | Engineering Preliminary |  | 2021 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21879 | 2021-09-17 |  | 26466 | 2021-09-13 | SUB | 2023-12-31 | Various |  |  | 345 | 34 |  | 69kv and up Substation replacements/upgrades based on age and condition, including but not limited to switches, breakers, transformers, and protection and communication equipment. |  | IN |  |  | Planned | 42330170 | Engineering Preliminary |  | 2021 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21880 | 2021-09-17 |  | 26467 | 2021-09-13 | LINE | 2023-12-31 | Various |  |  | 345 | 34 |  | 69kv and up line rebuilds/upgrades based on age and condition, including structures, conductor, switches and communication upgrades(fiber) |  | IN |  |  | Planned | 19261989 | Engineering Preliminary |  | 2021 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21881 | 2021-09-17 |  | 26468 | 2021-09-13 | SUB | 2024-12-31 | Various |  |  | 345 | 34 |  | 69kv and up Substation replacements/upgrades based on age and condition, including but not limited to switches, breakers, transformers, and protection and communication equipment. |  | IN |  |  | Planned | 32711473 | Engineering Preliminary |  | 2021 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21882 | 2021-09-17 |  | 26469 | 2021-09-13 | LINE | 2024-12-31 | Various |  |  | 345 | 34 |  | 69kv and up line rebuilds/upgrades based on age and condition, including structures, conductor, switches and communication upgrades(fiber) |  | IN |  |  | Planned | 31312504 | Engineering Preliminary |  | 2021 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21883 | 2021-09-17 |  | 26470 | 2021-09-13 | SUB | 2025-12-31 | various |  |  | 345 | 34 |  | 69kv and up Substation replacements/upgrades based on age and condition, including but not limited to switches, breakers, transformers, and protection and communication equipment. |  | IN |  |  | Planned | 26977092 | Engineering Preliminary |  | 2021 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21884 | 2021-09-17 |  | 26471 | 2021-09-13 | LINE | 2025-12-31 | VARIOUS |  |  | 345 | 34 |  | 69kv and up line rebuilds/upgrades based on age and condition, including structures, conductor, switches and communication upgrades(fiber) |  | IN |  |  | Planned | 30216017 | Engineering Preliminary |  | 2021 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21885 | 2021-09-17 |  | 26472 | 2021-09-13 | SUB | 2026-12-31 | Various |  |  | 345 | 34 |  | 69kv and up Substation replacements/upgrades based on age and condition, including but not limited to switches, breakers, transformers, and protection and communication equipment. |  | IN |  |  | Planned | 54852316 | Engineering Preliminary |  | 2021 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 21886 | 2021-09-17 |  | 26473 | 2021-09-13 | LINE | 2026-12-31 | Various |  |  | 345 | 34 |  | 69kv and up line rebuilds/upgrades based on age and condition, including structures, conductor, switches and communication upgrades(fiber) |  | IN |  |  | Planned | 68286845 | Engineering Preliminary |  | 2021 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | B | Central | NIPS | 21950 | 2021-09-20 |  | 26570 | 2022-05-19 | SUB | 2023-12-31 | Timmons |  |  | 69 | 12 | 14MVA | Build the new Timmons 69/12kV 14.4MVA sub. |  | IN |  |  | Planned | 5301167 | Engineering |  |  |  | 14MVA | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP22 | C | Central | NIPS | 21954 | 2022-05-18 |  | 26573 | 2022-05-19 | SUB | 2022-11-29 | Rosebud |  |  | 69 | 12 |  | Building new Rosebud 69/12 substation to feed load normally fed from existing Parr substation. Build new 0.25 mile 69kV line to feed new sub. |  | IN |  | 0.25 | Planned | 4947000 | Engineering |  |  |  |  | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP22 | C | Central | NIPS | 21955 | 2022-05-18 |  | 26574 | 2022-05-19 | SUB | 2024-10-17 | Fair Oaks |  |  | 69 | 12 | 22MVA | Add second 138/69/12kV 22.4MVA transformer to Fair Oaks substation to handle new load in area |  | IN |  |  | Proposed | 4176754 | Engineering |  |  |  | 22MVA | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP22 | C | Central | NIPS | 21956 | 2021-09-17 |  | 26575 | 2022-05-19 | SUB | 2023-12-31 | Yellow River |  |  | 69 | 12 | 14MVA | Build a new 69kv/12.5kv 14.4MVA substation near the Knox Industrial Park. Install 13MVAR cap bank. Build 0.5 miles of 69kV to new sub. |  | IN |  | 0.5 | Planned | 5255244 | Engineering |  |  |  | 14MVA | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP22 | C | Central | NIPS | 21956 | 2021-09-17 |  | 26576 | 2022-05-19 | SUB | 2022-06-01 | Yellow River |  |  | 69 | 12 | 14MVA | Build a new 69kv/12.5kv 14.4MVA substation near the Knox Industrial Park. Install 13MVAR cap bank. Build 0.5 miles of 69kV to new sub. |  | IN |  | 0.5 | Withdrawn_AltOrScope | 2000000 |  |  |  |  | 14MVA | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP22 | C | Central | NIPS | 21957 | 2021-09-24 |  | 26577 | 2022-05-19 | SUB | 2023-12-31 | Oregon |  |  | 69 | 12 | 14MVA | Replace existing 7 MVA substation transformer at the KVREMC owned Oregon Substation to a 14 MVA. Add a backup transmission line for Oregon Substation and tap the nearby 69105 (0.25mi) with new ATO scheme. |  | IN |  | 0.25 | Planned | 1338591 | Engineering |  |  |  | 14MVA | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP22 | C | Central | NIPS | 21959 | 2021-09-24 |  | 26579 | 2021-09-14 | SUB | 2022-09-01 | Moody |  |  | 69 | 12 |  | Purchase the Moody Substation from NIPSCO and replace the transformer (14.4MVA from Fair Oaks), regulators, fuses, and jumpers. Add oil containment around a new foundation. |  | IN |  |  | Proposed | 1500000 | [5 empty] | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP22 | C | Central | NIPS | 21961 | 2021-09-17 |  | 26581 | 2022-05-19 | SUB | 2022-12-30 | Marco |  |  | 69 | 12 | 14MVA | Build new Marco substation near the existing NIPS Argos substation. 69/12kV 14.4MVA Xfmr, design for 4 ckts used initially. Will replace Marshall MP. Add external control Hut for Fiber connections (Rochester Fiber). Build short tap from Nipsco 6968 to new sub |  | IN |  |  | Planned | 4947000 | Engineering |  |  |  | 14MVA | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP22 | C | Central | NIPS | 21962 | 2021-09-17 |  | 26582 | 2022-05-19 | SUB | 2022-09-30 | Berthaville |  |  | 69 | 12 | 14MVA | New Berthaville substation needed south of Goodland for new dairy farm and added load near Newton office. 14.4 MVA transformer, 4 distr exits, 69kV with manual switch to Nipsco 6964 line. |  | IN |  |  | Under Construction | 4200000 | Engineering |  |  |  | 14MVA | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP22 | C | Central | NIPS | 21964 | 2021-09-17 |  | 26583 | 2021-09-14 | SUB | 2023-11-30 | Colfax |  |  | 69 | 12 | 22MVA | Add 2nd transformer to Colfax substation. 138/69/12kV 22.4MVA transformer. Substation work to make space for new transformer. |  | IN |  |  | Proposed | 5000000 |  |  |  |  | 22MVA | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP22 | C | Central | NIPS | 21965 | 2021-09-17 |  | 26584 | 2022-05-19 | SUBmisc | 2023-07-31 | Otter |  |  | 69 | 12 |  | Otter substation in Steuben has an inoperable switch and transrupter that need replaced. Replacing switch with a load break manual switch and replacing the transrupter with a S&C Circuit Switcher. |  | IN |  |  | Planned | 872640 | Engineering |  |  |  |  | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP22 | C | Central | NIPS | 22630 | 2022-03-01 |  | 26820 | 2022-08-24 | SUB | 2023-10-20 | New Sub |  |  | 345 |  |  | New greenfield substation |  | IN |  |  | Planned | 19740094 | GIA |  | 2022 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 22630 | 2022-03-01 |  | 26821 | 2022-08-24 | INT | 2023-10-20 | Reynolds | Burr Oak |  | 345 |  |  | Connection of Reynolds to Burr Oak line to new Greenfield sub |  | IN |  |  | Planned | 3892549 | GIA |  | 2022 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | Central | NIPS | 22649 | 2022-03-01 |  | 26822 | 2022-08-24 | BUS | 2023-04-30 | Reynolds |  |  | 345 |  |  | New 345kV breaker in Bay 6 at Reynolds substation to accommodate new lead line into northern position, plus all associated equipment |  | IN |  |  | Planned | 2204486 | GIA |  | 2020 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP22 | C | West | OTP | 20385 | 2021-10-28 |  | 26009 | 2021-10-14 | LNrb | 2024-11-01 | Buffalo 115kV | Alice 115kV |  | 115 |  |  | Rebuild 7 miles of 115 kV line due to poor performance. |  | ND | 7 |  | M4_Pre-Construction | 2000000 | Construction |  |  | 10-14-2021 Project Manager, Tony Nelson reported this project has started Phase 1 this October 2021. OTP asking MISO to move from Appendix B to A. Planning Status changed from Proposed to M4_Pre-Construction and Estimate Type changed from Planning Preliminary to Construction. |  | Otter Tail Power Company | N | N | N
A in MTEP22 | B | West | OTP | 20565 | 2022-09-02 |  | 26963 | 2022-09-02 | TX | 2024-10-09 | Forman 230 kV (620363) | Forman 115 kV (620263) | 1 | 230 | 115 | 224 | Increase the capacity of the existing Forman 230/115 kV transformer. |  | ND |  |  | Proposed | 6062000 | Facility Study |  | 2022 | Updated cost and schedule 9-1-22 per Facility Study | 280 | Otter Tail Power Company | N | N | N
A in MTEP22 | B | West | OTP | 20565 | 2022-09-02 |  | 26964 | 2022-09-02 | TEQ | 2024-10-09 | Forman (620263) | WAPA Forman (652438) | 1 | 115 |  | 239.0 | Increase capacity of OTP owned equipment on the Forman - WAPA Forman 115 kV line. |  | ND |  |  | Proposed | 100000 | Facility Study |  |  | Updated expected in-service date based on Facility Study | 262.9 | Otter Tail Power Company | N | N | N
A in MTEP22 | C | West | OTP | 21427 | 2022-06-02 | OTP | 26260 | 2022-06-02 | SUB | 2022-08-31 | Max 41.6 kV |  |  | 41.6 |  |  | Add one 41.6 kV circuit breaker at the Max Substation. |  | ND |  |  | Planned | 350000 | Planning |  |  |  |  | Otter Tail Power Company | N | N | N
A in MTEP22 | C | West | OTP | 21427 | 2022-06-02 | OTP | 26262 | 2022-06-02 | LNrb | 2022-08-31 | Parshall 41.6 kV | Ryder 41.6 kV |  | 41.6 |  |  | Line rebuild between Parshall/Ryder 41.6 kV. Line mileage 38.7 miles. |  | ND | 38.7 |  | Withdrawn | 725000 | Planning |  |  |  |  | Otter Tail Power Company | N | N | N
A in MTEP22 | C | West | OTP | 21427 | 2022-06-02 | OTP | 26261 | 2022-06-02 | CAP | 2022-08-31 | Parshall 41.6 kV |  |  | 41.6 |  |  | Add 3 x 1 MVAR 41.6 kV Capacitor Banks at Parshall Substation |  | ND |  |  | Withdrawn | 1500000 | Planning |  |  |  |  | Otter Tail Power Company | N | N | N
A in MTEP22 | C | West | OTP | 22606 | 2022-09-13 |  | 26806 | 2022-09-13 | SUB | 2023-11-01 | Jamestown 115 kV (620269) | Jamestown 41.6 kV |  | 115 | 41.6 |  | Expansion of the Jamestown 115 kV bus and the Jamestown 41.6 kV bus. Addition of a, 115 kV circuit breaker, 115/41.6 kV transformer 24 MVA, 41.6 kV circuit breaker, relays, GFN relocation. These additions will allow capacity to serve the new customer. |  | ND |  |  | Planned | 2268000 | Planning |  | 2022 | 9-13-22: Jamestown 345/115/41.6 kV transformer failed. OTP is reevaluating the addition of the proposed 115/41.6 kV transformer. |  | Otter Tail Power Company | N | N | N
A in MTEP22 | C | West | OTP | 23148 | 2022-09-02 |  | 26972 | 2022-09-06 | LNup | 2023-08-30 | Canby 115 kV (620211) | Granite Falls 115 kV (652551) | 1 | 115 |  | 120.7 MVA | Increase the capacity of the Canby - Granite Falls 115 kV Facility to achieve a minimum of a 150 MVA continuous rating. |  | MN |  |  | Proposed | 1646000 | Facility Study |  | 2022 |  | 132.7 MVA | Otter Tail Power Company | N | N | N
A in MTEP22 | C | West | OTP | 23148 | 2022-09-02 |  | 26975 | 2022-09-06 | LNup |  | Fergus Falls 230 kV (658109) | Wahpeton 230 kV (620329) | 1 | 230 |  |  | Increase the capacity of the Fergus Falls - Wahpeton 230 kV Facility to achieve a minimum of a 425 MVA continuous rating. |  | MN,ND |  |  | Withdrawn | [6 empty] | Otter Tail Power Company | N | N | N
A in MTEP22 | C | West | OTP | 23148 | 2022-09-02 |  | 26974 | 2022-09-06 | LNup | 2023-07-20 | Hoot Lake 115 kV (620223) | Fergus Falls SE 115 kV (620170) | 1 | 115 |  | 120.7 MVA | Increase the capacity of the Hoot Lake - Fergus Falls SE 115 kV Facility to achieve a minimum of a 150 MVA continuous rating. |  | MN |  |  | Proposed | 39000 | Facility Study |  | 2022 |  | 132.7 MVA | Otter Tail Power Company | N | N | N
A in MTEP22 | C | West | OTP | 23148 | 2022-09-02 |  | 26973 | 2022-09-06 | LNup | 2023-06-30 | Hoot Lake 115 kV (620223) | Fergus Falls 115 kV (658110) | 1 | 115 |  | 120.7 MVA | Increase the capacity of the Hoot Lake - Fergus Falls 115 kV Facility to achieve a minimum of a 150 MVA continuous rating. |  | MN |  |  | Proposed | 20000 | Facility Study |  | 2022 |  | 132.7 MVA | Otter Tail Power Company | N | N | N
A in MTEP22 | B | Central | PPI | 19945 | 2021-09-17 |  | 25628 | 2021-09-24 | LN | 2025-12-31 | Topeka | Bishop | 1 | 69 |  | 69 | New ~8-mile Topeka to Bishop 69 kV line in Menard Electric Cooperative |  | IL |  | 8 | Planned | 5120000 | Budgetary |  | 2021 |  | 69 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 19950 | 2021-10-19 |  | 25633 | 2021-09-24 | LN | 2023-12-31 | St David | Wee-Ma-Tuk Tap | 1 | 69 |  | 50 | New 4.5 -mile St David - Wee-Ma-Tuk Tap 69 kV line in SREC |  | IL |  | 4.5 | Planned | 2737000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 19950 | 2021-10-19 |  | 26288 | 2021-09-24 | LN | 2023-12-31 | Canton | Wee-Ma-Tuk Tap | 1 | 69 |  | 50 | New 1.8-mile Canton - Wee-Ma-Tuk Tap 69 kV line in SREC |  | IL |  | 1.8 | Planned | 1095000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 19950 | 2021-10-19 |  | 25932 | 2021-09-24 | LN | 2023-12-31 | Wee-Ma-Tuk | Wee-Ma-Tuk Tap | 1 | 69 |  | 50 | New 2.9-mile Wee-Ma-Tuk - Wee-Ma-Tuk Tap 69 kV line in SREC |  | IL |  | 2.9 | Planned | 1764000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 19952 | 2021-09-17 |  | 25635 | 2021-09-24 | LNrb | 2024-12-31 | Walkerville | Eldred | 1 | 69 |  | 50 | Rebuild 7.3-mile Walkerville to Eldred 69 kV line in IEC |  | IL | 7.3 |  | Planned | 3942000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21746 | 2021-09-17 |  | 26338 | 2022-04-22 | LN | 2024-12-31 | Bluff Hall | E. Hannibal | 1 | 69 | 69 | 50 | New ~9-mile 69 kV line |  | IL |  |  | Planned | 4184000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21747 | 2021-09-17 |  | 26339 | 2021-12-28 | SwSta | 2022-12-31 | Barry |  |  | 69 | 69 | 50 | New 69 kV Barry transmission substation in IEC |  | IL |  |  | Under Construction | 1600000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21748 | 2021-09-28 |  | 26340 | 2022-07-15 | LNrb | 2022-12-31 | Barry | E. Hannibal Tap (S) - Pittsfield | 1 | 69 |  | 50 | Rebuild ~4.4-mile Barry to E. Hannibal Tap (S) double circuit 69 kV line in Illinois Electric Cooperative. |  | IL | 4 |  | Under Construction | 1800000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21748 | 2021-09-28 |  | 26699 | 2022-07-15 | LN | 2022-12-31 | Barry | E Hannibal | 1 | 69 |  | 69 | New ~0.3-mile Barry to E Hannibal 69kV line to existing E Hannibal Tap to E Hannibal line in Illinois Electric Cooperative. |  | IL |  | 0.3 | Under Construction | 162000 | Budgetary |  | 2021 |  | 69 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21748 | 2021-09-28 |  | 26341 | 2022-07-15 | LN | 2022-12-31 | Barry | E. Hannibal Tap (N) - Liberty | 1 | 69 |  | 50 | Second line of ~4.4-mile Barry to E. Hannibal Tap (N) double circuit 69 kV line in Illinois Electric Cooperative. |  | IL |  | 4 | Under Construction | 1800000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21749 | 2021-09-17 |  | 26342 | 2022-04-22 | SwSta | 2024-12-31 | Trailblazer |  |  | 69 | 69 | 50 | New Trailblazer 69 kV switching station. Terminals to St, Anthony, Liberty, and Barry. |  | IL |  |  | Planned | 2935000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21750 | 2021-09-27 |  | 26343 | 2021-09-03 | SwSta | 2025-12-31 | Rock Creek |  |  | 69 | 69 | 50 | New Rock Creek 69 kV breaker station with terminals looking towards Elvaston, Golden, Payson and Ursa. |  | IL |  |  | Planned | 2935000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21751 | 2021-09-17 |  | 26344 | 2021-09-24 | SUB | 2025-12-31 | Panther |  | 1 | 138 | 69 | 84 | New Panther 138/69 kV substation connecting to Ameren's Pana 138 kV substation. |  | IL |  |  | Planned | 6425000 | Budgetary |  | 2021 |  | 84 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21751 | 2021-09-17 |  | 26683 | 2021-09-24 | LN | 2025-12-31 | Ameren Pana N | PPI Panther | 1 | 138 |  | 229 | New ~2.3-mile line Ameren Pana to PPI Panther 138 kV Line in Shelby Electric Cooperative. |  | IL |  | 2.3 | Planned | 2000000 | Budgetary |  | 2021 |  | 229 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21752 | 2021-09-17 |  | 26345 | 2021-09-24 | LN | 2025-12-31 | Panther | Existing Pana Tap | 1 | 69 | 69 | 50 | New ~1.4-mile Panther to Existing Pana Tap 69 kV line from in Shelby Electric Cooperative. Existing Pana Tap to Ameren will be removed |  | IL |  | 1.4 | Planned | 900000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21752 | 2021-09-17 |  | 26684 | 2021-09-24 | LNrb | 2025-12-31 | Existing Pana Tap | New Pana Tap | 1 | 69 | 69 | 50 | Rebuild and Upgrade ~2.7-mile Existing Pana Tap to New Pana Tap 34 kV line to 69 kV Line in Shelby Electric Cooperative. Existing Pana Tap to Ameren will be disconnected. |  | IL | 2.7 |  | Planned | 1350000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21753 | 2021-09-17 |  | 26346 | 2021-09-03 | LN | 2025-12-31 | Pana Tap | Lakewood | 1 | 69 | 69 | 50 | New ~12-mile 69 kV line from Pana Tap to Lakewood substation in Shelby Electric Cooperative |  | IL |  | 12 | Planned | 7680000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21754 | 2021-09-24 |  | 26347 | 2021-09-24 | LN | 2025-12-31 | ISHI | New Herrick Tap | 1 | 69 |  | 50 | New ~6.6-mile ISHI to Herrick Tap 69 kV line in Shelby Electric Cooperative |  | IL |  | 6.6 | Planned | 4224000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21754 | 2021-09-24 |  | 26685 | 2021-09-24 | LNrb | 2025-12-31 | Lakewood | New Herrick Tap | 1 | 69 |  | 50 | Rebuild ~2.5-mile Lakewood to New Herrick Tap 69 kV Line in Shelby Electric Cooperative. |  | IL | 2.5 |  | Planned | 1250000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21755 | 2021-09-28 |  | 26348 | 2021-09-28 | LNrb | 2025-12-31 | Hadley Breaker | Barry | 1 | 69 | 69 | 50 | Rebuild 0.54-mile Hadley to Barry 69 kV line in Illinois Electric Cooperative. |  | IL | 0.54 |  | Planned | 270000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21756 | 2021-09-17 |  | 26349 | 2021-09-08 | LNrb | 2025-12-31 | Hadley Breaker | Hadley Distribution | 1 | 69 | 69 | 50 | Rebuild 1.61-mile Hadley Breaker to Hadley Distribution 69 kV line in Illinois Electric Cooperative |  | IL | 1.61 |  | Planned | 805000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | C | Central | PPI | 21757 | 2021-09-28 |  | 26350 | 2021-09-08 | LNrb | 2023-12-31 | E. Hannibal Tap | Liberty | 1 | 69 | 69 | 84 | Rebuild 6.35-mile E. Hannibal Tap to Liberty 69 kV line between Illinois Electric Cooperative and Adams Electric Cooperative. |  | IL | 6.35 |  | Planned | 3175000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21758 | 2021-09-17 |  | 26351 | 2021-09-24 | LNrb | 2025-12-31 | Pearl | Carrollton | 1 | 69 | 69 | 50 | Rebuild 0.7-mile Kampsville to Kampsville River Crossing 69 kV line in Illinois Electric Cooperative. |  | IL | 0.7 |  | Planned | 350000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21760 | 2021-09-17 |  | 26353 | 2021-09-03 | SwSta | 2024-12-31 | Rushville |  |  | 69 | 69 | 50 | New 69 kV Rushville Breaker Station in Adams Electric Cooperative |  | IL |  |  | Planned | 2935000 | Budgetary |  | 2021 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21788 | 2021-09-17 |  | 26364 | 2021-09-24 | LNrb | 2024-12-31 | Barclay | Andrew | 1 | 69 | 69 | 69 | Rebuild ~7.5-mile Barclay to Andrew 69 kV line in Menard Electric Cooperative |  | IL | 7.5 |  | Planned | 3755000 | Budgetary |  | 2021 |  | 69 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21789 | 2021-09-25 |  | 26365 | 2021-09-08 | LNrb | 2025-12-31 | Lanesville | Barclay | 1 | 69 | 69 | 69 | Rebuild ~11.5-mile Lanesville to Barclay 69 kV line in Menard Electric Cooperativ |  | IL | 11.5 |  | Planned | 5745000 | Budgetary |  | 2021 |  | 69 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21791 | 2021-09-17 |  | 26367 | 2021-09-07 | LNrb | 2024-12-31 | East Lanesville | Lanesville | 1 | 69 | 69 | 69 | Rebuild ~0.9-mile East Lanesville to Lanesville 69 kV line in Menard Electric Cooperative |  | IL | 0.9 |  | Planned | 450000 | Budgetary |  | 2021 |  | 84 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21792 | 2021-09-17 |  | 26369 | 2021-09-08 | LNrb | 2026-12-31 | Fancy Creek | Andrew | 1 | 69 | 69 | 69 | Rebuild ~4.5-mile Fancy Creek to Andrew 69 kV line in Menard Electric Cooperative. |  | IL | 4.5 |  | Planned | 2250000 | Budgetary |  | 2021 |  | 69 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21793 | 2021-09-17 |  | 26370 | 2021-09-24 | LN | 2025-12-31 | Forest City | Bishop | 1 | 69 |  | 69 | New ~2-mile Forest City to Bishop 69 kV line in Menard Electric Cooperative. |  | IL |  | 2 | Planned | 1415000 | Budgetary |  | 2021 |  | 69 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21794 | 2022-02-16 |  | 26371 | 2021-09-07 | SUB | 2025-12-31 | Forest City |  |  | 138 | 69 | 84 | New 138/69 kV substation near Forest City, IL in Menard Electric Cooperative. |  | IL |  |  | Planned | 7425000 | Budgetary |  | 2021 |  | 84 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21794 | 2022-02-16 |  | 26709 | 2021-10-21 | CAP | 2025-12-31 | forest City |  |  | 69 |  | 4.8 | 4.8 MVAR |  | IL |  |  | Planned | 300000 | Budgetary |  | 2021 | Added to help address P6-1-1 contingency | 4.8 | Prairie Power, Inc. | N | N | N
A in MTEP22 | B | Central | PPI | 21795 | 2021-09-24 |  | 26372 | 2021-09-24 | SwSta | 2025-12-31 | Middletown |  |  | 69 | 69 | 69 | New 69 kV breaker station near Middletown, IL in Menard Electric Cooperative |  | IL |  |  | Planned | 2107000 | Budgetary |  | 2021 |  | 69 | Prairie Power, Inc. | N | N | N
A in MTEP22 | C | Central | SIGE | 22002 | 2021-09-17 | 22SIGE01 | 26651 | 2021-09-15 | INT | 2022-12-15 | Francsico |  |  | 138 |  |  | New terminal for interconnecting generation project J1074 |  | IN |  |  | Planned | 1805104 | Engineering Preliminary |  | 2021 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP22 | C | Central | SIGE | 22004 | 2021-09-17 | 22SIGE02 | 26652 | 2021-09-15 | TX | 2023-06-01 | Southwind |  | T2 | 69 | 12 | 20 | Upgrade 69/12 kV distribution transformer T2 |  | IN |  |  | Planned | 2000000 | Budgetary |  | 2021 |  | 20 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP22 | C | Central | SIGE | 22005 | 2021-09-17 | 22SIGE03 | 26653 | 2021-09-15 | CB | 2023-06-01 | Duff |  |  | 345 |  |  | Replace two 345 kV breakers at the Duff substation |  | IN |  |  | Planned | 1500000 | Budgetary |  | 2021 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP22 | C | Central | SIGE | 22006 | 2021-09-17 | 22SIGE04 | 26654 | 2021-09-15 | Dist | 2023-06-01 | Anderson Rd. |  |  | 69 | 12 |  | Build new 69/12 kV distribution substation |  | IN |  |  | Planned | 8500000 | Budgetary |  | 2021 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP22 | C | Central | SIGE | 22007 | 2021-09-17 | 22SIGE05 | 26655 | 2021-09-15 | SwSta | 2023-07-01 | Warrick North |  |  | 138 |  |  | Expand 138 kV Warrick North switching station from ring bus to breaker and a half |  | IN |  |  | Planned | 3500000 | Budgetary |  | 2021 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP22 | C | Central | SIGE | 22008 | 2021-09-17 | 22SIGE06 | 26656 | 2021-09-15 | SUB | 2023-07-01 | Kaiser |  |  | 138 | 15 |  | Build new 138 kV substation to serve new large industrial customer |  | IN |  |  | Planned | 12000000 | Budgetary |  | 2021 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP22 | C | Central | SIGE | 22009 | 2021-09-17 | 22SIGE07 | 26657 | 2021-09-15 | SUB | 2023-12-01 | Midwest Fertilizer |  |  | 138 | 12 |  | Build new 138 kV substation for new large industrial customer |  | IN |  |  | Planned | 8000000 | Budgetary |  | 2021 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP22 | C | Central | SIGE | 22010 | 2021-09-17 | 22SIGE08 | 26658 | 2021-09-15 | INT | 2023-10-01 | Scott |  |  | 138 |  |  | New 138 kV terminal for generation interconnection project J856 |  | IN |  |  | Planned | 1552504 | Engineering Preliminary |  | 2021 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP22 | C | Central | SIGE | 22011 | 2021-09-17 | 22SIGE09 | 26659 | 2021-09-15 | LN | 2023-07-01 | Warrick North | Kaiser Aluminum | Z68 | 138 |  |  | New 138 kV line from existing Warrick North 138 kV switching station to new 138 kV Kaiser substation |  | IN |  | 2 | Planned | 2300000 | Budgetary |  | 2021 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP22 | B | East | WPSC | 15652 | 2021-08-19 |  | 23663 | 2021-08-19 | LNrb | 2024-12-31 | Atlanta | Gaylord OCB | 1 | 138 |  |  | Rebuild of line section to 138kV design. |  | MI |  | 22 | Proposed | 16500000 | Planning |  | 2024 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP22 | C | East | WPSC | 21425 | 2022-04-14 |  | 26325 | 2021-08-17 | LN | 2022-12-31 | Mill Creek Tap | Mill Creek Substation |  | 138 |  |  | .9 Miles of new transmission line on new ROW |  | MI |  | 0.9 | Proposed | 1000000 | Planning |  | 2022 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP22 | B | East | WPSC | 21665 | 2022-08-16 |  | 26323 | 2022-08-16 | ROW | 2024-06-01 | Day Tap | Day substation |  | 138 |  |  | New ROW for 4 Miles of transmission |  | MI |  | 4 | Proposed | 1000000 | Planning |  | 2022 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP22 | B | East | WPSC | 21665 | 2022-08-16 |  | 26324 | 2022-08-16 | LN | 2024-06-01 | Day Tap | Day substation |  | 138 |  |  | 4 Miles new 138kV line from Day Tap to Day substation |  | MI |  |  | Proposed | 2500000 | Planning |  | 2022 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP22 | C | East | WPSC | 21785 | 2021-09-17 |  | 26361 | 2021-09-07 | RLY | 2024-12-31 | Grawn |  |  | 69 |  |  | Protection system upgrade |  | MI |  |  | Proposed | 1500000 | Planning |  | 2024 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP22 | C | East | WPSC | 21787 | 2021-09-17 |  | 26363 | 2021-09-07 | SUB | 2024-12-31 | Westwood |  |  | 138 |  |  | Reconfigure station and install transformer |  | MI |  |  | Proposed | 5500000 | Planning |  | 2024 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP22 | C | East | WPSC | 21787 | 2021-09-17 |  | 26368 | 2021-09-07 | SUB | 2025-12-31 | Alba |  |  | 138 | 69 |  | Alba Station demolition. |  | MI |  |  | Proposed | 500000 | Planning |  | 2025 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP22 | C | East | WPSC | 21787 | 2021-09-17 |  | 26366 | 2021-09-07 | LNrb | 2024-12-31 | Westwood | Plum | 1 | 138 |  |  | Rebuild existing 69kV facility to 138kV WPSC standard and add circuit on existing METC double circuit structures to Plum station. |  | MI | 9 | 3 | Proposed | 12000000 | Planning |  | 2024 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP22 | C | West | XEL | 20505 | 2022-05-18 |  | 26040 | 2021-09-10 | LNrb | 2025-04-15 | Huntley | South Bend | 1 | 161 |  |  | Rebuild 30.0 miles of the Huntley-Blue Earth-South Bend 161 kV line. |  | MN | 30 |  | Proposed | 38000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 20505 | 2022-05-18 |  | 26042 | 2020-11-13 | TX | 2025-04-15 | South Bend |  |  | 161 | 115 |  | Replace the South Bend 161-115-13.8 kV transformer |  | MN |  |  | Proposed | 2000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 20505 | 2022-05-18 |  | 26041 | 2021-09-10 | LNrb | 2025-04-15 | South Bend | Wilmarth | 1 | 115 |  |  | Reconductor 8.8 miles of the South Bend-Northport-Wilmarth 115 kV line, replacing structures if necessary |  | MN | 8.8 |  | Withdrawn_AltOrScope | 8000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21285 | 2021-09-15 |  | 26224 | 2021-09-15 | TX | 2023-06-01 | Elm Creek |  |  | 345 | 115 |  | Install second 345/115 kV transformer at Elm Creek sub |  | MN |  |  | Planned | 6000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21285 | 2021-09-15 |  | 26644 | 2021-09-15 | IND | 2023-06-01 | Elm Creek |  |  | 345 |  |  | Add 50 MVAR Reactor to existing TR9. |  | MN |  |  | Planned | 750000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21285 | 2021-09-15 |  | 26226 | 2021-09-15 | LN | 2023-06-01 | Elm Creek | Sherco | 1 | 345 |  |  | Route SHC-CNC #1 345 kV Line Into Elm Creek Sub |  | MN |  |  | Planned | 1500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21285 | 2021-09-15 |  | 26225 | 2021-09-15 | LN | 2023-06-01 | Elm Creek | Coon Creek | 1 | 345 |  |  | Route SHC-CNC #1 345 kV Line Into Elm Creek Sub |  | MN |  |  | Planned | 1500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21833 | 2021-09-10 |  | 26421 | 2021-09-10 | BUS | 2023-05-15 | Mallard |  |  | 115 |  |  | NSP substation grading and fencing, 3 new box structures, control and wiring modifications. |  | ND |  |  | Planned | 2340000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21834 | 2022-05-23 |  | 26422 | 2021-09-10 | Remove | 2022-06-01 | Boyd |  |  | 69 |  |  | Retire Boyd substation |  | WI |  |  | Planned | 300000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21834 | 2022-05-23 |  | 26424 | 2022-05-23 | CAP | 2023-06-12 | Bateman |  |  | 69 |  |  | Install two 5 MVAR capacitor banks. |  | WI |  |  | Planned | 200000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21845 | 2021-09-10 |  | 26435 | 2021-09-10 | LNup | 2024-12-15 | Riverside | Main Street |  | 115 |  |  | Approximately 4-mile of triple circuit structure(35-structures) to be either replaced, painted or a combination of replace/paint |  | MN |  |  | Planned | 20000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21846 | 2021-09-10 |  | 26437 | 2021-09-10 | TX | 2022-10-15 | Hyland Lake |  |  | 115 | 13.8 |  | Upgrade TR1 and TR2 to 115/13.8 kV 70 MVA transformers at Hyland Lake Substation |  | MN |  |  | Planned | 5300000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21846 | 2021-09-10 |  | 26438 | 2021-09-10 | SUB | 2022-10-15 | Hyland Lake |  |  | 115 |  |  | Install high-side line breaker. Install new feeder bay. |  | MN |  |  | Planned | 1370000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21848 | 2022-05-25 |  | 26440 | 2022-05-25 | LNrl | 2022-07-09 | Willmar |  |  | 115 |  |  | Build new dead-end structure to re-terminate the 0823 line to a southern position at the Willmar sub |  | MN |  |  | Planned | 800000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21853 | 2021-09-10 |  | 26444 | 2021-09-10 | Remove | 2023-12-01 | Flambeau |  |  | 34.5 |  |  | Retire the Flambeau breaker station |  | WI |  |  | Planned | 750000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21853 | 2021-09-10 |  | 26445 | 2021-09-10 | TEQ | 2023-12-01 | North Fork |  |  | 34.5 |  |  | Add MOD’s to the switches at North Fork substation |  | WI |  |  | Planned | 750000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21866 | 2022-05-24 |  | 26447 | 2022-05-24 | CAP | 2023-06-01 | Sleepy Eye |  |  | 69 |  |  | Retire cap bank at Sleepy Eye substation to prevent unnecessary maintenance costs on the system. |  | MN |  |  | Planned | 100000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21868 | 2022-05-24 |  | 26448 | 2022-05-24 | CAP | 2023-06-01 | Canistota Junction |  |  | 69 |  |  | Retire cap bank at Canistota Junction substation to prevent unnecessary maintenance costs on the system. |  | MN |  |  | Planned | 100000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21869 | 2022-05-23 |  | 26450 | 2022-05-23 | CAP | 2023-06-01 | Buffalo Ridge |  |  | 34.5 |  |  | Retire 34.5kV cap banks at Buffalo Ridge feeders BRI311 and BRI312. |  | MN |  |  | Planned | 150000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21869 | 2022-05-23 |  | 26451 | 2022-05-23 | CAP | 2023-06-01 | Chanarambe |  |  | 34.5 |  |  | Retire 34.5kV cap bank at Chanarambe feeder CHB341. |  | MN |  |  | Planned | 100000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21877 | 2021-09-13 |  | 26465 | 2021-09-13 | SUB | 2023-12-31 | Coon Creek |  |  | 345 |  |  | Install three 345kV circuit breakers at the Coon Creek (CNC) substation. |  | MN |  |  | Planned | 2700000 | Planning |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21887 | 2021-09-13 |  | 26474 | 2021-09-13 | SUB | 2022-02-01 | Rogers Lake |  |  | 115 |  |  | Install two breakers at Rogers Lake to separate Airport – Rogers Lake 115 kV line and Rogers Lake TR2 |  | MN |  |  | Planned | 1860000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21888 | 2021-09-13 |  | 26477 | 2021-09-13 | LNrb | 2022-12-15 | Zumbrota | West Albany | 1 | 69 |  |  | Wreck-out 19.7 miles of existing 69kV on line 0761 rebuild to current 69kV Standards |  | MN |  |  | Planned | 8500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21891 | 2021-09-13 |  | 26478 | 2021-09-13 | LNrb | 2024-12-21 | Pipestone | Tracy Switching Station |  | 69 |  |  | NSM 0726-69kV Line Major line rebuild from Pipestone to Tracy Switching Station. |  | MN |  |  | Planned | 17150000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 21892 | 2021-09-13 |  | 26479 | 2021-09-13 | TAP | 2023-06-01 | Scott County | Dean Lake |  | 115 |  |  | City of Shakopee T-L Interconnection Request. In-and-out off NSP’s Scott County - Dean Lake 115kV transmission line. Joint substation, NSP will own the high side. |  | MN |  |  | Planned | 3000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 22629 | 2022-09-15 |  | 26818 | 2022-09-15 | SUB | 2023-06-01 | Wheaton |  |  | 161 |  |  | Breaker addition and associated subwork. |  | WI |  |  | Planned | 1500000 | Planning |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 22686 | 2022-05-16 |  | 26819 | 2022-08-24 | LNrc | 2023-05-15 | Briggs Road | LaCrosse |  | 161 |  |  | Age and Condition rebuild of Briggs Road - Mayfair - LaCrosse line, upgrading to larger conductor to remediate N-1-1 overloads. |  | WI | 10.4 |  | Planned | 4000000 | Planning |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 23452 | 2022-09-08 |  | 27220 | 2022-08-24 | LN | 2025-09-01 | Brookings County | Lyon County | 2 | 345 |  |  | Install second 345 kV circuit between the Brookings County and Lyon County substations utilizing the vacant second circuit positions that exist on those towers. |  | MN |  | 60 | Planned | 17000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 23452 | 2022-09-08 |  | 27296 | 2022-08-24 | SUB | 2025-09-01 | Helena |  |  | 345 |  |  | Upgrade substation equipment to support rating of new Hampton Corner - Helena 345kV 2nd circuit. |  | MN |  |  | Proposed | 5000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 23452 | 2022-09-08 |  | 27295 | 2022-08-24 | SUB | 2025-09-01 | Hampton Corner |  |  | 345 |  |  | Upgrade substation equipment to support rating of Hampton Corner - Helena 345kV 2nd Circuit |  | MN |  |  | Proposed | 5000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 23452 | 2022-09-08 |  | 27294 | 2022-08-24 | LN | 2025-09-01 | Hampton Corner | Helena | 2 | 345 |  |  | Install 2nd 345kV line between Hampton Corner and Helena using existing right of way for mitigation of N-1-1 violations. |  | MN | 39 |  | Proposed | 11700000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 23452 | 2022-09-08 |  | 27223 | 2022-08-24 | SUB | 2025-09-01 | Lyon County |  |  | 345 |  |  | Perform substation upgrades to accommodate rating of new Brookings Co - Lyon Co line |  | MN |  |  | Planned | 5000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP22 | C | West | XEL | 23452 | 2022-09-08 |  | 27222 | 2022-08-24 | SUB | 2025-09-01 | Brookings County |  |  | 345 |  |  | Perform substation upgrades to accommodate rating of new Brookings Co - Lyon Co line |  | MN |  |  | Planned | 5000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
Note on U1: Upgraded or on existing rights of way