## MTEP23 Appendix A
MTEP23 Appendix A - New Projects recommended for approval
Planning Region | Geographic Location by TO Member System | Project ID | Project Name | Project Description | State | Submitting Comp. | Board Approved | Project Type | Other Type | Expected ISD | Max kV | Estimated Cost
Central | DEI | 3382 | Vincennes Vigo St. 138kV Dist Sub | Build new radial 138kV line and add breaker at Vincennes 138kV sub to convert Vigo St. sub from 34kV to 138kV | IN | Duke Energy Corporation |  | Other | Other Local Needs | 2026-07-14 | 138 | 10932000
South | Entergy-LA | 9764 | Dixie Baker to Baker 69 kV: Reconductor Line | Upgrade the Dixie Baker to Baker 69 kV line section. This includes a reconductor/rebuild and upgrading substation equipment. | LA | Entergy |  | Other | Reliability | 2026-06-01 | 69 | 12800000
South | Entergy-AR | 12055 | Gum Springs 115kV: Build Breaker Station | Create a new 115kV switching station by tapping the Arkadelphia North – Richwood 115kV and the Arkadelphia West – Dalark 115kV line sections. | AR | Entergy Arkansas |  | Other | Reliability | 2026-06-01 | 115 | 14950800
South | Entergy-LA | 12084 | Dixie Baker to Zachary 69 kV: Upgrade Line | Upgrade the ~3.3 mile long line section. | LA | Entergy |  | Other | Reliability | 2027-06-01 | 69 | 18900000
South | Entergy-LA | 12098 | Delmont to Hazel 230 kV: Upgrade Line | Upgrade the Delmont to Hazel 230 kV conductor, bus work at both the stations, line bay bus ,jumpers and any station equipment to a minimum of 1600 A. | LA | Entergy |  | BRP |  | 2026-06-01 | 230 | 15600000
South | SMEPA | 12210 | South Hattiesburg Industrial Delivery Point | In order to serve the South Hattiesburg and Hattiesburg Industrial delivery points economically and reliably, service will be established by tapping L161 and constructing a 161kV breaker switching station. A new distribution station will be constructed adjacent to the 161kV switching station and the existing distribution feeders from both delivery points will be routed to the new station. | MS | South Mississippi Electric Power Association |  | Other | Other Local Needs | 2025-06-01 | 161 | 13884200
South | SMEPA | 12222 | Maxie Delivery Point | In order to serve the Maxie delivery point economically and reliably, service will be established by a short transmission feed by tapping the Cooperative Energy Lines 37 and 38 that are near the delivery point. | MS | South Mississippi Electric Power Association |  | Other | Other Local Needs | 2023-06-01 | 69 | 1939497
South | Entergy-LA | 15654 | Delhi - Tallulah 115 kV rebuild | Rebuild 20.7 miles of 115kV line from Delhi to Tallulah. Operate the series reactor at Delhi as normally open. | LA | Entergy |  | BRP |  | 2026-12-01 | 115 | 39900000
South | Entergy-MS | 15708 | North Jackson 115 kV: Install Circuit Breakers | Install Transmission Breakers at North Jackson 115 kV substation. | MS | Entergy Mississippi |  | Other | Reliability | 2025-12-15 | 115 | 7300000
East | METC | 15752 | Redstone – Tittabawassee 138 kV Rebuild | Rebuild ~13.4 miles of the ~21.5 mile-long Redstone – Tittabawassee 138 kV line from 336 ACSR to 1431 ACSR using future double-circuit construction with OPGW. | MI | METC |  | BRP |  | 2027-06-01 | 138 | 22170000
East | ITCT | 15872 | Brownstown-Monroe #2 345 kV Sag Remediation | Remediate the sag on the Brownstown - Monroe #2 345 KV line to at least 1400 MVA and upgrade switches at Monroe "FT" and "FM" positions. | MI | ITC Transmission |  | Other | Other Local Needs | 2026-12-31 | 345 | 2582000
South | Entergy-LA | 18236 | Winnsboro to Gilbert 115 kV: Rebuild Line | Rebuild approximately 9.5 miles of 115 kV line from Winnsboro to Gilbert. | LA | Entergy |  | BRP |  | 2026-12-01 | 115 | 20900000
South | Entergy-LA | 18247 | Gilbert to Wisner 115 kV: Rebuild Line | Rebuild Gilbert to Wisner 115 kV line. The line will be built using a double circuit configuration but only strung on one side. The unused side will be reserved for a future 230 kV line. | LA | Entergy |  | BRP |  | 2027-12-15 | 115 | 11900000
South | Entergy-TX | 18266 | New Long John to Dayton 138 kV: Rebuild line | Rebuild New Long John to Dayton Bulk 138 kV line. | TX | Entergy |  | BRP |  | 2026-06-01 | 138 | 24900000
Central | BREC | 19007 | Upgrade Kansas 69 kV line | Create double circuit from existing radial 69 kV tap | KY | Big Rivers Electric Corporation |  | Other | Load Growth | 2024-10-01 | 69 | 900000
South | Entergy-AR | 19911 | Dumas - Reed 115kV: Rebuild Line | Rebuild the 15 mile 115kV line from Dumas - Reed to a minimum through path rating of 259 MVA. | AR | Entergy Arkansas |  | BRP |  | 2025-06-01 | 115 | 18600000
Central | PPI | 19947 | New Allen-Mason City 69 kV Line | New Allen-Mason City 69 kV line | IL | Prairie Power, Inc. |  | Other | Reliability | 2027-12-31 | 69 | 6367500
Central | PPI | 19948 | New Mason City-Middletown 69 kV Line | New Mason City-Middletown 69 kV line | IL | Prairie Power, Inc. |  | Other | Reliability | 2027-12-31 | 69 | 9197500
West | ATC | 19963 | Kirkwood SS, Power Transformer and Breaker Asset Renewal | Replace T31, a 1974 vintage 138/69 kV 93 MVA power transformer with the onsite 138/69 kV 100 MVA system spare. • Replace station service transformers of 100 kVA • Replace all relays, RTU, batteries and charger and install new DC panel in existing building • Install battery monitoring solution instead of dual batteries to fit in existing building • Install new 138 kV and 69 kV bus tie breakers and associated disconnect switches • Replace two 69 kV and two 138 kV oil circuit breakers and replace with SF6 gas breakers • Remove and retire disconnect switches no longer in use and bypass switches • Replace one 69 kV disconnect switch due to condition • Replace capacitor cans and protection voltage transformers on existing 19.2 MVAR bank • Install new 138 kV 16.33 MVAR capacitor bank • Install new 138 kV bus PT’s and new 69 kV bus PT’s • Install new line side disconnects • Replace existing CCVT and wave trap • Replace brown glass insulation • Add corona rings to existing line dead-end polymer insulators | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2026-12-31 | 138 | 14100000
West | ATC | 20201 | Small Capital Project and Asset Renewal Program 2024 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2024. | WI,MI | American Transmission Co. LLC |  | Other | Age and Condition | 2026-06-30 | 345 | 47000000
West | ATC | 20202 | Communication Reliability Program 2024 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2024. | WI,MI | American Transmission Co. LLC |  | Other | Other Local Needs | 2026-06-30 | 0 | 11000000
West | ATC | 20203 | Line Clearance Mitigation Program 2024 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2024. | WI,MI | American Transmission Co. LLC |  | Other | Reliability | 2026-06-30 | 345 | 10000000
West | ATC | 20204 | Load Interconnection Program 2024 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2024. | WI,MI | American Transmission Co. LLC |  | Other | Load Growth | 2025-06-30 | 345 | 16000000
East | ITCT | 21725 | Horn - Trenton Channel 120 kV Sag Remediation | Fully remediate the sag on the Horn – Trenton Channel 120 kV circuit up to the conductor limit. Upgrade station equipment at Trenton Channel position HG. | MI | ITC Transmission |  | BRP |  | 2026-12-31 | 120 | 320000
South | Entergy-AR | 21807 | Brinkley East 230/115kV Auto: Change Tap Setting | Change the high side taps on the Brinkley East 230/115kV Auto to 242 kV [230kV Auto completed on 3/8/2022]. | AR | Entergy Arkansas |  | BRP |  | 2023-03-01 | 230 | 15000
South | Entergy-TX | 21844 | Deer to Doucette 138 kV: Upgrade Station Equipment and Line | Rebuild the ~6 mile Deer to Doucette 138 kV line. | TX | Entergy |  | BRP |  | 2025-12-01 | 138 | 18400000
West | ATC | 21921 | Groenier – Rosholt (ALTE) Tap, 69 kV (Y-71), Partial Rebuild and Rerate | Sectionalize of tap near existing Rosholt (ALTE) Substation with 3-Way T-Line switch. Assumed rebuild section off center due to radial connection. Bury distribution to resolve rerate issues. | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2025-12-31 | 69 | 16500000
Central | AmerenMO | 21927 | New Kinsey 69/12 kV Substation | Construct New Kinsey 69/12 kV Substation (5/7 MVA). | MO | Wabash Valley Power Association, Inc. |  | Other | Reliability | 2025-02-06 | 69 | 1200000
Central | AmerenMO | 21928 | New Valley View-Salem Bulk 69 kV line | Construct New Valley View-Salem Bulk 69 kV line. Construct 69 kV from Salem Bulk 69 kV Substation to Sprott substation, Sprott to Kinsey substation, Kinsey to Valley View substation. Construct with 477 kcm ACSR, 21 miles total. | MO | Wabash Valley Power Association, Inc. |  | Other | Reliability | 2025-02-06 | 69 | 44520000
West | ATC | 21985 | Chandler-Delta 69 kV (Delta1), Rebuild and OPGW | Rebuild approximately 5.5 miles of 69 kV line Delta1 from Delta SS to Chandler SS and install OPGW. | MI | American Transmission Co. LLC |  | Other | Age and Condition | 2026-06-30 | 69 | 11600000
East | ITCT | 22014 | ITCT Pole Top Switch Additions/Replacement Program 2024 | Installing pole-top switches, or replacing them as appropriate, at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. This significantly reduces service interruptions to the customers during planned maintenance work or restoration from the aftermath extreme weather events. | MI | ITC Transmission |  | Other | Reliability | 2024-12-31 | 120 | 2400000
Central | AmerenMO | 22066 | Replace Mason 345/138 kV Transformer No. 1 | Replace Mason 345/138 kV Transformer #1 with a 700 MVA Unit | MO | Ameren Services Company |  | Other | Reliability | 2026-12-01 | 345 | 7800000
East | METC | 22147 | Blackstone-Stable- J1310 Generator Interconnection | Build a new 138 kV 3 Breaker ring substation cut in from the Blackstone - Stable 138 kV line. System changes will require relay upgrades at Stable 138kV and Blackstone 138kV stations. | MI | METC |  | GIP |  | 2024-10-01 | 138 | 14648128
East | METC | 22165 | Brooks Industrial Mud Lake - J1430 Interconnection - NU | Build J1430 interconnection station as a breaker and half station with three breakers in a ring bus configuration. Brooks Industrial - Mud Lake 138kV line will be extended to loop in the J1430 Interconnection 138kV station. Relay upgrades will be required at Mud Lake, Stable, Marshall, and Brooks Industrial 138kV stations. | MI | METC |  | GIP |  | 2023-08-01 | 138 | 8609509
Central | AmerenIL | 22186 | Upgrade South Ottawa 138 kV Substation to Ring Bus | Create a 5 position 6 ultimate ring bus at the existing South Ottawa substation | IL | Ameren Services Company |  | Other | Reliability | 2025-06-01 | 138 | 9300000
Central | AmerenIL | 22266 | Rebuild Clinton-Oreana and Clinton-Goose Creek 345 kV lines | Rebuild existing double-circuit towers on the Clinton-Oreana-4571/Clinton-Goose Creek-4545 345 kV line due to deteriorated condition. Include the reroute of the 4571 line in to Leghorn. | IL | Ameren Services Company |  | Other | Age and Condition | 2024-12-01 | 345 | 34300000
West | ATC | 22587 | North Central WI Reliability Project | Address reliability concerns in the 115kV system in North Central Wisconsin for multiple P6 outage combinations. Scope: • Construct new 115kV source between Hilltop and Pine substations • OPGW to be installed on new line • Asset renewal work on relays at Hilltop, Maine, and Pine substation • Upgrade Pine SS Bus #51 to match rating of new line | WI | American Transmission Co. LLC |  | BRP |  | 2028-06-01 | 115 | 47900000
Central | AmerenIL | 22667 | New PPI - Forest City 138 kV Interconnection | Construct a new 138 kV substation in ring bus configuration on the existing Ameren Havana-Cincinnati-1352 138 kV line. A position will feed PPI Forest City 138/69 kV | IL | Ameren Services Company |  | Other | Reliability | 2025-12-01 | 138 | 8500000
Central | AmerenMO | 22706 | New Huck Finn Solar 345 kV interconnection (J956) | Connect a 200MW solar farm via 345 kV leadline from Interconnection Customer collector substation to existing Spencer Creek switching station. | MO | Ameren Services Company |  | GIP |  | 2024-06-01 | 345 | 4200000
Central | AmerenIL | 22728 | Reconfigure Decatur North—27th St. 138 kV substation | Rebuild this station to a 7 position BAAH, minimum 8 position ultimate BAAH. New name is Boxcar. | IL | Ameren Services Company |  | Other | Reliability | 2025-06-01 | 138 | 19800000
Central | AmerenMO | 22787 | Upgrade Warson 161 kV substation | Line BKRs on 4 line terminals, High Side interrupting devices on XFMRs 1,2,3,4, Add bus tie 2-3 BKR | MO | Ameren Services Company |  | Other | Reliability | 2026-12-01 | 138 | 8000000
Central | AmerenIL | 22789 | Upgrade Canton South 138 kV substation | New ring bus at Canton South | IL | Ameren Services Company |  | Other | Age and Condition | 2026-06-01 | 138 | 3250000
Central | AmerenMO | 22790 | Reconfigure Moreau 161 kV substation | Construct a four position (six ultimate) 161 kV ring bus at Moreau. New name is Jays. | MO | Ameren Services Company |  | Other | Reliability | 2026-12-01 | 161 | 8500000
Central | AmerenMO | 22791 | New McBaine 161 kV substation | New switching station at McBaine tap off LYMT-OVRT-3. New name is Katy. | MO | Ameren Services Company |  | Other | Reliability | 2026-12-01 | 161 | 14400000
Central | AmerenMO | 22801 | Rebuild Sioux-Meppen North-Hull 138 kV line | Rebuild the Sioux-Meppen North-4 from Str. 180-Meppen North and the entire Meppen North-Hull-1494 138 kV line to upgrade aging infrastructure and improve system reliability. | MO,IL | Ameren Services Company |  | Other | Age and Condition | 2026-12-01 | 138 | 77700000
Central | AmerenMO | 22806 | Upgrade Rush Island 345 kV Substation | Upgrade the Rush Island 345 kV bus to 3000A capability | MO | Ameren Services Company |  | Other | Reliability | 2024-04-01 | 138 | 1500000
Central | NIPS | 22809 | J1058 Network Upgrades 345 kV | New Substation(Dinwiddie) and 345kV line to Connect J1058 to NIPSCO's Schahfer to St. John line | IN | Northern Indiana Public Service Company |  | GIP |  | 2025-06-01 | 345 | 24060403
Central | AmerenIL | 22813 | Reconductor Coffeen North-Roxford 345 kV line | Reconductor the 51 mile Coffeen North-Roxford-4551 345 kV line with conductor capable of carrying 3,000 amps during Summer Emergency conditions. | IL | Ameren Services Company |  | Other | Age and Condition | 2025-12-01 | 345 | 25000000
Central | AmerenMO | 22814 | Upgrade Guthrie 161 kV substation | Add a 161 kV line breaker to the 161 kV GUTH-LYMT-3 line at Guthrie. | MO | Ameren Services Company |  | Other | Reliability | 2024-12-01 | 161 | 2000000
Central | AmerenMO | 22815 | Upgrade Hunter 161 kV substation | Add Line breakers on H2 and H10; High Side Interrupting Devices on XFMR 1, 2, 3 | MO | Ameren Services Company |  | Other | Age and Condition | 2025-12-01 | 161 | 3000000
Central | AmerenIL | 22816 | Rebuild Louisville - Newton 138 kV line | Replace the 134 original vintage wood structures on the Louisville-Newton-1 138 kV line due to age and condition. Replace the existing conductor with ones capable of carrying 2,000 amps under Summer Emergency conditions. Replace both shield wires with 72-fiber OPGW. | IL | Ameren Services Company |  | Other | Age and Condition | 2024-12-01 | 138 | 32000000
Central | AmerenIL | 22817 | Rebuild Mount Vernon West-Xenia 345 kV line (4591) | Rebuild the existing 37 mile Mount Vernon West-Xenia-4591 345 kV line due to replace decayed and severely woodpecker damaged wood poles. Newly rebuilt line will utilize conductors capable of 3000 amps at Summer Emergency conditions and 2 OPGW's. | IL | Ameren Services Company |  | Other | Age and Condition | 2026-12-01 | 345 | 51000000
Central | AmerenMO | 22846 | Upgrade Sioux 138 kV Substation | Upgrade 15H posn to higher ampacity to increase available capacity of the 700MVA Auto XFMR | MO | Ameren Services Company |  | Other | Age and Condition | 2026-12-01 | 138 | 10500000
East | ITCT | 22847 | Kings Point - New DTE 120kV Interconnection | DTE requested a new LDC 120kV substation interconnection, called Kings Point. ITCT will construct a new 120 kV station and cut the Boyne - Golf 120 kV line in to accommodate this new interconnection. The configuration for ITCT’s 120 kV station will be a straight bus station with one 40kA section breaker and two 40kA line breakers. ITCT will relocate a ~ 2.1 miles section of the Boyne-Golf 120kV circuit by utilizing DTE’s existing 40kV circuit on the North side of 21 Mile Rd, East side of N. Gratiot Ave, and South side of Hall Rd to rebuild this ~2.1 miles to 120kV with 40kV underbuilding to loop the Boyne-Golf line into the new 120kV substation. | MI | ITC Transmission |  | Other | Load Growth | 2027-03-31 | 120 | 20000000
Central | AmerenIL | 22848 | Rebuild Hutsonville-Heath 138 kV line (1311) | Rebuild the Hutsonville-Heath-1311 138 kV line from Hutsonville-Str. 95 with conductors capable of 2000 amps at Summer Emergency and OPGW. | IL | Ameren Services Company |  | Other | Reliability | 2025-06-01 | 138 | 12500000
Central | AmerenIL | 22851 | Rebuild Mount Vernon West-West Frankfort East 345 kV line (4561) | Rebuild the existing 36 mile Mount Vernon West-West Frankfort East-4561 345 kV line. Newly rebuilt line will utilize conductors capable of 3000 amps at Summer Emergency conditions and 2 OPGW's. | IL | Ameren Services Company |  | Other | Age and Condition | 2025-06-01 | 345 | 48000000
Central | AmerenMO | 22866 | Upgrade St Francois 345 kV substation | Install a new circuit breaker at St. Francois 345 kV Sub position V43 to complete the ring bus. Replace 138 kV breakers. Upgrade relaying. | MO | Ameren Services Company |  | Other | Reliability | 2027-06-01 | 345 | 12700000
Central | AmerenIL | 22868 | Upgrade Quincy South 138 kV substation | Replace 1753 and 1823 BKRs, Replace 1751 line switch. | IL | Ameren Services Company |  | Other | Age and Condition | 2024-12-01 | 138 | 3000000
Central | AmerenMO | 22869 | Rebuild Clark 138/161 kV Substation to 138 kV BAAH | Rebuild Clark 138/161 kV Substation to have a 138 kV BAAH bus with 8 positions (4 existing lines, 2 XFMRs, bring in RIV-ALFM-6636) and a 161 kV ring bus with 6 positions (2 existing lines, 2 XFMRs, and new line position to Viburnum). Rebuild the existing Clark-Viburnum 161 kV line to be double circuit 161 kV lines. Add a 161 kV terminal at Viburnum Substation. Route the RIV-ALFM-6636 138 kV line into the new Clark 138 kV BAAH bus. New name is Clemens. Install 161kV PCB (or CS) on XFMR 3. Install 138kV PCB on XFMR 3. Replace existing differential relaying with new 161kV bus diff, XFMR diff, and 138kV bus diff. | MO | Ameren Services Company |  | BRP |  | 2027-12-01 | 161 | 44350000
Central | AmerenMO | 22870 | Reconfigure Mason-Carrollton-Sioux 138 kV lines | Split the ~2 mile Mason-Carrollton-8/Carrollton-Sioux-8 138 kV lines into two separate circuits to avoid the loss of a single structure causing a long-term outage on both Carrollton supplies. | MO | Ameren Services Company |  | Other | Reliability | 2025-06-01 | 138 | 5000000
West | GRE | 22871 | Cedar Lake Line Rebuild | Relocate the existing Cedar Lake tap line to a new route to accommodate Hampton Corners - Helena 345 kV addition to the Hampton Corners - Chub Lake - Helena structures. | MN | Great River Energy |  | Other | Other Local Needs | 2025-08-01 | 69 | 12772504.79
Central | AmerenMO | 22873 | Upgrade Oran 161 kV substation | Add 161 kV ring bus to split the Kelso- Morley-3 line into two lines | MO | Ameren Services Company |  | Other | Reliability | 2026-06-01 | 161 | 7800000
West | MP | 22885 | Brainerd Crypto | Mitigation solutions to accommodate a 70 MW Load addition at Brainerd 115 kV bus, including a second 20 MVAR capacitor bank and thermal upgrade of the Brainerd - Riverton 115 kV Line | MN | Minnesota Power (Allete, Inc.) |  | Other | Load Growth | 2025-12-31 | 115 | 2750000
Central | AmerenIL | 22888 | Upgrade Edwards 345 kV substation | Install a new 345 kV Ring Bus near Edwards Switchyard to support the transmission system in the Peoria area. Reroute ~0.75 miles of the existing Mapleridge-Tazewell-4528 345 kV line on the west side of Edwards Switchyard to avoid conflicts with the existing 138 kV crossings. Remove the existing failed 345 kV underground cable between Str. 123 and 124. Design and build the rerouted line to support 2 - 345 kV circuits to support MISO planning needs. All new conductors should be minimum 3000 amp Summer Emergency rated. | IL | Ameren Services Company |  | Other | Reliability | 2027-06-01 | 345 | 32000000
Central | AmerenMO | 22890 | Upgrade Selma 161 kV substation | Add line breakers to Selma-Rivermines-2 & DPFE-Selma-1 Add High Side Interrupting devices to XFMR 1 & 2 | MO | Ameren Services Company |  | Other | Reliability | 2025-12-01 | 138 | 3000000
Central | AmerenIL | 22891 | Rebuild Tibbs-Steeleville 138 kV line | Repair issues found during inspections. Replace existing 477 ACSR conductor in line. | IL | Ameren Services Company |  | Other | Reliability | 2024-12-01 | 138 | 37000000
West | MP | 22909 | 40 Line Rebuild | Rebuild Badoura - Dog Lake 115 kV Line, new 795 ACSR and OPGW will be installed | MN | Minnesota Power (Allete, Inc.) |  | Other | Age and Condition | 2024-12-31 | 115 | 17307658
Central | AmerenMO | 22926 | Upgrade Dardenne 161 kV substation | Add line breakers to Dardenne | MO | Ameren Services Company |  | Other | Reliability | 2027-12-01 | 138 | 5000000
Central | AmerenMO | 22927 | Convert Viaduct 115 kV facilities to 161 kV | Convert 115 kV facilities at Viaduct to 161 kV. Eliminate Viaduct 161 to 115kV transformer T1 by bypassing it, and by changing the taps on Viaduct XFMR 1 from 115 to 161kV. Replace 115kV OCB #5210 with a 161kV puffer breaker. | MO | Ameren Services Company |  | Other | Age and Condition | 2024-12-01 | 161 | 5000000
Central | AmerenIL | 22946 | New Alta - Pioneer 138 kV Line | Construct a new 138 kV line from Alta to Pioneer. Rebuild Alta 138 kV substation as a 4-position initial, 6-position ultimate 138 kV ring bus. Rebuild Pioneer 138 kV substation as 5-position initial, 6-position ultimate 138 kV ring bus. TP5161 was created to rebuild Pioneer as a ring bus to address aging infrastructure. The aging infrastructure will be addressed by this project. | IL | Ameren Services Company |  | Other | Reliability | 2025-12-01 | 138 | 26700000
Central | AmerenMO | 22947 | Upgrade Lakeshire 138 kV substation | Add line breaker to Pos. J (Baum-Wat-1) | MO | Ameren Services Company |  | Other | Age and Condition | 2025-12-01 | 138 | 3400000
Central | AmerenIL | 22966 | New Baldwin Area Reactive Support | Add 4 138 kV dynamic reactive 250 Mvar each located at Turkey Hill, Moro, Jarvis, and Granite City 23rd Street. | IL | Ameren Services Company |  | Other | Reliability | 2027-06-01 | 138 | 170000000
Central | AmerenMO | 23006 | Upgrade Pilot Knob 161 kV substation | Add circuit switcher for XFMR 1 and line breaker for 161 kV FLET –PKNB -2 | MO | Ameren Services Company |  | Other | Reliability | 2025-12-01 | 161 | 4000000
Central | AmerenIL | 23026 | New South Central Illinois Transmission Expansion | Construct a new 138 kV substation as an ultimate six-position ring bus requiring one 3000 A 138 kV breaker initially adjacent to the Continental Tire facility. Construct a ~3.5 mile 138 kV line from Mt. Vernon 42nd St. to the new substation ~0.3 miles NE of the Continental Tire facility with minimum 2000 A summer emergency capability. Add a new 3000 A 138 kV breaker at Mt. Vernon 42nd St. for this new 138 kV line position | IL | Ameren Services Company |  | Other | Reliability | 2028-06-01 | 138 | 167850000
Central | AmerenIL | 23072 | Rebuild Newton-Tanner 345 kV line | Rebuild the Newton-Tanner 345 kV line with conductors capable of 3000 amps Summer Emergency rating and two OPGWs. | IL | Ameren Services Company |  | Other | Reliability | 2026-12-01 | 138 | 29000000
Central | AmerenMO | 23087 | Rebuild Troy-Pike 161 kV line | Add Dual OPGW to the TROY-PIKE-1 Line from Pike to the Auburn tap (Structure 309 or so). Adding OPGW to the TROY-PIKE-1 line will require the line to be rebuilt. Since the line is being rebuilt, dual OPGW is to be added. At the Auburn tap the OPGW will be terminated to allow a connection to the AECI Fiber on their portion of the TROY-PIKE-1 line and brought the rest of the way to the new Harley Substation. | MO | Ameren Services Company |  | Other | Reliability | 2024-12-01 | 161 | 16000000
Central | AmerenIL | 23088 | Upgrade Quincy East 138 substation | Replace BKR 1442 Replace switch 1456. | IL | Ameren Services Company |  | Other | Age and Condition | 2024-06-01 | 138 | 1500000
Central | IPL | 23107 | New J993 Brickyard Solar 345 kV | Interconnection Customer shall install a 217 MVA solar facility. | IN | Indianapolis Power & Light Company |  | GIP |  | 2023-12-01 | 345 | 20000000
South | SMEPA | 23126 | J1249 Morrow Repower | A single steam turbine unit will be repowered at Plant Morrow for combined cycle operation utilizing a new natural gas fired combustion turbine (CT). In order to support a single unit repower at Plant Morrow with a max net capacity, Cooperative Energy has identified the need for transmission and substation projects on its system. | MS | South Mississippi Electric Power Association |  | GIP |  | 2023-02-08 | 161 | 15903000
West | OTP | 23129 | OTP Casselton 115 kV Capacitor Addition | The project consists of expanding the existing 115 kV bus at OTP's Casselton, ND substation with two additional 115 kV breakers to allow for another position in the substation. A new 115 kV 15 MVAR capacitor and breaker will be added into the new position created in the Casselton 115 kV bus. | ND | Otter Tail Power Company |  | Other | Load Growth | 2024-06-01 | 115 | 1200000
West | OTP | 23146 | OTP Big Stone Network Upgrades - J722 | J722, a 200 MW wind project, has requested to interconnect into OTP's Big Stone South 230 kV substation as part of the MISO August 2017 DPP study cycle. J722 has been assigned to complete the following network upgrades on OTP's transmission system to interconnect at Big Stone South 230 kV. 1. Increase capacity on the Big Stone South - Big Stone 230 kV circuits #1 and #2. 2. Increase capacity on the Big Stone - Blaire 230 kV circuit. | SD | Otter Tail Power Company |  | GIP |  | 2023-05-31 | 230 | 1756087
Central | AmerenMO | 23152 | New Copley 138-12 kV Substation | Build a new four position 138 kV Ring bus needed to connect two 13/12 kV transformers | MO | Ameren Services Company |  | Other | Load Growth | 2024-12-01 | 138 | 20000000
East | ITCT | 23171 | J1319 Generator Interconnection | J1319 generator will utilize the existing POI established for J327 Deerfield Wind Energy at the ITCT Rapson 120 kV substation. | MI | ITC Transmission |  | GIP |  | 2023-02-28 | 0 | 0
Central | AmerenIL | 23207 | Rebuild Mattoon West-Tuscola West 138 kV line | Rebuild the 24.6 mile Mattoon West-Tuscola West-1 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL | Ameren Services Company |  | Other | Reliability | 2025-12-01 | 138 | 18500000
Central | AmerenIL | 23286 | New [PPI] Paragon 138 kV substation | Add interconnection point to the Pana substation for PPI's new bulk substation which will be called Paragon (name changed from Panther) | IL | Ameren Services Company |  | Other | Load Growth | 2025-06-01 | 138 | 900000
Central | AmerenMO | 23306 | Rebuild Stoddard-Essex 161 kV line | Rebuild the 5.4 mile Stoddard-Essex-3 161 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | MO | Ameren Services Company |  | Other | Reliability | 2025-06-01 | 161 | 3300000
East | METC | 23329 | R1009 Replacement Generator Interconnection | R1009 generator will replace existing Hillman generating unit and utilize the existing POI established for Hillman Cogeneration connected at the METC Airport-Mio Dam 138 kV line (Progress Street Tap). | MI | METC |  | GIP |  | 2023-12-31 | 0 | 0
West | XEL | 23347 | Blue Lake Substation - FRM13 | Replace ammeter on Blue Lake 345kV breaker 8M33 to increase rating on the Blue Lake - Scott County 345 kV line. | MN | Northern States Power (Xcel Energy) |  | Other | Reliability | 2022-09-02 | 345 | 127000
South | Entergy-MS | 23348 | Grenada Industrial 115 kV: New Station | Entergy is proposing to construct a new 115 kV substation (Grenada Industrial 115 kV Substation) which will serve the industrial customer’s 10 MW of new load and future area load growth in Grenada, MS and the industrial park. Entergy will construct a new (4) breaker ring bus substation with (1) – 40 MVA, LTC 115/13.8 kV transformer. The new substation will have (1) main and (3) feeder breakers. The new substation will cut into the current Grenada – Tillatoba 115 kV line. | MS | Entergy Mississippi |  | Other | Load Growth | 2024-12-01 | 115 | 32610000
Central | PPI | 23350 | New Forest City-Allen Tap 69 kV Line | New Forest City-Allen Tap 69kV line | IL | Prairie Power, Inc. |  | Other | Reliability | 2027-12-31 | 69 | 2880000
Central | AmerenMO | 23351 | New Bugle 138 kV Capacitor (120 Mvar) | 120 Mvar Capacitor at Bugle | MO | Ameren Services Company |  | Other | Reliability | 2024-12-01 | 138 | 26000000
Central | AmerenIL | 23367 | New Lincoln Land Energy Center 345 kV substation (J955) | Project will connect to the existing Austin substation this requires us to install a new 345 kV breaker position. This is a 1165 MW combined cycle project. | IL | Ameren Services Company |  | GIP |  | 2024-12-01 | 345 | 2700000
Central | AmerenMO | 23388 | New Firebrick Wind Farm (J1026) | J1026 is seeking interconnection service for 380 MW for Wind facility. The Connection will be made at the 345 kV Spencer Creek Substation | MO | Ameren Services Company |  | GIP |  | 2024-06-01 | 345 | 1700000
Central | DEI | 23406 | Upgrade Bedford 345 kV - 138 kV Bus 9 | Bedford 345 KV - Upgrade 138KV Bus 9 - from (1)954acsr@120C (overhead line rating) to (2)954ACSR@120C | IN | Duke Energy Corporation |  | BRP |  | 2027-06-01 | 138 | 532500
Central | DEI | 23407 | Upgrade Bloomington 230 - Bk1 138kV Bus | Bloomington 230 - Upgrade Bk1 138KV Bus - from 300CU to 954AL | IN | Duke Energy Corporation |  | BRP |  | 2024-06-01 | 230 | 387100
Central | PPI | 23427 | New Disco-Carthage 69 kV Line | New Disco-Carthage 69 kV line | IL | Prairie Power, Inc. |  | Other | Reliability | 2026-12-31 | 69 | 8320000
Central | PPI | 23428 | New Golden-Denver 69 kV Line | New Golden-Denver 69 kV line | IL | Prairie Power, Inc. |  | Other | Reliability | 2026-12-31 | 69 | 12800000
Central | PPI | 23429 | Upgrade Feldon 69 kV Substation | Two new motor-operated SCADA-controlled switches on the Hardin Tap to Eldred 69 kV line. | IL | Prairie Power, Inc. |  | Other | Reliability | 2023-07-01 | 69 | 100000
Central | AmerenMO | 23430 | New Zachary generation interconnection FCAs (J1025-J1182) | Install a 2nd Zachary 345/161 kV transformer, construct a 2nd Zachary - Adair 161 kV transmission line, and re-route existing Appanoose-Adair 161 kV Transmission line. | MO | Ameren Services Company |  | GIP |  | 2025-12-01 | 345 | 17000000
Central | AmerenIL | 23431 | Upgrade Decatur-Main St. 138 kV line (J955) | Replace two Wood structures and re-frame 3 others to increase capacity of the Decatur - Main St. 138 kV line. | IL | Ameren Services Company |  | GIP |  | 2024-12-01 | 138 | 500000
West | XEL | 23446 | W3502 Rebuild and Connection to W3503 | Construct a new line from the end of the existing line W3502 to Xcel’s W3503 1.3 miles to the east. The new connection would be made with a group of one way pole mounted switches. The new connection will allow the sections between the substations to be sequentially rebuilt. The existing line W3502 will be rebuilt to serve as a redundant connection. | WI | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-06-15 | 69 | 3000000
West | XEL | 23447 | W3441 Extension to W3510 | Extend the line from Birchwood substation to the east to connect to Xcel line W3510 in the vicinity of the town of Wieger, a distance of about 13 miles. Install motor operated switches at Birchwood to sectionalize the line. Install manual switches at the connection to W3510. The line would initially be operated as a normally open second source to Birchwood. | WI | Northern States Power (Xcel Energy) |  | Other | Reliability | 2025-12-01 | 69 | 9000000
West | XEL | 23448 | W3430 Rebuild | Rebuild 2 ¼ miles from Luck - Luck (DPC) to 69 kV standard. | WI | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2023-06-01 | 69 | 1000000
West | XEL | 23449 | W3429 Clear Lake to STR 214 Rebuild | Rebuild 10 miles of line W3429 from Clear Lake to Structure 214 to 69 kV standard and add OPGW. | WI | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-07-31 | 69 | 5250000
West | XEL | 23450 | STY Install TR3 & 115kV Bus Tie | Install new 115kV bus tie and associated disconnect switches and bus work and re-terminate 0818/5529 at Rogers Lake Sub. | MN | Northern States Power (Xcel Energy) |  | Other | Reliability | 2024-12-15 | 115 | 5300000
West | XEL | 23451 | Pine Lake - Stanton 69kV Rebuild | Rebuild 16.1 miles from Pine Lake - Stanton to 69kV standard. | WI | Northern States Power (Xcel Energy) |  | Other | Reliability | 2023-09-01 | 69 | 9500000
West | XEL | 23453 | Line 0811 - Riverside Substation - FRM13 | Replace switches 5M330B, 5M331B, 5M329A, 5M330A, 5M329B, 5M331A, aux current transformers on 5M304 and 5M305, and two sections of busbar. | MN | Northern States Power (Xcel Energy) |  | Other | Reliability | 2022-12-31 | 115 | 900000
West | XEL | 23454 | Line 0838 - Red Rock Substation - FRM13 | Replace bushing current transformers on breaker K2, switches K2B1, 946B, K2B2, 946A, and meters on 946 and K2. | MN | Northern States Power (Xcel Energy) |  | Other | Reliability | 2022-12-31 | 115 | 650000
West | XEL | 23455 | Parkers Lake TR09 ELR | Replace Parkers Lake 345/115 kV TR09 (3 phases). | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2025-12-31 | 345 | 6000000
West | XEL | 23456 | Lake Yankton TR02 ELR | Replace Lake Yankton 115/69 kV TR02. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2026-12-31 | 115 | 1500000
West | XEL | 23457 | Hydro Lane TR05 ELR | Replace Hydro Lane 115/69 kV TR05. | WI | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2026-12-31 | 115 | 3000000
West | XEL | 23458 | Line 0893 NSS-BCK Rebuild | Rebuild 3.4 miles of 115 kV line between North Star Steel and Battle Creek substations. Portions of this line are double circuited with 0892, this project will separate the two circuits. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2023-12-15 | 115 | 3437000
West | XEL | 23459 | Line 0749 Waseca - ITC Tap Rebuild | Rebuild 6.7 miles of 69 kV line 0749 from Waseca - ITC Tap and add OPGW. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-06-15 | 69 | 6000000
West | XEL | 23460 | Line 0714 Medelia - Watonwan Rebuild | Rebuild 22 miles of line 0714 69 kV from Medelia - Watonwan. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-12-31 | 69 | 11000000
West | XEL | 23461 | Line 0708 STR 78 to 476 Rebuild | Rebuild 16 miles of line 0708 69 kV from Eagle Lake - Waterville and add OPGW. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-12-31 | 69 | 9000000
West | XEL | 23462 | Line 0718 Arlington - Winthrop Rebuild | Rebuild 15 miles line 0718 69 kV from Arlington - Winthrop. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-06-15 | 69 | 9000000
West | XEL | 23463 | Nighthawk Breaker Station | New 4-line terminal breaker station connecting to Minnesota Valley – Troy 69 kV transmission line (0724), Crook’s substation, and the SMBSC plant. | MN | Northern States Power (Xcel Energy) |  | Other | Reliability | 2024-06-01 | 69 | 5000000
West | ITCM | 23464 | Abbott-Traer 161kV 15 mile Rebuild | Due to aging condition, ITC will rebuild the Abbott – Traer 161kV circuit with T2-Grosbeak. | IA | ITC Midwest |  | Other | Age and Condition | 2027-12-31 | 161 | 16836000
West | XEL | 23466 | W3351 88kv Rebuild STR 336 to Saxton Pump | Rebuild line W3551 from structure 336 to Saxton Pump. Design the 88kv circuit to be 115kv capable. Include provision for a 34.5 kv under build circuit to connect to W3628 north of Saxton Pump. | WI | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-12-31 | 88 | 8000000
West | XEL | 23467 | Line 0859 Str 16 to Chemolite rebuild | Rebuild 6.9 miles of line 0859 115 kV from Chemolite substation to structure 16. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-12-31 | 115 | 9000000
West | XEL | 23468 | Chisago County Substation - FRM13 | Replace primary and secondary 115 kV bus 1 differential relays for TR05 and TR06. | MN | Northern States Power (Xcel Energy) |  | Other | Reliability | 2022-08-01 | 115 | 200000
West | XEL | 23469 | Scott County Substation - FRM13 | Replace busbar. | MN | Northern States Power (Xcel Energy) |  | Other | Reliability | 2022-12-31 | 115 | 200000
Central | AmerenMO | 23470 | New Northeast Missouri Wind interconnection (J1025) | Construct the new 345 kV Fabius substation in Knox County, Missouri to provide a Point of Interconnection for the Generating Facility with a terminal that will consist of all necessary terminal equipment to connect the J1025 leadline to 345kV Fabius substation bus. J1025 is a 300 MW Wind project interconnecting to the Zachary-Maywood 345 kV line | MO | Ameren Services Company |  | GIP |  | 2024-06-01 | 345 | 11000000
Central | NIPS | 23471 | Upgrade Roxana to Mittal 2 138 kV Line | Reconductor 2 miles of the Roxana to Mittal 2 138kV OH Conductor. Upgrade Roxana terminal connections. | IN | Northern Indiana Public Service Company |  | BRP |  | 2025-05-31 | 138 | 5648342
Central | NIPS | 23472 | Upgrade Leesburg Substation 138 kV | Leesburg substation upgrade to eliminate common breaker betweeen Leesburg Transformer and Circuit 13821. | IN | Northern Indiana Public Service Company |  | BRP |  | 2026-12-31 | 138 | 2392215
West | XEL | 23473 | Line 0892 RRK-BCK Rebuild | Rebuild 3.4 miles of 115 kV line between Red Rock and Battle Creek substations. Portions of this line are double circuited with 0893, this project will separate the two circuits. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2023-12-15 | 115 | 5237000
West | XEL | 23474 | Line 0736 Arden Hills - Lawrence Creek Rebuild | Rebuild 33 miles of line 0736 69 kV from Arden Hills - Lawrence Creek and add OPGW. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2025-12-31 | 69 | 20000000
West | XEL | 23475 | Line 0721 STR 71 to 476 Rebuild | Rebuild 22 miles line 0721 69 kV from Structure 71 - Structure 476. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2025-12-31 | 69 | 11000000
West | XEL | 23476 | Line 0822 Empire to STR 107 Rebuild | Rebuild 7 miles of line 0822 115 kV from Empire to Str 107 and add OPGW. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-12-31 | 115 | 6000000
West | XEL | 23477 | Line 0772 Prairie to MNPC Connection Rebuild | Rebuild 12 miles of line 0772 69 kV from Prairie - Emerado. | ND | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2025-12-31 | 69 | 6000000
West | XEL | 23479 | Iron River Substation Rebuild | Rebuild the existing Iron River substation to include a 115 kV ring bus and new 115/34.5 kV transformer. | WI | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-06-01 | 115 | 7000000
East | ITCT | 23481 | S1007 Surplus Generator Interconnection | S1007 Surplus generator will utilize the existing POI established for J202 Starkey Wind Farm at the ITCT Dixon 120 kV substation. | MI | ITC Transmission |  | GIP |  | 2023-09-01 | 0 | 0
West | ITCM | 23483 | J1174 GIA - Bluebill TOIF | A new Bluebill 345 kV switching station will be constructed to interconnect projects J1174 and J1175. The Bison – Colby 345 kV line will be tapped and re-routed to new positions in the Bluebill station. The TOIF will include dead-end, disconnect switch, arresters, PT’s, relay panel, and associated equipment. | IA | ITC Midwest |  | GIP |  | 2025-06-30 | 345 | 864989
West | ITCM | 23484 | J1175 GIA - Bluebill TOIF | A new Bluebill 345 kV switching station will be constructed to interconnect projects J1174 and J1175. The Bison – Colby 345 kV line will be tapped and re-routed to new positions in the Bluebill station. The TOIF will include dead-end, disconnect switch, arresters, PT’s, relay panel, and associated equipment. | IA | ITC Midwest |  | GIP |  | 2025-06-30 | 345 | 864989
West | ITCM | 23485 | J1174 & J1175 MPFCA - Network Upgrades | A new Bluebill 345 kV switching station will be constructed to interconnect projects J1174 and J1175. The Bison – Colby 345 kV line will be tapped and re-routed to new positions in the Bluebill station. ITC will TO self-fund the Network Upgrades and will earn a return of and return on investment under a FSA for 90% of the cost. 10% of the Network Upgrades costs will be recovered under Attachment GG. | IA | ITC Midwest |  | GIP |  | 2025-06-30 | 345 | 16216106
West | XEL | 23486 | Inver Hills Substation - FRM13 | Replace busbar. | MN | Northern States Power (Xcel Energy) |  | Other | Reliability | 2023-03-01 | 115 | 200000
West | XEL | 23487 | Kohlman Lake Substation - FRM13 | Replace meter on breaker 5P106. | MN | Northern States Power (Xcel Energy) |  | Other | Reliability | 2022-12-31 | 115 | 50000
West | XEL | 23488 | Prairie Substation - FRM13 | Replace meter on breaker 5G8. | ND | Northern States Power (Xcel Energy) |  | Other | Reliability | 2022-12-31 | 115 | 50000
West | XEL | 23489 | Wilmarth Substation - FRM13 | Replace bushing current transformer on breaker 5S11 as well as switches 8S26B1, 8S25B, 8S25A, 8S26B1. | MN | Northern States Power (Xcel Energy) |  | Other | Reliability | 2022-12-31 | 115 | 550000
West | XEL | 23490 | Crystal Cave TR01 ELR | Replace Crystal Cave 161/115 kV TR01. | WI | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-12-31 | 161 | 3500000
West | XEL | 23491 | Parkers Lake TR10 ELR | Replace Parkers Lake 345/115 kV TR10 with a single 3 phase transformer. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2022-12-31 | 345 | 3500000
West | XEL | 23492 | Pine Lake TR03 ELR | Replace Pine Lake 161/115 kV TR03. | WI | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2027-12-31 | 161 | 3500000
West | XEL | 23493 | Monticello TR06 & TR10 ELR | Replace Monticello 345/230 kV TR06 and 345/115 kV TR10. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2025-09-16 | 345 | 7000000
West | XEL | 23494 | Prairie Island TR10 ELR | Replace Prairie Island 345/161 kV TR10 | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-12-15 | 345 | 3500000
West | XEL | 23495 | Pipestone TR05 & TR06 ELR | Replace Pipestone TR05 and TR06 115/69 kV transformers. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-12-31 | 115 | 3000000
West | XEL | 23496 | Inver Grove TR02 ELR | Replace Inver Grove 115/69 kV TR02. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2025-12-31 | 115 | 2500000
West | XEL | 23497 | Lake Pulaski TR05 ELR | Replace Lake Pulaski 115/69 kV TR05. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2026-12-31 | 115 | 2500000
West | XEL | 23498 | Minnesota Valley TR11 ELR | Replace Minnesota Valley 115/69 kV TR11. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2027-12-31 | 115 | 2500000
West | XEL | 23499 | Osprey TR05 ELR | Replace Osprey 115/69 kV TR05. | WI | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2027-12-31 | 115 | 3500000
Central | AmerenMO | 23500 | New Morris Solar interconnection (J1182) | One 345 kV terminal in the Zachary substation. The terminal will consist of all necessary terminal equipment to connect the J1182 leadline to the Zachary substation bus. J1182 is a 250 MW Solar project interconnecting to the Zachary substation 345 kV bus | MO | Ameren Services Company |  | GIP |  | 2024-11-01 | 345 | 2593000
West | XEL | 23501 | Line 0840 Elliot Park Pumping Plants | Upgrades to pumping station for HPFF. | MN | Northern States Power (Xcel Energy) |  | Other | Reliability | 2025-06-01 | 115 | 5000000
West | XEL | 23502 | Line 0771 Rebuild | Rebuild 2 miles of line 0771 from Young America - Carver County 69 kV substations and add OPGW. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-06-30 | 69 | 1500000
West | XEL | 23503 | Line 0719 Winthrop to STR 45 Rebuild | Rebuild 1.5 miles of line 0719 69 kV from Winthrop - Structure 45. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2025-12-31 | 69 | 2000000
Central | AmerenIL | 23504 | Rebuild Vermillion-Tilton Energy Center 138 kV line (1572) | Rebuild the 11.4 mile Vermillion-Tilton Energy Center-1572 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL | Ameren Services Company |  | Other | Reliability | 2024-12-01 | 138 | 13000000
Central | AmerenIL | 23505 | Relocate Bosco 138 kV substation (fka Murdock) | Relocate station due to the contamination, build a ring bus at a new location. | IL | Ameren Services Company |  | Other | Age and Condition | 2025-06-01 | 138 | 14400000
West | XEL | 23506 | Gingles TR05 ELR | Replace Gingles 115/69 kV TR05. | WI | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2025-12-31 | 115 | 2500000
West | XEL | 23508 | Line 5503 Cherry Creek - Great Plains - West Sioux Falls Rebuild | Rebuild 2 miles 115 kV Cherry Creek - Great Plains. Rebuild 1 mile 115 kV Great Plains - West Sioux Falls (single circuit portion) as bifurcated double circuit. Rebuild 0.7 mile 115 kV Great Plains - West Sioux Falls (double circuit portion). | SD | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2024-06-01 | 115 | 5000000
West | XEL | 23509 | Junction Mill Substation | Build new Junction Mill substation near 3-terminal 115kV connection with Glenmont, River Falls and Crystal Cave lines. In addition, this substation will install a new 115/69kv transformer and change the operating voltage of the River Falls tap to 69kV. The transformation at the River Falls substation will be removed as well any 115kV equipment. | WI | Northern States Power (Xcel Energy) |  | Other | Reliability | 2024-06-01 | 115 | 12000000
West | ITCM | 23510 | Rock Creek T3 Replacement | The existing Rock Creek T3 transformer is at the end of its useful life and in need of replacement. T3 will be replaced with a new 150 MVA 161/69 kV transformer with LTC. In addition, there is an 800 amp relay thermal limit on T3, so the existing relaying needs to be upgraded to remove the 800 amp thermal limit to allow full use of the 150 MVA transformer rating. | IA | ITC Midwest |  | Other | Age and Condition | 2025-12-31 | 161 | 4267194
West | ITCM | 23511 | Grinnell South 69kV Substation & 20MVAR Cap | IPL has notified ITC that they will be rebuilding the Grinnell South substation in a new location directly south of the existing substation location which will replace the existing Grinnell South substation. ITC will construct the 69 kV portion of Grinnell South in the new location including two busses, two line breakers, and a bus tie breaker. ITC will also install a new 69 kV capacitor bank at the new Grinnell South substation to provide improved area voltage support for existing and potential additional future load growth in the area. | IA | ITC Midwest |  | Other | Load Growth | 2025-12-31 | 69 | 5637400
West | XEL | 23512 | Prairie View Substation | Rebuild the Wheaton Substation on a new location with a 4-row breaker and a half 161 kV configuration in order to separate it from the Generation facility. | WI | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2026-06-01 | 161 | 17000000
West | XEL | 23513 | Emerald Substation | Line W3209 – Replace 3 way switch with new 161kv to 115kv substation. Rebuild 1 mile of double circuit 161-115kv line to single circuit 115kv line. Retire Pine Lake 161kv to 115kv yard. | WI | Northern States Power (Xcel Energy) |  | Other | Reliability | 2025-06-15 | 161 | 12000000
West | XEL | 23514 | Sauk Centre North Interconnection | Build three 1-way switches on line 0794 to accommodate new Sauk Centre Municipal distribution substation. | MN | Northern States Power (Xcel Energy) |  | Other | Load Growth | 2024-12-31 | 69 | 800000
West | XEL | 23515 | Eau Claire TR09 Replacement | Upgrade Eau Claire TR09. | WI | Northern States Power (Xcel Energy) |  | Other | Reliability | 2025-06-01 | 345 | 8000000
Central | AmerenMO | 23526 | Reconfigure Warrenton 161 kV substation | Install a 161 kV Ring bus at Warrenton Substation | MO | Ameren Services Company |  | Other | Reliability | 2024-12-01 | 161 | 15000000
West | XEL | 23527 | Line W3428 Clear Lake - New Richmond Rebuild | Rebuild 19.8 miles of line W3428 from Clear Lake - New Richmond. | WI | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2023-03-15 | 69 | 10000000
West | XEL | 23528 | Gaiter Lake Substation | Build new Gaiter Lake substation in Waseca to pick up load off of Clarks Grove, Meridan, and Waseca substations. Retire Clarks Grove and Meridan substations. | MN | Northern States Power (Xcel Energy) |  | Other | Age and Condition | 2025-10-15 | 69 | 7800000
Central | PPI | 23532 | New Pleasant View-Ishi 69 kV Line | New Pleasant View to Ishi 69 kV line in SEC. This line has three line segments: 1) New Pleasant View-Moweaqua 69 kV Line 2) New Moweaqua-Yantisville 69 kV Line 3) New Yantisville-Henton 69 kV Line | IL | Prairie Power, Inc. |  | Other | Reliability | 2029-12-31 | 69 | 23498000
West | ITCM | 23546 | Jefferson County 161kV Substation Rebuild | The relaying and SCADA equipment at the Jefferson County substation is nearing the end of its useful lifespan. In addition, the existing 161/69 kV transformer does not have a high side protective device, there is not adequate space to add it, and the existing 161 kV bus configuration does not allow the flexibility needed. Due to this, ITC will rebuild the 161 kV bus at Jefferson to a 3 position ring bus configuration and will replace all existing relays at the station except on two 69 kV lines going towards NEMO. ITC will also replace and upgrade existing SCADA equipment and add 69 kV line PTs on all lines except those going towards NEMO. | IA | ITC Midwest |  | Other | Reliability | 2025-12-31 | 161 | 7922995
West | XEL | 23547 | 21829 - South Dayton Interconnection | New GRE interconnection (MTEP ID 21829). Xcel will own high side of new sub with an in-and-out configuration on the Elm Creek - Champlin Tap 115kV line. | MN | Northern States Power (Xcel Energy) |  | Other | Load Growth | 2023-06-15 | 115 | 5000000
Central | PPI | 23567 | Rebuild Pearl-Kampsville 69 kV Line | Rebuild Pearl-Kampsville 69 kV line | IL | Prairie Power, Inc. |  | Other | Age and Condition | 2029-12-31 | 69 | 7285000
Central | IPL | 23568 | Replace Southwest 138 kV #16 Breaker | Replacement of one (1) 138 kV breaker at Southwest #16 | IN | Indianapolis Power & Light Company |  | BRP |  | 2025-12-31 | 138 | 900000
Central | BREC | 23569 | New [BREC] McCracken-[GLH] Joppa 161 kV Tie Line | This relatively small and confined project will consist of one additional terminal at an existing Big Rivers’ substation (Big Rivers owned), 2 miles of 161 kV transmission line (Big Rivers owned), and a three bay switching station (GLH owned). Without this proposed project transmission voltages are very near a contingent TPL violation with normal forecasted load levels. Loads associated with extreme weather or a small load increase in this region will cause a contingent TPL violation. In addition to the TPL violation relief and providing needed capacity in the western part of Big Rivers system, the proposed project will alleviate the need to purchase transmission service from TVA. During contingent conditions, the majority of Jackson Purchase Energy (distribution cooperative served by Big Rivers) is dependent on one 161 kV interconnection with TVA. Therefore, Big Rivers must purchase transmission service as available from TVA during various planned and unplanned outage scenarios. The proposed project will provide a second MISO source to this load and alleviate the reliance on TVA transmission service and eliminate the need to purchase such service. This project will coincide with project ID 23827 submitted by GridLiance Heartland. | KY | Big Rivers Electric Corporation |  | Other | Reliability | 2025-07-02 | 161 | 5300000
West | MEC | 23570 | Valley Trail 161 kV Substation | Construct Valley Trail 161-13.2 kV Sub and Line Taps | IA | MidAmerican Energy Company |  | Other | Load Growth | 2026-06-01 | 161 | 9500000
West | MEC | 23571 | Humboldt 69 kV Reconfiguration | Network Humboldt Central Substation and establish tie with Corn Belt's Weaver Switching Station | IA | MidAmerican Energy Company |  | Other | Reliability | 2027-12-01 | 69 | 9900000
West | MEC | 23572 | Franklin: Replace 161 kV Breaker 9210 | Franklin: Replace 161 kV Breaker 9210 | IA | MidAmerican Energy Company |  | Other | Other Local Needs | 2023-12-01 | 161 | 500000
West | MEC | 23573 | Black Hawk: 161-69 kV, 167 MVA Transformer | Replace existing 161-69 kV, 50 MVA Transformer | IA | MidAmerican Energy Company |  | Other | Reliability | 2025-12-01 | 161 | 9000000
East | WPSC | 23574 | Pellston to Cross Village | Rebuild and upgrade 9 miles of 69kV line to 138 kV standard with steel poles, 336ACSS conductor, and OPGW. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Age and Condition | 2028-12-31 | 69 | 9500000
East | WPSC | 23575 | Pellston Relocation and Upgrades | Project will replace capacity limiting equipment and existing protection system at the Pellston substation and relocate the Pellston to Cross Village line to improve reliability on that line. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Reliability | 2027-12-31 | 69 | 1600000
West | MEC | 23590 | Granger Substation 161 kV Line Breakers | Install 161 kV line breakers and associated relaying | IA | MidAmerican Energy Company |  | Other | Reliability | 2027-12-01 | 161 | 2100000
West | MEC | 23591 | Nashua Tap-Plainfield Junction 69 kV Rebuild | Replace conductor on section of Nashua Tap-Plainfield Junction 69 kV line using existing right of way | IA | MidAmerican Energy Company |  | Other | Age and Condition | 2024-12-31 | 69 | 2500000
West | MEC | 23592 | Floyd Substation: Add 69 kV Bus PTs, Remove Wave Trap and Incorporate Fiber | Add 69 kV Bus PTs; remove wave trap and employ fiber for Floyd-Emery 161 kV line relaying | IA | MidAmerican Energy Company |  | Other | Reliability | 2024-12-31 | 161 | 350000
West | MEC | 23593 | Charles City North add 69 kV Breakers | Charles City North Add 69 kV Breakers | IA | MidAmerican Energy Company |  | Other | Reliability | 2027-12-31 | 69 | 800000
East | WPSC | 23594 | Scottville RTU Upgrade | Replace communication equipment at the Scottville substation. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Age and Condition | 2025-12-31 | 69 | 40000
East | WPSC | 23595 | Weidman RTU Upgrade | Replace communication equipment at the Weidman substation. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Age and Condition | 2025-12-31 | 69 | 40000
West | MDU | 23596 | Glenham rebuild | Rebuilding the current Glenham substation 230/115/41.6 kV. | SD | Montana-Dakota Utilities Company |  | Other | Age and Condition | 2025-10-31 | 230 | 23500000
West | MEC | 23608 | E. 29th & Hubbell 69 kV Expansion and Line Tap | Expand substation steel for a second 69 kV line tap | IA | MidAmerican Energy Company |  | Other | Reliability | 2024-06-01 | 69 | 500000
West | MEC | 23609 | Delaware Substation 161 kV Line Breakers | Install 161 kV line breakers and associated relaying | IA | MidAmerican Energy Company |  | Other | Reliability | 2025-06-01 | 161 | 1900000
West | MEC | 23610 | Washburn: 161-69 kV, 125 MVA Transformer | Replace existing 161-69 kV, 50 MVA Transformer | IA | MidAmerican Energy Company |  | Other | Reliability | 2026-12-01 | 161 | 7500000
West | ITCM | 23611 | J982 Affected System Upgrades | MISO Facilities Study for Affected System upgrades for project J982, a 300 MW wind-powered generating facility with proposed interconnection on MEC’s Obrien County – Kossuth 345kV circuit. The system impact study has indicated the interconnection of project J982 will require sag mitigation on the Fox Lake to Rutland 161 kV circuit. | MN | ITC Midwest |  | GIP |  | 2023-09-01 | 161 | 338000
East | WPSC | 23612 | Altona Protection System Upgrade | Replace the control building to install modern digital relays and install an additional circuit breaker to increase reliability on Altona to Morley transmission line. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Age and Condition | 2026-12-31 | 69 | 1500000
East | WPSC | 23613 | 2025 WPSC Fiber Retrofit | Installation of fiber on recently rebuilt (post 2006) 138kV structures utilizing ADSS (All Dielectric Self Supporting) and OPGW (Optical Ground Wire). | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Reliability | 2025-12-31 | 69 | 5000000
East | WPSC | 23614 | Casnovia to Cedar Springs Rebuild | Rebuild and upgrade 11 miles of 69kV line to 138 kV standard with steel poles, 795ACSS conductor, and OPGW. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Age and Condition | 2027-12-31 | 69 | 9250000
East | WPSC | 23615 | Copemish Protection System Upgrade | Replace the circuit breaker and its associated controls and protective relaying, bringing the station to Wolverine’s standard for 138kV transmission operation. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Age and Condition | 2026-12-31 | 69 | 1500000
East | WPSC | 23616 | Gaylord Protection System Upgrade | Upgrade existing electromechanical relays with digital relays. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Age and Condition | 2026-12-31 | 138 | 800000
East | WPSC | 23617 | Hayes Junction to Hayes Rebuild | Rebuild and upgrade 12 miles of 69kV line to 138 kV standard with steel poles, 336ACSS conductor, and OPGW. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Age and Condition | 2028-12-31 | 69 | 11850000
East | WPSC | 23618 | Lake County Protection System Upgrade | Upgrade Lake County Protection system with new line relays. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Reliability | 2024-12-31 | 138 | 75000
East | WPSC | 23619 | Mulliken Jct to Grand Ledge Rebuild | Rebuild and upgrade 4 miles of 69kV line to 138 kV standard with wood poles, 336ACSS conductor, and OPGW. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Age and Condition | 2027-12-31 | 69 | 4250000
East | WPSC | 23620 | North Shade Protection System Upgrade | Upgrade existing electromechanical relays with digital relays. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Age and Condition | 2026-12-31 | 69 | 1250000
East | WPSC | 23621 | Redwood RTU Upgrade | Replace communication equipment at the Redwood substation. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Age and Condition | 2024-12-31 | 69 | 150000
West | MEC | 23628 | Waverly Junction: Reconfigure 69 kV Terminals | Reconfigure 69 kV line terminals to eliminate tapped substation transformer | IA | MidAmerican Energy Company |  | Other | Reliability | 2024-06-01 | 69 | 1300000
West | MEC | 23629 | Charles City South-Nashua Tap 69 kV Rebuild | Rebuild Charles City South-Nashua Tap 69 kV Line on new Right of Way | IA | MidAmerican Energy Company |  | Other | Age and Condition | 2025-12-01 | 69 | 7700000
West | MEC | 23630 | Wida-Streeter 69 kV Rebuild | Replace conductor on MidAmerican section of Wida-Streeter 69 kV line. | IA | MidAmerican Energy Company |  | Other | Age and Condition | 2024-04-01 | 69 | 1000000
East | WPSC | 23631 | Petosky Protection System Upgrade | Upgrade existing electromechanical relays with digital relays. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Age and Condition | 2026-12-31 | 69 | 1000000
Central | AmerenIL | 23632 | New Beehive-Dupo Ferry 138 kV line | Install new Beehive to Dupo Ferry 138 kV line. Add breaker to new Dupo Ferry ring bus. Add position at Beehive. | IL | Ameren Services Company |  | Other | Reliability | 2024-12-01 | 138 | 6300000
West | MDU | 23633 | Ellendale load addition | MDU has new customer requesting service at Ellendale, ND for total demand of 180 MW. MDU will serve the customer from the existing Ellendale 2 transformer's 34.5 kV tertiary. An overhead line will be built from the tertiary of the transformer to the customers sub. | ND | Montana-Dakota Utilities Company |  | Other | Load Growth | 2023-02-15 | 34.5 | 3060359.76
West | MDU | 23634 | Wishek rebuild | Will be expanding the 230 kV to add new wind farm and rebuilding the 115 and 41.6 kV. | ND | Montana-Dakota Utilities Company |  | Other | Age and Condition | 2025-12-31 | 230 | 18650000
Central | AmerenIL | 23635 | New Baldwin Solar Interconnection (J1202) | Install one 345 kV terminal in the Baldwin substation. The terminal will consist of all necessary terminal equipment to connect the J1202 leadline to the Baldwin substation 345 kV bus. | IL | Ameren Services Company |  | GIP |  | 2024-06-01 | 345 | 150000
West | ITCM | 23636 | ITCM Customer Interconnects (short lead time) 2025 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL | ITC Midwest |  | Other | Load Growth | 2025-12-31 | 345 | 3600000
Central | AmerenIL | 23637 | New Hennepin Solar Interconnection (J1200) | Install one 138 kV terminal in the Putnam substation. The terminal will consist of all necessary terminal equipment to connect the J1200 leadline to the Putnam substation 138 kV bus. Install upgrades at Putnam substation. Raise existing PUTN-HKOK-1556, PUTN-HENN-1771, PUTN-HENN-1765, PUTN-ESK-1757, and PUTN-BURE-1552 transmission lines | IL | Ameren Services Company |  | GIP |  | 2024-06-01 | 138 | 1800000
West | MEC | 23655 | Shenandoah: Replace 69 kV Breakers 601 & 602 | Replace 69 kV breakers at Shenandoah Substation | IA | MidAmerican Energy Company |  | Other | Age and Condition | 2024-12-01 | 69 | 600000
West | MEC | 23675 | Avoca: Install 69 kV Breaker on 161-69 kV Transformer 8T3 and 161 kV & 69 kV Breaker Replacements | Install a 69 kV breaker on the low-side of Avoca 161-69 kV Transformer 8T3, replace/rolocate Avoca Breakers 622 and 623 to accommodate new 69 kV breaker and replace Breakers 801, 802 and 620 due to condition | IA | MidAmerican Energy Company |  | Other | Reliability | 2025-12-01 | 161 | 4100000
Central | AmerenIL | 23676 | New Coffeen Solar Interconnection (J1201) | Install one 138 kV terminal in the Coffeen North substation. The terminal will consist of all necessary terminal equipment to connect the J1201 leadline to the Coffeen North substation 138 kV bus. Raise existing Coffeen North-Pana 345kV Transmission line. 44.2 MW solar generator | IL | Ameren Services Company |  | GIP |  | 2024-06-01 | 345 | 1500000
West | ITCM | 23677 | ITC Midwest Asset Replacement Program 2025 | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA,MN,IL | ITC Midwest |  | Other | Age and Condition | 2025-12-31 | 345 | 38400000
Central | AmerenIL | 23678 | New Duck Creek Solar Interconnection (J1199) | Install one 345 kV terminal in the Duck Creek substation. The terminal will consist of all necessary terminal equipment to connect the J1199 leadline to the Duck Creek substation 345 kV bus. Upgrade control and relay fiber panel at the Duck Creek substations as well as the remote end substatio | IL | Ameren Services Company |  | GIP |  | 2024-06-01 | 345 | 2500000
West | GRE | 23679 | Cromwell Breaker Replacement | Replace 115 kV circuit breakers 13L and 26L. | MN | Great River Energy |  | Other | Age and Condition | 2023-11-01 | 115 | 1359267.96
West | GRE | 23680 | Frog Creek Breaker Replacement | Replace Circuit Switcher FC161-10 at Frog Creek substation with breaker and add disconnect switches. Replacement of Panel #2 relaying to also be included. | MN | Great River Energy |  | Other | Age and Condition | 2025-01-31 | 69 | 1030196.45
West | GRE | 23681 | Riverton Breaker Replacement | This project will remove 69kV bus differential relaying, replace GE-T60 with SEL-487E using existing panel 7, protect the 69kV bus zone with the transformer relays, replace Riverton IR8600 RTU with Cybectec RTU, replace Westinghouse 3-phase 115kV PT with 3 single phase CCVTs on 115kV bus, and replace the 115-kV 25WB1 oil breaker. In addition to this work there will also be some 69-kV and 115-kV bus work and jumper modifications. | MN | Great River Energy |  | Other | Reliability | 2024-06-30 | 115 | 849708.75
West | GRE | 23682 | Princeton Breaker Addition | Add breaker and relaying to address incomplete topology and relaying load limit issue at Princeton. The plan to accommodate this work is to bring the OL line around to the west bay of the four structure and place breaker in PT occupied bay. Bus PT’s will be replaced and relocated to a different location on site to accommodate the breaker addition in west bay. This project will also require that we rebuild to OL line tapping into the north by bringing it in to the west bay with the characteristics of the new line rebuild plan of the OL line. | MN | Great River Energy |  | Other | Other Local Needs | 2024-06-21 | 69 | 763118.2
West | MEC | 23683 | Sheldon: 69 kV Breaker and Relay Replacements | Replace Sheldon 69 kV Breakers 7730, 7740, 7880 and 7890 and associated disconnect switches and relaying | IA | MidAmerican Energy Company |  | Other | Age and Condition | 2024-10-01 | 69 | 2800000
West | ITCM | 23684 | Kittyhawk 69kV Substation Interconnection | IPL has notified ITC that they will be rebuilding the Kittyhawk substation in the existing location to allow the addition of a 2nd IPL distribution transformer. ITC will construct the 69 kV portion of Kittyhawk which will include two busses/single box structures, two line breakers, and a bus tie breaker. | IA | ITC Midwest |  | Other | Load Growth | 2025-12-31 | 69 | 3902741
West | MEC | 23685 | Neal North-Southbridge Tap-Knox-State Steel Tap 69 kV Line Rebuild | Rebuild approximately 9 miles of line | IA | MidAmerican Energy Company |  | Other | Age and Condition | 2024-12-05 | 69 | 8600000
West | MEC | 23686 | Obrien County-Hospers 161 kV Line, Obrien County 345-161 kV Transformer Addition & Hospers 161-69 kV Transformer Addition | Construct new 161 kV line from Obrien County Substation to Hospers Substation, expand Obrien County Substation to install 345-161 kV, 560 MVA transformer and 161 kV bus and expand Hospers Substation to install 161-69 kV, 167 MVA transformer and 161 kV bus | IA | MidAmerican Energy Company |  | BRP |  | 2026-12-01 | 345 | 45000000
West | MEC | 23687 | Storm Lake Industrial 69 kV Line Taps | Construct 69 kV line taps into new Storm Lake Industrial 69-13.8 kV Substation | IA | MidAmerican Energy Company |  | Other | Load Growth | 2026-12-01 | 69 | 800000
West | MEC | 23688 | Macksburg - Winterset 161 kV Reconductor | Reconductor the 161 kV line from Macksburg to Winterset. Line identified as a constraint in the MTEP22 generator deliverability analysis. | IA | MidAmerican Energy Company |  | BRP |  | 2027-06-01 | 161 | 12500000
West | MEC | 23689 | Sub 93 Louisa: Replace 345 kV Breaker 934 | Replace 345 kV breaker in Sub 93 (Louisa) ring. | IA | MidAmerican Energy Company |  | Other | Age and Condition | 2023-04-07 | 345 | 390000
West | MEC | 23690 | Quad Cities Enron Substation: Install 161 kV Line Switches | Install new 161 kV line switches on both sides of the QEN Quad City Enron substation to increase switching flexibility. | IA | MidAmerican Energy Company |  | Other | Reliability | 2025-12-31 | 161 | 500000
West | MEC | 23691 | Riverdale 161-13.2 kV Substation | Construct new 161-13.2 kV substation and 161 kV line taps. | IL | MidAmerican Energy Company |  | Other | Reliability | 2026-12-31 | 161 | 4100000
West | MEC | 23692 | Sub 28 Add 161 kV Line Breakers and Install New Control Building | Install new 161 kV line breakers and new control building to replace existing control enclosure. | IL | MidAmerican Energy Company |  | Other | Reliability | 2027-12-31 | 161 | 3700000
West | ITCM | 23693 | J1132 GIA Network Upgrades | Expansion of the Creston Roundhouse 69kV bus with an additional box structure. | IA | ITC Midwest |  | GIP |  | 2024-06-01 | 69 | 316693
West | MEC | 23694 | Wall Lake 161 kV Terminal Equipment Upgrades | Replace limiting jumpers on Wright - Wall Lake and Wall Lake - Franklin 161 kV line terminals. | IA | MidAmerican Energy Company |  | Other | Other Local Needs | 2026-12-31 | 161 | 100000
East | ITCT | 23697 | Beck - Stephens 120 kV Sag Remediation | Remediate the sag limit on the Beck - Stephens 120 kV circuit up to a minimum summer emergency rating of 242 MVA. | MI | ITC Transmission |  | BRP |  | 2026-12-31 | 120 | 540000
West | MEC | 23699 | Gifford Road 161-13.2 kV Substation and 161 kV Line Taps | Construct Gifford Road 161-13.2 kV Sub and Line Taps | IA | MidAmerican Energy Company |  | Other | Load Growth | 2026-09-01 | 161 | 5500000
West | ITCM | 23701 | J1135 GIA Huntwoods 69 kV TOIF | Install equipment dedicated to the J1135 generating facilities. The J1135 line will be connected to a new breaker position on the Huntwoods 69 kV bus. TOIF cost to include the new breaker, switches, relay panel and any new associated equipment. | IA | ITC Midwest |  | GIP |  | 2027-06-01 | 69 | 558384
West | MEC | 23703 | J982 POI New 345 kV Interconnection Substation and 345 kV Line Taps | Construct new 345 kV POI substation and 345 kV line taps for J982 wind farm. | IA | MidAmerican Energy Company |  | GIP |  | 2025-06-01 | 345 | 15250000
East | METC | 23704 | Abbe Jct - Mio 138kV Sag Remediation | Remediate sag on the 266.8 ACSR up to conductor’s limit on the Abbe Jct. – Mio Dam section of the Airport – Mio Dam 138 kV circuit. | MI | METC |  | BRP |  | 2026-12-31 | 138 | 1700000
West | MP | 23707 | Maturi Substation Expansion | The Maturi Expansion Project will add three circuit breakers to allow for the transmission line to be looped in and out of the Maturi Substation. | MN | Minnesota Power (Allete, Inc.) |  | Other | Other Local Needs | 2025-12-31 | 115 | 3580000
West | MP | 23708 | Mahtowa Substation Expansion | The Mahtowa Expansion project will add 3-115 kV circuit breakers to reconfigure the existing Mahtowa Substation into a 3 position ring bus. | MN | Minnesota Power (Allete, Inc.) |  | Other | Age and Condition | 2027-12-31 | 115 | 2500000
East | METC | 23709 | Campbell – Blendon 138kV Loop Into Tyler | Loop the Campbell - Blendon 138kV line into Tyler to create Campbell - Tyler and Tyler - Blendon 138kV lines. Install (3) new breakers at Tyler and OPGW from Port Sheldon to Campbell. | MI | METC |  | BRP |  | 2027-06-01 | 138 | 6916517
West | MRES | 23710 | Atlantic 161 kV Breaker Replacement | Replace two 161 kV oil filled breakers with SF6. | IA | Missouri River Energy Services (MRET) |  | Other | Age and Condition | 2024-01-01 | 161 | 800000
West | XEL | 23712 | Lyon County Substation - FRM13 | Replace 5N130 actuator secondary current limitation to increase TR9 rating back up to it's transformer limits. | MN | Northern States Power (Xcel Energy) |  | Other | Reliability | 2023-09-01 | 345 | 300000
Central | WVPA | 23714 | Rebuild Citizens 69kV Line (Groups C & E) | Rebuild 69kV line group on CEC 69 kV System - Phase 2 | MO | Wabash Valley Power Association, Inc. |  | Other | Age and Condition | 2024-12-31 | 69 | 675000
Central | WVPA | 23715 | New Charmin Bulk 161 kV Sub. Breakers | Add breakers to Charmin Bulk to have 2 separate 161kV feeds from Trail of Tears. | MO | Wabash Valley Power Association, Inc. |  | Other | Reliability | 2024-02-28 | 161 | 4485000
West | GRE | 23717 | Deer River Breaker Replacement | Replace breakers 21NB1,2 & 3. Oil containment and SSVT relocation project is be combined with this project to create more efficiencies with project execution. Replace bus PTs as well due to relay prioritization recommendation. Replace single phase 115kV CCVT with 3 single-phase CCVTs. Move Zemple line relays to the 115kV CTs (current transformers) and CCVTs. Replace EEE and internal equipment, address bus work and jumper issues, and fix wood high side dead-end. | MN | Great River Energy |  | Other | Age and Condition | 2025-04-09 | 69 | 3823670.01
West | GRE | 23718 | Rush City Ring Bus Upgrade | This project will establish a 230 kV ring bus topology at Rush City. For GRE to address the rating exceedances experienced with the current shared breaker position, GRE will add breakers and associated equipment/relaying/etc. to the 230-kV Rush City bus between the Linwood, Red Rock, and Rock Creek lines | MN | Great River Energy |  | BRP |  | 2025-03-27 | 230 | 4013958.83
West | MEC | 23719 | Oakland: Add 69 kV, 12 MVAR Capacitor Bank and 69 kV Line Breakers | Install 69 kV, 12 MVAR capacitor bank and install 69 kV line breakers at Oakland Substation. | IA | MidAmerican Energy Company |  | Other | Reliability | 2026-06-01 | 69 | 5000000
West | MEC | 23720 | Hickory Avenue-Sioux Center 69 kV Line & Substation Line Terminals | Construct new 69 kV line from Hickory Avenue Substation to Sioux Center Substation. Expand Hickory Avenue and Sioux Center Substations to install new 69 kV line terminals. | IA | MidAmerican Energy Company |  | BRP |  | 2025-06-01 | 69 | 12000000
West | MEC | 23721 | Monona: Replace 161 kV Transformer | Replace the existing Monona 161-69 kV transformer with a 125 MVA unit. Convert Monona 161 kV bus to a ring bus configuration. Also, replace two 69 kV breakers and upgrade associated terminal equipment | IA | MidAmerican Energy Company |  | Other | Reliability | 2025-12-01 | 161 | 7000000
West | ITCM | 23722 | J1132 GIA TOIF | TOIF includes facilities and equipment dedicated to the Generating Facility including; 69kV switch | IA | ITC Midwest |  | GIP |  | 2024-06-01 | 69 | 40968
West | MEC | 23723 | Edgington 161-13.2 kV Substation | Construct new 161-13.2 kV sub and 161 kV line taps. Install fiber for communication and protective relaying. | IL | MidAmerican Energy Company |  | Other | Reliability | 2027-12-31 | 161 | 10500000
West | MEC | 23724 | Pomeroy 161 kV Substation 69 kV Breaker Replacement and Addition | Replace 69 kV breaker 7290. Convert 34.5 kV system to 69 kV due to condition. Expand Pomeroy 69 kV bus to accommodate additional 69 kV line terminal and add 69 kV bus differential relaying. | IA | MidAmerican Energy Company |  | Other | Age and Condition | 2023-12-31 | 161 | 600000
West | MEC | 23725 | Palo Alto 345 kV Substation Expansion for J877 | Add one new 345 kV line terminal at Palo Alto substation for J877 solar farm generator tie line. | IA | MidAmerican Energy Company |  | GIP |  | 2025-07-01 | 345 | 3800000
West | MEC | 23726 | Raun - Remsen 345 kV Line Uprate for DPP 2018 | Replace line structures to increase line rating. | IA | MidAmerican Energy Company |  | GIP |  | 2024-12-01 | 345 | 1200000
West | MEC | 23727 | Sub 56 161 kV Substation Expansion for J1131 | Add one new 161 kV line terminal at Sub 56 for J1131 solar farm generator tie line. | IA | MidAmerican Energy Company |  | GIP |  | 2027-09-01 | 161 | 2025000
West | XEL | 23728 | Owen Area Substation | Install new Owen Area Substation and convert Owen Distribution to 23.9 kV. | WI | Northern States Power (Xcel Energy) |  | Other | Load Growth | 2026-10-15 | 69 | 7854000
West | MEC | 23739 | Sub 42: Install 69 kV Line Switches | Install new 69 kV line switches on both sides of the Sub 42 substation to increase switching flexibility. | IL | MidAmerican Energy Company |  | Other | Reliability | 2027-12-31 | 69 | 800000
West | MEC | 23740 | Webster: Replace 161 kV Breaker 9250 | Replace 161 kV breaker 9250 in Webster substation | IA | MidAmerican Energy Company |  | Other | Other Local Needs | 2026-12-31 | 161 | 300000
West | MEC | 23741 | Wright 161 kV Terminal Equipment Upgrades | Replace 1200A substation terminal equipment on Webster - Wright and Wall Lake- Wright 161 kV line terminals. | IA | MidAmerican Energy Company |  | Other | Other Local Needs | 2026-12-31 | 161 | 150000
East | METC | 23743 | Deja Junction - Vestaburg 138 kV Rebuild | Rebuild 4.3 miles section between Deja Jct. and Vestaburg of the Eureka - Vestaburg 138kV line. | MI | METC |  | BRP |  | 2027-06-01 | 138 | 8822000
Central | SIGE | 23748 | Rebuild Y74-1 NE - Modification 69 kV | Rebuild ~1.75 miles of 69 kV line to increase rating for local operational flexibility and contingency support | IN | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | Other | Other Local Needs | 2024-12-31 | 69 | 710600
Central | SIGE | 23749 | Rebuild Y39 Cato - Winslow 69 kV | Rebuild ~9.5 miles of 69 kV due to aging infrastructure and pole condition (conductor size not changing) | IN | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | Other | Age and Condition | 2024-12-31 | 69 | 14130000
Central | SIGE | 23751 | Replace Maryland 69/12 kV T1 and New 69/12 kV T2 transformers | Replace existing 69/12 kV distribution T1 at Maryland due to age, and add new 69/12 kV T2 for distribution system contingency support | IN | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | Other | Reliability | 2024-12-31 | 69 | 3900000
Central | SIGE | 23755 | Replace Point Dist. 69/12 kV Transformer | Replace existing 69/12 kV distribution transformer due to age and condition | IN | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | Other | Age and Condition | 2024-12-31 | 69 | 12257000
Central | SIGE | 23756 | Replace Yankeetown 69/12 kV Transformer | Replace existing 69/12 kV distribution transformer T1 due to age and condition | IN | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | Other | Age and Condition | 2025-12-31 | 69 | 1102500
Central | SIGE | 23757 | New Garvin 69/12 kV Transformer | Add second 69/12 kV distribution transformer to provide distribution system support and contingency | IN | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | Other | Reliability | 2024-12-31 | 69 | 2500000
Central | SIGE | 23758 | New Bergdolt 138/12 kV Transformer | Add second 138/12 kV distribution transformer at the Bergdolt sub to provide distribution system and contingency support | IN | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. |  | Other | Reliability | 2024-12-31 | 138 | 2500000
West | XEL | 23760 | Nobles County Substation - FRM13 | Upgrade flexible busbar to increase ratings of TR9 and TR10. | MN | Northern States Power (Xcel Energy) |  | Other | Reliability | 2023-09-01 | 345 | 450000
West | GRE | 23761 | NW Litchfield Substation Tap | Tap Xcel’s Grove City – Litchfield Mun 69 kV line and Construct about 3 miles of 69 kV radial line to the high side of Meeker’s new NW Litchfield distribution substation. Install metering and telecom at the new sub. | MN | Great River Energy |  | Other | Load Growth | 2027-01-04 | 69 | 2969551
West | GRE | 23762 | Trimont Substation Retirement | Retire GRE assets in the Trimont SMEC distribution substation. | MN | Great River Energy |  | Other | Other Local Needs | 2024-04-30 | 69 | 243446.12
West | GRE | 23763 | Laketown Substation Tap | Install 3-way MOD 2000 A 115 kV switch on GRE’s MV-VTT and construct about 3 mile 115 kV transmission line from the three way switch to the high side of MVEC’s Laketown distribution substation. | MN | Great River Energy |  | Other | Load Growth | 2028-09-26 | 115 | 6308542
West | GRE | 23764 | Stinson Breaker Addition | Add low side breaker and SEL-487E secondary transformer relay. Move 69kV line relays to the 69kV CTs. New panel will be installed with SEL-487E and breaker controls. | MN | Great River Energy |  | Other | Reliability | 2025-09-02 | 69 | 664368
Central | GLH | 23765 | Rebuild Joppa-Joppa TS-Grahamville 161 line (854) | Rebuild the GridLiance Heartland portion of Joppa - Joppa TS - Grahamville 161 kV Ckt 854 three terminal line | KY,IL | Gridliance |  | Other | Age and Condition | 2026-12-31 | 161 | 21900000
Central | IPL | 23766 | New IU Health Substation 138 kV | New 138 kV, two 40 MVA transformer, three-breaker straight bus substation to serve customer load | IN | Indianapolis Power & Light Company |  | Other | Load Growth | 2023-12-31 | 138 | 15000000
Central | WVPA | 23779 | Rebuild Citizens 69kV Line (Groups A & B) | Rebuild 69kV line group on CEC 69 kV System - Phase 1 | MO | Wabash Valley Power Association, Inc. |  | Other | Age and Condition | 2023-12-31 | 69 | 1600000
Central | WVPA | 23780 | Relocate T23 69kV for Ameren Wittenberg-Whipple Line | Relocate T23 69kV to allow for Ameren's new 138kV Line (Wittenberg - Whipple) | MO | Wabash Valley Power Association, Inc. |  | Other | Reliability | 2023-12-31 | 69 | 4588146
West | GRE | 23781 | Shannon Breaker Addition | Add low side breaker and SEL-487E secondary transformer relay. Move 69kV line relays to the 69kV CTs. New panel will be installed with SEL-487E and breaker controls. Replace RTU. Replace two (2) 69kV Bus PTs (G.E. Superbute) | MN | Great River Energy |  | Other | Reliability | 2024-10-15 | 69 | 596069
West | GRE | 23782 | Dotson Corners Breaker Replacement | Replace 69kv oil breakers 860, 861, and 862 and associated equipment. | MN | Great River Energy |  | Other | Age and Condition | 2026-07-18 | 69 | 778017
West | GRE | 23783 | Maple Lake Breaker Replacement | Replace 69kV relaying & Breakers 1NB4 & 5 at the Maple Lake sub and associated equipment. | MN | Great River Energy |  | Other | Age and Condition | 2025-02-28 | 69 | 1158346
West | GRE | 23784 | Blackberry Breaker Addition | Remove existing switch 20NSM1 from Blackberry and replace with a circuit breaker and disconnect. OR Retain existing switch 20NSM1 at Blackberry and add a circuit breaker between the 115/69 kV transformer and switch 20NSM1. | MN | Great River Energy |  | Other | Other Local Needs | 2025-09-01 | 69 | 704466
East | METC | 23785 | J1550 Generator Interconnection | Install a new 138kV switching station. Install five 138kV breakers rated at 40kA and two bus sections. Cut the METC Batavia - Barton Lake and Batavia - J1320 (Coldwater) 138 kV circuits into the new 138 kV switching station. | MI | METC |  | GIP |  | 2025-03-03 | 138 | 15666608
South | Entergy-MS | 23786 | Ft Redwood - Rawhide 115kV Line | Tap the Entergy MS owned Flowers - Tinsley 115kV line and construct a new Cooperative Energy owned 115kV breaker switching station near Rawhide Road in Warren, MS. Construct a new 115kV line from a new Cooperative Energy owned breaker 115kV switching station near the Ft Redwood substation to the new Cooperative Energy owned switching station near Rawhide Road. Rebuild the existing Cooperative Energy owned Redwood - Ft Redwood 115kV line to support the industrial customer's full load during unplanned on-site generation outages. | MS | South Mississippi Electric Power Association |  | BRP |  | 2026-06-01 | 115 | 13492500
West | GRE | 23799 | Benton County 115 kV Breaker Replacement | Replace 115kV breakers 5N52 and 5N53. | MN | Great River Energy |  | Other | Age and Condition | 2023-11-16 | 115 | 526695.97
West | GRE | 23800 | Gilman - Milaca 69 kV Line Rebuild | Rebuild the JC line (18.93 miles) and switch SS2888 to 69kV with 477 ACSS . | MN | Great River Energy |  | Other | Reliability | 2026-08-21 | 69 | 12048956
West | GRE | 23801 | Cotton Substation Tap Rebuild | LCP is rebuilding the existing Cotton Distribution site to the north, the 115 kV (TT Line) will need to adjust to terminate on LCP’s new high side structure. The EEE from Goodland distribution substation will be placed at the new Cotton substation. | MN | Great River Energy |  | Other | Reliability | 2023-09-29 | 115 | 468450.72
West | GRE | 23802 | West Otsego Substation Tap | Install a 3-way 69 kV switch on GRE’s Otsego to Albertville 69 kV line and construct about 0.5 miles of 69 kV tap line to the high side of Wright Hennepin’s West of Otsego area substation. | MN | Great River Energy |  | Other | Load Growth | 2025-10-31 | 69 | 1283329
West | GRE | 23803 | Big Swan Capacitor Bank Addition | Add a new 40 MVAr capacitor on the extended 115-kV bus and replace 69-kV bus relaying, station power, and battery bank. | MN | Great River Energy |  | BRP |  | 2024-11-01 | 115 | 2633876.19
West | GRE | 23804 | Kimball Substation Tap | Install a 3-way 69 kV, 1200 A switch on Xcel Energy’s Kimball – Watkins 69 kV line and construct about 2 miles of 69 kV line with 477 ACSR conductor to the high side of Meeker’s new Kimball area distribution substation. | MN | Great River Energy |  | Other | Reliability | 2025-07-29 | 69 | 1036304.63
West | GRE | 23805 | Searles Capacitor Bank Retirement | Retire the 5.4 MVar Searles Capacitor Bank and associated components. | MN | Great River Energy |  | Other | Other Local Needs | 2023-08-31 | 69 | 116968.65
West | OTP | 23806 | OTP Lake Preston, SD Load Addition | OTP has a new customer requesting to be served in Lake Preston, SD. OTP will serve the new customer by extending a 115 kV line from our Hetland 115 kV substation to a new Lake Preston 115/34.5 kV substation. A new 115 kV line will be extended from the new Lake Preston 115/34.5 kV substation to Xcel's Brookings County 345/115 kV substation to create a 115 kV looped network. Capacitors will be installed at the new Lake Preston 115/34.5 kV substation for additional voltage support. The Facilities will consist of the following: 1. Hetland 115 kV substation termination addition 2. Approximate 9.5 mile 115 kV line from Hetland 115 kV substation to a new Lake Preston 115/34.5 kV substation 3. A new Lake Preston 115/34.5 kV substation with capacitors installed at the 115 kV level 4. Approximate 45 mile 115 kV line from the new Lake Preston 115/34.5 kV substation to Xcel's Brookings County 345/115 kV substation | SD | Otter Tail Power Company |  | Other | Load Growth | 2024-12-31 | 115 | 42600000
East | METC | 23807 | Alma - Vestaburg 138 kV Reconductor | Reconductor from Vestaburg to structure #2W8472 (~16.24 miles) from 954 ACSR to 954 ACSS. Also, upgrade 1590 SAC buses and 1200A switches at Alma position “477” to at least 455 MVA for summer emergency rating. | MI | METC |  | BRP |  | 2027-06-01 | 138 | 16660000
West | GRE | 23819 | Eidswold Substation Tap | New 115/12.47 kV substation for Dakota Electric Association (DEA) in the Elko New Market area. | MN | Great River Energy |  | Other | Load Growth | 2024-11-22 | 115 | 207813.44
South | Entergy-MS | 23820 | Gloster 13.8kV Delivery Point | A new 13.8kV feeder breaker will be added at the Entergy Mississippi LLC owned Gloster substation in order to serve Cooperative Energy's distribution member's new customer. | MS | South Mississippi Electric Power Association |  | Other | Load Growth | 2024-06-01 | 115 | 483800
West | GRE | 23821 | Penelope Capacitor Bank Retirement | Retire the 5.4 MVar Penelope Capacitor Bank and associated components. | MN | Great River Energy |  | Other | Other Local Needs | 2023-08-18 | 69 | 121351
West | GRE | 23822 | Matawan - St. Olaf Lake 69 kV Rebuild | Rebuild SW-MB line segments 1 and 2 (11.01 miles) (Matawan switches to St. Olaf Lake switches) to 69 kV minimum conductor size 477 ACSR would meet voltage and thermal considerations per planning. | MN | Great River Energy |  | Other | Age and Condition | 2026-09-07 | 69 | 7309835
West | GRE | 23823 | Burnsville Capacitor Bank Retirement | Remove existing cap bank and 5M201. Relocate breaker 5M198 to 5M201 location. Leave A3 for future termination. | MN | Great River Energy |  | Other | Other Local Needs | 2025-12-31 | 69 | 1022278
West | GRE | 23824 | Virginia Breaker Addition | Add low side breaker and SEL-487E secondary transformer relay. Move 69kV line relays to the 69kV CTs. New panel will be installed with SEL-487E and breaker controls. Replace RTU. Replace three (3) 69kV Bus Pts (G.E. Superbute) | MN | Great River Energy |  | Other | Reliability | 2024-11-11 | 69 | 555894.89
Central | IPL | 23825 | Reconfigure Rockville 138 kV substation | Conversion of Rockville 138 kV to a ring bus configuration | IN | Indianapolis Power & Light Company |  | BRP |  | 2024-12-01 | 138 | 8500000
Central | GLH | 23826 | Rebuild Joppa - Grahamville 161 line (804) | Rebuild the GridLiance Heartland portion of Joppa - Grahamville 161 kV Ckt 804 line | KY,IL | Gridliance |  | Other | Age and Condition | 2026-12-31 | 161 | 21900000
Central | GLH | 23827 | New 3-breaker ring bus substation | Build new 3-breaker ring bus switching station near Heath, KY bisecting Joppa - Shawnee 161 kV ckt 1 line with one terminal for connection with Big Rivers Electric McCracken station. Additionally, add 1-161 kV breaker at Joppa TS station and remove existing Joppa - Joppa TS - Shawnee 161 kV ckt 1 three terminal in Illinois by bringing line in and out of Joppa TS station. | KY | Gridliance |  | Other | Reliability | 2026-12-31 | 161 | 15900000
East | ITCT | 23828 | Hurst 120 kV 33.3 MVAR Capacitor | Install a 33.3 MVAR capacitor at bus 102, position HJ, with a new 120 kV, 40 kA synchronous breaker and associated disconnect switch. Install a 3000 A, 40 kA breaker at position HK on the Hurst – Genoa 120 kV circuit. | MI | ITC Transmission |  | BRP |  | 2025-06-01 | 120 | 3125000
East | METC | 23829 | Tompkins 345/138 kV Transformer #1 Replacement | Replace the 345/138 KV transformer #1 at Tompkins with a new, standard transformer of similar size. | MI | METC |  | Other | Age and Condition | 2026-12-31 | 345 | 5231640
East | METC | 23830 | MCV 138 kV Station Equipment Upgrade | Upgrade thermal relay at position "3141" to at least 620 MVA. | MI | METC |  | BRP |  | 2026-12-31 | 138 | 190000
Central | IPL | 23831 | New Gillette 138 kV Substation | New 138 kV, two 40 MVA transformer, three-breaker straight bus substation to serve customer load | IN | Indianapolis Power & Light Company |  | Other | Load Growth | 2024-11-01 | 138 | 15000000
Central | IPL | 23832 | New 138/13.2 Transformer at Thompson Substation | One new 138/13.2 kV 40 MVA distribution transformer with one new 138 kV breaker | IN | Indianapolis Power & Light Company |  | Other | Load Growth | 2023-11-01 | 138 | 16000000
Central | DEI | 23833 | New Edinburgh Industrial Park 69/12kV sub | DEI to construct high-side and loop 69kV lines into a new IMPA-owned Edinburgh Industrial Park substation; one 69/12kV 20MVA transformer; SCADA controlled MOLB 69kV line switches; two 69kV buses with a manually operated 69kV bus tie switch; 69kV connections from the 6950 and 69146 ckts. | IN | Duke Energy Corporation |  | Other | Reliability | 2025-06-01 | 69 | 4570000
Central | IPL | 23834 | New Valley Avenue 138 kV Substation | New 138 kV, two 40 MVA transformer, three-breaker straight bus substation to serve customer load | IN | Indianapolis Power & Light Company |  | Other | Load Growth | 2024-12-31 | 138 | 15000000
East | METC | 23835 | Pere Marquette Transformer 2 Replacement | Replace 345/138KV transformer 2 at Pere Marquette with a new, standard transformer of similar size. Install a 345 kV breaker and associated switch on the high side of the transformer. Also, install a 138 kV switch on the low side of the transformer. | MI | METC |  | Other | Age and Condition | 2026-12-31 | 345 | 8500000
West | ATC | 23836 | Perch Lake - National 138kV (468) Partial Retirement Project | Reconfigure 138kV line 468, from Perch-Lake to Presque Isle, by terminating into National SS to establish a new Perch Lake – National line. The remaining 23mi of line from National to Presque Isle will be retired. | MI | American Transmission Co. LLC |  | Other | Reliability | 2025-11-01 | 138 | 10400000
West | ATC | 23837 | Northeast - Revere Dr. 69kV (C-103), Uprate or Rebuild | Scope to include partial rebuild • Substation scope is for Revere Drive • Fiber optic installation | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2030-01-31 | 69 | 8600000
West | ATC | 23838 | High Falls – Mountain 69kV (Y-77), Rebuild & OPGW | Rebuild ~16.4 miles with new wire mesh wrapped wood pole structures and steel poles on foundation. - T2 4/0 Conductor and 48 Fiber OPGW. Conductor would meet and exceed planning needs. - Assumed to obtain Certificate of Authority (CA) application by rebuilding off center (30’ shift) and obtaining new 80’ easements typically. This is due to radial connection and uncertainty at this time if outage and distribution could be taken out for period of time. This may not be necessary once project gets into details and could result in savings as listed under alternatives. • Real Estate, Environmental, Vegetation - Majority of existing easements are 80' in width with VM and access rights. 2 DNR parcels will require permit/easement. - Project assumes new easements at $800k due to shift in ROW, rest through NEPA permit. - Shifting centerline will require going through the NEPA process (schedule impacts), likely an Environmental Assessment (EA), with a resulting Special Use Permit from the Chequamegon-Nicolet National Forest. - Federal forest lands currently limit herbicide spray, resulting in brush growing up along the Rights-of-Way. Within 2 years of next cycle and in decent shape with prior aerial saw work. | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2028-12-31 | 69 | 33000000
West | OTP | 23842 | OTP Wilmot - Peever Jct. 41.6 kV | Rebuild 4 miles of 41.6 kV line between Wilmot 41.6 kV and Peever Jct. 41.6 kV. | SD | Otter Tail Power Company |  | Other | Reliability | 2024-12-31 | 41.6 | 1125000
Central | AmerenIL, AmerenMO | 23844 | Replace Pole and Insulator Program - MTEP23 | Pole and Insulator Replacements requested by Maintenance. | IL,MO | Ameren Services Company |  | Other | Age and Condition | 2025-12-01 | 345 | 20000000
Central | AmerenIL, AmerenMO | 23845 | Replace Breakers and Relays Program - MTEP23 | Breaker and Relay Upgrades Requested by Maintenance (Missouri and Illinois) | IL,MO | Ameren Services Company |  | Other | Age and Condition | 2025-12-01 | 345 | 5000000
Central | AmerenIL, AmerenMO, WVPA | 23846 | New Seminary - Wittenberg - Grand Tower 138 kV line | This project will include building a new Perryville (Seminary) - Wittenberg - Grand Tower 138 kV line. | MO | Ameren Services Company |  | BRP |  | 2026-12-31 | 138 | 68000000
East | METC | 23847 | Bingham - Looking Glass 138 kV Rebuild | Rebuild approximately 19.3 miles of the Bingham – Looking Glass 138 kV circuit to 1431 ACSR conductor utilizing 138 kV double- circuit structures with OPGW. Leave the East side of the double-circuit structures vacant. Connect OPGW at Bingham 138 kV position WM6. | MI | METC |  | Other | Age and Condition | 2026-12-31 | 138 | 35395000
Central | DEI | 23848 | Rebuild WVPA Montclair to Montclair Jct. 69kV | WVPA Montclair to Montclair Jct. 69134 69kV Rebuild: rebuild 69kV line section | IN | Duke Energy Corporation |  | Other | Reliability | 2023-12-18 | 69 | 8888000
West | GRE | 23849 | Big Swan - Wakefield Storm Structures | Install (2) new storm structures every 5 miles along the ME-BW line between structures 306 and 415 as there are no full stop deadends in this section of line. Possible locations are structures 340 or 349 and 374 or 383. | MN | Great River Energy |  | Other | Reliability | 2024-10-31 | 115 | 526381
Central | DEI | 23850 | Rebuild WVPA Lee Hanna to Lee Hanna Jct 69 kV (Phase 3) | Rebuild 5.6 miles of 69 kV to match line conductor for Fortville to Mohawk line. (954 ACSR) | IN | Duke Energy Corporation |  | Other | Reliability | 2023-10-31 | 69 | 3274000
Central | IPL | 23852 | New Petersburg Energy Center 138 kV (R1011) | Interconnection Customer shall install a 279.45 MVA generator facility. | IN | Indianapolis Power & Light Company |  | GIP |  | 2025-12-31 | 345 | 35000000
East | ITCT | 23853 | Wayne Transformer 301 Replacement | Replace 345/120kV transformer 301 at Wayne station with a new transformer rated at least 750 MVA for summer emergency. | MI | ITC Transmission |  | Other | Age and Condition | 2026-12-31 | 345 | 5635000
South | Entergy-AR | 23855 | Keo 500kV Bus Reconfigure | Reconfigure the Keo 500 kV substation so that the Keo – White Bluff & Keo - Wrightsville 500kV lines are not lost for a P2.3 internal breaker fault. | AR | Entergy Arkansas |  | BRP |  | 2027-12-01 | 500 | 15015000
West | ATC | 23856 | Benson Lake SVC SCM Layer Asset Renewal | Replace hardware and software of the Benson Lake SVC plant System Control and Monitoring (SCM) Layer with supported hardware and software with a design life of 10 years. | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2026-12-01 | 20.5 | 4500000
West | ATC | 23857 | Pine Hy Tap – Pine Hy 69kV (ASPY31-1), Rebuild & OPGW | Install 6.3 miles of new single circuit line on existing ROW. | MI | American Transmission Co. LLC |  | Other | Age and Condition | 2027-12-31 | 69 | 11500000
West | ATC | 23858 | Wick Drive – Black Earth 69kV, (Y-62), OPGW Addition & Partial Rebuild | Installation of 6 miles OPGW with (57) Structure Replacements and (2.2) miles of new (T2-477 HAWK) conductor added to scope between the Wick Drive to Mazomanie Tap substations • 55 replacements assumed due to engineering usage analysis of 1985 and earlier structures. Of the 55 replacements, 22 also are legacy with asset renewal condition need. • 2 additional structures from WKS-MAZT to replace due to ground clearance for new T2-477. • OPGW Termination from Wick Drive and Black Earth substation Dead-End structures into the control houses • Substation Router Configuration to route SCADA and Relay communications on to ATC’s private fiber network infrastructure • Real Estate Easements Required to address gaps and areas of inadequate width. (~$500k) | WI | American Transmission Co. LLC |  | Other | Other Local Needs | 2026-12-31 | 69 | 7000000
West | OTP | 23859 | OTP Granville - Granville Station 41.6 kV | Rebuild of 41.6 kV line between Granville 41.6 kV and Granville Station 41.6 kV. | ND | Otter Tail Power Company |  | Other | Reliability | 2023-12-31 | 41.6 | 1000000
West | OTP | 23860 | OTP Grenville - Veblen 41.6 kV | Rebuild of 41.6 kV line between Grenville 41.6 kV and Veblen 41.6 kV. | SD | Otter Tail Power Company |  | Other | Reliability | 2025-11-30 | 41.6 | 4600000
Central | DEI | 23861 | Upgrades Columbus 345 kV Sub Breaker | Columbus 345 Sub Breaker Upgrades: Replace (3) 138kV CBs on Xfmr Banks 1, 2, and 3 with higher fault interrupting capacity | IN | Duke Energy Corporation |  | BRP |  | 2026-12-31 | 138 | 1500000
Central | DEI | 23862 | Upgrade Bedford 345 kV Sub - 138-138 Bus Tie | Bedford 345 KV Sub 138-138 bus tie path - Upgrade 138kV bus (increase to 2-1590AL), CTs (reconnect at 2000A:5A ratio), and (2) switches (replace with 3000A) | IN | Duke Energy Corporation |  | BRP |  | 2032-04-01 | 138 | 667000
Central | DEI | 23863 | Upgrade Cayuga to Nucor 34501 Line Terminal 345 kV | Cayuga to Nucor 34501 Line Terminal Bus Upgrades: Upgrade 2500AL bus to 2-1590AL at both line terminals | IN | Duke Energy Corporation |  | BRP |  | 2027-04-01 | 345 | 320000
Central | DEI | 23864 | New Bloomington Area 138kV Source | Construct new 345/138kV substation on the west side of Bloomington with (1) 138kV line to Bloomington Rogers St. | IN | Duke Energy Corporation |  | BRP |  | 2028-06-01 | 345 | 44500000
East | METC | 23865 | Elephant - Phase 1 | CE has requested a new 103 MW (expanding to 206 MW) Industrial interconnection near METC's Mecosta substation. To accommodate this request, METC would install a new, 3-row, 138 kV substation near the customer site, and loop the existing Chase-Mecosta 138 kV line approx. 1.5 miles into the new substation. A 138 kV, 54 MVAR cap bank would be installed at the new substation. METC would also rebuild the entire Chase-Mecosta 138 kV circuit (approx. 17.6 miles), and rebuild a 7.8 mile segment of the Croton-Mecosta 138 kV line. | MI | METC |  | Other | Other Local Needs | 2025-03-01 | 138 | 56025000
West | OTP | 23866 | OTP Veblen 41.6 kV Breaker Replacement | Replacement of Veblen 41.6 kV breaker. | SD | Otter Tail Power Company |  | Other | Age and Condition | 2023-12-31 | 41.6 | 450000
Central | DEI | 23867 | Rebuilding WVPA Anderson Grain 69/12kV Sub | Relocate transmission and add in&out with SCADA switches for new Anderson Grain substation. Install 69kV ckt switcher and relaying for high side protection. | IN | Duke Energy Corporation |  | Other | Age and Condition | 2024-08-07 | 69 | 1750000
Central | DEI | 23868 | New WVPA IPC to 69162 Tap loop 69 kV | Build 69 kV from IPC to 69162 Tap 2.8 miles. Add 2 ATO switchs at IPC tap & 3 switches at 69162 line tap. 90 amps minimum. 477 ACSR. | IN | Duke Energy Corporation |  | Other | Reliability | 2023-12-31 | 69 | 6000000
West | GRE | 23869 | Ramsey Breaker Replacement | Replace breaker 33RB1 | MN | Great River Energy |  | Other | Age and Condition | 2024-06-28 | 230 | 471468
South | Entergy-TX | 23870 | 2024 ETI Asset Renewal Program | This project is for the ETI Asset Renewal Program that will be executed in 2024. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. | TX | Entergy |  | Other | Age and Condition | 2024-12-31 | 500 | 34240000
Central | DEI | 23871 | New WVPA NSC Lick Creek 69/12kV Sub. | Build new WVPA NSC (Ninestar Connect) Lick Creek substation; Install 22.4MVA 69/12kV sub with 3-way switches at line jct.; preliminary plan is to be fed from the 69198 ckt. | IN | Duke Energy Corporation |  | Other | Load Growth | 2026-10-31 | 69 | 6923547
East | METC | 23872 | Kraft 138 kV Station Equipment Upgrade | Upgrade existing 500 circuit switcher, two line switches with new breakers at Kraft 138kV station and remove N.O. 3317 PTS. | MI | METC |  | Other | Reliability | 2026-12-31 | 138 | 6075105
West | ATC | 23874 | Harrison Tap – Iola 69kV (Y-70), Rebuild & OPGW | Rebuild approximately 11 miles of 69 kV with new wood monopoles wrapped with mesh. | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2026-12-31 | 69 | 16000000
West | ATC | 23875 | Madison Area Relay Projects | Asset Renewal of Blount control building and contents. Retire the existing 69kV control building at Sycamore. Install new relaying at Blackhawk(MGE), Blount, East Campus, Ruskin, Sycamore, Walnut GIS and Wingra SS. | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2026-12-01 | 138 | 21900000
West | ATC | 23876 | Cornell Tap – Watson Tap 69kV (Chandler), Partial Rebuild | Rebuild approximately 18 miles of 69kV Chandler line between Cornell Tap and Watson Tap. | MI | American Transmission Co. LLC |  | Other | Age and Condition | 2026-12-31 | 69 | 30000000
West | GRE, MP | 23877 | Nelson Lake 230 kV Substation | New 230 kV switching station tying together MP Square Butte East - Bison and GRE Square Butte - Stanton 230 kV lines | ND | Minnesota Power (Allete, Inc.) |  | Other | Reliability | 2026-06-01 | 230 | 25000000
East | ITCT | 23880 | 2023 ITCT Line Relocation Blanket | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI | ITC Transmission |  | Other | Other Local Needs | 2023-12-31 | 345 | 2400000
South | Entergy-LA | 23881 | Holiday to Lafayette 69 kV: Reterminate into Elks | Re-terminate the Holiday to Lafayette 69 kV line into the LUS Elks 69 kV substation, creating an Elks to Holiday 69 kV path. Demolish the unused portions of the Holiday - Lafayette 69 kV line. Upgrade/Rebuild Holiday to Elks line. | LA | Entergy |  | Other | Reliability | 2025-06-01 | 69 | 29400000
South | Entergy-LA | 23882 | Barnett Oil Mill 69 kV Relocation | Build new 69kV T-line from Barnett Oil Mill Sub to a tap point on the existing CLECO Guidry to South Park 69kV line . Install new 3-way motor operated GOAB switch cut-in to CLECO T-line. Demolish the L-658 69kV T-line from the BROM Tap to the Barnett Oil Mill substation. Some of the L-658 structures support CLECO distribution facilities, that distribution will be relocated and/or rebuilt. | LA | Entergy |  | Other | Reliability | 2025-06-01 | 69 | 23700000
West | GRE | 23883 | Cedar Mountain Capacitor Bank Addition | Installation of (2) 75 MVar capacitor banks, installation od of 3 new 345kV breakers to complete the breaker and a half | MN | Great River Energy |  | GIP |  | 2024-05-31 | 345 | 4025164
East | ITCT | 23884 | 2025 ITCTransmission Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | ITC Transmission |  | Other | Age and Condition | 2025-12-31 | 345 | 44250000
East | METC | 23885 | 2026 METC Customer Interconnections | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in service date within the year 2026 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million a separate project will be submitted for approval | MI | METC |  | Other | Other Local Needs | 2026-12-31 | 138 | 2500000
Central | DEI | 23886 | New J1234 - J1235 IN Solar 1 | J1234 - J1235 IN Solar 1 - 150MW net solar farm (100 MW for J1234 and 50 MW for J1235) | IN | Duke Energy Corporation |  | GIP |  | 2023-12-31 | 138 | 17232683
Central | DEI | 23887 | J1378 Crossroads Solar | J1378 Crossroads Solar - 200MW: 230kV connection at existing Veedersburg West sub | IN | Duke Energy Corporation |  | GIP |  | 2024-11-15 | 230 | 5992933
Central | DEI | 23892 | Reconfigure Shelbyville Northeast 138kV Ring bus | Shelbyville Northeast: build 138kV ring bus; replace CIR 6946, 6976, 69183, 13803, 13865 relays, replace OCBs 6946, 6976, 69183, 69138-1, 13803, replace Bank 1 ground switch with circuit switcher, and station battery. | IN | Duke Energy Corporation |  | Other | Reliability | 2026-06-30 | 138 | 10800000
Central | IPL | 23893 | New Winding Ridge 138 kV Substation | New 138 kV, two 40 MVA transformers, 8 breaker, breaker and a half substation to serve AES-IPL customer load and provide transmission service to TOs whom have requested as such | IN | Indianapolis Power & Light Company |  | Other | Load Growth | 2024-12-31 | 138 | 15000000
East | ITCT | 23894 | Jewell 301 Transformer Replacement | Replace the 345/230 KV transformer #301 at Jewell with a new, standard transformer of similar size. | MI | ITC Transmission |  | Other | Age and Condition | 2026-12-31 | 345 | 6600000
West | ATC | 23895 | McCue SS Control House and Relay Asset Renewal | Replace control building and contents • Install relay panels, no remote end work needed • Replace Siemens Station Manager RTU • Replace 69kV OCB Westinghouse model 690-GS-2500 • Replace existing 69kV cap bank with 16.3MVAR in the same bus position, replace zero crossing breaker. • Retire or replace 796-A when reconductoring the 69kV bus • Provisions to meet battery standard TPL-001-5 requirements with either dual battery or monitoring. • Install 138kV line side disconnects if practical • Install 138kV line breaker and relaying for the section of 138kV bus that leaves the McCue yard to feed Kennedy SS • Replacement of 954.0 kcmil AAC 37 Magnolia bus and jumpers in MCU 69 kV Bus 1 and 2 | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2026-12-01 | 138 | 9500000
West | OTP | 23896 | OTP Devils Lake, ND 115 kV Delivery | OTP is converting the 4.16 kV distribution system in the town of Devils Lake, ND to a 12.5 kV system. With this conversion, the town will be removed from our 41.6 kV system and be served via the 115 kV system. In order to move the town to the 115 kV system, a new 115 kV delivery will be established by tapping the Devils Lake East to Sweetwater 115 kV line with a two way switch. 2 miles of 115 kV line will be constructed from the new switch over to the town of Devils Lake where a new 115/12.5 kV distribution substation will be established which will include a 115 kV breaker on the high side of the 115/12.5 kV transformer. | ND | Otter Tail Power Company |  | Other | Load Growth | 2026-12-31 | 115 | 1550000
West | ATC | 23897 | Ohmstead SS Control House and Relay Asset Renewal | Replace control building and contents • Install approximately 5 relay panels, no remote end work needed • Replace Siemens Station Manager RTU • Replace one Bus power potential transformer • Add 4 new 138kV line side disconnects • Provisions to meet battery standard TPL-001-5 requirements with either dual battery or monitoring | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2026-12-01 | 138 | 5700000
South | Entergy-AR | 23898 | McNeil 500kV Relay Improvement SPOF | Ensure the McNeil – El Dorado 500 kV line, the McNeil 500/115 kV auto and the McNeil – Etta 500 kV line have redundant high-speed protection. This includes protection schemes with independent CT and PT winding inputs. Ensure dual battery installations or monitoring sufficient to FERC 754 guidelines. | AR | Entergy Arkansas |  | BRP |  | 2026-12-01 | 500 | 3970000
South | Entergy-AR | 23899 | 2024 EAL Asset Renewal Program | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. | AR | Entergy Arkansas |  | Other | Age and Condition | 2024-12-31 | 500 | 24638000
South | Entergy-AR | 23900 | Dell 161kV Breaker Upgrades | Upgrade Dell 161 kV Breakers B2240, B2205, and B2235 with a 63kA breaker. | AR | Entergy Arkansas |  | BRP |  | 2025-06-01 | 161 | 2515000
West | ATC | 23901 | Shoto SS, Power Transformer Asset Renewal | Replace T1, a 1972 vintage 69/138 kV 84 MVA power transformer with a new 69/138 kV 100 MVA replacement. • Install oil containment system for the new transformer. • Install online monitoring to the new transformer and existing T2 transformer. • Replace fuses and assemblies, capacitors, protection voltage transformers, and reactors on existing capacitor bank and rack for a life extension of the existing asset. • Investigate and provide mitigation as needed to existing ground grid per current guidelines | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2026-12-01 | 138 | 6200000
West | ATC | 23902 | SS Physical Security Switch and SS Asset Renewal Enhancement | o Replace the existing Cisco 2520 switches at approximately 28 substation control house locations including dedicated firewall additions at the enhanced security sites o Replace the existing Cisco 3750/3850 physical security switches at approximately 56 control house locations o Install station wi-fi functionality at approximately 67 control house locations o Replace the existing network speakers and network door video stations at approximately 67 control house locations o Migrate mission critical equipment from AC inverted power to the station DC power at approximately 67 control house locations o Implement rogue device detection at approximately 67 control house locations | WI,MI | American Transmission Co. LLC |  | Other | Age and Condition | 2025-12-01 | 345 | 10000000
West | ATC | 23903 | North Beaver Dam SS Asset Renewal | Reconfigure 138 kV bus layout • Install a fire wall between ATC and Alliant power transformers • Install online monitoring per approved 2020 program to T31 power transformer • Replace one 1980’s vintage 138 kV circuit switcher with a circuit breaker. • Replace control building which will include relay replacements, RTU replacement, and battery replacement • Replace 69kV 10.8 MVAR fused capacitor bank with a 12.25 MVAR fuseless bank • Install future 138kV bus-tie disconnect switches and a set of 138kV bus PTs to allow for bus sectionalizing • Install new line side disconnect switch on the X-47 terminal, does not currently exist • Upgrade jumpers per Planning requirements on the Y-59 line to meet future transmission line renewal needs • Upgrade strain bus in the 69 kV bus per Planning requirements to meet future needs | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2026-12-01 | 138 | 16100000
West | ATC | 23904 | South Beaver Dam – North Beaver Dam, 69kV (Y-59) Line Rebuild & OPGW | Rebuild line and install OPGW on 4.1 miles and install 0.9 miles of OPGW on remaining section. Assumes newer legacy vintage structures can remain. | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2026-12-31 | 69 | 11200000
West | ATC | 23905 | Waupun - South Fond du Lac 69kV (Y-25), Partial Rebuild | Replace remaining legacy monopoles poles (~60%) as ~40% were replaced in 2011. Replace conductor and static with new material. | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2026-12-31 | 69 | 22600000
West | ATC | 23906 | South Fond du Lac SS, Power Transformer and Breaker Asset Renewal | South Fond du Lac: - Replace 2 power transformers with new single larger voltage transformer - Install new bus for auxiliary station service - Install new motor operated switches - Relocation one gas circuit breaker to a new position to support new transformer location - Retire 3 CCVTs and relocate 1 CCVT - Install motor operators on 2 line disconnect switches - Retire one oil circuit breaker and replace with gas breaker - Replace portions of strain bus with rigid bus and replace bus PTs to support new transformer location - Retire a portion of strain bus and replace bus PTs - Replace 8 disconnect switches to support bus rebuilds and breaker replacement - Replace 4 disconnect switches Columbia: - Purchase a new spare transformer | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2026-12-01 | 345 | 9500000
West | ATC | 23911 | Shoto – Northeast 69kV (K-11), Rebuild | Line rebuild • Substation work at Northeast • Fiber optic installation | WI | American Transmission Co. LLC |  | Other | Age and Condition | 2030-10-31 | 69 | 5400000
West | ATC | 23912 | East Krok SS Transformer Replacement | This project will replace the existing East Krok Transformer 1 with a new 138/69kV 100 MVA transformer. | WI | American Transmission Co. LLC |  | BRP |  | 2027-12-31 | 138 | 8700000
West | ATC | 23913 | Northern Adams County Area Network Improvement Project | Construct 9.2 miles of 69 kV single circuit transmission line (5 miles between Badger West and Y-302, and 4.2 miles between Y-302 and Colburn). • Expand Badger West substation with three 138 kV breakers, a 138/69 kV, 100/167/187 MVA base transformer, a new ATC control building, and one 69 kV line breaker. • Modify X-43 at Badger West to cross over the new 69kV t-line. | WI | American Transmission Co. LLC |  | Other | Load Growth | 2027-05-01 | 69 | 39900000
West | ATC | 23915 | Delta County, DIC, Upgrades | ATC will construct a 138 kV, four-breaker ring configuration substation, with ultimate provisions for a six-position 138 kV ring bus. • ATC will loop the existing Holmes-Old Mead Rd 138 kV line (OMDG81) into the new 138 kV substation, raising the OMDG81 line over the existing Old Mead Rd-Delta OMDY51 line. • ATC will retire a portion of the existing Old Mead Rd-Mead Paper 69 kV line (OMDY71), retire OMDY51/OMDY71 bypass equipment and retire the remaining portion of OMDY71 in place. • ATC will remove a 69 kV breaker and OMDY71 line MOD at Old Mead Rd. • ATC will replace 31 structures on the Arnold-Perkins 138 kV double circuit lines (ARNG81/29051). • ATC will implement reverse power blocking and/or LTC tap limiting on the Chandler and Old Mead Rd 138/69 kV transformer LTC controls. | MI | American Transmission Co. LLC |  | Other | Load Growth | 2027-01-31 | 138 | 21000000
West | OTP | 23917 | OTP Fordville - Fordville Jct. 41.6 kV | Rebuild of 41.6 kV line between Fordville 41.6 kV and Fordville Jct. 41.6 kV. | ND | Otter Tail Power Company |  | Other | Reliability | 2025-11-30 | 41.6 | 1450000
West | OTP | 23918 | OTP Michigan - Mapes 41.6 kV | Rebuild of the 41.6 kV line between Michigan 41.6 kV and Mapes 41.6 kV. | ND | Otter Tail Power Company |  | Other | Reliability | 2023-12-31 | 41.6 | 1000000
West | MRES | 23919 | Morris to Grant County to East Fergus Falls Upgrade | Increase the rating of 115 kV lines from Morris to Grant County to East Fergus Falls. | MN | Missouri River Energy Services (MRET) |  | MPFP |  | 2024-07-01 | 115 | 1336540
West | GRE | 23920 | Missouri River Line Crossing Relocation | Replace/relocate 5 towers and reconductor the river crossing to avoid structure/line segments from falling into Missouri river. | MN | Great River Energy |  | Other | Reliability | 2023-10-13 | 230 | 3122886.14
West | GRE | 23921 | Pilot Knob to Deerwood Area Projects | Rebuild the Pilot Knob Substation to a breaker and a half configuration due to age and condition of the current equipment. Upgrade the DA-PD line from Deerwood to Pilot Knob substation to increase the capacity. Upgrade to be built to 115kV standards but operated at 69kV. Retire the underground portion of the DA-PLX at Pilot Knob and replace with overhead Retire the DA-RE line from Pilot Knob road to Black Hawk Road Retire the DA-PKX from Pilot Knob to Cliff Road Retire SS-2820 and replace with a turning structure. Retire SS-2819 | MN | Great River Energy |  | Other | Age and Condition | 2027-05-21 | 115 | 29572823.69
Central | DEI | 23922 | Rebuild WVPA Bringhurst 69/12kV Sub | Rebuild Bringhurst 69/12kV substation. 4.5MVA loading on 6.25MVA existing bank.Possibly bring #1 & #2 sectionalizing line switches inside of substation for an in&out. WVPA owns the loop through portion of the substation. | IN | Duke Energy Corporation |  | Other | Age and Condition | 2024-04-03 | 69 | 5800000
Central | DEI | 23923 | New WVPA Vandalia 69/12 kV Substation | Vandalia (Fillmore) Substation - Incorporate SCADA operated 69 kV flow-through switches into 6996 line between Greensboro and Amo. | IN | Duke Energy Corporation |  | Other | Reliability | 2024-07-15 | 69 | 5450000
South | Entergy-LA | 23924 | Mossville 69 kV Upgrade Breaker 17955 | Breaker number 17955 at the Mossville 69 kV substation will be replaced due to the short circuit analysis. | LA | Entergy |  | Other | Reliability | 2024-06-01 | 69 | 3600000
Central | DEI | 23925 | New Slugger 138kV Load | Project Slugger - large new customer load - early phases to be served from 138kV system followed by 345/138kV transformation as load projections increase. | IN | Duke Energy Corporation |  | Other | Load Growth | 2029-12-31 | 345 | 123500000
South | Entergy-MS | 23932 | 2024 EML Asset Renewal Program | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. | MS | Entergy Mississippi |  | Other | Age and Condition | 2024-12-31 | 500 | 50427385
South | Entergy-TX | 23933 | Sabine 230-138 kV Auto Upgrade | Replace the existing 300 MVA 230-138 kV Sabine Autotransformer with a 500 MVA unit. | TX | Entergy |  | Other | Reliability | 2026-06-01 | 230 | 15500000
South | Entergy-LA | 23934 | 2024 ELL Asset Renewal Program | This project is for the ELL Asset Renewal Program that will be executed in 2024. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. | LA | Entergy |  | Other | Age and Condition | 2024-12-31 | 500 | 43882621
West | OTP | 23936 | OTP Milbank, SD Load Addition | OTP has received a new load request in Milbank, SD. In order to serve this new load a new 115 kV line will be constructed from Big Stone 230/115 kV substation to Milbank, SD where a new 115/12.5 kV substation will be built to offload the existing 41.6 kV system. An additional 115 kV line will be built from the new Milbank, SD substation to a new 115 kV switching station that will be located on the Big Stone - Marietta 115 kV line. The Facilities will consist of the following: 1. Expansion of the Big Stone 115 kV bus to accommodate an additional 115 kV terminal 2. Approximate 12.5 mile 115 kV line from Big Stone 115 kV to a new Milbank 115/12.5 kV substation 3. A new Milbank 115/12.5 kV substation 4. Approximate 15 mile 115 kV line from the new Milbank 115/12.5 kV substation to a new switching station located on the Big Stone - Marietta 115 kV line 5. A new 115 kV switching station on the Big Stone - Marietta 115 kV line | SD | Otter Tail Power Company |  | Other | Load Growth | 2026-12-31 | 115 | 32300000
South | Entergy-LA | 23937 | Willow Glen 138 kV Reconnect Bus | Construct rigid bus to tie in the Willow Glen 138 kV southwest bus and southeast bus together. | LA | Entergy |  | BRP |  | 2023-03-10 | 138 | 2900000
South | Entergy-LA | 23938 | Port Hudson - Jackson 69 kV: Switch upgrades | This project is to upgrade switches on the Port Hudson to Jackson 69 kV line to increase the through path rating of the line. | LA | Entergy |  | Other | Reliability | 2024-12-01 | 69 | 3900000
South | Entergy-LA | 23939 | Blount to Devil Swamp New 69 kV line | Construct new 2.8 mile line from the existing Blount to Devil Swamp 69 kV stations. | LA | Entergy |  | Other | Reliability | 2025-06-01 | 69 | 32300000
South | Entergy-LA | 23940 | Tiger 69 kV: Bus upgrades | Upgrade the Tiger 69 kV bus tie, including breakers and switches, to increase through path rating. | LA | Entergy |  | Other | Reliability | 2025-06-01 | 69 | 1494000
South | SMEPA | 23941 | Silver Creek Delivery Point | In order to serve the Silver Creek delivery point economically and reliably, service will be established by tapping the Cooperative Energy owned Line 571 115kV line. A 115kV GOAB will be installed at the tap point and a new 115kV tap line will be constructed to the delivery point. | MS | South Mississippi Electric Power Association |  | Other | Other Local Needs | 2024-06-01 | 115 | 2075000
West | OTP | 23942 | OTP Gackle - Jamestown 41.6 kV | Reconductor and rebuild sections of the 41.6 kV line between Gackle 41.6 kV and Jamestown 41.6 kV. | ND | Otter Tail Power Company |  | Other | Reliability | 2024-11-30 | 41.6 | 1000000
West | OTP | 23943 | OTP Pickert - McVille 41.6 kV | Rebuild portions of the 41.6 kV line between Pickert 41.6 kV and McVille 41.6 kV. | ND | Otter Tail Power Company |  | Other | Reliability | 2024-11-30 | 41.6 | 3800000
West | OTP | 23944 | OTP Wabek - Parshall 41.6 kV | Rebuild and Reconductor the 41.6 kV line between Parshall 41.6 kV and Wabek 41.6 kV | ND | Otter Tail Power Company |  | Other | Reliability | 2027-12-31 | 41.6 | 930000
South | Entergy-LA | 23946 | MTEP23 ELL Capacitor Bank Retirements | Retire the Snakefarm 115 kV and Jaguar 69 kV capacitor banks. | LA | Entergy |  | Other | Age and Condition | 2023-12-31 | 230 | 0
East | ITCT | 23947 | 2026 ITCT Customer Interconnections | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in service date within the year 2026 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million a separate project will be submitted for approval. | MI | ITC Transmission |  | Other | Load Growth | 2026-12-31 | 120 | 2500000
East | METC | 23948 | 2025 METC Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | METC |  | Other | Age and Condition | 2025-12-31 | 345 | 41750000
East | METC | 23949 | METC Pole Top Switch Additions/Replacement Program 2025 | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. | MI | METC |  | Other | Age and Condition | 2025-12-31 | 138 | 2400000
East | METC | 23950 | 2023 METC Line Relocation Blanket | Relocation of portions of transmission lines located in public right of way at the government entity's mandate. | MI | METC |  | Other | Other Local Needs | 2023-12-31 | 345 | 2400000
South | Entergy-TX | 23952 | SETEX Area Reliability Project | Construct Babel, a new 500 kV 4 breaker ring substation on the Layfield to Hartburg 500 kV line near the Toledo Bend Reservoir. Install two 70 MVAR Reactors • East of Lewis Creek, construct a 500-230-138 kV Station named Running Bear. • Install a 500-230 kV and 230-138 kV Autotransformer • Cut the Lewis Creek to Peach Creek and Lewis Creek to Porter 230 kV lines into Running Bear 230 kV • Cut the Lewis Creek to Texas, Lewis Creek to Sheawill, and Lewis Creek to Caney Creek 138 kV lines into Running Bear 138 kV. Upgrade Running Bear to Caney Creek 138 kV. • Construct a new ~150-mile 500 kV line from Babel 500 kV to Running Bear 500 kV station. | TX | Entergy |  | BRP |  | 2030-12-19 | 500 | 1111000000
Central | DEI | 23953 | Rebuild WVPA Greencastle 69/12kV Substation | Rebuild the existing 69-12.47 kV Greencastle Substation with 69 kV flow-through in another location due to size of site. Replace bank with 14.4 MVA. | IN | Duke Energy Corporation |  | Other | Age and Condition | 2024-05-31 | 69 | 4828000
West | OTP | 23955 | OTP Wilton 41.6 kV Breaker Addition | Install a new line sectionalizing 41.6 kV breaker at Wilton, ND. | ND | Otter Tail Power Company |  | Other | Reliability | 2024-12-31 | 41.6 | 250000
South | Entergy-LA | 23957 | Amite South Reliability Project - Phase 2 | Construct a 14-mile 230 kV line from the Willow Glen substation to the Conway substation. • Station work at both Willow Glen and Conway including additional breakers to accommodate the new line. • Construct a new 500 kV Station near Conway and install a 1200 MVA 500-230 kV Autotransformer. • Build approximately 5 miles of 500 kV to cut the Willow Glen to Waterford 500 kV station into the new Conway 500 kV station. | LA | Entergy |  | Other | Reliability | 2026-06-30 | 500 | 290000000
South | Entergy-LA | 23960 | 2024 ENOL Asset Renewal Program | This project is for the ENOL Asset Renewal Program that will be executed in 2024. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. | LA | Entergy |  | Other | Age and Condition | 2024-12-31 | 230 | 2190124
Central | DEI | 23962 | Rebuild 6958 Line 69 kV for FAA | 6958 Line Rbld as required by FAA - Rebuild 39 Structures and replace conductor from HE Whitehall to structure 815-1069-01. Replace individual poles 815-1060 and 815-1061. Install monitored FAA warning lights on 37 of the poles. Install 36 marker balls on the static wire. | IN | Duke Energy Corporation |  | Other | Reliability | 2025-06-01 | 69 | 3385000
Central | DEI | 23963 | Rebuild 6932 Potato Crk to Thorntown 69 kV | 6932 Rebuild Potato Crk to Manson Jct to Clarks Hill to Thorntown with 954ACSR conductor | IN | Duke Energy Corporation |  | GIP |  | 2024-05-17 | 69 | 41811862
Central | DEI | 23964 | New Kokomo Fusion Phase 1 - 230/69 kV Sub | Kokomo Project Fusion Phase 1 - 110MW new load: new 230/69kV substation inserted in the 23022 ckt. with breaker and 1/2 layout (between Greentown and Kokomo Webster St.); (2) 150MVA -230/69kV transformers; (14) 69kV breakers in a breaker and 1/2 layout; loop 69172 ckt. (between Kokomo East and Kokomo Chrysler North) through new sub; also loop the 69174 ckt. (between Kokomo Touby Pike Tap 1 and Chrysler North Jct.); (3) 60MVA - 69/34.5kV transformers; As of 9/14/23: Customer has Phase 2 plans to increase the load here: scope/cost increase in Phase 1 to partially prepare for Phase 2 (MTEP24 project - 155MWs load addition) - includes 2nd 230/69kV transformer in parallel at existing Kokomo Webster St. | IN | Duke Energy Corporation |  | Other | Load Growth | 2025-06-01 | 230 | 92073454
Central | DEI | 23965 | Replace 13832 Line Structure 138 kV | Replace 14 structures in the 13832 line: 849-2103 thru 2106, and 849-2113 thru 2122 | IN | Duke Energy Corporation |  | Other | Age and Condition | 2024-05-01 | 138 | 2566706
Central | DEI | 23966 | Reconfigure Greensburg 138kV Ring Bus | Greensburg 138kV expand sub and reconfigure to (4) breaker ring bus | IN | Duke Energy Corporation |  | Other | Reliability | 2023-06-01 | 138 | 5884000
Central | DEI | 23967 | J1295 Gibson Solar | J1295 Gibson Solar farm 280MW +/- w/ 345kV POI between Gibson and Francisco in ckt. 34516 (3-breaker ring); Includes required relay work at Gibson | IN | Duke Energy Corporation |  | GIP |  | 2024-06-01 | 345 | 17700000
Central | DEI | 23968 | New Greensfork East 69/12kV Sub | Greensfork East new 69/12kV - 22.4MVA Sub: looped-through feed from 69100 ckt. | IN | Duke Energy Corporation |  | Other | Load Growth | 2028-08-08 | 69 | 1440000
Central | DEI | 23969 | New Williamsport 69/12kV Sub | Williamsport new 69/12kV - 22.4MVA sub: looped-through feed from the 6936 ckt. | IN | Duke Energy Corporation |  | Other | Load Growth | 2026-10-02 | 69 | 3152000
Central | DEI | 23970 | Rebuild 69100 Greensfork to HE Jacksonburg Jct 69kV | Rebuild 69100 from Greensfork #1 switch (pole #862-3176) to Jacksonburg Jct switch (pole #862-3074) using light duty steel poles, 477ACSR and OPGW | IN | Duke Energy Corporation |  | Other | Reliability | 2025-10-09 | 69 | 10800000
Central | AmerenIL, AmerenMO | 23971 | Upgrade Effingham NW-Neoga 138 kV line | Upgrade terminal equipment at Hannibal West, replace two structures and shunts in Neoga – Effingham NW 138 kV line. These are Non-SSR related needs. | MO | Ameren Services Company |  | Other | Reliability | 2024-12-01 | 138 | 1750000
East | ITCT | 23976 | ITCT Pole Top Switch Additions/Replacement Program 2025 | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. | MI | ITC Transmission |  | Other | Reliability | 2025-12-31 | 120 | 2400000
West | OTP | 23977 | OTP Cooperstown 41.6 kV | Reroute and rebuild 5 miles of 41.6 kV line near Cooperstown 41.6 kV. | ND | Otter Tail Power Company |  | Other | Reliability | 2024-11-30 | 41.6 | 1150000
Central | DEI | 23978 | New Bargersville North 69kV Switching Station | Build new Bargersville North 69kV three breaker ring bus switching station in the 69102 line | IN | Duke Energy Corporation |  | Other | Reliability | 2025-12-31 | 69 | 11659302
Central | DEI | 23979 | New Trafalgar 69 kV Ring Bus | Convert the existing Trafalgar 69 kV switching station to a three breaker ring bus | IN | Duke Energy Corporation |  | Other | Reliability | 2026-03-03 | 69 | 9980000
Central | DEI | 23980 | New Glenwood West 10.5MVA 69/12kV Sub | Glenwood West (new) - Install 10.5MVA, 69-12kV non-LTC transformer; build/re-route the existing 6920 line to loop through the new substation with ATO/TLS switches | IN | Duke Energy Corporation |  | Other | Reliability | 2023-12-29 | 69 | 1400000
Central | DEI | 23981 | New Saint Paul Northwest 10.5MVA 69/12kV Sub | Saint Paul Northwest (new) - Install 10.5MVA, 69-12kV non-LTC transformer; build/re-route the existing 6937 line to loop through the new substation with ATO/TLS switches | IN | Duke Energy Corporation |  | Other | Reliability | 2025-11-06 | 69 | 1377000
Central | AmerenIL | 23982 | New Newton Solar Interconnection (J1198) | Install one 345 kV terminal in the Newton substation. The terminal will consist of all necessary terminal equipment to connect the J1198 leadline. | IL | Ameren Services Company |  | GIP |  | 2025-12-01 | 345 | 1500000
Central | AmerenIL | 23983 | New Bison 345 kV Substation for J1289 Lotus Wind E&P | A 200 MW wind project interconnecting the Ameren Illinois system along the Turner - Austin 345 kV line. | IL | Ameren Services Company |  | GIP |  | 2024-11-01 | 345 | 12000000
West | CFU | 23993 | Streeter-Wida Rebuild | Rebuild of the eastern half of CFU's part of the Streeter Switch Substation to MEC's WIDA substation. This will include reconductor and structures. | IA | Cedar Falls Utilities |  | Other | Load Growth | 2024-04-01 | 69 | 2000000
Central | NIPS | 24032 | Upgrade J1482 Network 138kV | 138kV substation and line work to connect J1482 to Springboro to Monticello 138kV line | IN | Northern Indiana Public Service Company |  | GIP |  | 2024-05-01 | 138 | 17892294
South | CLECO | 24033 | J1286 Manuel Expansion | Expand Manuel Substation for the interconnection of J1286 Generation Plant | LA | Cleco Power LLC |  | GIP |  | 2025-04-01 | 138 | 2831239
Central | AmerenIL | 24052 | New Nile 138 kV Substation for J1208-J1209 Chariot Solar I & ll | A 160 MW solar project connecting to a new switching station in Saline County, Illinois. | IL | Ameren Services Company |  | GIP |  | 2025-12-01 | 138 | 9250000
South | Entergy-LA | 24053 | J1431 Interconnection Project at Vacherie 230 kV | Facilities required for the interconnection of J1431 at the existing Vacherie 230 kV substation. | LA | Entergy |  | GIP |  | 2024-05-01 | 230 | 1420000
East | ITCT | 24072 | Resource Equipment Removal and Bypass | Remove ITC assets at Resource substation. Bypass Resource substation to form a direct Alfred to Frisbie 120 kV circuit. | MI | ITC Transmission |  | Other | Reliability | 2026-12-31 | 120 | 3530000
West | MDU | 24092 | Baker upgrades MP funded | Market Funded project to upgrade terminal equipment at Baker. | ND | Montana-Dakota Utilities Company |  | MPFP |  | 2023-12-31 | 230 | 50000
West | ATC | 24093 | Rocky Run SS T2 and T4 Power Transformer Replacement | Planning Scope: o Remove Rocky Run 345/115kV transformers T2 and T4. Replace with on-site spare 500MVA 345/115kV transformer in the T4 position. o Upgrade two (2) 345kV bus switches and five (5) 115kV bus switches. o Remove breaker 4-2 and shorten 345kV ring bus. o Purchase new 500MVA 345/115kV system spare. Asset Renewal Scope: o Replace W-8 secondary relay SEL-321 (component replacement). o Replace all physical security cameras. | WI | American Transmission Co. LLC |  | BRP |  | 2027-06-01 | 345 | 17600000
South | Entergy-LA | 24094 | J1463 Interconnection: Bueche 230 kV Station | This project is to support the interconnection of solar project J1463 at the new Bueche 230 kV station on the 230 kV line 731 (Addis to Big Cajun). | LA | Entergy |  | GIP |  | 2023-11-01 | 230 | 128000
South | CLECO | 24112 | J1205 Perkins Substation | Tap the existing Centennial to West Bay 138 kV line and build a new Perkins Substation. J1205 Generation Plant will interconnect to this substation. | LA | Cleco Power LLC |  | GIP |  | 2023-10-31 | 138 | 2607000
South | CLECO | 24113 | J1424 Singer Substation | Tap the existing Cooper to Penton 230 kV line and add Singer Substation. This substation is needed for J1424's generation interconnection. | LA | Cleco Power LLC |  | GIP |  | 2024-09-15 | 230 | 2967565
South | CLECO | 24114 | J1367 Caneland Expansion | Expand Caneland 230 kV substation for the interconnection of J1367 Generation Plant | LA | Cleco Power LLC |  | GIP |  | 2024-09-29 | 230 | 5163000
East | ITCT | 24115 | Mack - Northeast 120kV UG Cable Relocation | Relocation and replacement of 1230 ft. of 1500kcmil CU cable with 2100 ft. of 2500kmil CU cable of the Mack-Northeast 120 kV circuit to accommodate future interstate infrastructure improvements directed by the Michigan Department of Transportation (MDOT). | MI | ITC Transmission |  | Other | Other Local Needs | 2024-06-03 | 120 | 5540000
Central | AmerenIL | 24133 | J1360 Goose Creek Wind PGIA | A 300 MW wind project connecting at the existing Goose Creek substation in McLean County, IL. Install Gas circuit breaker and relocate Rising Line terminal. Reterminate the Goose Creek-Rising 345 kV transmission line to provide a position for J1360 | IL | Ameren Services Company |  | GIP |  | 2024-06-01 | 345 | 4200000
South | Entergy-TX | 24134 | Mustang 138 kV New Customer Substation | Entergy is proposing to construct a new 138 kV substation called Mustang, which will serve an industrial customer’s 150 MW of new load near Orange, TX. The new Mustang 138 kV station is being laid out as a four bay breaker and a half station with twelve breakers initially installed and cut in on the existing Orange to Bunch Gully 138 kV circuit. | TX | Entergy |  | Other | Load Growth | 2024-10-30 | 138 | 28000000
South | Entergy-TX | 24152 | Moscow 138 kV Customer Load Addition Project | Entergy is proposing to construct new 138 kV transmission facilities at the existing Moscow 138 kV substation which will serve an existing industrial customers new load. The proposed new facilities include installing two 138 kV breakers at the Moscow substation and a new capacitor bank. | TX | Entergy |  | Other | Load Growth | 2023-06-30 | 138 | 10470000
Central | HMPL | 24172 | Re-route HMPL Sub 4 to HMPL Sub 4 Tap 161 kV Transmission Line | HMPL plans to reroute the HMPL Sub 4 to HMPL Sub 4 Tap 161 kV transmission line due to Big Rivers Electric Corporation (BREC) Pratt Paper transmission project (MISO Project ID 21685). | KY | Henderson Municipal Power & Light |  | Other | Reliability | 2023-07-01 | 161 | 155000
South | AECC | 24192 | UIG | NUCOR is expanding their operations by adding to two locations manufacturing facilities to produce liquid products for both their operations and the market. AECC and Mississippi County Electric will be building out the AECC Barfield substation by adding a new 25 MVA; 161/13.8 kV transformer to support 20 MW of new load. AECC and Mississippi County Electric will also be building out the AECC Hickman North substation by adding a new 40 MVA; 161/13.8 kV transformer to support 30 MW of new load. This project will be submitted as an Expedited Process project. This project should be in MTEP23. | AR | Arkansas Electric Coopertive Corporation |  | Other | Load Growth | 2025-04-01 | 0 | 0
West | MEC | 24212 | Badger Creek Substation | Construct Badger Creek Substation that will bisect the existing Arbor Hill-Raccoon Trail 345 kV line. Construct a new 345 kV line from Badger Creek Substation to the Raccoon Trail Substation. | IA | MidAmerican Energy Company |  | Other | Other Local Needs | 2025-12-01 | 345 | 0
West | MRES | 24232 | ALP SE Substation | Alexandria Light & and Power (ALP) will build a new distribution substation on the southeast part of town. The substation will tap and existing 115 kV line with an in and out substation. The substation will have a 115 kV to distribution transformer. | MN | Missouri River Energy Services (MRET) |  | Other | Load Growth | 2025-12-31 | 115 | 1358000
South | Entergy-LA | 24252 | MPFCA J1246, J1367, J1465: Install 2nd Bayou Labutte 500-230 kV Autotransformer and Construct New Wise to Bayou Labutte 230 kV Line | Install 2nd 500-230 kV Autotransformer at Bayou Labutte 500 kV, including all associated station and relay work. Construct new Wise to Bayou Labutte 230 kV line, including all associated station and relay work. | LA | Entergy |  | GIP |  | 2025-09-20 | 500 | 45202000
South | Entergy-LA | 24253 | MPFCA J1246, J1421, J1463: Willow Glen 230 kV Breaker Replacements | Replace sixteen 230 kV breakers at Willow Glen 230 kV station with IPO circuit breakers rated at 80 kA. | LA | Entergy |  | GIP |  | 2025-08-09 | 230 | 16510000
South | Entergy-LA | 24254 | J1465 138 kV Interconnection Station | This project is to support the interconnection of J1465 on 138 kV line between existing Livonia and Colonial Springs stations. | LA | Entergy |  | GIP |  | 2025-06-01 | 138 | 14400000
South | Entergy-LA | 24272 | J1421 230 kV Interconnection Project | This project is to support the interconnection of solar project J1421 at a new station cut in between Colfel and Moler 230 kV stations. Convert Moler 230 kV into a four breaker ring bus. Upgrade the Coly to Moler 230 kV line as identified during the MISO DPP cycle. | LA | Entergy |  | GIP |  | 2026-03-01 | 230 | 32259000
Central | IPL | 24273 | New - 138kV - Airtech Substation | New 138kV, two 20 MVA transformer, three-breaker substation | IN | Indianapolis Power & Light Company |  | Other | Load Growth | 2026-12-31 | 138 | 10700000
East | METC | 24275 | Morocco - J1226 GIA NU | Install two 345 kV breakers rated at 40 kA and associated disconnect switches to complete row 36 in Morocco Substation. Install one 345 kV breaker rated at 40 kA and associated disconnect switch to complete row 34 in Morocco Substation. | MI | METC |  | GIP |  | 2024-06-06 | 345 | 4260888
East | METC | 24276 | Vergennes - Marquette - J1255 GIA (Hawley) NU | J1255 is a 200MW solar project connecting in Keene Township on the Vergennes - Marquette 138kV. Build the J1255Interconnection 138kV station as a breaker and half station with three 40kA breakers in a ring bus configuration. Extend the Marquette - Vergennes 138kV line to loop in the station. Connect the generators at position WM12 as TOIF. Generators are part of the DPP 2019 Cycle 1. | MI | METC |  | GIP |  | 2025-12-31 | 138 | 6939380
East | METC | 24277 | Gaines - Thompson Road 138kV - J1292 GIA (Peddler) NU | Build a new 138 kV 3 breaker ring substation cut in from the Gaines - Thompson Road 138kV line. | MI | METC |  | GIP |  | 2025-12-31 | 138 | 6934580
West | XEL | 24278 | Edina Switch Replacement | Project will replace 115kV switch at Edina, which is limiting the rating of the Edina - St. Louis Park 115kV line. | MN | Northern States Power (Xcel Energy) |  | BRP |  | 2023-12-31 | 115 | 135000
East | METC | 24279 | Claremont - Cornell #2 - J1297 GIA (Hathon) NU | J1297 is a 170MW solar project interconnecting in Venice Township, Shiawassee, MI. METC will need to build a new 138kV breaker and half station with three 40kA breakers. METC will need to extend the Claremont - Cornell #2 138kV line 0.1 miles to loop in the J1297 Interconnection station for transmission service. Loop in the Cornell - Goss 138kV line to mitigate anti - islanding at Bell Road. J1297 is queued within the DPP 2019 Cycle 1. | MI | METC |  | GIP |  | 2026-01-28 | 138 | 18106637
East | ITCT | 24280 | Greenwood - J1331 GIA NU | Add row P and install two 120 kV breakers rated at 40 kA and four disconnect switches at Greenwood Substation. | MI | ITC Transmission |  | GIP |  | 2025-02-28 | 120 | 2881189
East | METC | 24282 | Leoni - Parr Road - J1472 GIA(Vargo) NU | J1472 is a generation interconnection request for 100 MW Solar Power Plant proposing to connect to the METC Leoni – Parr Road 138kV Line. J1472 is queued within the DPP 2019 Cycle 1. | MI | METC |  | GIP |  | 2025-03-31 | 138 | 7130467
West | GRE | 24285 | Benton County Solar Farm | The existing 115kV Benton County substation is built as a two row breaker-and-a-half breaker station. A new breaker and a half row would be built out to accommodate the interconnection of the 100 MW solar farm for J1426. The network upgrades at the substation will include the installation of a new 115kV Breaker, Line arrestors, line CCVTs, Primary/Secondary Relay Panels, Metering, new metering CTs, and disconnects in the breaker-and-a-half row. | MN | Great River Energy |  | GIP |  | 2025-08-01 | 115 | 2386979
Central | IPL | 24293 | New - 138 kV - New Pleasant Acres Substation | New 138 kV, two 22.4 MVA transformers, 3 breaker, straight bus substation to serve WVPA load | IN | Indianapolis Power & Light Company |  | Other | Load Growth | 2025-12-31 | 138 | 10000000
East | METC | 24294 | Mio Dam - Twining - J1210 GIA (Quarry) - NU | Construct new Quarry 138 kV station. Install five 138 kV breakers rated at 40 kA, associated disconnects, and two new bus sections. Loop in the Mio Dam – Twining circuit to the new Quarry station. Loop in the Iosco – Karn circuit to the new Quarry station. Remove Twining 177 sparing and install approximately 4.3 miles of fiber on the Quarry – Twining circuit. | MI | METC |  | GIP |  | 2025-03-31 | 345 | 11049936
East | METC | 24295 | Marshall - Blackstone (Stable) - J1248 GIA (Bearcat) NU | J1248 is a 100.9MW solar farm connecting on the Marshal - Stable 138kv line in Calhoun County, MI. Construct J1248 as a breaker and half station with three 40kA breakers in a ring bus configuration. Construct BM14 as a TOIF to connect J1248. Generator is part of the DPP 2019 Cycle 1. | MI | METC |  | GIP |  | 2025-11-30 | 138 | 9711426
West | ATC | 24296 | Valders SS, New 138/69 kV Substation | Construct a new 138/69 kV Valders Substation with 100 MVA transformer looping in Forest Junction - Howards Grove 138 kV (971K51) and Custer - St Nazianz - New Holstein 69 kV (P-68) lines. | WI | American Transmission Co. LLC |  | Other | Reliability | 2028-07-31 | 138 | 24200000
South | Entergy-TX | 24298 | J1442 Interconnection Project on Livingston to Rich 138 kV line | This project is to construct the interconnection station for the solar project J1442 on the Livingston to Rich 138 kV line. | TX | Entergy |  | GIP |  | 2025-05-01 | 138 | 15590000
East | ITCT | 24299 | J1196 Generator Interconnection TOIF | Install required entrance structures and 345 kV disconnect switch at the new Wedge station. | MI | ITC Transmission |  | GIP |  | 2025-03-31 | 345 | 0
East | METC | 24300 | J1320 Generator Interconnection TOIF | Install required line entrance structures and 138 kV disconnect at new Byers switching station. | MI | METC |  | GIP |  | 2025-12-10 | 138 | 0
East | METC | 24301 | Leoni - Parr Road - J1472 GIA(Vargo) TOIF | Install a line entrance structure and a switch for the generator to connect at position WM13. | MI | METC |  | GIP |  | 2024-11-29 | 138 | 0
East | ITCT | 24313 | Greenwood-Rapson(Banner)-J1196 GIA(Wedge) NU | Construct new Wedge 345 kV station. Install three 345 kV breakers rated at 40 kA with associated disconnects and two new bus sections. Cut the ITCT Greenwood – Rapson (Banner) 345 kV circuit into the new Wedge station. | MI | ITC Transmission |  | GIP |  | 2025-03-31 | 345 | 12620784
East | METC | 24314 | Thetford-J1203 GIA NU | Install three 345 kV breakers rated at 40 kA and associated disconnect switches and complete row 29 in the METC Thetford Substation. | MI | METC |  | GIP |  | 2025-05-05 | 345 | 4245703
West | XEL | 24315 | Dubay Lake Substation | Install new 115/34.5kV substation in the Dayton area to meet area load growth. | MN | Northern States Power (Xcel Energy) |  | Other | Load Growth | 2025-06-16 | 115 | 12400000
East | METC | 24317 | DuPont - Cobb - J1375 GIA (Lamos) NU | Construct the new Lamos 138 kV station. Extend the White Lake – DuPont – Cobb 138 kV line to loop in the new Lamos 138 kV station. Install three 138 kV breakers rated at 40 kA and two new bus sections at the new Lamos station. Loop the White Lake – Du Pont – Cobb 138 kV line into the White Lake 138 kV station. Install approximately 3.1 miles of fiber from White Lake to Lamos Switching Station. Implement anti-islanding protection for identified islanding scenarios. Replace an existing bus at White Lake Substation. Install new bus and 500 tie-breaker with associated disconnects at White Lake Substation. Install 677 and 777 breakers with associated disconnects at White Lake Substation. Cut White Lake – Cobb circuit and reconnect to the new bus at White Lake. | MI | METC |  | GIP |  | 2025-05-12 | 138 | 14998507
East | METC | 24318 | Eureka - Vestaburg - J1379 GIA NU | Install a new 138kV switching station. Install four 138kV breakers rated at 40kA and two bus sections. Cut the METC Eureka - Vestaburg 138 kV circuit into the new 138 kV switching station. Rebuild the METC Eureka - Vestaburg 138 kV line from Deja to Eureka. Rebuild the METC Eureka - North Belding 138 kV line. Add a new 138 kV line from the new switching station to North Belding. | MI | METC |  | GIP |  | 2024-05-31 | 138 | 50088736
East | METC | 24319 | Delhi-Thompkins #2 J1399 (Edgar) NU | J1399 Interconnection is a 90MW solar project in Lesli Township, MI. Build the J1399 Interconnection station as a breaker and half station with three 40kA breakers in a ring bus configuration. Extend the Delhi – Tompkins 138kV line to loop in the J1399 Interconnection station. J1399 is queued within the DPP 2019 Cycle 1. | MI | METC |  | GIP |  | 2025-12-31 | 138 | 10010107
East | ITCT | 24333 | Majestic-Milan - J1224 & J1329 GIA (Neblo) NU | Build a new 345 kV 3 Breaker ring substation cut in from the Majestic-Milan 345kV line. System changes will require relay upgrades at Majestic 345 kV and Milan 345 kV stations. | MI | ITC Transmission |  | GIP |  | 2025-12-29 | 345 | 13156394
West | ATC | 24373 | Manogue Rd SS DIC, New Substation | New tapped substation to serve 4.3 MVA motor load between the existing Edgerton Business Park and Russell substations on the 138 kV Line X-31. Line breakers will be installed at the Edgerton Business Park Substation on the Rockdale-Edgerton Business Park-ANR Manogue Rd-Russell 138kV (X-31) line due to high network flow. | WI | American Transmission Co. LLC |  | Other | Load Growth | 2025-08-01 | 138 | 7100000
West | XEL | 24374 | Steep Bank Lake Line Swap | Move J460 Steep Bank Lake interconnection to new 345kV second circuit being built between Brookings County - Lyon County (MTEP ID 23452). | MN | Northern States Power (Xcel Energy) |  | Other | Reliability | 2025-09-02 | 345 | 300000
East | ITCT | 24376 | Majestic-Milan - J1224 & J1329 GIA (Neblo) TOIF | Install a line entrance structure and switch for the generator to connect to position CQ at the Neblo (J1224&J1329) 345 kV station. | MI | ITC Transmission |  | GIP |  | 2025-12-29 | 345 | 0
East | METC | 24377 | Coldwater - Byers Rebuild (J1320) - Network Upgrade | Rebuild entire J1320 - Coldwater 138 kV line with OPGW. Replace existing 336 and 477 ACSR conductor with 954 ACSR. | MI | METC |  | GIP |  | 2024-12-23 | 138 | 7296394
East | ITCT | 24393 | MDOT I-375 Construction - Underground Cable Relocation | Relocate a portion of the Alfred-St. Antoine and Esset-St. Antoine 120 kV underground cables currently located in the Larned I-375 bridge to accommodate the reconstruction of I-375 in downtown Detroit as directed by the Michigan Department of Transportation (MDOT). | MI | ITC Transmission |  | Other | Other Local Needs | 2024-12-31 | 120 | 8200000
East | METC | 24395 | Luce - Summerton Line Reconductor (J1379) - Network Upgrade | Reconductor the entire ~10.5 mile-long Luce – Summerton 138 kV line with OPGW. Replace the existing 336 ACSR conductor with new 795 ACSS conductor. Replace any structures as necessary. | MI | METC |  | GIP |  | 2025-11-26 | 138 | 9682800
East | METC | 24396 | J1210 Generator Interconnection TOIF | Install required line entrance structures and 138 kV disconnect switch at the new Quarry station. | MI | METC |  | GIP |  | 2025-03-31 | 138 | 0
East | WPSC | 24414 | WPSC Elephant Interconnection (Project 23865 Partial Alternative) | CE has requested a new 103 MW (expanding to 206 MW) Industrial interconnection near METC's Mecosta substation. To accommodate this request, METC would install a new, 3-row, 138 kV substation near the customer site, and loop the existing Chase-Mecosta 138 kV line approx. 1.5 miles into the new substation. A 138 kV, 54 MVAR cap bank would be installed at the new substation. METC would also rebuild the entire Chase-Mecosta 138 kV circuit (approx. 17.6 miles). Wolverine's portion of the project will be to will cut in the Hersey to White Cloud by building 4 miles of double circuit 138kV on new ROW. | MI | Wolverine Power Supply Cooperative, Inc. |  | Other | Other Local Needs | 2025-03-01 | 138 | 6000000
South | CLECO | 24415 | Ragely Substation | Tap the existing 138 kV line between Nelson and Longville 11.3 miles from Longville. At this location build a new 138 kV Substation Turps. Build a new 6.1 mile 138 kV line from Turps to a new substation Ragley. This project will also add a 14 MVAR cap bank at Ragley. | LA | Cleco Power LLC |  | Other | Load Growth | 2024-07-17 | 138 | 40000000
South | CLECO | 24416 | Rosepine Substation | Build a new 230 kV substation Rosepine tapped into the existing Leesville to Cooper 138 kV line 11.5 miles from Leesville. Build a new 230 kV line 3.4 miles from Rosepine to Deridder. This substation and line will be energized at 138 kV. | LA | Cleco Power LLC |  | BRP |  | 2027-07-15 | 138 | 35585000
East | ITCT | 24417 | J1350 Generator Interconnection Network Upgrades | Build a new 345 kV 3 Breaker ring substation and cut in the Milan - Lulu 345kV 345 kV line. System changes will require relay upgrades at Milan 345kV station. | MI | ITC Transmission |  | GIP |  | 2025-05-16 | 345 | 13376550
East | ITCT | 24418 | J1350 Generator Interconnection TOIF | Install a line entrance structure and a switch for the generator to connect at position CI. | MI | ITC Transmission |  | GIP |  | 2025-05-16 | 345 | 0
East | METC | 24419 | J1320 Generator Interconnection Network Upgrades | Construct new Byers switching station. Install three 138 kV breakers rated at 40 kA and two new bus sections. Loop in the Batavia – Coldwater circuit to the new Byers station. Remove existing X and Z phase wave traps and tuners at Batavia and Coldwater. Install approximately 6 miles of fiber from Byers Switching Station to Batavia and approximately 2 miles of fiber from Byers Switching Station to Coldwater. | MI | METC |  | GIP |  | 2025-12-10 | 138 | 14607533
East | METC | 24420 | Cobb - Peterson Tap Sag Remediation (J1375) - Network Upgrade | Remediate the sag on the 336 ACSR conductor on the Cobb - Peterson Tap 138 kV line section to meet or exceed a rating of 125 MVA Summer Emergency. | MI | METC |  | GIP |  | 2024-12-23 | 138 | 418800
East | METC | 24433 | Vergennes - Marquette - J1255 GIA (Hawley) TOIF | Install WM14 line position and disconnect at the Hawley station to interconnect J1255 generation. | MI | METC |  | GIP |  | 2025-12-31 | 138 | 0
East | METC | 24434 | J1203 Generator Interconnection TOIF | Install required entrance structures and 345 kV disconnect switch at METC Thetford Substation. | MI | METC |  | GIP |  | 2025-05-05 | 345 | 0
East | METC | 24435 | J1226 Generator Interconnection TOIF | Install required entrance structures and 345 kV disconnect switch at Morocco station. | MI | METC |  | GIP |  | 2024-06-06 | 345 | 0
East | METC | 24436 | J1375 Generator Interconnection TOIF | Install required line entrance structures and 138 kV disconnect at new Lamos station. | MI | METC |  | GIP |  | 2025-05-12 | 138 | 0
East | METC | 24437 | Delhi-Thompkins #2 J1399 (Edgar) TOIF | Install a line entrance structure and a switch for the generator to connect at position BM14. | MI | METC |  | GIP |  | 2025-12-31 | 138 | 0
East | METC | 24438 | J1401 Generator Interconnection Network Upgrades | Install one 138 kV breaker rated at 40 kA and associated disconnects. | MI | METC |  | GIP |  | 2024-04-05 | 138 | 1053802
East | METC | 24439 | J1401 Generator Interconnection TOIF | Install a line entrance and 138 kV disconnect switch at Wagner Station. | MI | METC |  | GIP |  | 2024-04-05 | 138 | 0
East | ITCT | 24441 | J1331 Generator Interconnection TOIF | Install required entrance structures and 120 kV disconnect switch at Greenwood Substation. | MI | ITC Transmission |  | GIP |  | 2025-02-28 | 120 | 0
West | ATC | 24445 | J1374 Ebenezer SS Network Upgrades and Interconnection Facilities | Wind Turbine generating Facility located in Grant County, Wisconsin. | WI | American Transmission Co. LLC |  | GIP |  | 2024-08-01 | 138 | 1577013
West | ATC | 24446 | J1251 Summer Meadow Switching Station Network Upgrades and Interconnection Facilities | A 100 MW solar farm located in Marquette County, Michigan. | MI | American Transmission Co. LLC |  | GIP |  | 2025-06-12 | 345 | 8002656
West | ATC | 24447 | J1483 Hill Valley SS Network Upgrades and Interconnection Facilities | Wind farm in Iowa County, Wisconsin. | WI | American Transmission Co. LLC |  | GIP |  | 2026-09-01 | 345 | 2252888
East | METC | 24448 | Murphy-Styx - J1389 Generator Interconnection - Network Upgrades | Build a new 345 kV 3 Breaker ring substation (Palomino) cut in from the Murphy - Styx (J984) 345 kV line. | MI | METC |  | GIP |  | 2025-10-31 | 345 | 12375600
West | ITCM | 24449 | Nevada Area Load Interconnections | IPL has requested a new substation interconnection in the Ames/Nevada area for a new load in their Prairie View Industrial Center. As part of this request, ITC Midwest will be building a new 3 row 161 kV breaker and ½ substation with 4 line positions and 2 transformer positions initially, with the ability to add 3 additional rows in the future for additional transformer positions as well as additional line positions. The new Prairie View Industrial Center substation will be PD and the common facilities will be owned by IPL. ITC will build a new 161 kV line from Prairie View Industrial Center substation to the ITC Ames substation, approximately 5 miles in length, to support the load additions/growth in this area. The existing Ames 161 kV bus will be required to be rebuilt to a ring bus to accommodate the new 161 kV line position for the line to Prairie View Industrial Center substation. IPL has also requested to interconnect a new substation/load directly south of the existing Nevada Lincoln Highway Industrial Substation. ITC will be building a new 4 position ring bus substation (expandable to future 4 row breaker and ½) named “Teller” to serve this load. There is a possibility to connect this substation to Lincoln Highway Industrial in the future to convert that from 69 kV to 161 kV. ITC will also be building a new approximately 2.5 mile 161 kV line from the Prairie View Industrial Center substation to the Teller Substation, and a new approximately 8 mile 161 kV line from the Fernald substation to the Teller Substation. ITC will also need to add an additional 161 kV line terminal at the Fernald 161 kV substation by adding an additional 161 kV breaker to the existing ring bus. In addition, the Prairie View Industrial Center Substation will interconnect to the existing City of Ames 161 kV line that runs the Ames Plant and NE Ankeny substations, providing 4 161 kV lines into the Prairie View Industrial Center substation initially, with the ability to add a 2nd line to the City of Ames Plant substation in the future. | IA | ITC Midwest |  | Other | Load Growth | 2024-12-31 | 161 | 56519142.5
East | METC | 24453 | Hawley-Peddler - New Circuit #1 and #2 (J1255, J1292) - Common Use Network Upgrade | Install two breakers at positions 8B7 and 8W8 at J1292, and two breakers at positions at positions 8W8 and 10B7. Install about 15 miles of 954 ACSR DCT in new Right of Way to connect J1292 Interconnection Station to J1255 Interconnection Station. | MI | METC |  | GIP |  | 2025-12-31 | 138 | 27716208
East | METC | 24454 | Leoni - Lark 138 kV Sag Remediation (J1310, J1472) - Network Upgrade | Remediate the sag on the 477 ACSR conductor on the Leoni – Washtenaw Tap 138 kV segment to meet or exceed a summer emergency rating of 179 MVA. | MI | METC |  | GIP |  | 2024-04-05 | 138 | 660000
East | METC | 24455 | Verona - Mud Lake #1 Rebuild (J1248, J1310, J1430) - Network Upgrade | Replace existing 336 ACSR conductor on the Verona – Mud Lake #1 138 kV line with 954 ACSR including one 48 count OPGW ~ 3.6 Miles. Any new 138kV towers should be expandable to double circuit in the future. | MI | METC |  | GIP |  | 2024-12-23 | 138 | 8770564
East | METC | 24456 | Marshall - Blackstone (Stable) - J1248 GIA (Bearcat) TOIF | Stable - Install a line entrance structure and switch for the generator to connect at position WM14. | MI | METC |  | GIP |  | 2025-11-30 | 138 | 0
West | OTP | 24457 | OTP Bagley Jct. 115 kV Capacitor Addition | Expand the Bagley Jct. 115 kV switching station to allow for the installation of a single step 20 MVAR 115 kV capacitor bank. The project will consist of the addition of two 115 kV breakers, three disconnect switches, a single 20 MVAR 115 kV capacitor bank, and other associated equipment to allow for the installation of a 20 MVAR 115 kV capacitor bank. | MN | Otter Tail Power Company |  | GIP |  | 2024-07-31 | 115 | 1153145
East | METC | 24459 | J1379 Generator Interconnection TOIF | Install an Entrance structure and 138 kV disconnect switch at the new switching station. | MI | METC |  | GIP |  | 2024-05-31 | 138 | 0
South | Entergy-TX | 24460 | Coldspring Load Addition | A member of ETEC is adding a total of 21.2 MW to the existing Coldspring substation to serve a new customer load. The load addition will be completed in two phases. Phase I - Serving 5MW of additional load via the existing distribution transformer. Phase II - Adding a new distribution transformer to serve 16.2 MW of additional load. | TX | East Texas Electric Cooperative Inc. |  | Other | Load Growth | 2024-07-31 | 138 | 3740960
West | ITCM | 24464 | Eagle to Tharp 69kV Line Relocation | A 0.75 section of the Eagle - Tharp 69 kV line is required to be moved to a new permanent location by the Iowa DOT due to a project to rebuild the I-380 and Wright Bros Blvd interchange. Thirteen new wooden poles, three new steel poles, and new T2-477 ACSR cabling is to be constructed as shown in the sketched figures. PTS 1158 is to be retired and PTS 1114 is to have the jumpers remade to face towards Eagle. PTS 1114 will remain in this configuration until the switch is retired with the Kitty Hawk rebuild. | IA | ITC Midwest |  | Other | Other Local Needs | 2024-05-01 | 69 | 1618750
West | ATC | 24465 | Walworth - Brick Church (Y-159), OPGW Addition & Partial Rebuild | OPGW Addition on the Walworth - Brick Church (Y-159) line and partial transmission line rebuild. | WI | American Transmission Co. LLC |  | Other | Other Local Needs | 2026-06-30 | 69 | 4600000
East | ITCT | 24466 | MDOT I-96 Construction - Cody - Nolan Structure Relocation | Relocate five structures on the Cody – Nolan 120 kV line that are in conflict with the reconstruction and rehabilitation project along US-23 at the I-96/Grand River intersection. | MI | ITC Transmission |  | Other | Other Local Needs | 2024-08-01 | 120 | 1250000
West | ATC | 24473 | Rock River SS, DIC, Additional Transformer | Expanding Rock River 138kV Bus 3 to interconnect a distribution transformer | WI | American Transmission Co. LLC |  | Other | Load Growth | 2024-07-01 | 138 | 3000000
West | ATC | 24475 | Tommy's Turnpike DIC, New Sub | ATC will construct an approximately 0.3 mile 115 kV double-circuit transmission line extension from the Whiting Ave – Okray 115kV line (B-106) to interconnect the proposed T-D substation. • ATC will construct a 115 kV loop-through straight bus with line switches, bus-tie switches, and space reserved for potential line and bus-tie breakers. • WPS to construct a new substation site, install two new 115/24.9 kV 33/38 MVA transformers with high side breaker protection for each and other supporting equipment. | WI | American Transmission Co. LLC |  | Other | Load Growth | 2025-12-31 | 115 | 7700000
East | METC | 24493 | Claremont - Cornell #2 - J1297 GIA (Hathon) TOIF | Install a line entrance structure and a switch for the generator to connect at position BM10. | MI | METC |  | GIP |  | 2026-01-31 | 138 | 0
West | ITCM | 24513 | Maquoketa (CIPCO) 161 kV Sub Rebuild | CIPCO has notified ITC that they will be rebuilding the 161 kV portion of their Maquoketa substation to a ring bus. ITC will need to relocate the Grand Mound – Maquoketa and Maquoketa – Sale 161 kV lines into new bus positions at Maquoketa to accommodate the new layout of the substation. T2-636 ACSR should be used for new conductor for the new line taps. | IA | ITC Midwest |  | Other | Reliability | 2024-05-30 | 161 | 2028750
East | METC | 24514 | Murphy-Styx - J1389 Generator Interconnection - TOIF | Install a line entrance structure and a switch for the generator to connect at position RH31. | MI | METC |  | GIP |  | 2024-01-29 | 345 | 0
Central | NIPS | 24562 | J1333 -J1340 Network Upgrades | Greenfield 345kV double breaker double bus station named Hinshaw. | IN | Northern Indiana Public Service Company |  | GIP |  | 2024-06-01 | 345 | 47288518
West | ATC | 24575 | DPC Clearfield Jct Tap, New T-T | New T-T interconnection to Council Creek-Hilltop 69 kV (Y-74), and constructing a new 69 kV loop-through substation near New Lisbon Tap with three line breakers to replace an existing three-way GOAB. | WI | American Transmission Co. LLC |  | Other | Load Growth | 2026-06-01 | 69 | 11100000
East | ITCT | 24593 | GM Orion Plant Expansion | At Sunbird, expand the existing substation to include 3-120 kV line breakers, 1-120 kV section breaker, and create bus 103. Construct a 2nd Pontiac-Sunbird 120 kV line and install 2-120 kV pole top switches on the Colorado taps on the Pontiac-Sunbird #1 and Sunbird-Bloomfield 120 kV lines. At Pontiac, bypass the existing series reactor and install a line breaker on the new Pontiac-Sunbird #2 line position. Install OPGW between Pontiac and Sunbird. | MI | ITC Transmission |  | Other | Load Growth | 2025-05-31 | 120 | 25796000
West | ATC | 24613 | J1214 J1326 Rockdale SS Network Upgrades and Interconnection Facilities | Solar development with energy storage in Dane County, Wisconsin. | WI | American Transmission Co. LLC |  | GIP |  | 2025-06-01 | 345 | 4069937
East | METC | 24673 | Project Hickory Load connection | METC will construct the new 138 kV, 3-row, breaker and a half Charge substation to be fed by looping the existing Highfield-Brooks Industrial 138 kV line approximately 0.2 miles into the new substation. | MI | METC |  | Other | Other Local Needs | 2024-05-31 | 138 | 16623125
Central | AmerenIL | 24695 | New Fauna 345 kV Sub for Flora Solar (J1679) | 125 MW solar generation project J1679. Interconnection at Fauna sub on Xenia - Mt Vernon West 345 kV Line 4591. | IL | Ameren Services Company |  | GIP |  | 2025-12-01 | 345 | 11000000
Central | AmerenMO | 24696 | New Vanhorn 345 kV Substation for Wolf Creek Solar (J1352) | Construct the Interconnection Facilities at the J1352 Interconnection Switching Station, line cut-in and relay upgrades. Vanhorn sub on Montgomery-Spencer Creek 345 kV line. | MO | Ameren Services Company |  | GIP |  | 2025-06-01 | 345 | 11000000
South | Entergy-AR | 24697 | Aurelle 115kV: POI for J1612 | A new point of interconnection for J1612 100 MW solar project. The interconnection customer will install the SANU. Network Upgrades at El Dorado 115kV and Sterlington 115kV will be installed by Entergy as well as the transmission line cut-in. New underground fiber will be installed between Strong and Huttig tap stations. | AR | Entergy Arkansas |  | GIP |  | 2024-11-27 | 115 | 13031000
Central | AmerenIL | 24718 | New Quotient 345 kV Substation for Casey Fork Solar(J1241) | Construct a new 345kV Quotient switching station in Jefferson County, IL to provide a Point of Interconnection for the Generating Facility. The new J1241 Interconnection Switching Station will split the existing Xenia – Mt Vernon West 345 kV transmission line | IL | Ameren Services Company |  | GIP |  | 2025-12-01 | 345 | 11000000
West | ITCM | 24740 | Commercial (JCE) 69 kV Substation | For ITC’s portion of the Commercial Substation ITC will install a new 69 kV substation with 2 69 kV line breakers, one distribution transformer position, and one mobile transformer position. All the ITC equipment will be capable of 600A or greater. | IL | ITC Midwest |  | Other | Load Growth | 2024-06-01 | 69 | 3801869
West | ATC | 24758 | J1410 J1411 North Arlington Swt St MPFCA & Network Upgrades | J1410 is a solar facility located in Dane County, Wisconsin. J1411 is an energy storage facility co-located in Dane County with J1410. | WI | American Transmission Co. LLC |  | GIP |  | 2026-06-03 | 345 | 21988404
Central | AmerenIL | 24779 | New Hoot 138kV Substation (J1266) | Hoots J1266 Interconnection Switching Station will cut the existing Kinmundy – Salem West 138 kV transmission line | IL | Ameren Services Company |  | GIP |  | 2025-12-01 | 138 | 10500000
Central | AmerenIL | 24780 | Fayetteville Bee Hollow Substation (J1311) | The Fayetteville Bee Hollow Substation will be rebuilt to a 4 position (6 position ultimate) 138kV ring bus to allow J1311 interconnection. | IL | Ameren Services Company |  | GIP |  | 2025-12-01 | 138 | 8000000
Central | AmerenIL | 24781 | New Greenwave 138kV Substation (J1232) | The J1232 Generating Facility will interconnect at the Greenwave substation cutting the Mattoon West-Arland-1539 138 kV Transmission Line. | IL | Ameren Services Company |  | GIP |  | 2025-12-01 | 138 | 8000000
West | ATC | 24782 | J1304 J1305 J1460 MPFCA Network Upgrades | Transmission owner will reconductor one of the two segments of the line UNIG52. | WI | American Transmission Co. LLC |  | GIP |  | 2025-12-31 | 138 | 4930697
West | ATC | 24783 | Hodag SS, DIC, Add Additional Transformer | Expand and reconfigure substation to a loop through straight bus configuration. | WI | American Transmission Co. LLC |  | Other | Load Growth | 2024-12-31 | 115 | 2700000
West | ATC | 24784 | Ellisville SS, DIC, New Substation | ATC will construct approximately 0.7 miles of 138 kV double-circuit transmission line extension from line M-39 to interconnect the proposed T-D substation. • ATC will construct a 138 kV loop-through straight bus with two-line breakers and provisions for a future bus-tie breaker. | WI | American Transmission Co. LLC |  | Other | Load Growth | 2025-06-01 | 138 | 10200000
West | ATC | 24785 | Pleasant Prairie 345 kV Capacitor Bank Addition | Install four 345 kV 75 Mvar capacitor banks at Pleasant Prairie substation | WI | American Transmission Co. LLC |  | Other | Reliability | 2025-06-30 | 345 | 7600000
West | ATC | 24799 | J1377 Blitz SS Network Upgrades and Interconnection Facilities | Solar generating facility in Rock County, WI. | WI | American Transmission Co. LLC |  | GIP |  | 2026-11-12 | 345 | 14574360
West | ATC | 24801 | J1253 El Dorado SS Network Upgrades and Interconnection Facilities | Solar generating facility along with substation and network upgrades in Fond du Lac County, Wisconsin. | WI | American Transmission Co. LLC |  | GIP |  | 2027-11-12 | 345 | 50461169
West | ATC | 24802 | J1460 Sunrise SS Network Upgrades and Interconnection Facilities | Solar generating facility and substation upgrades in Rock County, WI. | WI | American Transmission Co. LLC |  | GIP |  | 2025-12-27 | 138 | 4465266
West | ATC | 24819 | Racine 345 kV Capacitor Bank Addition | Install two 345 kV 75 Mvar capacitor banks at Racine substation. | WI | American Transmission Co. LLC |  | Other | Reliability | 2025-06-30 | 345 | 8400000
West | ATC | 24838 | J1316 Paris SS Network Upgrades | J1316 is an energy storage facility interconnected at the same location as J878, a solar facility located in Kenosha County, WI. | WI | American Transmission Co. LLC |  | GIP |  | 2028-12-29 | 345 | 22432466
South | Entergy-TX | 24839 | J1671 230 kV Interconnection Project(Rocky Creek to Veteran) | Facilities required for the interconnection of J1671 on the Rocky Creek to Veteran 230 kV. | TX | Entergy |  | GIP |  | 2025-12-04 | 230 | 18847000
Central | AmerenIL | 24840 | New Zeke 345kV J1263 Interconnection Switching Station | New 345¿kV Switching Station on Casey West – Kansas 345 kV for the Generating Facility J1263 | IL | Ameren Services Company |  | GIP |  | 2025-12-01 | 345 | 10000000
West | ATC | 24841 | J1214 J1326 J1377 J1410 J1411 MPFCA Network Upgrades | Network upgrades to support new interconnections J1214 (solar), J1326 (storage), J1377 (solar), J1410 (solar), J1411 (storage). | WI | American Transmission Co. LLC |  | GIP |  | 2025-05-30 | 138 | 1279961
West | ATC | 24858 | J1253 J1410 J1411 MPFCA Network Upgrades | Network upgrades to support new interconnections J1253 (solar), J1410 (solar), and J1411 (energy storage). | WI | American Transmission Co. LLC |  | GIP |  | 2025-12-30 | 138 | 55520
Central | AmerenIL | 24859 | Casey West 345 kV- New Position for Union Center Solar(J1204) | A new 345 kV position will be constructed at Casey West Substation to serve as the Point of Interconnection for Union Center Solar, LLC under GIA J1204. The CSYW-NWTY-1 line position will also be moved from the southwest corner of the substation to the southeast corner to avoid line crossing with the IC. | IL | Ameren Services Company |  | GIP |  | 2025-12-01 | 345 | 1200000
Central | AmerenMO | 24860 | Bullion 161 kV Add Breaker Position for Kelso 2 Solar (J1299) | This project will construct a new Point of Interconnection for the Interconnection Customer's Generating Facility, Kelso 2 Solar LLC, to the Buillion Switching Station. The 161 kV lead line from Kelso 2 Solar LLC will terminate into the fourth position. | MO | Ameren Services Company |  | GIP |  | 2025-12-01 | 161 | 1000000
South | Entergy-LA | 24861 | J1583 Interconnection on Evergreen to Donaldsonville 230 kV | Facilities required for the interconnection of J1583 on the Evergreen to Donaldsonville 230 kV. | LA | Entergy |  | GIP |  | 2025-06-01 | 230 | 5000000
South | Entergy-LA | 24862 | J1644 Generator Interconnection on Champagne to Plaisance 138 kV | Facilities required for the interconnection of J1644 on the Champagne to Plaisance 138 kV. | LA | Entergy |  | GIP |  | 2024-12-15 | 138 | 4329000
Central | AmerenIL | 24878 | Ashley-IL 138 kV New Position for Ashley Solar (J1216) | This project will tap into the existing Ashley 138 kV 3-position ring bus to serve as the Point of Interconnection for the Interconnection Customer's Generating Facility, Ashley Solar, LLC. The existing ASHL-JORD-1536 138 kV transmission line will be raised to provide adequate space for the new interconnection line. The 138 kV lead line from Ashley Solar, LLC will terminate into the third position. | IL | Ameren Services Company |  | GIP |  | 2025-12-01 | 138 | 1000000
South | Entergy-AR | 24879 | Prairie Creek 161kV: POI for J1816 | A new interconnection three breaker ring-bus substation will be constructed on the Fisher - Cherry Valley 161kV transmission line. Line protection and breaker control panels will be installed at Newport and Parkin 161kV stations. The existing wave trap will be removed from Pecan Street 161kV station. New underground fiber will be installed between Prairie Creek and Cherry Valley 161kV substation. | AR | Entergy Arkansas |  | GIP |  | 2025-11-01 | 161 | 12604000
South | Entergy-MS | 24880 | Cotton Blossom 230 kV: Solar Interconnection (J1747) | Interconnect a 50 MW solar generation facility to the Cotton Blossom 230 kV substation. | MS | Entergy Mississippi |  | GIP |  | 2024-07-31 | 230 | 724000
South | Entergy-AR | 24898 | Flat Lake 161kV J1562: Cut-in Switching Station | The interconnection customer will self build the switching station needed to interconnect J1562 200 MW solar project. The cut-in will connect the new POI station to the existing Blytheville I-55 and AECC Blytheville North 161kV line section. Entergy will install new line protection panel and breaker control panel at Blytheville I-55 161kV substation and AECC Blytheville North 161kV substation. Two existing breakers at Blytheville Elm St. 161kV will also be replace with new surge arresters, line protection and breaker control panels and a new RTU. New underground fiber will be installed between the new POI station to Blytheville I-55 and AECC Blytheville North substations. | AR | Entergy Arkansas |  | GIP |  | 2025-01-31 | 161 | 5161000
South | Entergy-MS | 24899 | Twinkletown 230 kV: Solar Interconnection (J1748) | Interconnect a 100 MW generation facility to the Twinkletown 230 kV substation. | MS | Entergy Mississippi |  | GIP |  | 2024-07-31 | 230 | 672000
Central | AmerenIL | 24900 | Ipava 138 kV New Position (J1383) | Interconnection Facilities shall consist of one 138 kV terminal in the Ipava substation to connect the J1383 leadline. | IL | Ameren Services Company |  | GIP |  | 2025-12-01 | 138 | 1000000
Central | AmerenIL | 24901 | Morganfield 138 kV New Position (J1302) | Add 138 kV terminal in the Morganfield substation to connect the J1302 and J1096 leadline to the Morganfield substation | IL | Ameren Services Company |  | GIP |  | 2025-12-01 | 138 | 1000000
West | XEL | 24902 | Brookings - Lyon, Hampton - Helena OPGW Replacement | This project will replace the aging OPGW on the Brookings - Lyon County and Hampton - Helena 345kV lines. This project will be performed in tandem with the installation of the Brookings - Lyon County and Hampton - Helena 2nd circuit installation project. | MN,SD | Northern States Power (Xcel Energy) |  | MVP |  | 2025-09-01 | 345 | 4007320
South | Entergy-AR | 24918 | Hamrick 161kV J1842: Cut-in Switching Station | The Hamrick 161kV switching station will be constructed for the 135 MW wind farm (J1842) per the terms of the executed GIA. The wind farm will be connected by a 4 mile 161kV gen-tie line to the new Hamrick 161kV SS that will be constructed by the Interconnection Customer. Entergy Arkansas will construct the the 161kV cut-in as well as relay settings updates at the remote end stations. New underground fiber will also be installed between Hamrick and Wynne South 161kV. | AR | Entergy Arkansas |  | GIP |  | 2024-10-31 | 161 | 2073000
South | Entergy-TX | 24920 | Cole Road 138 kV New Customer Station | Entergy is proposing to construct a new 138 kV transmission station called Cole Road 138 kV which will serve a new industrial customer’s 10 MW of load near Cleveland, TX. Cole Road 138 kv station will be cut into the Jacinto to Splendora 138 kV line. | TX | Entergy |  | Other | Load Growth | 2024-10-31 | 138 | 29600000
West | MEC | 24923 | Sidney-Percival 69 kV Line Rebuild | Rebuild the Sidney-Percival 69 kV line and replace line structures. | IA | MidAmerican Energy Company |  | Other | Age and Condition | 2025-06-01 | 69 | 9100000
South | Entergy-AR | 24938 | Driver - Hybar 230kV: New transmission line | Entergy Arkansas will build a new 2 mile 230kV radial transmission line from the Driver 230kV substation to a new customer build Hybar 230kV substation. A new circuit breaker and relay upgrades will be needed at Driver 230kV substation. Two 500kV transmission lines will be raised for the new 230kV line crossing. | AR | Entergy Arkansas |  | Other | Load Growth | 2025-05-01 | 230 | 10632090
West | MDU | 24978 | Tatanka Load Addition | MDU will be signing agreement to serve 100 MW of load at the Tatanka Wind Farm collector substation off the Tatanka South Substation. There will be no cost to MDU to serve the customer. | SD,ND | Montana-Dakota Utilities Company |  | Other | Load Growth | 2023-12-01 | 230 | 0
South | Entergy-TX | 24984 | J1760 Generator Interconnection on Plum Grove to Colony 230 kV | Facilities required for the interconnection of J1760 on the Plum Grove to Colony 230 kV. | TX | Entergy |  | GIP |  | 2026-06-01 | 230 | 16300000
South | Entergy-LA | 24985 | J1827 Generator Interconnection Bastrop Tap 115 kV | Facilities required for the interconnection of J1827 at the Bastrop Tap 115 kV station. | LA | Entergy |  | GIP |  | 2026-04-01 | 115 | 18500000
South | Entergy-LA | 24986 | J1795 Generator Interconnection on Richard to Bayou Cove 138 kV(Ln 258) | Facilities required for the interconnection of J1795 on the Richard to Bayou Cove 138 kV Line 258. | LA | Entergy |  | GIP |  | 2025-12-04 | 138 | 17700000
West | MEC | 24999 | Southland Expansion & Upgrades | Expand 345 kV bus at existing Southland Substation to serve new customer load. Construct new 345 kV line from Overland Trail to Pony Creek Substation, reroute the existing Pony Creek-Rolling Hills 345 kV line into Southland Substation and rebuild the existing CBEC-Pony Creek 345 kV line. | IA | MidAmerican Energy Company |  | Other | Load Growth | 2027-06-03 | 345 | 58000000
East | METC | 25038 | Murphy - Orr Road #3 138 kV Line | Construct a 3rd 138 kV circuit from Murphy to Orr Rd utilizing 954 ACSR on the open side of the existing structures currently carrying the Orr Rd-Murphy #2 138 kV circuit. This scope will potentially add some structures at Murphy and Orr Road station ends to terminate the new 138 kV line. Install OPGW on the new circuit and terminate it at both ends. Install a new breaker at Murphy Pos. 4B7, and install a new breaker at Orr Road Pos. 6B7. | MI | METC |  | Other | Other Local Needs | 2025-03-31 | 138 | 7600000
West | ITCM | 25060 | Grant Milford Interconnection | Rebuild approximately 4 miles of existing 34.5 kV line to 69 kV construction standards to interconnect new IPL Grant Milford substation and facilitate future area conversion to 69 kV operation as part of CIPCO's SW IA 34.5 to 69 kV conversion plans. | IA | ITC Midwest |  | Other | Reliability | 2025-06-30 | 69 | 3483750
South | Entergy-LA | 25083 | J1794 Generator Interconnection on Richard to Scott 138 kV | Facilities required for the interconnection of J1794 on the Richard to Scott 138 kV | LA | Entergy |  | GIP |  | 2025-05-06 | 138 | 12840000
South | Entergy-MS | 25086 | Tinnin Road 230 kV: Solar Gen Interconnection (J1672) | Interconnect a 150 MW generation facility to the Tinnin Road 230 kV substation. | MS | Entergy Mississippi |  | GIP |  | 2025-11-16 | 230 | 5529000
South | CWL | 25094 | Commerce to Ringier 69 kV Relocation | Relocation of JCWL Commerce – Ringier 69kV line due to ARDOT project | AR | City Water & Light - Jonesboro, Arkansas |  | Other | Other Local Needs | 2023-09-30 | 69 | 315000
South | Entergy-LA | 25101 | J1564 Generator Interconnection on the Bogalusa to Talisheek 230 kV | Facilities required for the interconnection of J1564 on the Bogalusa to Talisheek 230 kV | LA | Entergy |  | GIP |  | 2025-12-22 | 230 | 18820000
South | Entergy-TX | 25102 | J1709 Generator Interconnection at Grimes 138 kV | Facilities required for the interconnection of J1709 at the Grimes 138 kV station. | TX | Entergy |  | GIP |  | 2025-02-01 | 138 | 7212000
South | Entergy-LA | 25122 | J1542 Generator Interconnection on Vacherie to Chackbay 230 kV | Facilities required for the interconnection of J1542 on the Vacherie to Chackbay 230 kV | LA | Entergy |  | GIP |  | 2026-06-01 | 230 | 19300000
South | Entergy-LA | 25140 | J1669 Generator Interconnection on Lake Charles Bulk to Henning 138 kV | Facilities required for the interconnection of J1669 on the Lake Charles Bulk to Henning 138 kV | LA | Entergy |  | GIP |  | 2025-12-04 | 138 | 16910000
South | Entergy-LA | 25143 | J1602 Generator Interconnection at Rilla 115 kV | Facilities required for the interconnection of J1602 at Rilla 115 kV. The J1602 battery will be interconnected behind the main step up transformer for J1239 (Rilla 115 kV POI) | LA | Entergy |  | GIP |  | 2024-10-25 | 115 | 0
West | ATC | 25154 | CRP Substation Ethernet Migration (Phase 2) | The telecommunication companies will construct fiber infrastructure to the substation locations. This fiber will extend from the road right of way to a telecommunications handhole located outside of the fence. When a handhole does not exist outside of the fence, a new ATC owned handhole will be installed. • The telecommunication companies will install fiber from this handhole through existing conduit and into the control house. • The telecommunication companies will install a network interface device (NID) and any other needed associated equipment on the telecommunications board to terminate their fiber. • ATC will power the NID from at least one direct current (DC) circuit and will coordinate turn up of the new ethernet circuit with the telecommunication companies. • ATC will coordinate with AT&T for the decommissioning of the existing T1 service. • ATC will replace the substation router at 14 locations. Some of these locations will also require a cellular router and cell booster to be installed as the backup communications medium, replacing the existing plain old telephone service (POTS). • ATC will install Voice over Internet Protocol (VoIP) phones at ATC owned control houses with existing analog phones. | WI,MI | American Transmission Co. LLC |  | Other | Other Local Needs | 2024-06-30 | 0 | 5500000
West | ATC | 25207 | Forsyth - Empire (Forsyth) 138 kV, Rerate | Rerate Line Forsyth conductor for the Forsyth to Empire section to keep up with the system demand. The thermal study identified 18 clearance issues needed to be fixed to bring the rating up to meet Operations/Planning's needs. | MI | American Transmission Co. LLC |  | Other | Reliability | 2024-10-20 | 138 | 5000000
South | Entergy-LA | 25242 | Amite South Reliability Project Phase 1 - alternative | Construct 500/230 kV Commodore station near the existing Derrick 230 kV Station o Cut in Derrick to Iberville and Richardson to Wise 230 kV lines. Cut in the Webre to Bayou Labutte 500 kV line o Install one 500-230 kV Autotransformer o Commodore 230 kV station will be a breaker and half station o Commodore 500 kV station will be a 4 breaker ring • Construct a new ~60 mile 230 kV line between Commodore and Waterford. • Construct a new ~85 mile 500 kV line between Commodore and Churchill. • Expand Waterford 500 kV into a three-breaker ring. Add additional bay at Waterford 230 kV to accommodate the new 230 kV line. • Construct a new 500 kV four-breaker ring at Churchill, to accommodate two 500 kV lines and two Autotransformers. Install two 500-230 kV Autotransformers. • Convert existing Waterford to Churchill 230 kV to 500 kV operation. | LA | Entergy |  | Other | Reliability | 2028-07-01 | 500 | 1700000000
West | SMMPA | 25252 | Fairmont, MN Area 69kV Transmission Expansion | Building of a new 69/12.5kV distribution substation “West Industrial Park” (WIP) west of Fairmont, construction of a new 69 kV SMMPA breaker station and construction two 69kV transmission lines, one from WIP to the SMMPA’s Fairmont Energy Station (FES) substation (approx. 2mi) and one from WIP which will tap Great River Energy’s 69 kV line between Rutland substation and the Fairmont 10th Street Substation (0.5mi). | MN | Southern Minnesota Municipal Power Agency |  | Other | Load Growth | 2026-03-01 | 69 | 8920000
West | OTP | 25256 | OTP Jamestown, ND Load Addition #2 | OTP has received a customer request to add an additional 10 MWs of load at an existing site that is being served from the Jamestown 345 kV substation. In order to serve this new load, the 115 kV bus at the Jamestown 345 kV substation will be expanded to allow for the addition of a new 115/41.6 kV transformer. The 41.6 kV side will serve the new load and be tied into the existing 41.6 kV transmission system to provide backup via a normally open breaker. | ND | Otter Tail Power Company |  | Other | Load Growth | 2024-06-01 | 115 | 3250000
West | ATC | 25262 | J1305 Norwegian Creek SS Network Upgrades and Interconnection Facilities | Solar generating facility in Green County, Wisconsin. | WI | American Transmission Co. LLC |  | GIP |  | 2023-11-08 | 138 | 8132415

## MTEP23 Facilities
Target Appendix | App ABC | Planning Region | Geographic Location by TO Member System | PrjID | Prj Rec Date | Owner PrjID | Facility ID | Record Date | Facility Type | Expected ISD | From Sub | To Sub | Ckt | Max kV | Min kV | Facility Rating | Description | Map Grid | State | Miles Upgrade | Miles New | Plan Status | Estimated Cost | Estimate Type | Gen Int Upgrade Type | Est. Year Dollars | Comments | Emerg. Rating | Submitting Comp. | TSR Cond Upg | Cost Shared | Postage Stamp
A in MTEP23 | C | West | MDU | 23633 |  |  | 27374 | 45114 | LN | 2023-02-15 | Ellendale 345 |  |  | 34.5 |  |  | New overhead line, bus work, and relaying. |  | ND |  |  | M5_In Service | 3060359.76 | Actual |  | 2022 |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 23596 |  |  | 27381 | 45183 | LN | 2025-10-31 | Glenham | Mobridge |  | 41.6 |  |  | Relocation of line to new sub |  | SD |  |  | Planned | 600000 |  |  | 2022 |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 23596 |  |  | 27380 | 45183 | LN | 2025-10-31 | Glenham | Selby |  | 41.6 |  |  | Relocation of line to new sub |  | SD |  |  | Planned | 600000 |  |  | 2022 |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 23596 |  |  | 27379 | 45183 | LN | 2025-10-31 | Glenham | Greenway |  | 41.6 |  |  | Relocation of line to new sub |  | SD |  |  | Planned | 600000 |  |  | 2022 |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 23634 |  |  | 27394 | 44936 | LN | 2025-12-31 | Wishek | REC |  | 41.6 |  |  | Line rerouted to new location in sub |  | ND |  |  | Planned | 500000 | Planning Preliminary |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 23634 |  |  | 27390 | 44936 | LN | 2025-12-31 | Wishek | Greenway |  | 41.6 |  |  | Relocation of line to new sub |  | ND |  |  | Planned | 500000 | Budgetary |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 23634 |  |  | 27389 | 44936 | LN | 2025-12-31 | Wishek | Ellendale |  | 41.6 |  |  | Relocation of line to new sub |  | ND |  |  | Planned | 500000 | Budgetary |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 23634 |  |  | 27388 | 44936 | LN | 2025-12-31 | Wishek | Ellendale |  | 41.6 |  |  | Relocation of line to new sub |  | ND |  |  | Planned | 500000 | Budgetary |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 23634 |  |  | 27387 | 44936 | LN | 2025-12-31 | Wishek | Herbert Weber |  | 41.6 |  |  | Relocation of line to new sub |  | ND |  |  | Planned | 500000 | [5 empty] | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | ATC | 24575 |  | PR09254 | 28046 | 45182 | LN | 2026-06-01 | Council Creek | Hilltop | Y-74 | 69 |  |  | New T-T interconnection to Council Creek-Hilltop 69 kV (Y-74), and constructing a new 69 kV loop-through substation near New Lisbon Tap with three line breakers to replace an existing three-way GOAB. |  | WI |  |  | Planned | 11100000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | B | Central | AmerenMO | 21928 |  |  | 26537 | 45124 | LN | 2025-02-06 | Salem Bulk | Valley View | 1 | 69 |  | 81MVA | Construct 69 kV line from Valley View Substation to new Kinsey 69/12.47 kV Substation, 477 kcm ACSR, 4.8 miles. This line is needed to serve the new Kinsey Substation and Loop Valley View to Salem Bulk. |  | MO |  | 20.5 | Planned | 44520000 | Engineering |  |  |  | 81MVA | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP23 | C | Central | DEI | 23868 |  | WVPA-2023-4 | 27648 | 45168 | LN | 2023-12-31 | WVPA IPC | 69162 Tap |  | 69 |  | 100 | WVPA IPC to 69162 Tap 69 kV loop: Build 69 kV from IPC to 69162 Tap 2.8 miles. Add 2 ATO switchs at IPC tap & 3 switches at 69162 line tap. 90 amps minimum. 477 ACSR. |  | IN |  | 2.8 | Proposed | 6000000 | Engineering |  | 2023 |  | 100 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23881 |  | 23-ELF-002 | 27863 | 45082 | LN | 2025-06-01 | Holiday | Elks |  | 69 |  |  | Small portion of new line connecting Holiday to Elks. |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23882 |  | 23-ELF-003 | 27867 | 44938 | LN | 2025-06-01 | Barnett Oil Mill | New Tap |  | 69 |  |  | Construct a new 69 kV line from Barnett Oil Mill to new tap point on CLECO 69 kV line near Guidry. |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23939 |  | 23-ELB-003 | 27838 | 44937 | LN | 2025-06-01 | Blount | Devil Swamp |  | 69 |  |  | Construct new 69 kV line between existing Blount and Devil Swamp stations. |  | LA |  |  | Proposed | 32300000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | West | GRE | 22871 |  | 209680 | 27833 | 45156 | LN | 2025-08-01 | Cedar Lake | Cedar Lake Tap | 1 | 69 |  |  | Relocate the existing Cedar Lake tap line to a new route to accommodate Hampton Corners - Helena 345 kV addition to the Hampton Corners - Chub Lake - Helena structures. |  | MN |  | 6.5 | Proposed | 12772504.79 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | ITCM | 23511 |  | Grinnell South | 27278 | 44945 | LN | 2025-12-15 | Grinnell South | Powesheik County | 1 | 69 | 69 |  | Grinnell South-Powesheik County 69kV line tap work associated with new Grinnell South sub. |  | IA |  |  | Proposed | 132500 | Engineering |  | 2022 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 23511 |  | Grinnell South | 27277 | 44945 | LN | 2025-12-15 | Grinnell | Grinnell South | 1 | 69 | 69 |  | Grinnell-Grinnell South 69kV line tap work for new Grinnell South sub. |  | IA |  |  | Proposed | 182500 | Engineering |  | 2022 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 23684 |  | Kittyhawk Sub Rebuild | 27414 | 44945 | LN | 2025-12-31 | Kittyhawk | Line Taps |  | 69 | 69 |  | Line tap work to allow for the expansion of the Kittyhawk 69kV substation. |  | IA |  |  | Proposed | 250000 | Engineering |  | 2022 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 24464 |  | Eagle to Tharp 69kV | 27970 | 44950 | LN | 2024-05-01 | Eagle | Tharp | 1 | 69 | 69 |  | A 0.75 section of the Eagle - Tharp 69 kV line is required to be moved to a new permanent location by the Iowa DOT due to a project to rebuild the I-380 and Wright Bros Blvd interchange. Thirteen new wooden poles, three new steel poles, and new T2-477 ACSR cabling is to be constructed as shown in the sketched figures. PTS 1158 is to be retired and PTS 1114 is to have the jumpers remade to face towards Eagle. PTS 1114 will remain in this configuration until the switch is retired with the Kitty Hawk rebuild |  | IA |  | 0.75 | Proposed | 1618750 | Engineering |  | 2023 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 24740 |  | Commercial 69kV Sub | 28074 | 45015 | LN | 2024-06-01 | Commercial (JCE) | Chadwick | 1 | 69 | 69 |  | Line tap for the new Commercial 69kV Substation. |  | IL |  |  | Proposed | 422500 | Construction |  | 2023 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 24740 |  | Commercial 69kV Sub | 28073 | 45015 | LN | 2024-06-01 | Commercial (JCE) | Savanna | 1 | 69 | 69 |  | Line tap for the new Commercial (JCE) Substation. |  | IL |  |  | Proposed | 302500 | Engineering |  | 2023 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | MEC | 23720 |  |  | 27417 | 44812 | LN | 2025-06-01 | Hickory Avenue | Sioux Center |  | 69 |  |  | Construct new 69 kV line from Hickory Avenue Substation to Sioux Center Substation. Expand Hickory Avenue and Sioux Center Substations to install new 69 kV line terminals |  | IA |  |  | Planned | 7000000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | B | Central | PPI | 19947 |  |  | 25630 | 45160 | LN | 2027-12-31 | Allen | Mason City | 1 | 69 | 69 | 69 | New Allen-Mason City 556 ACSR 69 kV line |  | IL |  | 9 | Proposed | 6367500 | Budgetary |  | 2023 |  | 69 | Prairie Power, Inc. | N | N | N
A in MTEP23 | B | Central | PPI | 19948 |  |  | 25631 | 45100 | LN | 2027-12-31 | Mason City | Middletown | 1 | 69 | 69 | 69 | New Mason City-Middletown 556 ACSR 69 kV line |  | IL |  | 13 | Proposed | 9197500 | Budgetary |  | 2021 |  | 69 | Prairie Power, Inc. | N | N | N
A in MTEP23 | C | Central | PPI | 23350 |  |  | 27070 | 45100 | LN | 2027-12-31 | Forest City | Allen Tap | 1 | 69 | 69 | 69 | New Forest City-Allen Tap 556 ACSR 69 kV line |  | IL |  | 4.4 | Planned | 2880000 | Planning |  | 2022 |  | 69 | Prairie Power, Inc. | N | N | N
A in MTEP23 | C | Central | PPI | 23427 |  |  | 27078 | 45100 | LN | 2026-12-31 | Disco | Carthage | 1 | 69 | 69 | 50 | New Disco-Carthage 336 ACSR 69 kV line |  | IL |  | 13 | Planned | 8320000 | Budgetary |  | 2022 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP23 | C | Central | PPI | 23428 |  |  | 27079 | 45100 | LN | 2026-12-31 | Golden | Denver | 1 | 69 | 69 | 50 | New Golden-Denver 336 ACSR 69 kV line |  | IL |  | 20 | Planned | 12800000 | Budgetary |  | 2022 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP23 | C | Central | PPI | 23532 |  |  | 27313 | 45160 | LN | 2029-12-31 | Pleasant View | Moweaqua | 1 | 69 | 69 | 50 | New Pleasant View-Moweaqua 336 ACSR 69 kV line |  | IL |  | 3.5 | Planned | 4375000 | Planning |  | 2023 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP23 | C | Central | PPI | 23532 |  |  | 27318 | 45160 | LN | 2029-12-31 | Yantisville | Henton | 1 | 69 | 69 | 50 | New Yantisville-Henton 336 ACSR 69 kV line |  | IL |  | 7.81 | Planned | 5076500 | Planning |  | 2023 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP23 | C | Central | PPI | 23532 |  |  | 27317 | 45160 | LN | 2029-12-31 | Moweaqua | Yantisville | 1 | 69 | 69 | 50 | New Moweaqua-Yantisville 336 ACSR 69 kV line |  | IL | 9.51 | 12.1 | Planned | 14046500 | Planning |  | 2023 |  | 50 | Prairie Power, Inc. | N | N | N
A in MTEP23 | B | South | SMEPA | 12222 |  |  | 27676 | 44946 | LN | 2023-06-01 | Maxie |  |  | 69 |  |  | In order to serve the Maxie delivery point economically and reliably, service will be established by a short looped transmission feed that will connect the Maxie delivery point with Cooperative Energy Lines 37 and 38. |  | MS |  |  | Proposed | 49497 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | West | SMMPA | 25252 |  |  | 28345 | 45155 | LN | 2026-03-01 | Fairmont Energy Station | West Industrial Park Substation | 1 | 69 | 12.5 | 117 | Approximately 2 miles of 69kV transmission line being built on preexisting ROW and on new ROW as applicable. |  | MN |  | 2 | Proposed | 3520000 | Engineering Preliminary |  | 2023 |  | 129 | Southern Minnesota Municipal Power Agency | N | N | N
A in MTEP23 | C | West | XEL | 23446 |  |  | 27206 | 44785 | LN | 2024-06-15 | Hormel | W3503 Tap | 1 | 69 |  |  | Construct a new line from the end of the existing line W3502 to Xcel’s W3503 1.3 miles to the east. The new connection would be made with a group of one way pole mounted switches. |  | WI |  | 1.3 | Planned | 1500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23447 |  |  | 27208 | 44785 | LN | 2025-12-01 | Birchwood | W3510 | 1 | 69 |  |  | Extend the line from Birchwood substation to the east to connect to Xcel line W3510 in the vicinity of the town of Wieger, a distance of about 13 miles. Install motor operated switches at Birchwood to sectionalize the line. Install manual switches at the connection to W3510. The line would initially be operated as a normally open second source to Birchwood. |  | WI |  | 13 | Planned | 9000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | MEC | 23571 |  | T90W4, T90W7, T90W8, T90WA | 27330 | 45156 | TAP | 2027-12-01 | Humboldt East | Humboldt (Corn Belt) |  | 69 |  |  | T90W8: Remove approximately 1 miles section of 69 kV line. Remove 69 kV line switch 7108. |  | IA |  |  | Planned | 100000 | Budgetary |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23571 |  | T90W4, T90W7, T90W8, T90WA | 27329 | 45156 | TAP | 2027-12-01 | Humboldt East | Humboldt Central |  | 69 |  |  | T90W7: Build approximately 1/4 mile of 69 kV line to form the Humboldt East-Humboldt Central 69 kV line. |  | IA |  |  | Planned | 1500000 | Budgetary |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23687 |  |  | 27424 | 45156 | TAP | 2026-12-01 | Storm Lake East | CBPC Storm Lake |  | 69 |  |  | Construct 69 kV line taps into new Storm Lake Industrial 69-13.8 kV Substation |  | IA |  |  | Proposed | 800000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | Central | PPI | 23429 |  |  | 27080 | 45170 | TAP | 2023-07-01 | Feldon |  |  | 69 | 69 | 72 | Install two line switches between Hardin Tap-Eldred 69 kV line |  | IL |  |  | M5_In Service | 100000 | Budgetary |  | 2022 |  | 72 | Prairie Power, Inc. | N | N | N
A in MTEP23 | B | South | SMEPA | 12222 |  |  | 28009 | 44957 | TAP | 2023-06-01 | Maxie |  |  | 69 |  |  | In order to serve the Maxie delivery point economically and reliably, service will be established by a short transmission feed by tapping the Cooperative Energy Lines 37 and 38 that are near the delivery point. |  | MS |  |  | Proposed | 125000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | West | XEL | 23514 |  |  | 27287 | 44792 | TAP | 2024-12-31 | Sauk Centre | West Union | 1 | 69 |  |  | Build three 1-way switches on line 0794 to accommodate new Sauk Centre Municipal distribution substation. |  | MN |  |  | Planned | 800000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | SMMPA | 25252 |  |  | 28347 | 45155 | LN | 2023-03-01 | West Industrial Park Substation | West Tap |  | 69 |  | 117 | New 0.5mi 69kV transmission line being built on new ROWs. |  | MN |  | 0.5 | Proposed | 880000 | Engineering Preliminary |  | 2023 |  | 129 | Southern Minnesota Municipal Power Agency | N | N | N
A in MTEP23 | C | South | Entergy-MS | 23786 |  |  | 27523 | 44946 | LN | 2026-06-01 | Ft Redwood | Rawhide | 1 | 115 |  |  | Construct a new 115kV line from a new Cooperative Energy owned 115kV switching station near the FT Redwood substation to the new Cooperative Energy owned 115kV switching station near Rawhide Road. |  | MS |  |  | Proposed | 7000000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | West | MDU | 23596 |  |  | 27383 | 45183 | LN | 2025-10-31 | Glenham | Mobridge |  | 115 |  |  | Relocation of line to new sub |  | SD |  |  | Planned | 600000 |  |  | 2022 |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 23596 |  |  | 27382 | 45183 | LN | 2025-10-31 | Glenham | Bowdle East |  | 115 |  |  | Relocation of line to new sub |  | SD |  |  | Planned | 600000 |  |  | 2022 |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 23634 |  |  | 27391 | 44936 | LN | 2025-12-31 | Wishek | Linton NW |  | 115 |  |  | Relocation of line to new sub |  | ND |  |  | Planned | 650000 | Budgetary |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | OTP | 23806 |  |  | 27552 | 45058 | LN | 2024-12-31 | Hetland 115 kV (620209) | Lake Preston 115 kV (New) | 1 | 115 |  |  | Construction of a new approximate 9.5 mile 115 kV line from Hetland 115 kV substation to a new Lake Preston 115 kV substation. |  | SD |  |  | M1_Final SPM or OOC | 5600000 | Engineering Preliminary |  | 2023 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23806 |  |  | 27556 | 45058 | LN | 2024-12-31 | Lake Preston 115/34.5 kV (new) | Brookings County 115 kV (603192) | 1 | 115 |  |  | A new approximate 45 mile 115 kV line from a new Lake Preston 115/34.5 kV substation to Xcel's Brookings County 345/115 kV substation. |  | SD |  |  | M1_Final SPM or OOC | 25900000 | Engineering Preliminary |  | 2023 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23896 |  |  | 27585 | 45125 | LN | 2026-12-31 | New Tap along Devils Lake East - Sweetwater 115 kV line | New Devils Lake 115/12.5 kV Distribution Substation | 1 | 115 |  |  | New approximate 2 mile 115 kV line from the new tap along the Devils Lake East - Sweetwater 115 kV to the new 115/12.5 kV distribution substation. Addition of a 115 kV breaker on the high side of the 115/12.5 kV transformer. |  | ND |  |  | Proposed | 1250000 | Planning |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23936 |  |  | 27661 | 45058 | LN | 2026-12-31 | Milbank 115/12.5 kV | New Switching Station on Big Stone - Marietta 115 kV line |  | 115 |  |  | Construct a new approximate 15 mile 115 kV line from Milbank 115/12.5 kV substation to a new switching station on the Big Stone - Milbank 115 kV line. |  | SD |  |  | M1_Final SPM or OOC | 9800000 | Engineering Preliminary |  | 2023 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23936 |  |  | 27658 | 45058 | LN | 2024-12-31 | Big Stone (620214) | New Milbank 115/12.5 kV substation | 1 | 115 |  |  | Construct a new approximate 12.5 mile 115 kV line from Big Stone 115 kV to a new Milbank 115/12.5 kV substation |  | SD |  |  | M1_Final SPM or OOC | 8100000 | Engineering Preliminary |  | 2023 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | South | SMEPA | 23941 |  |  | 27665 | 45175 | LN | 2024-06-01 | Silver Creek |  |  | 115 |  |  | In order to serve the Silver Creek delivery point economically and reliably, service will be established by tapping the Cooperative Energy owned Line 571 115kV line. A 115kV GOAB will be installed at the tap point and a new 115kV tap line will be constructed to the delivery point. |  | MS |  |  | Proposed | 150000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | West | OTP | 23896 |  |  | 27584 | 45125 | TAP | 2026-12-31 | Devils Lake East 115 kV (620265) | Sweetwater (657720) | 1 | 115 |  |  | Tap the Devils Lake East 115 kV to Sweetwater 115 kV line with a two way 115 kV switch. |  | ND |  |  | Proposed | 300000 | Planning |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | South | SMEPA | 23941 |  |  | 27664 | 45175 | TAP | 2024-06-01 | Silver Creek |  |  | 115 |  |  | In order to serve the Silver Creek delivery point economically and reliably, service will be established by tapping the Cooperative Energy owned Line 571 115kV line. A 115kV GOAB will be installed at the tap point and a new 115kV tap line will be constructed to the delivery point. |  | MS |  |  | Proposed | 200000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | West | XEL | 23547 |  |  | 27286 | 44792 | TAP | 2023-06-15 | Elm Creek | Champlin Tap | 1 | 115 |  |  | New GRE interconnection (MTEP ID 21829). Xcel will own high side of new sub with an in-and-out configuration on the Elm Creek - Champlin Tap 115kV line. |  | MN |  |  | Planned | 5000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | East | ITCT | 24593 |  |  | 28050 | 44970 | LN | 2025-05-31 | Pontiac | Sunbird | 2 | 120 |  |  | Create a second Pontiac-Sunbird 120 kV line by rebuilding existing lines to double circuit structures between the 2 substations. |  | MI |  | 2.67 | Planned | 5901000 | Engineering |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP23 | B | East | ITCT | 24072 |  | ITCT_22_043 | 27732 | 44935 | LNug | 2026-12-31 | Alfred | Frisbie | 1 | 120 |  |  | Bypass Resource substation to form a direct Alfred-Frisbie 120 kV line. |  | MI |  | 0.01 | Proposed | 3070000 | Engineering |  |  |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 22014 |  |  | 26662 | 45068 | TAP | 2024-12-31 | ITCT 120 kV Lines |  |  | 120 |  |  | Install or replace an existing pole top switch with a new 120 kV, 1-way full-load-break pole top switch at tap points. |  | MI |  |  | Proposed | 2400000 | Budgetary |  | 2021 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 23976 |  |  | 27689 | 44819 | TAP | 2025-12-31 | ITCT 138 kV Lines |  |  | 120 |  |  | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. |  | MI |  |  | Proposed | 2400000 | Budgetary |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23026 |  | TP1570 | 27377 | 44806 | LN | 2028-06-01 | Benton NW | Franklin |  | 138 |  |  | Benton NW to Franklin 138 kV line |  | IL |  |  | Proposed | 22100000 | [5 empty] | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23026 |  | TP1570 | 27376 | 44806 | LN | 2027-12-01 | Kays | Hamilton |  | 138 |  |  | New Kays to Hamilton 138 kV line |  | IL |  |  | Proposed | 51000000 | Budgetary |  |  |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23026 |  | TP1570 | 27375 | 45158 | LN | 2026-12-01 | Reifen | Kays |  | 138 |  |  | New 138 kV line from Reifen to Kays |  | IL |  |  | Proposed | 51000000 | Budgetary |  |  |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23026 |  | TP1570 | 26942 | 45160 | LN | 2025-12-01 | Reifen | Mt Vernon 42 2nd |  | 138 |  |  | Construct a ~3.5 mile 138 kV line from Mt. Vernon 42nd St. to the new substation |  | IL |  |  | Planned | 18500000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23632 |  | TP1027 | 27371 | 44987 | LN | 2024-12-01 | Beehive | Dupo Ferry |  | 138 |  |  | New 138 kV line from Beehive to Dupo Ferry |  | IL |  |  | Planned | 4000000 | Construction |  |  |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL, AmerenMO | 23846 |  | TP1718 | 27633 | 44819 | LN | 2026-12-01 | Grand Tower | Wittenberg |  | 138 |  |  | Construct a new greenfield line between Wittenberg and Grand Tower. The Grand Tower - Wittenberg line will include a new Mississippi river crossing. |  | IL,MO |  |  | Proposed | 0 | [5 empty] | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | DEI | 23864 |  |  | 27622 | 44819 | LN | 2028-06-01 | West of Bloomington 345 (new) | Bloomington Rogers St. | 1 | 138 |  | 602 | Build new 138kV line from new West of Bloomington 345 Sub to Rogers St. |  | IN |  | 9.14 | Proposed | 23500000 | Planning Preliminary |  | 2022 |  | 602 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | East | METC | 22147 |  |  | 26711 | 45001 | LN | 2024-10-01 | Blackstone | Stable |  | 138 |  |  | Extend the Blackstone - Stable 138kV line to loop in the J1310 Interconnection station |  | MI |  | 0.2 | M2a_Pre-Project Approval | 8724000 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 22165 |  |  | 26715 | 44935 | LN | 2023-08-01 | Brooks Industrial | Mud Lake |  | 138 |  |  | Extend the Brooks Industrial - Mud Lake 138kV line to loop in the J1430 Interconnection station. |  | MI |  |  | M2a_Pre-Project Approval | 2355600 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23785 |  |  | 27519 | 45028 | LN | 2025-01-01 | Batavia | Coldwater |  | 138 |  |  | Extend the Batavia - Coldwater 138kV line 1.5 miles to loop in the J1550 POI station. OPGW will be required on the line as well. |  | MI | 0 | 1.5 | Proposed | 5091840 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23785 |  |  | 27516 | 45001 | LN | 2025-01-01 | Batavia | Barton Road |  | 138 |  |  | Extend the Batavia - Barton Lake 138kV line 0.2 miles to loop in the J1550 POI station. OPGW will be required on the line as well. |  | MI |  | 0.2 | Proposed | 898560 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23865 |  | METC_22_071 | 27719 | 44841 | LN | 2025-03-01 | Mecosta | Elephant | 1 | 138 |  |  | Loop the existing Chase-Mecosta 138 kV line approx. 1.5 miles on new ROW, into the new Elephant substation. This will create 2 new 138 kV lines, Chase-Elephant and Mecosta-Elephant. |  | MI |  | 1.5 | Proposed | 2900000 | Engineering Preliminary |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24276 |  |  | 27794 | 44943 | LN | 2025-12-31 | Marquette | Vergennes | 1 | 138 | 138 |  | Extend the Vergennes - Marquette 138kV line to loop in the J1255 Generator |  | MI |  |  | Proposed | 546000 | Facility Study |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24279 |  |  | 27801 | 45001 | LN | 2026-01-28 | Claremont | Cornell | 2 | 138 | 138 |  | Extend the Claremont - Cornell 138kV line to loop in J1297 |  | MI |  |  | Proposed | 5350800 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24279 |  |  | 27799 | 45001 | LN | 2026-01-28 | Cornell | Goss |  | 138 | 138 |  | Extend the Cornell - Goss 138kV line to loop in J1297 |  | MI |  |  | Proposed | 3981600 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24282 |  |  | 27821 | 45154 | LN | 2025-03-31 | Leoni | Parr Road | 1 | 138 | 138 |  | Extend the Leoni - Parr Road 138kV line to loop in the new station. |  | MI |  |  | Proposed | 482400 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24294 |  |  | 27782 | 44944 | LN | 2025-03-31 | Iosco | Karn | 1 | 138 | 138 |  | Loop the Iosco-Karn 138kV circuit into the new J1210 switching station. |  | MI |  |  | M3_Long Lead Materials | 1357200 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24295 |  |  | 27790 | 44943 | LN | 2025-11-30 | Marshall | Blackstone | 1 | 138 | 138 |  | Extend the Marshall - Blackstone (Stable) 138kV line 0.2 miles to loop in the New Station. |  | MI |  |  | Proposed | 3170400 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24317 |  |  | 27809 | 44944 | LN | 2025-05-12 | Dupont | Cobb |  | 138 | 138 |  | Loop the Dupont - Cobb 138kV circuit into the White Lake 138kV station. |  | MI |  |  | M3_Long Lead Materials | 543600 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24317 |  |  | 27806 | 44944 | LN | 2025-05-12 | Dupont | Cobb | 1 | 138 | 138 |  | Loop the Dupont - Cobb 138kV circuit into the new J1375 switching station. |  | MI |  |  | M3_Long Lead Materials | 652800 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24318 |  |  | 27814 | 44944 | LN | 2024-05-31 | Deja | Derby | 1 | 138 | 138 |  | Rebuild approximately 8 miles of 138kV line from Derby - Deja with 954 ACSR 138kV double circuit standards. Reconductor should be where appropriate in the cost estimate. Install circuit from North Belding to the J1379 switching station using the vacant side of double circuit tower using 954 ACSR. |  | MI |  |  | M3_Long Lead Materials | 12793200 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24318 |  |  | 27811 | 44944 | LN | 2024-05-31 | Eureka | Vestaburg | 1 | 138 | 138 |  | Loop the Eureka - Vestaburg 138kV circuit into the new J1379 substation. |  | MI |  |  | M3_Long Lead Materials | 825600 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24319 |  |  | 27817 | 44944 | LN | 2025-12-31 | Delhi | Thompkins | 2 | 138 | 138 |  | J1399 Interconnection is a 90MW solar project in Lesli Township, MI. Build the J1399 Interconnection station as a breaker and half station with three 40kA breakers in a ring bus configuration. Extend the Delhi – Tompkins 138kV line to loop in the J1399 Interconnection station. J1399 is queued within the DPP 2019 Cycle 1. |  | MI |  |  | Proposed | 703200 | Facility Study |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24319 |  |  | 27819 | 44944 | LN | 2025-12-31 | Edgar | Churchhill |  | 138 | 138 |  | Disconnect the Churchill tap and add 0.5 miles of 954 ACSR to reterminate the Churchill radial at J1399. |  | MI |  |  | Proposed | 1482000 | Facility Study |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24453 |  |  | 27904 | 44946 | LN | 2025-12-31 | Hawley | Peddler |  | 138 |  |  | Install about 12 miles of 954 ACSR to connect J1255-J1292 forming circuit #1 |  | MI |  | 15 | M3_Long Lead Materials | 12099600 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24453 |  |  | 27905 | 44943 | LN | 2025-12-31 | Hawley | Peddler |  | 138 |  |  | Install about 12 miles of 954 ACSR to connect J1255-J1292 forming circuit #2 |  | MI |  | 15 | M3_Long Lead Materials | 12099600 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24673 |  |  | 28057 | 44987 | LN | 2024-05-31 | Highfield | Brooks Industrial | 1 | 138 |  |  | Cut existing line approx. 0.2 miles into Charge substation. |  | MI |  | 0.2 | Planned | 2450000 | Engineering |  | 2023 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 25038 |  | METC_23_070 | 28185 | 45092 | LN | 2025-03-31 | Murphy | Orr Road | 3 | 138 |  |  | Construct a 3rd 138 kV circuit from Murphy to Orr Rd utilizing 954 ACSR on the open side of the existing structures currently carrying the Orr Rd-Murphy #2 138 kV circuit. This scope will potentially add some structures at Murphy and Orr Road station ends to terminate the new 138 kV line. Install OPGW on the new circuit and terminate it at both ends. |  | MI |  |  | Proposed | 4800000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | East | WPSC | 24414 |  |  | 27865 | 44966 | LN | 2025-03-01 | Hersey | White Cloud |  | 138 |  |  | Build new double circuit 138kV structures from existing ROW to the new Elephant plant. |  | MI |  |  | Proposed | 6000000 | Planning |  |  |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | Central | WVPA | 23846 |  | TP1718 | 27629 | 44819 | LN | 2026-12-31 | Seminary | Wittenberg |  | 138 |  |  | Build new ~21.3 miles of 138kV between Seminary and Wittenberg. |  | MO |  |  | Proposed | 42000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | South | CLECO | 24415 |  |  | 27872 | 44938 | LN | 2024-07-15 | Turps | Ragley | 1 | 138 |  | 377 | Build a new 6.1 mile 138 kV line from Turps to Ragley |  | LA |  | 6.1 | Proposed | 15800000 | Budgetary |  |  |  | 377 | Cleco Power LLC | N | N | N
A in MTEP23 | C | East | METC | 24317 |  |  | 27807 | 44944 | LNug | 2025-05-12 | White Lake |  |  | 138 | 138 |  | Install underground fiber on the J1375 - White Lake line. |  | MI |  |  | M3_Long Lead Materials | 2064000 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23872 |  | METC_22_070 | 27551 | 44897 | TAP | 2026-12-31 | Spaulding | Broadmoor | 1 | 138 |  |  | Remove N.O. 3317 PTS |  | MI |  |  | Proposed | 116250 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23949 |  |  | 27680 | 44819 | TAP | 2025-12-31 | METC 138 kV Lines |  |  | 138 |  |  | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. |  | MI |  |  | Proposed | 2400000 | Budgetary |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | B | Central | AmerenMO | 23430 |  | TP1699 | 27082 | 45056 | LN | 2025-12-01 | Zachary | Adair |  | 161 |  |  | construct a 2nd Zachary - Adair 161 kV transmission line |  | MO |  |  | Planned | 1500000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | BREC | 23569 |  |  | 27321 | 44805 | LN | 2025-07-02 | McCracken |  | 1 | 161 |  |  | BREC McCracken to new GLH switching station. |  | KY |  |  | Proposed | 4300000 | Planning |  | 2022 |  |  | Big Rivers Electric Corporation | N | N | N
A in MTEP23 | C | Central | GLH | 23827 |  |  | 27528 | 45030 | LN | 2026-12-31 | Joppa | Joppa TS | 1 | 161 |  |  | Looping Joppa - Joppa TS - Shawnee 161 kV three terminal portion of ckt in and out of Joppa TS station. |  | IL |  | 0.4 | Proposed | 0 | [5 empty] | Gridliance | N | N | N
A in MTEP23 | C | West | ITCM | 23546 |  | Jefferson Co 161kV Ring | 27273 | 44816 | LN | 2025-12-31 | Henry County | Jefferson County | 1 | 161 | 161 |  | Line work associated with the 161kV bus conversion to a ring on the Henry County-Jefferson County 161kV line. |  | IA |  |  | Proposed | 742800 | Engineering |  |  |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 23546 |  | Jefferson Co 161kV Ring | 27272 | 44816 | LN | 2025-12-31 | Jefferson County | Woody | 1 | 161 | 161 |  | Line work associated with the 161kV bus conversion to a ring on the Jefferson County-Woody 161kV line. |  | IA |  |  | Proposed | 736800 | Engineering |  |  |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 24449 |  | Nevada Area Load Interconnections | 27985 | 45063 | LN | 2024-12-31 | Prairieview Industrial | Teller | 1 | 161 | 161 |  | Construct new Prairie view industrial - Teller 161 kV line. |  | IA |  |  | Proposed | 4517500 | Engineering |  | 2023 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 24449 |  | Nevada Area Load Interconnections | 27984 | 45063 | LN | 2024-12-31 | Ames | Prairieview | 1 | 161 | 161 |  | Construct new Ames Transmission - Prairieview Industrial 161 kV line. |  | IA |  |  | Proposed | 7325000 | Engineering |  | 2023 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 24449 |  | Nevada Area Load Interconnections | 27983 | 45063 | LN | 2024-12-31 | Teller | Verbio |  | 161 | 161 |  | Construct new lines from Teller to Verbio substation transformers. |  | IA |  |  | Proposed | 1250000 | Engineering |  | 2023 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 24449 |  | Nevada Area Load Interconnections | 27982 | 45063 | LN | 2024-12-31 | Fernald | Teller | 1 | 161 | 161 |  | Construct new Fernald - Teller 161 kV line. |  | IA |  | 8 | Proposed | 13688750 | Engineering |  | 2023 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 24513 |  | Maquoketa (CIPCPO) 161 kV Sub Rebuild | 27971 | 44950 | LN | 2024-05-30 | Grand Mound | Maquoketa | 1 | 161 | 161 |  | Relocate the Grand Mound – Maquoketa 161 kV Line Tap to new bus position in CIPCO 161 kV ring bus rebuild |  | IA |  |  | Proposed | 1067500 | Engineering |  | 2023 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 24513 |  | Maquoketa (CIPCPO) 161 kV Sub Rebuild | 27972 | 44950 | LN | 2024-05-30 | Maquoketa | Sale | 1 | 161 | 161 |  | Relocate the Grand Mound – Maquoketa 161 kV Line Tap to new bus position in CIPCO 161 kV ring bus rebuild. |  | IA |  |  | Proposed | 961250 | Engineering |  | 2023 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | MEC | 23686 |  |  | 27421 | 44812 | LN | 2026-12-01 | Obrien County | Hospers |  | 161 |  |  | Construct new 161 kV line from Obrien County Substation to Hospers Substation, expand Obrien County Substation to install 345-161 kV, 560 MVA transformer and 161 kV bus and expand Hospers Substation to install 161-69 kV, 167 MVA transformer and 161 kV bus |  | IA |  |  | Proposed | 30000000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23699 |  |  | 27411 | 45126 | LN | 2026-09-01 | Indian Creek East | Gifford Road |  | 161 |  |  | Construct Gifford Road 161-13.2 kV Sub and Line Taps |  | IA |  |  | Proposed | 1250000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23699 |  |  | 27410 | 45126 | LN | 2026-09-01 | CBEC | Gifford Road |  | 161 |  |  | Construct Gifford Road 161-13.2 kV Sub and Line Taps |  | IA |  |  | Proposed | 1250000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | B | South | SMEPA | 12210 |  |  | 28008 | 44957 | LN | 2025-06-01 | Purvis Bulk | South Hattiesburg Industrial |  | 161 |  |  | In order to serve the South Hattiesburg and Hattiesburg Industrial delivery points economically and reliably, service will be established by tapping L161 and constructing a 161kV breaker switching station. |  | MS |  |  | Proposed | 1332500 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | South | SMEPA | 23126 |  |  | 27009 | 44952 | LN | 2022-08-05 | Morrow | Purvis Bulk | 3 | 161 |  |  | Non-Stand Alone Network Upgrades: Build a new bundled 161kV line from Morrow – Purvis Bulk on a separate right-of-way corridor. |  | MS |  |  | M5_In Service | 4013000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | South | SMEPA | 23126 |  |  | 27005 | 44952 | LN | 2022-01-27 | Morrow |  |  | 161 |  |  | Interconnection Facilities: New 161kV generator tie line for new natural gas fired combustion turbine (CT). |  | MS |  |  | M5_In Service | 450000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | West | MEC | 23691 |  | H014F, H014H, T928G | 27432 | 45156 | TAP | 2026-12-31 | Sub 17 | Sub 28 | 1 | 161 |  |  | New 161 kV line taps for new Riverdale substation bisecting existing Sub 17-Sub 28 161 kV line |  | IL |  |  | Proposed | 900000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23723 |  | H01B4, H01B5, T92LM, T92LP | 27435 | 45125 | TAP | 2027-12-31 | Sub 18 | Sub 112 | 1 | 161 |  |  | New 161 kV line taps for new Edgington substation bisecting existing Sub 18-Sub 112 161 kV line |  | IL |  |  | Planned | 900000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | South | Entergy-AR | 24938 |  | 23-EAL-001 | 28139 | 45069 | LN | 2025-05-01 | Driver | Hybar |  | 230 |  |  | New 2 mile 230kV radial transmission line |  | AR |  |  | Planned | 10632090 | Planning |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23957 |  | 23-ELB-004 | 27914 | 45145 | LN | 2026-06-30 | Willow Glen | Conway |  | 230 |  |  | Construct new 14 mile 230 kV line |  | LA |  |  | Proposed | 290000000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 24252 |  | 23-ELS-008 | 27767 | 44894 | LN | 2025-09-20 | Wise | Bayou Labutte |  | 230 |  |  | Construct new Wise to Bayou Labutte 230 kV line |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 25242 |  | 23-ELS-002 | 28275 | 45166 | LN | 2028-07-01 | Commodore | Waterford |  | 230 |  |  | 60 mile 230 kV |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | West | GRE | 23877 |  | Nelson Lake 230 kV | 27670 | 44819 | LN | 2026-06-01 | Nelson Lake | Square Butte / Stanton |  | 230 |  |  | Tie in existing GRE Square Butte - Stanton 230 kV Line |  | ND |  | 0.5 | Proposed | 2000000 | Planning |  | 2022 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP23 | C | West | MDU | 23596 |  |  | 27385 | 45183 | LN | 2025-10-31 | Glenham | Bismarck WAPA |  | 230 |  |  | Relocation of line to new sub |  | SD |  |  | Planned | 750000 | [5 empty] | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 23596 |  |  | 27384 | 45183 | LN | 2025-10-31 | Glenham | Whitlock |  | 230 |  |  | Relocation of line to new sub |  | SD |  |  | Planned | 750000 |  |  | 2022 |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 23634 |  |  | 27393 | 44936 | LN | 2025-12-31 | Wishek | Merricourt |  | 230 |  |  | Line rerouted to new location in sub |  | ND |  |  | Planned | 600000 | Planning Preliminary |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 23634 |  |  | 27392 | 44936 | LN | 2025-12-31 | Wishek | Napoleon |  | 230 |  |  | Line rerouted to new location in sub |  | ND |  |  | Planned | 600000 | Planning |  |  |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MP | 23877 |  | Nelson Lake 230 kV | 27669 | 44819 | LN | 2022-06-01 | Nelson Lake | Square Butte East / Bison |  | 230 |  |  | Tie in existing MP Square Butte East - Bison 230 kV Line and build a second Nelson Lake - Square Butte East line parallel to existing |  | ND |  | 2 | Proposed | 5000000 | Planning |  | 2022 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP23 | C | West | ATC | 24801 |  | PR09207 | 28107 | 45182 | LN | 2027-03-19 | Eldorado | South Fond du Lac | W33 | 345 |  |  | F318 345kV Line Modifications |  | WI |  |  | Planned | 1286794 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | Central | IPL | 23852 |  |  | 27626 | 45184 | LN | 2025-12-31 | Petersburg | R1011 |  | 345 |  |  | Transmission line to serve new energy center |  | IN |  | 2 | Planned | 5000000 | Planning |  | 2022 |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP23 | C | West | ITCM | 23485 |  | J1174 & J1175 NU | 27311 | 44806 | LN | 2025-06-30 | Bison | Colby | 1 | 345 | 345 |  | The Bison – Colby 345 kV line will be tapped and re-routed to new positions in the Bluebill station. ITC will TO self-fund the Network Upgrades and will earn a return of and return on investment under a FSA for 90% of the cost. 10% of the Network Upgrades costs will be recovered under Attachment GG. |  | IA |  |  | Planned | 2400000 | Engineering |  | 2022 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 23636 |  | Cust Interconnect Blanket | 27402 | 44812 | LN | 2025-12-31 | Blanket for Customer Interconnections under $1 million for 2025 |  |  | 345 | 69 |  | Throughout system |  | IA,MN,IL |  |  | Planned | 3600000 | Engineering Preliminary |  |  |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 23677 |  | ITC Midwest Asset Replacement Program 2025 | 27401 | 44816 | LN | 2025-12-31 | ITCM Asset Blanket for 2025 | Throughout system |  | 345 | 69 |  | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. |  | IA,MN,IL |  |  | Planned | 38400000 | Engineering Preliminary |  |  |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | East | ITCT | 24313 |  |  | 27777 | 44944 | LN | 2025-03-31 | Greenwood | Rapson | 1 | 345 | 345 |  | Loop the Greenwood-Rapson #1 345kV circuit into the new J1196 switching station. |  | MI |  |  | M3_Long Lead Materials | 1233600 | GIA |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24333 |  |  | 27785 | 44944 | LN | 2025-12-29 | Majestic | Milan | 1 | 345 | 345 |  | Extend the Majestic - Milan 345kV line by adding 0.2 miles of 1431ACSR to loop in the New Station. |  | MI |  |  | Proposed | 1678800 | Facility Study |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | West | MEC | 24212 |  |  | 27764 | 44896 | LN | 2025-12-01 | Badger Creek | Raccoon Trail | 1 | 345 |  |  | Construct a new 345 kV line from Badger Creek Substation to Raccoon Trail Substation. |  | IA |  | 16 | Planned | 0 | Planning |  |  | Estimated cost: $0 ($59.5m is estimated 100% customer reimbursement as a contribution in aid of construction) |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 24999 |  |  | 28163 | 45083 | LN | 2026-06-03 | Overland Trail | Pony Creek | 1 | 345 |  |  | Construct a new 345 kV line from Overland Trail Substation to Pony Creek Substation |  | IA |  |  | Proposed | 7000000 | Planning |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | East | METC | 24294 |  |  | 27781 | 44944 | LN | 2025-03-31 | Mio Dam | Twining | 1 | 345 | 345 |  | Loop the Mio Dam - Twining 138kV circuit into the new J1210 switching station. Install fiber on the J1210-Twining circuit. |  | MI |  |  | M3_Long Lead Materials | 2204400 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | Central | NIPS | 22809 |  |  | 26841 | 45043 | LN | 2025-06-01 | Schahfer | St. John |  | 345 |  |  | Connection of Schahfer to St. John line |  | IN |  |  | Planned | 3063450 | Facility Study |  | 2024 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP23 | C | West | MEC | 23703 |  | T92K7, T92K8 | 27445 | 45029 | TAP | 2025-06-01 | Clay County | Palo Alto |  | 345 |  |  | Network Upgrades for J982 Generator (345 kV line taps) |  | IA |  |  | Planned | 2500000 | GIA |  | 2020 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 24212 |  |  | 27763 | 44896 | TAP | 2025-12-01 | Arbor Hill | Raccoon Trail | 1 | 345 |  |  | Construct two 345 kV line taps into new Badger Creek Substation. |  | IA |  |  | Planned | 0 | Planning |  | 2022 | Estimated cost: $0 ($59.5m is estimated 100% customer reimbursement as a contribution in aid of construction) |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | XEL | 24374 |  |  | 27839 | 44937 | TAP | 2025-09-02 | Brookings County | Lyons County | 2 | 345 |  |  | Move J460 Steep Bank Lake interconnection to new 345kV second circuit being built between Brookings County - Lyon County (MTEP ID 23452). |  | MN |  |  | Proposed | 300000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | South | Entergy-LA | 25242 |  | 23-ELS-002 | 28274 | 45166 | LN | 2028-07-01 | Commodore | Churchill |  | 500 |  |  | ~85 mile 500 kV |  | LA |  |  | Proposed | 1700000000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-TX | 23952 |  | 23-ETI-004 | 27943 | 44946 | LN | 2030-12-19 | Babel | Running Bear |  | 500 |  |  | Construct ~150 mile 500 kV line from Babel to Running Bear 500 kV station |  | TX |  |  | Proposed | 1111000000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | West | OTP | 23944 |  | T05008.021 | 27667 | 45125 | LNrb | 2027-12-31 | Parshall 41.6 kV | Wabek 41.6 kV | 1 | 41.6 |  |  | Rebuild and Reconductor the 41.6 kV line between Parshall 41.6 kV and Wabek 41.6 kV |  | ND |  |  | Proposed | 930000 | Planning |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23977 |  | 7223 | 27691 | 44819 | LNrb | 2024-11-30 | Cooperstown 41.6 kV |  |  | 41.6 |  |  | Reroute and rebuild 5 miles of 41.6 kV line near Cooperstown 41.6 kV substation. |  | ND |  |  | Proposed | 1150000 | Planning |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23942 |  | 7541 | 27663 | 44819 | LNrc | 2024-11-30 | Jamestown 41.6 kV | Gackle 41.6 kV |  | 41.6 |  |  | Reconductor and rebuild sections of the 41.6 kV line between Gackle 41.6 kV and Jamestown 41.6 kV. |  | ND |  |  | Proposed | 1000000 | Planning |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23842 |  | 6979 | 27607 | 44819 | LNup | 2024-12-31 | Wilmot 41.6 kV | Peever Jct. 41.6 kV |  | 41.6 |  |  | Rebuild 4 miles of 41.6 kV line between Wilmot 41.6 kV and Peever Jct. 41.6 kV. |  | SD |  |  | Proposed | 1125000 | Planning |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23859 |  |  | 27616 | 44819 | LNup | 2023-12-31 | Granville 41.6 kV | Granville Station 41.6 kV | 1 | 41.6 |  |  | Rebuild of 41.6 kV line between Granville 41.6 kV and Granville Station 41.6 kV. |  | ND |  |  | Proposed | 1000000 | Planning |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23860 |  | T05014.021 | 27617 | 44819 | LNup | 2025-11-30 | Grenville 41.6 kV | Veblen 41.6 kV | 1 | 41.6 |  |  | Rebuild of 41.6 kV line between Grenville 41.6 kV and Veblen 41.6 kV. |  | SD |  |  | Proposed | 4600000 | Planning |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23917 |  |  | 27614 | 44819 | LNup | 2025-11-30 | Fordville 41.6 kV | Fordville Jct. 4.6 kV | 1 | 41.6 |  |  | Rebuild of 41.6 kV line between Fordville 41.6 kV and Fordville Jct. 41.6 kV. |  | ND |  |  | Proposed | 1450000 | Planning |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23918 |  |  | 27615 | 44819 | LNup | 2023-12-31 | Michigan 41.6 kV | Mapes 41.6 kV | 1 | 41.6 |  |  | Rebuild of the 41.6 kV line between Michigan 41.6 kV and Mapes 41.6 kV. |  | ND |  |  | Proposed | 1000000 | Planning |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23943 |  |  | 27666 | 44819 | LNup | 2024-11-30 | Pickert 41.6 kV | McVille 41.6 kV |  | 41.6 |  |  | Rebuild portions of the 41.6 kV line between Pickert 41.6 kV and McVille 41.6 kV. |  | ND |  |  | Proposed | 3800000 | Planning |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | East | WPSC | 23613 |  |  | 27357 | 44806 | LINE | 2025-12-31 | TBD |  |  | 69 |  |  | Installation of fiber on recently rebuilt (post 2006) 138kV structures utilizing ADSS (All Dielectric Self Supporting) and OPGW (Optical Ground Wire). |  | MI |  |  | Proposed | 5000000 | Planning |  | 2025 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | West | ATC | 21921 |  | PR09121 | 26529 | 45182 | LNrb | 2025-12-31 | Groenier | Rosholt (ALTE) Tap | Y-71 | 69 |  |  | Groenier – Rosholt (ALTE) Tap, 69 kV (Y-71), Partial Rebuild and Rerate |  | WI |  |  | Planned | 16500000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 21985 |  | PR09090 | 26628 | 45182 | LNrb | 2026-06-30 | Chandler | Delta |  | 69 |  |  | Rebuild approximately 5.5 miles of 69 kV line Delta1 and install OPGW. |  | MI |  |  | Planned | 11600000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23837 |  |  | 27601 | 45182 | LNrb | 2030-01-31 | Northeast | Revere Dr | C-103 | 69 |  |  | Uprate or Rebuild |  | WI |  |  | Planned | 8600000 | Planning |  | 2030 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23838 |  |  | 27602 | 45182 | LNrb | 2028-12-31 | High Falls | Mountain | 69 | 69 |  |  | Rebuild |  | WI |  |  | Planned | 33000000 | Planning |  | 2028 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23857 |  | PR09052 | 27598 | 45182 | LNrb | 2027-12-31 | Pine Hy Tap | Pine Hy | PSPY3 | 69 |  |  | Rebuild and OPGW |  | MI |  |  | Planned | 11500000 | Planning Preliminary |  | 2027 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23874 |  | PR09096 | 27577 | 45182 | LNrb | 2026-12-31 | Harrison Tap | Iola | Y-70 | 69 |  |  | Rebuild and OPGW |  | WI |  |  | Planned | 16000000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23876 |  |  | 27597 | 45182 | LNrb | 2026-12-31 | Cornell Tap | Watson Tap | Chan | 69 |  |  | Cornell Tap – Watson Tap 69kV (Chandler), Partial Rebuild |  | MI |  |  | Planned | 30000000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23904 |  | PR09205 | 27590 | 45182 | LNrb | 2026-12-31 | South Beaver Damn | North Beaver Dam | Y-59 | 69 |  |  | South Beaver Dam – North Beaver Dam, 69kV (Y-59) Line Rebuild |  | WI |  |  | Planned | 11200000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23905 |  |  | 27591 | 45182 | LNrb | 2026-12-31 | Waupun | South Fond du Lac | Y-25 | 69 |  |  | Waupun - South Fond du Lac 69kV, (Y-25) Partial Rebuild |  | WI |  |  | Planned | 22600000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23911 |  |  | 27600 | 45182 | LNrb | 2030-10-31 | Shoto | Northeast | K-11 | 69 |  |  | Rebuild |  | WI |  |  | Planned | 5400000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | Central | BREC | 19007 |  |  | 25368 | 44546 | LNrb | 2024-10-01 | Kansas (BREC) | Kansas tap | 1 | 69 |  | 42 | Rebuild 5.1 mile 69 kV radial as double circuit 69 kV line. |  | KY | 5.1 |  | Proposed | 900000 | Budgetary |  | 2020 |  | 42 | Big Rivers Electric Corporation | N | N | N
A in MTEP23 | C | West | CFU | 23993 |  |  | 27708 | 45113 | LNrb | 2024-04-01 | Streeter Switch | WIDA |  | 69 |  |  | Rebuild CFU's part of the East half of the Streeter Switch to WIDA 69 Line |  | IA | 2.1 |  | Proposed | 2000000 | Budgetary |  | 2022 | Updated to reflect material delivery delays that will change in-service date. |  | Cedar Falls Utilities | N | N | N
A in MTEP23 | C | Central | DEI | 23848 |  | WVPA-2023-4 | 27649 | 44936 | LNrb | 2023-12-18 | Montclair | Montclair Jct. |  | 69 |  | 150 | WVPA Montclair to Montclair Jct. 69134 69kV Rebuild: rebuild 69kV line section |  | IN | 5.75 |  | Proposed | 8888000 | Planning Preliminary |  | 2022 |  | 150 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23850 |  | WVPA-2023-5 | 27652 | 44819 | LNrb | 2023-10-31 | Lee Hanna | Lee Hanna Jct |  | 69 |  | 150 | WVPA Lee Hanna to Lee Hanna Jct 69 kV rebuild (Phase 3): Rebuild 5.6 miles of 69 kV to match line conductor for Fortville to Mohawk line. (954 ACSR) |  | IN | 5.6 |  | Proposed | 3274000 | Planning Preliminary |  | 2022 |  | 150 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23962 |  |  | 27698 | 45168 | LNrb | 2025-06-01 | HE Whitehall Switch Pole | structure 815-1069-01 |  | 69 |  | 150 | 6958 Line Rbld as required by FAA - Rebuild 39 Structures and replace conductor from HE Whitehall to structure 815-1069-01. Replace individual poles 815-1060 and 815-1061. Install monitored FAA warning lights on 37 of the poles. Install 36 marker balls on the static wire. |  | IN | 2.13 |  | Proposed | 3385000 | Planning Preliminary |  | 2022 |  | 150 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23963 |  | M220131 | 27699 | 45168 | LNrb | 2024-05-17 | Potato Creek | Thorntown |  | 69 |  | 150 | 6932 Rebuild Potato Crk to Manson Jct to Clarks Hill to Thorntown with 954ACSR conductor |  | IN | 18.39 |  | Proposed | 41811862 | Planning Preliminary |  | 2022 |  | 150 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23970 |  | M180434 | 27705 | 45168 | LNrb | 2025-10-09 | Greensfork | HE Jacksonburg Jct |  | 69 |  | 100 | Rebuild 69100 from Greensfork #1 switch (pole #862-3176) to Jacksonburg Jct switch (pole #862-3074) using light duty steel poles, 477ACSR and OPGW |  | IN | 5.08 |  | Proposed | 10800000 | Engineering w/AFUDC |  | 2023 |  | 100 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23881 |  | 23-ELF-002 | 27862 | 44938 | LNrb | 2025-06-01 | Elks | Holiday |  | 69 |  |  | Rebuild/Reconductor Elks to Holiday 69 kV line. |  | LA |  |  | Proposed | 29400000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | West | GRE | 23800 |  | 208542 | 27562 | 45068 | LNrb | 2026-08-21 | Gilman | Milaca | 1 | 69 |  |  | Rebuild the JC line (18.93 miles) and switch SS2888 to 69kV with 477 ACSS. |  | MN | 18.93 |  | Proposed | 12048956 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23822 |  | 209300 | 27547 | 45068 | LNrb | 2026-09-07 | Matawan | St. Olaf Lake | 1 | 69 |  |  | Rebuild SW-MB line segments 1 and 2 (11.01 miles) (Matawan switches to St. Olaf Lake switches) to 69 kV minimum conductor size 477 ACSR would meet voltage and thermal considerations per planning. |  | MN | 11 |  | Proposed | 7309835 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23921 |  | 207418 | 27641 | 45156 | LNrb | 2027-04-29 | Deerwood | Pilot Knob | 1 | 69 |  |  | Rebuild the Pilot Knob Substation to a breaker and a half configuration due to age and condition of the current equipment. Upgrade the DA-PD line from Deerwood to Pilot Knob substation to increase the capacity. Upgrade to be built to 115kV standards but operated at 69kV. Retire the underground portion of the DA-PLX at Pilot Knob and replace with overhead Retire the DA-RE line from Pilot Knob road to Black Hawk Road Retire the DA-PKX from Pilot Knob to Cliff Road Retire SS-2820 and replace with a turning structure. Retire SS-2819 |  | MN |  |  | Proposed | 11019399.69 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | ITCM | 25060 |  |  | 28192 | 45100 | LNrb | 2025-06-30 | Grant Tap | Grant Milford |  | 69 | 69 | 91 | Rebuild existing 4 mile 34.5 kV line to 69 kV construction standards |  | IA | 4 |  | Proposed | 3483750 | Engineering |  | 2023 |  | 91 | ITC Midwest | N | N | N
A in MTEP23 | C | West | MEC | 23571 |  | T90W4, T90W7, T90W8, T90WA | 27332 | 45156 | LNrb | 2027-12-01 | Humboldt East | Weaver Switching Station | 1 | 69 |  |  | Rebuild due to condition and to support networked operation. |  | IA |  |  | Planned | 6000000 | Budgetary |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23591 |  | T90BO | 27336 | 45156 | LNrb | 2024-12-31 | Nashua Tap | Plainfield Junction | 1 | 69 |  |  | Replace conductor on section of Nashua Tap-Plainfield Junction 69 kV line using existing right of way |  | IA |  |  | Planned | 2500000 | Budgetary |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23629 |  | T9048; T92A2; T929X | 27335 | 45030 | LNrb | 2025-12-01 | Charles City South | Nashua Tap | 1 | 69 |  |  | Rebuild Charles City South-Nashua Tap 69 kV Line on new Right of Way |  | IA |  |  | Planned | 6100000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23630 |  | T90DB | 27337 | 45030 | LNrb | 2024-04-01 | Wida | Streeter | 1 | 69 |  |  | Replace conductor on MidAmerican section of Wida-Streeter 69 kV line. |  | IA |  |  | Planned | 1000000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23685 |  |  | 27415 | 45029 | LNrb | 2024-10-18 | Southbridge Tap | Knox | 1 | 69 |  |  | Rebuild line |  | IA |  |  | Planned | 2000000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23685 |  |  | 27690 | 45029 | LNrb | 2024-09-05 | Neal North | Southbridge Tap |  | 69 |  |  | Rebuild line |  | IA |  |  | Planned | 2500000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23685 |  |  | 27416 | 45029 | LNrb | 2024-12-05 | Knox | State Steel Tap |  | 69 |  |  | Rebuild single circuit section of line |  | IA |  |  | Planned | 4100000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 24923 |  |  | 28159 | 45156 | LNrb | 2025-06-01 | Sidney | Percival |  | 69 |  |  | Rebuild Sidney-Percival 69 kV line and replace line structures. |  | IA | 10.11 |  | Proposed | 9000000 | Planning |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | Central | PPI | 23567 |  |  | 27316 | 45160 | LNrb | 2029-12-31 | Pearl | Kampsville | 1 | 69 | 69 | 35 | Rebuild Pearl-Kampsville 336 ACSR 69 kV line |  | IL | 9.4 |  | Planned | 7285000 | Planning |  | 2022 | There will still be a ~6.5miles of line from Pearl-Carrollton that is limited to 35MVA so the overall MVA rating of the branch will not change. | 35 | Prairie Power, Inc. | N | N | N
A in MTEP23 | C | Central | SIGE | 23749 |  | 2022-6 | 27473 | 44813 | LNrb | 2024-12-31 | Cato | Winslow | Y39 | 69 |  |  | Rebuild ~9.5 miles of 69 kV due to aging infrastructure (conductor size not changing) |  | IN | 9.5 |  | Planned | 14130000 | Budgetary |  | 2022 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP23 | C | East | WPSC | 23574 |  |  | 27365 | 45146 | LNrb | 2028-12-31 | Pellston | Cross Village |  | 69 |  |  | Rebuild and upgrade 9 miles of 69kV line to 138 kV standard with steel poles, 336ACSS conductor, and OPGW. |  | MI | 9 |  | Proposed | 9500000 | Planning |  | 2028 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | East | WPSC | 23614 |  |  | 27358 | 45146 | LNrb | 2027-12-31 | Casnovia | Cedar Springs |  | 69 |  |  | Rebuild and upgrade 11 miles of 69kV line to 138 kV standard with steel poles, 795ACSS conductor, and OPGW. |  | MI | 11 |  | Proposed | 9250000 | Planning |  | 2027 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | East | WPSC | 23617 |  |  | 27361 | 45146 | LNrb | 2028-12-31 | Hayes Junction | Hayes |  | 69 |  |  | Rebuild and upgrade 12 miles of 69kV line to 138 kV standard with steel poles, 336ACSS conductor, and OPGW. |  | MI | 12 |  | Proposed | 11850000 | Planning |  | 2028 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | East | WPSC | 23619 |  |  | 27363 | 45146 | LNrb | 2027-12-31 | Mulliken Jct | Grand Ledge |  | 69 |  |  | Rebuild and upgrade 4 miles of 69kV line to 138 kV standard with wood poles, 336ACSS conductor, and OPGW. |  | MI |  |  | Proposed | 4250000 | Planning |  | 2027 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | Central | WVPA | 23714 |  |  | 27508 | 44817 | LNrb | 2024-12-31 | Seminary |  |  | 69 |  |  | Rebuild 69kV line group on CEC 69 kV System - Phase 2 |  | MO | 0.5 |  | Planned | 675000 | Engineering |  | 2024 |  |  | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP23 | C | Central | WVPA | 23779 |  |  | 27506 | 44817 | LNrb | 2023-12-31 | New Bourbon |  |  | 69 |  |  | Blanket for several lines |  | MO | 2 |  | Planned | 1600000 | Engineering |  | 2023 |  |  | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP23 | C | West | XEL | 23446 |  |  | 27207 | 44785 | LNrb | 2024-06-15 | Hormel | W3502 Tap | 1 | 69 |  |  | The existing line W3502 will be rebuilt to serve as a redundant connection. |  | WI | 2 |  | Planned | 1500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | B | South | Entergy-LA | 9764 |  | 16-EGL-005 | 21138 | 44819 | LNrc | 2026-06-01 | Dixie Baker | Baker | 1 | 69 |  |  | Upgrade line |  | LA |  |  | Proposed | 12800000 | Planning |  |  |  |  | Entergy | N | N | N
A in MTEP23 | B | South | Entergy-LA | 12084 |  | 17-ELB-003 | 22170 | 44819 | LNrc | 2027-06-01 | Dixie Baker | Zachary |  | 69 |  |  | The ~3.3 mile long line should be upgraded to a minimum rating of 143 MVA. If any station equipment is rated lower than 143 MVA (1200 Amps), it should be upgraded as well. |  | LA | 3.3 |  | Conceptual | 18900000 | Planning |  |  |  |  | Entergy | N | N | N
A in MTEP23 | C | Central | SIGE | 23748 |  | 2022-5 | 27472 | 44813 | LNrc | 2024-12-31 | Northeast | Modification | Y74-1 | 69 |  | 103 | Rebuild ~1.75 miles of 69 kV conductor to increase rating from 70 MVA to 103 MVA |  | IN | 1.75 |  | Planned | 710600 | Budgetary |  | 2022 |  | 103 | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP23 | C | West | XEL | 23448 |  |  | 27209 | 44785 | LNrc | 2023-06-01 | Luck | Luck (DPC) | 1 | 69 |  |  | Rebuild 2 ¼ miles from Luck - Luck (DPC) to 69 kV standard. |  | WI | 2.25 |  | Planned | 1000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23449 |  |  | 27210 | 45161 | LNrc | 2024-07-31 | Clear Lake | Turtle Lake | 1 | 69 |  |  | Rebuild 10 miles of line W3429 from Clear Lake to Structure 214 to 69 kV standard and add OPGW. |  | WI | 10 |  | Planned | 5250000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23451 |  |  | 27213 | 44785 | LNrc | 2023-09-01 | Pine Lake | Stanton | 1 | 69 |  |  | Rebuild 16.1 miles from Pine Lake - Stanton to 69kV standard. |  | WI | 16.1 |  | Planned | 9500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23459 |  |  | 27250 | 44790 | LNrc | 2024-06-15 | Waseca | ITC Tap | 1 | 69 |  |  | Rebuild 6.7 miles of 69 kV line 0749 from Waseca - ITC Tap and add OPGW. |  | MN |  |  | Planned | 6000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23460 |  |  | 27258 | 44790 | LNrc | 2024-12-31 | Medelia | Watonwan | 1 | 69 |  |  | Rebuild 22 miles of line 0714 69 kV from Medelia - Watonwan. |  | MN |  |  | Planned | 11000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23461 |  |  | 27259 | 44790 | LNrc | 2024-12-31 | Eagle Lake | Waterville | 1 | 69 |  |  | Rebuild 16 miles of line 0708 69 kV from Eagle Lake - Waterville and add OPGW. |  | MN |  |  | Planned | 9000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23462 |  |  | 27262 | 44790 | LNrc | 2024-06-15 | Arlington | Winthrop | 1 | 69 |  |  | Rebuild 15 miles line 0718 69 kV from Arlington - Winthrop. |  | MN |  |  | Planned | 9000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23474 |  |  | 27251 | 44790 | LNrc | 2025-12-31 | Arden Hills | Lawrence Creek | 1 | 69 |  |  | Rebuild 33 miles of line 0736 69 kV from Arden Hills - Lawrence Creek and add OPGW. |  | MN |  |  | Planned | 20000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23475 |  |  | 27252 | 44790 | LNrc | 2025-12-31 | Franklin | Winthrop |  | 69 |  |  | Rebuild 22 miles line 0721 69 kV from Structure 71 - Structure 476. |  | MN |  |  | Planned | 11000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23477 |  |  | 27261 | 44790 | LNrc | 2025-12-31 | Prairie | Emerado | 1 | 69 |  |  | Rebuild 12 miles of line 0772 69 kV from Prairie - Emerado. |  | ND |  |  | Planned | 6000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23502 |  |  | 27249 | 44790 | LNrc | 2024-06-30 | Young America | Carver County | 1 | 69 |  |  | Rebuild 2 miles of line 0771 from Young America - Carver County 69 kV substations and add OPGW. |  | MN |  |  | Planned | 1500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23503 |  |  | 27253 | 44790 | LNrc | 2025-12-31 | Winthrop | Lafayette | 1 | 69 |  |  | Rebuild 1.5 miles of line 0719 69 kV from Winthrop - Structure 45. |  | MN |  |  | Planned | 2000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23527 |  |  | 27264 | 44790 | LNrc | 2023-03-15 | Clear Lake | New Richmond | 1 | 69 |  |  | Rebuild 19.8 miles of line W3428 from Clear Lake - New Richmond. |  | WI |  |  | Planned | 10000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23938 |  | 23-ELB-001 | 27834 | 44937 | TEQ | 2024-12-01 | Port Hudson |  |  | 69 |  |  | Upgrade 69 kV switches to achieve higher rating on Port Hudson to Sandy Creek to Jackson 69 kV line |  | LA |  |  | Proposed | 3900000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23938 |  | 23-ELB-001 | 27836 | 44937 | TEQ | 2024-12-01 | Jackson |  |  | 69 |  |  | Upgrade 69 kV switches to achieve a higher rating on the Port Hudson to Sandy Creek to Jackson 69 kV line. |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23938 |  | 23-ELB-001 | 27835 | 44937 | TEQ | 2024-12-01 | Sandy Creek |  |  | 69 |  |  | Upgrade 69 kV switches to achieve a higher rating on the Port Hudson to Sandy Creek to Jackson 69 kV line. |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23940 |  | 23-ELB-002 | 27837 | 45071 | TEQ | 2025-06-01 | Tiger |  |  | 69 |  |  | Upgrade bus, breakers and switches at Tiger 69 kV to achieve a higher rating on the 69 kV bus tie. |  | LA |  |  | Proposed | 1494000 | Scoping |  |  |  |  | Entergy | N | N | N
A in MTEP23 | C | West | MEC | 24923 |  |  | 28160 | 45156 | TEQ | 2025-06-01 | Sidney |  |  | 69 |  |  | Replace terminal equipment at Sidney Substation on Sidney-Percival line terminal |  | IA |  |  | Proposed | 100000 | Planning |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | XEL | 23466 |  |  | 27212 | 44785 | LNrc | 2024-12-31 | Saxon Pump | Norrie | 1 | 88 |  |  | Rebuild W3551 with twisted pair 4/0 wire (477 eq.) and direct embedded steel structures from structure 336 to Saxton Pump. Design the 88kv circuit to be 115kv capable. Include provision for a 34.5 kv under build circuit to connect to W3628 north of Saxton Pump. |  | WI | 9 |  | Planned | 8000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | ATC | 22587 |  | PR09066, PR09206 | 26802 | 45182 | LNrb | 2028-06-01 | In development |  |  | 115 |  |  | Line rebuild or reconductor |  | WI |  |  | Planned | 47900000 | Planning |  | 2027 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | B | South | Entergy-AR | 19911 |  | 21-EAL-001 | 25595 | 44803 | LNrb | 2025-06-01 | Dumas | Reed |  | 115 |  |  | Rebuild Dumas - Reed 115kV |  | AR |  |  | Planned | 18600000 | Planning |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP23 | B | South | Entergy-LA | 15654 |  | 19-ELN-001 | 23667 | 44819 | LNrb | 2026-12-01 | Delhi | Tallulah | 1 | 115 |  |  | Rebuild 20.8 miles of 115kV line from Delhi to Tallulah with a minimum through-path rating of 259 MVA (1300A). |  | LA | 20.8 |  | Proposed | 39900000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | B | South | Entergy-LA | 18236 |  | 20-ELN-002 | 25074 | 44819 | LNrb | 2026-12-01 | Winnsboro | Gilbert | 1 | 115 |  |  | Rebuild Winnsboro to Gilbert 115 kV line to a minimum of 259 MVA. The line will be built using a double circuit configuration but only strung on one side. The unused side will be reserved for a future 230 kV line. |  | LA | 9.6 |  | Proposed | 20900000 | Planning |  |  |  |  | Entergy | N | N | N
A in MTEP23 | B | South | Entergy-LA | 18247 |  | 20-ELN-003 | 25076 | 44938 | LNrb | 2027-12-15 | Gilbert | Wisner | 1 | 115 |  |  | Rebuild Winnsboro to Gilbert 115 kV line to a minimum of 259 MVA. The line will be built using a double circuit configuration but only strung on one side. The unused side will be reserved for a future 230 kV line. |  | LA | 5 |  | Proposed | 11900000 | Planning |  |  |  |  | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-MS | 23786 |  |  | 27525 | 44946 | LNrb | 2026-06-01 | Redwood | Ft Redwood |  | 115 |  |  | Rebuild the existing Cooperative Energy owned Redwood - Ft Redwood 115kV line. |  | MS |  |  | Proposed | 772500 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | West | MP | 22909 |  | 40 Line Rebuild | 26860 | 45183 | LNrb | 2024-12-31 | Badoura 115 kV | Dog Lake | 1 | 115 |  | 159 SUM/159 WTR | Rebuild Badoura-Dog Lake 115 kV, installing 795 ACSR and OPGW |  | MN | 35 |  | Under Construction | 17307658 | Engineering |  | 2022 |  | 175 SUM/175 WTR | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP23 | C | West | XEL | 23458 |  |  | 27247 | 44790 | LNrc | 2023-12-15 | North Star Steel | Battle Creek | 1 | 115 |  |  | Rebuild 3.4 miles of 115 kV line between North Star Steel and Battle Creek substations. Portions of this line are double circuited with 0892, this project will separate the two circuits. |  | MN |  |  | Planned | 3437000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23467 |  |  | 27214 | 44788 | LNrc | 2024-12-31 | Chemolite | Inver Hills | 1 | 115 |  |  | Rebuild 6.9 miles of line 0859 115 kV from Chemolite substation to structure 16 and add OPGW. |  | MN | 6.9 |  | Planned | 9000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23473 |  |  | 27248 | 44790 | LNrc | 2023-12-15 | Red Rock | Battle Creek | 1 | 115 |  |  | Rebuild 3.4 miles of 115 kV line between Red Rock and Battle Creek substations. Portions of this line are double circuited with 0893, this project will separate the two circuits. |  | MN |  |  | Planned | 5237000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23476 |  |  | 27260 | 44790 | LNrc | 2024-12-31 | Empire | Rosemount | 1 | 115 |  |  | Rebuild 7 miles of line 0822 115 kV from Empire to Str 107 and add OPGW. |  | MN |  |  | Planned | 6000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23508 |  |  | 27263 | 44790 | LNrc | 2024-06-01 | Cherry Creek | West Sioux Falls | 1 | 115 |  |  | Rebuild 2 miles 115 kV Cherry Creek - Great Plains. Rebuild 1 mile 115 kV Great Plains - West Sioux Falls (single circuit portion) as bifurcated double circuit. Rebuild 0.7 mile 115 kV Great Plains - West Sioux Falls (double circuit portion). |  | SD |  |  | Planned | 5000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | GRE | 23849 |  | 208674 | 27650 | 45156 | LNup | 2024-10-31 | Big Swan | Wakefield | 1 | 115 |  |  | Install (2) new storm structures every 5 miles along the ME-BW line between structures 306 and 415 as there are no full stop deadends in this section of line. Possible locations are structures 340 or 349 and 374 or 383. |  | MN |  |  | Proposed | 526381 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | MP | 22885 |  | Brainerd Crypto | 26859 | 45163 | LNup | 2025-12-31 | Brainerd | Riverton | 1 | 115 |  | 90 | Thermal upgrade existing line to 75C |  | MN | 13 |  | Proposed | 2000000 | Planning |  | 2022 |  | 99 | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP23 | C | West | MRES | 23919 |  |  | 27637 | 45082 | LNup | 2024-07-01 | GRANTCO7 | MORRIS 7 |  | 115 |  |  | Increase line rating. |  | MN |  |  | Proposed | 859510 | Budgetary |  |  |  |  | Missouri River Energy Services (MRET) | N | N | N
A in MTEP23 | C | West | MRES | 23919 |  |  | 27639 | 45082 | LNup | 2024-06-01 | GRANTCO7 | EFERGUS7 |  | 115 |  |  | Increase line rating. |  | MN |  |  | Proposed | 477030 | Budgetary |  |  |  |  | Missouri River Energy Services (MRET) | N | N | N
A in MTEP23 | C | West | XEL | 23501 |  |  | 27246 | 44789 | LNup | 2025-06-01 | Elliot Park | Hiawatha West | 1 | 115 |  |  | Upgrades to pumping station for HPFF. |  | MN |  |  | Planned | 5000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | B | South | Entergy-LA | 15654 |  | 19-ELN-001 | 23669 | 44819 | TEQ | 2026-12-01 | Tallulah |  |  | 115 |  |  | Upgrading terminal equipment at Tallulah to 1300 amps minimum |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | B | South | Entergy-LA | 15654 |  | 19-ELN-001 | 23668 | 44819 | TEQ | 2026-12-01 | Delhi |  |  | 115 |  |  | Upgrading terminal equipment at Delhi to 1300 amps |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | West | XEL | 24278 |  |  | 27797 | 44911 | TEQ | 2023-12-31 | Edina |  |  | 115 |  |  | Replace Edina 115kV switch for Edina - St. Louis Park 115kV line, remediating overloads on the line under contingency. |  | MN |  |  | Planned | 135000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | East | ITCT | 24593 |  |  | 28049 | 45077 | LNrb | 2025-05-31 | Pontiac | Sunbird | 1 | 120 |  |  | Rebuild segments to double circuit structures and reconductor portions of the existing Pontiac-Sunbird #1 and Pontiac-Walton #1 lines. Install OPGW between Pontiac and Sunbird. Install PTS on Colorado tap of the line |  | MI | 2.67 |  | Planned | 9500000 | Engineering |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP23 | B | East | ITCT | 22847 |  | ITC_22_001 | 26848 | 45027 | LNup | 2027-03-31 | New Substation | Golf | 1 | 120 |  |  | Install OPGW from New 120kV Substation - Golf for relay communication. |  | MI |  |  | Proposed | 1400000 | Engineering |  |  |  |  | ITC Transmission | N | N | N
A in MTEP23 | B | East | ITCT | 22847 |  | ITC_22_001 | 26847 | 45027 | LNup | 2027-03-31 | Boyne | New 120kV Sub |  | 120 |  |  | Install OPGW from Boyne – New 120kV Substation for relay communication. |  | MI |  |  | Proposed | 680000 | Engineering |  |  |  |  | ITC Transmission | N | N | N
A in MTEP23 | B | East | ITCT | 23697 |  |  | 27499 | 44935 | LNup | 2026-12-31 | Beck | Stephens | 1 | 120 |  |  | Remediate the sag limit on the Beck - Stephens 120 kV circuit up to a minimum summer emergency rating of 242 MVA. |  | MI |  |  | Proposed | 540000 | Engineering |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24593 |  |  | 28051 | 44970 | LNup | 2024-04-30 | Bloomfiled | Sunbird | 1 | 120 |  |  | Add 120 kV pole top switch on the tap side of the Colorado 2 tap. |  | MI | 0.1 |  | Planned | 1260000 | Engineering |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | West | ATC | 23836 |  | PR09152 | 27572 | 45182 | LINE | 2025-11-01 | Perch Lake | National | 468 | 138 |  |  | Partial Retirement Project |  | MI |  |  | Planned | 10400000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24446 |  | PR09162 | 27963 | 45182 | LINE | 2025-06-12 | Arnold SS | Perkins SS | 29051 | 138 |  |  | Transmission Line Modifications |  | MI |  |  | Planned | 981969 | GIA |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24802 |  | PR09208 | 28110 | 45182 | LINE | 2025-12-27 | Sunrise |  |  | 138 |  |  | 4434 X69 (138kV) Line Modifications |  | WI |  |  | Planned | 790368 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 25262 |  | PR08874 | 28377 | 45182 | LINE | 2023-11-08 | North Monroe | Bass Creek | X-12 | 138 |  |  | X12 Sectionalizing |  | WI |  |  | Planned | 707123 | GIA |  | 2020 | WO #604900 |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23431 |  | TP1700 | 27084 | 44952 | LINE | 2024-12-01 | Decatur | Main |  | 138 |  |  | replace two Wood structures and re-frame 3 others to increase capacity of the Decatur - Main St. 138 kV line. |  | IL |  |  | Planned | 500000 | GIA |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | South | CLECO | 24416 |  |  | 27876 | 44938 | LINE | 2027-07-15 | Rosepine | Deridder | 1 | 138 |  |  | Build a new 3.4 mile 230 kV line from Rosepine to Deridder energized at 138 kV. |  | LA |  | 3.4 | Proposed | 12000000 | Budgetary |  |  |  |  | Cleco Power LLC | N | N | N
A in MTEP23 | C | East | METC | 23709 |  | METC_22_078 | 27489 | 44897 | LINE | 2027-06-01 | Campbell | Blendon | 1 | 138 |  |  | Loop the Campbell - Blendon 138kV line into Tyler to create Campbell - Tyler and Tyler - Blendon 138kV lines. |  | MI |  |  | Proposed | 1245000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24319 |  |  | 28063 | 44994 | LINE | 2025-12-31 | Delhi | Tompkins |  | 138 |  |  | Remove pole mounted CTs and control boxes on switches 3435 and 3527 |  | MI |  |  | Proposed | 258750 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24319 |  |  | 28062 | 44994 | LINE | 2025-12-31 | Delhi | Tompkins |  | 138 |  |  | Remove pole top switch controllers (SEL-2411) at switch locations 3535 & 3527 |  | MI |  |  | Proposed | 12500 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24419 |  |  | 27887 | 44946 | LINE | 2025-12-10 | Batavia | Coldwater |  | 138 |  |  | Loop the Batavia - Coldwater 138kV circuit into the new Byers switching station. Install fiber on the Byers-Batavia circuit. Install fiber on the Byers-Coldwater circuit. |  | MI |  | 0.1 | M3_Long Lead Materials | 7780800 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | West | ATC | 24801 |  | PR09207 | 28099 | 45182 | LNrb | 2027-11-12 | North Fond du Lac | Aviation | G111 | 138 |  |  | G111 138kV(NFL-AVN) Rebuild |  | WI |  |  | Planned | 26434797 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24801 |  | PR09207 | 28101 | 45182 | LNrb | 2027-11-12 | Progress | Ellinwood | X50 | 138 |  |  | X50 138kV (PRG-EOD) Rebuild |  | WI |  |  | Planned | 3207076 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24801 |  | PR09207 | 28100 | 45182 | LNrb | 2027-11-12 | Aviation | Progress | X50 | 138 |  |  | X50 138kV (AVN-PRG) Rebuild |  | WI |  |  | Planned | 3878149 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24858 |  | PR09217 | 28118 | 45182 | LNrb | 2025-12-30 | Neevin | Butte Des Morts | 43021 | 138 |  |  | 43021 (138KV) Rebuild- Conductor Upgrade Cost |  | WI | 3 |  | Planned | 55520 | GIA |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22816 |  | TP1507 | 26877 | 44948 | LNrb | 2024-12-01 | Louisville | Newton |  | 138 |  |  | Replace the 134 original vintage wood structures on the Louisville-Newton-1 138 kV line due to age and condition. Replace the existing conductor with ones capable of carrying 2,000 amps under Summer Emergency conditions. Replace both shield wires with 72-fiber OPGW. |  | IL |  |  | Planned | 32000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22891 |  | TP1527 | 26895 | 44950 | LNrb | 2024-12-01 | Tibbs | Steelville |  | 138 |  |  | Replace 477 ACSR and repair issues found during inspection. |  | IL |  |  | Planned | 37000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22946 |  | TP1534 | 26904 | 45158 | LNrb | 2025-12-01 | Alta | Pioneer |  | 138 |  |  | Construct a new 138 kV line from Alta to Pioneer |  | IL |  |  | Proposed | 9000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23072 |  | TP1581 | 26958 | 45158 | LNrb | 2026-12-01 | Newton | Tanner |  | 138 |  |  | Rebuild the Newton-Tanner 345 kV line with conductors capable of 3000 amps Summer Emergency rating and two OPGWs. |  | IL |  |  | Proposed | 29000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23207 |  | TP1595 | 26992 | 45155 | LNrb | 2025-12-01 | Mattoon West | Tuscola West |  | 138 |  |  | Rebuild the 24.6 mile Mattoon West-Tuscola West-1 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. |  | IL |  |  | Planned | 18500000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23504 |  | TP1600 | 27254 | 44847 | LNrb | 2024-12-01 | Vermillion | Tilton Energy Center |  | 138 |  |  | Rebuild the 11.4 mile Vermillion-Tilton Energy Center-1572 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. |  | IL |  |  | Proposed | 13000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22801 |  | TP1569 | 26865 | 45158 | LNrb | 2026-12-01 | Sioux | Meppen North |  | 138 |  |  | Rebuild the Sioux-Meppen North-4 from Str. 180-Meppen North and the entire Meppen North-Hull-1494 138 kV line to upgrade aging infrastructure and improve system reliability. |  | MO,IL |  |  | Planned | 77700000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | DEI | 23965 |  | M220218 | 27701 | 45168 | LNrb | 2024-05-01 | 13832 Line Structures | replace |  | 138 |  |  | Replace 14 structures in the 13832 line: 849-2103 thru 2106, and 849-2113 thru 2122 |  | IN |  |  | Proposed | 2566706 | Planning Preliminary |  | 2022 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | B | South | Entergy-TX | 18266 |  | 20-ETI-002 | 25101 | 44819 | LNrb | 2026-06-01 | Dayton | New Long John |  | 138 |  |  | Rebuild the Dayton to New Long John 138 kV line. |  | TX | 7 |  | Proposed | 24900000 | Planning |  |  |  |  | Entergy | N | N | N
A in MTEP23 | B | East | METC | 15752 |  | METC_18_066 | 23767 | 44937 | LNrb | 2027-06-01 | Redstone | Tittabawassee | 1 | 138 |  |  | Rebuild ~13.4 miles of the Redstone – Tittabawassee 138 kV line that is comprised of 336 ACSR conductor only utilizing 1431 ACSR conductor. The rebuild is using future double-circuit construction with OPGW. |  | MI | 13.4 |  | Proposed | 22070000 | Engineering |  | 2023 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23743 |  | METC_22_075 | 27467 | 44894 | LNrb | 2027-06-01 | Deja Junction | Vestaburg | 1 | 138 |  |  | Rebuild 4.3 miles section between Deja Jct. and Vestaburg of the Eureka - Vestaburg 138kV line using 1431 ACSR with standard double circuit structures. |  | MI | 4.3 |  | Proposed | 8822000 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23847 |  |  | 27642 | 44936 | LNrb | 2026-12-31 | Bingham | Looking Glass | 1 | 138 |  |  | Rebuild approximately 19.3 miles of the Bingham – Looking Glass 138 kV circuit to 1431 ACSR conductor utilizing 138 kV double- circuit structures with OPGW. Leave the East side of the double-circuit structures vacant. |  | MI |  |  | Proposed | 35300000 | Engineering |  | 2023 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23865 |  | METC_22_071 | 27720 | 44841 | LNrb | 2025-03-01 | Mecosta | Chase | 1 | 138 |  |  | Rebuild the entire 17.6 mile Chase-Mecosta 138 kV circuit to hold larger conductor |  | MI | 17.6 |  | Proposed | 34400000 | Engineering Preliminary |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24318 |  |  | 27816 | 44944 | LNrb | 2024-05-31 | Eureka | North Belding |  | 138 | 138 |  | Rebuild approximately 6 miles of 138kV line from Eureka - North Belding with 954 ACSR 138kV double circuit standards. Install circuit from North Belding to the J1379 switching station using the vacant side of double circuit tower using 954 ACSR. |  | MI |  |  | M3_Long Lead Materials | 10574400 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24318 |  |  | 27815 | 44944 | LNrb | 2024-05-31 | Derby | Eureka | 1 | 138 | 138 |  | Rebuild approximately 8.6 miles of 138kV line from Derby to Eureka with 954 ACSR 138kV double circuit standards. Reconductor should be where appropriate in the cost estimate. Install circuit from North Belding to the J1379 switching station using the vacant side of double circuit tower using 954 ACSR. |  | MI |  |  | M3_Long Lead Materials | 13827600 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24377 |  |  | 27884 | 44946 | LNrb | 2024-12-23 | Coldwater | Byers |  | 138 |  |  | Rebuild Coldwater-Byers 138 kV line utilizing 954 ACSR and OPGW. |  | MI | 2 |  | M3_Long Lead Materials | 7230000 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24455 |  |  | 27897 | 44946 | LNrb | 2024-12-23 | Mud Lake | Verona |  | 138 |  |  | Rebuild Verona-Mud Lake 138 kV #1 utilizing 954 ASCR and OPGW |  | MI | 3.6 |  | M3_Long Lead Materials | 8592000 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | West | ATC | 24782 |  | PR09204 | 28098 | 45182 | LNrc | 2025-12-31 | University (UWW) | Mukwonago | UNIG5 | 138 |  |  | UNIG52 (138KV) Line Reconductor |  | WI | 3.5 |  | Planned | 4930697 | GIA |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22848 |  | TP1515 | 26884 | 45158 | LNrc | 2025-06-01 | Hutsonville | Heath |  | 138 |  |  | Rebuild the Hutsonville-Heath-1311 138 kV line from Hutsonville-Str. 95 with conductors capable of 2000 amps at Summer Emergency and OPGW. |  | IL |  |  | Proposed | 12500000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | South | Entergy-TX | 21844 |  | 22-ETI-005 | 26434 | 44819 | LNrc | 2025-12-01 | Deer | Doucette |  | 138 |  |  | Upgrade line bay bus at Doucette and rebuild Deer to Doucette 138 kV line. |  | TX |  |  | Proposed | 18400000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | East | METC | 23807 |  | METC_22_083 | 27542 | 44935 | LNrc | 2027-06-01 | Alma | Vestaburg | 1 | 138 |  |  | Reconductor from Vestaburg to structure #2W8472 (~16.24 miles) from 954 ACSR to 954 ACSS. |  | MI | 16.24 |  | Proposed | 16330000 | Engineering |  | 2023 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24395 |  |  | 27892 | 44946 | LNrc | 2025-11-26 | Luce | Summerton |  | 138 |  |  | Reconductor the entire ~10.5 mile-long Luce – Summerton 138 kV line. Replace the existing 336 ACSR conductor with new 795 ACSS conductor. Replace any structures as necessary. |  | MI | 10.5 |  | M3_Long Lead Materials | 9682800 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | B | Central | NIPS | 23471 |  |  | 27244 | 45133 | LNrc | 2025-05-31 | Roxana | MITTAL2 | 1 | 138 |  |  | Reconductor 2.2 miles of line. |  | IN |  |  | Proposed | 5648342 | Engineering Preliminary |  | 2022 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP23 | C | West | ATC | 24841 |  | PR09235 | 28134 | 45182 | LNup | 2025-05-30 | Concord | Crawfish River | 9043 | 138 |  |  | 9043 (138KV) Uprate |  | WI |  |  | Planned | 1279961 | GIA |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 25207 |  | PR09214, F6512 | 28278 | 45182 | LNup | 2024-10-20 | Forsyth | Empire |  | 138 |  |  | Rerate Line Forsyth conductor for the Forsyth to Empire section to keep up with the system demand. The thermal study identified 18 clearance issues needed to be fixed to bring the rating up to meet Operations/Planning's needs. |  | MI |  |  | Planned | 5000000 | Actual |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23971 |  | TP5228 | 27735 | 45158 | LNup | 2024-12-01 | Effingham NW | Neoga South |  | 138 |  |  | Raise clearances on two structures to increase line rating |  | IL |  |  | Planned | 1300000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | East | METC | 23704 |  | METC_22_074 | 27456 | 45062 | LNup | 2026-12-31 | Mio Dam | Abbe | 1 | 138 |  |  | Remediate sag on the 266.8 ACSR up to conductor’s limit on the Abbe Jct. – Mio Dam section of the Airport – Mio Dam 138 kV circuit. |  | MI |  |  | Proposed | 1700000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24420 |  |  | 27891 | 44946 | LNup | 2024-12-23 | Cobb | White Lake |  | 138 |  |  | Remediate the sag on the Cobb - Peterson Tap 138 kV section to meet or exceed 125 MVA Summer Emergency |  | MI |  |  | M3_Long Lead Materials | 418800 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24454 |  |  | 27896 | 44946 | LNup | 2024-04-05 | Lark | Leoni |  | 138 |  |  | Remediate the sag on the Leoni-Washtenaw Tap 138 kV section to a target rating of 765 Amps Summer Emergyency, |  | MI |  |  | M3_Long Lead Materials | 660000 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23709 |  | METC_22_078 | 27492 | 44897 | TEQ | 2027-06-01 | Campbell | Port Sheldon | 1 | 138 |  |  | Install OGPW/Fiber from Port Sheldon to Campbell use existing fiber paths to get to Tyler, CE to upgrade relaying at Port Sheldon |  | MI |  |  | Proposed | 730000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23807 |  | METC_22_083 | 27543 | 44935 | TEQ | 2027-06-01 | Alma |  |  | 138 |  |  | Upgrade 1590 SAC buses and 1200A switches at Alma position “477” to at least 455 MVA for summer emergency rating. |  | MI |  |  | Proposed | 330000 | Engineering |  | 2023 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23830 |  | METC_22_084 | 27544 | 44935 | TEQ | 2026-12-31 | MCV |  |  | 138 |  |  | Upgrade thermal relay at position "3141" to at least 620 MVA. |  | MI |  |  | Proposed | 190000 | Engineering |  | 2023 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23847 |  |  | 27643 | 44936 | TEQ | 2026-12-31 | Bingham |  |  | 138 |  |  | Connect OPGW at Bingham 138 kV position WM6. |  | MI |  |  | Proposed | 95000 | Engineering |  | 2023 |  |  | METC | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22869 |  | TP1523 | 27969 | 44951 | LNrb | 2027-12-01 | Clark | Viburnam |  | 161 |  |  | Rebuild the existing Clark-Viburnum 161 kV line to be double circuit 161 kV lines. |  | MO |  |  | Planned | 34350000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 23087 |  | TP1582 | 26959 | 45158 | LNrb | 2024-12-01 | Troy | Pike | 1 | 161 |  |  | Rebuild and Add Dual OPGW to the TROY-PIKE-1 Line from Pike to the Auburn tap (Structure 309 or so). |  | MO |  |  | Planned | 16000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 23306 |  | TP1599 | 27012 | 44956 | LNrb | 2025-06-01 | Stoddard | Essex |  | 161 |  |  | Rebuild the 5.4 mile Stoddard-Essex-3 161 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. |  | MO |  |  | Planned | 3300000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | GLH | 23765 |  |  | 27521 | 45030 | LNrb | 2026-12-31 | Joppa | Grahamville |  | 161 |  |  | Rebuild GridLiance Heartland portion of Joppa - Joppa TS - Grahamville ckt 854 tie line to LG&E. |  | KY,IL | 10.4 |  | Proposed | 21900000 | Planning |  | 2022 |  |  | Gridliance | N | N | N
A in MTEP23 | C | Central | GLH | 23826 |  |  | 27522 | 45030 | LNrb | 2026-12-31 | Joppa | Grahamville |  | 161 |  |  | Rebuild the GridLiance Heartland portion of Joppa - Grahamville 161 kV Ckt 804 tie line to LG&E |  | KY,IL | 10.1 |  | Proposed | 21900000 | Planning |  | 2022 |  |  | Gridliance | N | N | N
A in MTEP23 | C | West | ITCM | 23464 |  | Abbott-Traer 161 | 27269 | 44791 | LNrb | 2027-12-31 | Abbott | Trear | 1 | 161 | 161 |  | Rebuild the Abbott-Traer 161kV line to using T2 Grosbeak. |  | IA | 15 |  | Proposed | 16836000 | Engineering |  | 2022 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | MEC | 23688 |  |  | 27425 | 44812 | LNrb | 2027-06-01 | Macksburg | Winterset |  | 161 |  |  | Reconductor the 161 kV line from Macksburg to Winterset. |  | IA |  |  | Proposed | 12500000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | XEL | 23513 |  |  | 27284 | 44792 | LNrc | 2025-06-15 | Emerald | Pine Lake | 1 | 161 | 115 |  | Rebuild 1 mile of double circuit 161-115kv line to single circuit 115kv line. |  | WI | 1 |  | Planned | 2000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | ITCM | 23611 |  | J982 Affected System Upgrades | 27340 | 44817 | LNup | 2023-09-01 | Fox Lake | Rutland | 1 | 161 | 161 |  | MISO Facilities Study for Affected System upgrades for project J982, a 300 MW wind-powered generating facility with proposed interconnection on MEC’s Obrien County – Kossuth 345kV circuit. The system impact study has indicated the interconnection of project J982 will require sag mitigation on the Fox Lake to Rutland 161 kV circuit. |  | MN |  |  | Planned | 338000 | Engineering |  |  |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | Central | BREC | 23569 |  |  | 27322 | 44805 | TEQ | 2025-07-02 | McCracken |  |  | 161 |  |  | Add new 161 kV terminal. |  | KY |  |  | Proposed | 1000000 | Planning |  |  |  |  | Big Rivers Electric Corporation | N | N | N
A in MTEP23 | C | Central | GLH | 23827 |  |  | 27530 | 45030 | TEQ | 2026-12-31 | Joppa TS |  |  | 161 |  |  | Add one breaker and equipment for additional position at Joppa TS |  | IL |  |  | Proposed | 0 | [5 empty] | Gridliance | N | N | N
A in MTEP23 | C | West | MEC | 23694 |  |  | 27440 | 44812 | TEQ | 2026-12-31 | Wall Lake |  |  | 161 |  |  | Wall Lake 161 kV terminal equipment upgrades |  | IA |  |  | Planned | 100000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23741 |  |  | 27439 | 44812 | TEQ | 2026-12-31 | Wright |  |  | 161 |  |  | Wright 161 kV terminal equipment upgrades |  | IA |  |  | Planned | 150000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | B | South | Entergy-LA | 12098 |  | 17-ELB-007 | 22204 | 44819 | LNrc | 2026-06-01 | Delmont | Hazel |  | 230 |  |  | Upgrade the Delmont to Hazel kV conductor, bus work at both the stations, line bay bus ,jumpers and any station equipment to a minimum of 1600 A to increase the final rating on Delmont to Hazel 230 kV circuit to a minimum of 1600 A. |  | LA |  |  | Proposed | 15600000 | Planning |  |  |  |  | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 24272 |  | 23-ELB-020 | 27772 | 44894 | LNrc | 2025-07-15 | Moler | Coly |  | 230 |  |  | Upgrade Coly to Moler 230 kV line. |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | West | OTP | 23146 |  |  | 26969 | 44701 | LNrc | 2023-05-31 | Big Stone (620314) | Big Stone South (620322) | 1 & 2 | 230 |  |  | J722 is required to uprate the Big Stone - Big Stone South 230 kV line circuit #1 and circuit #2 to a minimum of 681.7 MVA. In order to increase the ratings of Big Stone - Big Stone South 230 kV circuit #1 and circuit #2, structure replacements will be required and new conductor will be required. |  | SD |  |  | M3_Long Lead Materials | 1101010 | Facility Study |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23146 |  |  | 26968 | 44701 | LNup | 2023-05-31 | Big Stone (620314) | Blair (655465) | 1 | 230 |  |  | J722 is required to uprate the Big Stone - Blair 230 kV line to a minimum of 672.3 MVA. In order to increase the rating of Big Stone - Blair 230 kV, structure replacements will be required. |  | SD |  |  | M3_Long Lead Materials | 655077 | Facility Study |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | B | South | Entergy-LA | 12098 |  | 17-ELB-007 | 22206 | 44819 | TEQ | 2026-06-01 | Delmont | Hazel |  | 230 |  |  | Upgrade the Delmont to Hazel kV conductor, bus work at both the stations, line bay bus ,jumpers and any station equipment to a minimum of 1600 A to increase the final rating on Delmont to Hazel 230 kV circuit to a minimum of 1600 A. |  | LA |  |  | Proposed | 0 | Planning |  |  |  |  | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23957 |  | 23-ELB-004 | 27917 | 45145 | TEQ | 2026-06-30 | Willow Glen |  |  | 230 |  |  | Install 2 new breakers and 4 new switches, replace 1 breaker. Other station equipment required |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23957 |  | 23-ELB-004 | 27916 | 45145 | TEQ | 2026-06-30 | Conway |  |  | 230 |  |  | Install 6 new breakers, 12 new switches, replace 4 breakers (due to fault current), relocate Panama line to new node. Station will be breaker and a half configuration |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23960 |  | 23-ENO-001 | 27855 | 44938 | TEQ | 2024-12-31 | Multiple |  |  | 230 | 69 |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  | LA |  |  | Proposed | 2190124 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | East | ITCT | 24417 |  |  | 27881 | 44939 | LINE | 2025-05-16 | Milan | Monroe-Morocco |  | 345 |  |  | Extend the Milan - Monroe - Morocco 345kV line to loop in the New 345kV station. |  | MI |  | 0.1 | M3_Long Lead Materials | 1736400 | GIA |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | West | MEC | 24999 |  |  | 28166 | 45086 | LINE | 2026-06-03 | Rolling Hills | Southland | 1 | 345 |  |  | Reroute the existing Pony Creek-Rolling Hills 345 kV line into Southland Substation |  | IA |  |  | Proposed | 4000000 | Planning |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | East | METC | 24448 |  |  | 27974 | 45114 | LINE | 2025-10-31 | Murphy | Styx |  | 345 |  |  | Loop the Murphy - Styx (J984) 345kV circuit (Currently Murphy - Nelson Road 345kV circuit) into the new J1389 Interconnection station. |  | MI |  |  | Proposed | 1120800 | Facility Study |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22266 |  | TP1474 | 26769 | 45158 | LNrb | 2024-12-01 | Clinton | Oreana | 4571 | 345 |  |  | Rebuild existing double-circuit towers on the Clinton-Oreana-4571/Clinton-Goose Creek-4545 345 kV line due to deteriorated condition. Include the reroute of the 4571 line in to Leghorn. |  | IL |  |  | Planned | 27800000 | Budgetary |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22266 |  | TP1474 | 26770 | 45158 | LNrb | 2024-12-01 | Clinton | Goose Creek | 4545 | 345 |  |  | Rebuild existing double-circuit towers on the Clinton-Oreana-4571/Clinton-Goose Creek-4545 345 kV line due to deteriorated condition. Include the reroute of the 4571 line in to Leghorn. |  | IL |  |  | Planned | 6500000 | Budgetary |  |  |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22817 |  | TP1508 | 26878 | 44979 | LNrb | 2026-12-01 | Mount Vernon | Xenia |  | 345 |  |  | Rebuild the existing 37 mile Mount Vernon West-Xenia-4591 345 kV line due to replace decayed and severely woodpecker damaged wood poles. Newly rebuilt line will utilize conductors capable of 3000 amps at Summer Emergency conditions and 2 OPGW's. |  | IL |  |  | Planned | 51000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22851 |  | TP1519 | 26888 | 45158 | LNrb | 2025-06-01 | Mt Vernon West | West Frankfort East |  | 345 |  |  | Rebuild the existing 36 mile Mount Vernon West-West Frankfort East-4561 345 kV line due to replace decayed and severely woodpecker damaged wood poles. Newly rebuilt line will utilize conductors capable of 3000 amps at Summer Emergency conditions and 2 OPGW's. |  | IL |  |  | Planned | 48000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | West | MEC | 24999 |  |  | 28167 | 45086 | LNrb | 2027-06-03 | CBEC | Pony Creek | 1 | 345 |  |  | Rebuild the existing CBEC-Pony Creek 345 kV line |  | IA | 2.81 |  | Proposed | 11000000 | Planning |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | ATC | 24838 |  | PR09216 | 28116 | 45182 | LNrc | 2028-12-29 | North Appleton | Fox River |  | 345 |  |  | NAPL121 345kV Transmission Line Reconductor (J1316) |  | WI | 8 |  | Planned | 22347091 | GIA |  | 2027 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22813 |  | TP1503 | 26874 | 44948 | LNrc | 2025-12-01 | Coffeen North | Roxford | 1 | 345 |  |  | Reconductor the 51 mile Coffeen North-Roxford-4551 345 kV line with conductor capable of carrying 3,000 amps during Summer Emergency conditions. |  | IL | 51 |  | Planned | 25000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | B | West | ATC | 20203 |  | WO 603839 | 26318 | 45182 | LNup | 2026-06-30 | Various Lines |  |  | 345 | 69 |  | Line Clearance Mitigation |  | WI,MI |  |  | Planned | 10000000 | Budgetary |  |  |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24758 |  | PR09191 | 28078 | 45182 | LNup | 2026-06-03 | Columbia | North Madison | LCOL2 | 345 |  |  | J1410 J1411 TL Modification (W31) |  | WI |  |  | Planned | 4680062 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24799 |  | PR09198 | 28090 | 45182 | LNup | 2026-11-12 | Blitz | Rockdale | W-32 | 345 |  |  | W32 (345kV)-Loop-in New SS |  | WI |  |  | Planned | 3181676 | GIA |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23676 |  | TP1715 | 27399 | 44943 | LNup | 2024-06-01 | Coffeen North | Pana |  | 345 |  |  | Raise existing Coffeen North-Pana 345kV Transmission line. |  | IL |  |  | Planned | 400000 | GIA |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL, AmerenMO | 23844 |  |  | 27623 | 44819 | LNup | 2025-12-01 | Various |  |  | 345 | 138 |  | Pole and Insulator replacements requested by Maintenance (Missouri and Illinois) |  | IL,MO |  |  | Proposed | 20000000 | Budgetary |  | 2025 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | DEI | 23863 |  | M220321 | 27620 | 44873 | LNup | 2027-04-01 | Cayuga Gen. Sta. | Nucor | 1 | 345 |  | 1374 | Cayuga Gen Station and Nucor 34501 Line Terminal Bus Upgrades (transitions between the line conductors and the ring buses): Upgrade 2500AL and/or 2-954AL bus conductor to 2-1590AL at both line terminal locations. |  | IN |  |  | Proposed | 320000 | Planning Preliminary |  | 2022 |  | 1374 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | IPL | 23107 |  |  | 27013 | 44739 | LNup | 2023-11-01 | DEI Whitestown | DEI Hortonville |  | 345 |  |  | OPGW Fiber Installation |  | IN |  |  | Proposed | 4000000 | GIA |  | 2022 |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP23 | B | Central | ITCT | 15872 |  | ITC_19_026 | 23965 | 44894 | LNup | 2026-12-31 | Brownstown | Monroe | 2 | 345 |  |  | Raise the sag limit on Brownstown – Monroe #2 345 kV line to at least 1361 MVA. |  | MI |  |  | Proposed | 1329000 | Engineering |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | West | MEC | 23726 |  | T92KD | 27451 | 45156 | LNup | 2024-12-01 | Raun | Remsen |  | 345 |  |  | Network Upgrades for J982 Generator (345 kV structure replacement) |  | IA |  |  | Planned | 1200000 | GIA |  | 2020 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | XEL | 23347 |  |  | 27035 | 44785 | LNup | 2022-09-02 | Blue Lake | Scott County | 1 | 345 |  |  | Replace ammeter on Blue Lake 345 kV breaker 8M33. |  | MN |  |  | Planned | 127000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | B | East | ITCT | 15872 |  | ITC_19_026 | 27518 | 44894 | TEQ | 2026-12-31 | Monroe |  |  | 345 |  |  | Upgrade switches at Monroe positions FT and FM to raise rating to at least 1400 MVA (2343A). |  | MI |  |  | Proposed | 1253000 | Engineering |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | South | Entergy-AR | 23899 |  | 23-EAL-008 | 27582 | 45120 | TEQ | 2024-12-31 | Woodward |  |  | 500 |  |  | Replace aging and failing infrastructure on EAL's transmission system. |  | AR |  |  | Planned | 24638000 | Budgetary |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23934 |  | 23-ELS-004 | 27854 | 44938 | TEQ | 2024-12-31 | Multiple |  |  | 500 | 69 |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  | LA |  |  | Proposed | 43882621 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-TX | 23870 |  | 23-ETI-012 | 27853 | 45152 | TEQ | 2024-12-31 | Multiple |  |  | 500 | 69 |  | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  | TX |  |  | Proposed | 34240000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | B | West | ATC | 20202 |  | WO 603838 | 26317 | 45182 | COM | 2026-06-30 | Various Sites |  |  | 0 |  |  | Communications Reliabiity |  | WI,MI |  |  | Planned | 11000000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 25154 |  | PR09101, F6364 | 28243 | 45182 | COM | 2024-06-30 | n/a |  |  | 0 |  |  | The objective of Substation Ethernet Migration Phase 2 project is to replace legacy (T1) copper circuits with next-generation Ethernet telecommunication circuits at select ATC substation locations. This project will also install cellular and VoIP equipment at a number select ATC substations for back-up SCADA and house phone communications updates. This project will improve and stabilize primary substation SCADA communications reliability while lowering long-term O&M expense. Select sites will also have the substation router upgraded. |  | WI,MI |  |  | Planned | 5500000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | South | SMEPA | 23126 |  |  | 27003 | 44952 | GEN | 2023-02-08 | Morrow |  |  | 20 |  |  | A single steam turbine unit will be repowered at Plant Morrow for combined cycle operation utilizing a new natural gas fired combustion turbine (CT). |  | MS |  |  | Under Construction | 0 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | South | SMEPA | 23126 |  |  | 27002 | 44952 | GEN | 2023-02-08 | Morrow |  |  | 22 |  |  | New natural gas fired combustion turbine (CT) for combined cycle operation with existing Plant Morrow steam turbine (ST). |  | MS |  |  | Under Construction | 0 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | Central | IPL | 23852 |  |  | 27632 | 45184 | GEN | 2025-12-31 | R1011 |  |  | 34.5 | 0.6 |  | Interconnection Customer shall install a 279.45 MVA facility, rated at 279.45 MW gross and 250 MW new with all studies performed at or below these outputs. The Generating Facility is composed of sixty-nine (69) TMEIC NINJA inverter units in a solar farm rated at 4.05 MVA each |  | IN |  |  | Planned | 15000000 | Planning |  | 2022 |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP23 | C | West | ATC | 23858 |  | PR09259 | 27608 | 45182 | COM | 2026-12-31 | Wick Drive | Black Earth | Y-62 | 69 |  |  | OPGW Addition |  | WI |  |  | Planned | 7000000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24465 |  | PR09247 | 27986 | 45182 | COM | 2026-06-30 | Walworth | Brick Church | Y-159 | 69 |  |  | OPGW Addition |  | WI |  |  | Planned | 4600000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | South | CWL | 25094 |  |  | 28242 | 45141 | LNrl | 2023-09-30 | Commerce | Ringier | 1 | 69 |  |  | Relocation of JCWL Commerce – Ringier 69kV line due to ARDOT project, reconductoring relocated portion |  | AR |  |  | Planned | 315000 | [5 empty] | City Water & Light - Jonesboro, Arkansas | N | N | N
A in MTEP23 | C | Central | WVPA | 23780 |  |  | 27510 | 44817 | LNrl | 2023-12-31 | Trail of Tears | Altenburg | 1 | 69 |  |  | Relocate T23 69kV to allow for Ameren's new 138kV Line (Wittenberg - Whipple) |  | MO | 11.6 |  | Planned | 4588146 | Engineering |  | 2023 |  |  | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23881 |  | 23-ELF-002 | 27864 | 44938 | Remove | 2025-06-01 | Lafayette | Holiday |  | 69 |  |  | Remove Lafayette to Holiday 69 kV line |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23882 |  | 23-ELF-003 | 27866 | 44938 | Remove | 2025-06-01 | Barnett Oil Mill | Barnett Oil Mill Tap |  | 69 |  |  | Remove Barnett Oil Mill to Barnett Oil Mill Tap 69 kV line |  | LA |  |  | Proposed | 23700000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23946 |  | 23-ELS-005 | 27868 | 44938 | Remove | 2023-12-31 | Jaguar |  |  | 69 |  |  | Remove Jaguar 69 kV Capacitor bank |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | East | WPSC | 23575 |  |  | 27366 | 44806 | RLY | 2027-12-31 | Pellston |  |  | 69 |  |  | Project will replace capacity limiting equipment and existing protection system at the Pellston substation and relocate the Pellston to Cross Village line to improve reliability on that line. |  | MI |  |  | Proposed | 1600000 | Planning |  | 2027 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | East | WPSC | 23594 |  |  | 27369 | 44806 | RLY | 2025-12-31 | Scottville |  |  | 69 |  |  | Obsolete communication equipment must be replaced with a new RTU. |  | MI |  |  | Proposed | 40000 | Planning |  | 2025 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | East | WPSC | 23595 |  |  | 27370 | 44806 | RLY | 2025-12-31 | Weidman |  |  | 69 |  |  | Replace communication equipment at the Weidman substation. |  | MI |  |  | Proposed | 40000 | Planning |  | 2025 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | East | WPSC | 23620 |  |  | 27364 | 45146 | RLY | 2026-12-31 | North Shade |  |  | 69 |  |  | Upgrade existing electromechanical relays with digital relays. |  | MI |  |  | Proposed | 1250000 | Planning |  | 2026 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | East | WPSC | 23621 |  |  | 27368 | 44806 | RLY | 2024-12-31 | Redwood |  |  | 69 |  |  | Replace communication equipment at the Redwood substation. |  | MI |  |  | Proposed | 150000 | Planning |  | 2024 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | East | WPSC | 23631 |  |  | 27367 | 45146 | RLY | 2026-12-31 | Petoskey |  |  | 69 |  |  | Upgrade existing electromechanical relays with digital relays. |  | MI |  |  | Proposed | 1000000 | Planning Preliminary |  | 2026 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | B | South | Entergy-LA | 15654 |  | 19-ELN-001 | 23670 | 44819 | RLY | 2026-12-01 | Delhi | Tallualh | 1 | 115 |  |  | Upgrading relaying to 1300 amps minimum |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | B | East | ITCT | 22847 |  | ITC_22_001 | 26846 | 45027 | LNrl | 2027-03-31 | Boyne | Golf | 1 | 120 |  |  | Cut the Boyne – Golf 120kV line into the new 120kV substation to provide transmission service to a new LDC Kings Point. Relocate a ~ 2.1 miles section of the Boyne-Golf 120kV circuit by utilizing DTE’s existing 40kV circuit on the North side of 21 Mile Rd, East side of N. Gratiot Ave, and South side of Hall Rd to rebuild this ~2.1 miles to 120kV with 40kV underbuilding to loop the Boyne-Golf line into the new 120kV substation. |  | MI |  |  | Proposed | 12800000 | Engineering |  |  |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24115 |  |  | 27744 | 44852 | LNrl | 2024-06-03 | Mack | Northeast | 1 | 120 |  |  | Relocation and replacement of 1230 ft. of 1500kcmil CU cable with 2100 ft. of 2500kmil CU cable of the Mack-Northeast 120 kV circuit to accommodate future interstate infrastructure improvements directed by the Michigan Department of Transportation (MDOT). |  | MI |  | 0.4 | Proposed | 5540000 | Engineering |  |  |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24393 |  | ITCT_22_049 | 27831 | 45125 | LNrl | 2024-12-31 | Alfred | St. Antoine | 1 | 120 |  |  | Relocate a portion of the Alfred-St. Antoine 120 kV underground cable currently located in the Larned I-375 bridge to accommodate the reconstruction of I-375 in downtown Detroit as directed by the Michigan Department of Transportation (MDOT). |  | MI |  |  | M2a_Pre-Project Approval | 4100000 | Engineering Preliminary |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24393 |  | ITCT_22_049 | 27832 | 45125 | LNrl | 2024-12-31 | Essex | St. Antoine | 1 | 120 |  |  | Relocate a portion of the Esset-St. Antoine 120 kV underground cable currently located in the Larned I-375 bridge to accommodate the reconstruction of I-375 in downtown Detroit as directed by the Michigan Department of Transportation (MDOT). |  | MI |  |  | M2a_Pre-Project Approval | 4100000 | Engineering Preliminary |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP23 | B | East | ITCT | 24466 |  | ITCT_23_003 | 28010 | 45068 | LNrl | 2024-08-01 | Cody | Nolan | 1 | 120 |  |  | Relocate five structures (22993, 22992, 22991, 22990, and 22989) on the Cody - Nolan 120 kV line per Michigan Department of Transportation's request. |  | MI |  |  | Proposed | 1250000 | Engineering Preliminary |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP23 | B | East | ITCT | 22847 |  | ITC_22_001 | 26850 | 45027 | RLY | 2027-03-31 | Golf |  |  | 120 |  |  | Identify any necessary relaying required for the protection at Golf HD Pos |  | MI |  |  | Proposed | 320000 | Engineering |  |  |  |  | ITC Transmission | N | N | N
A in MTEP23 | B | East | ITCT | 22847 |  | ITC_22_001 | 26849 | 45027 | RLY | 2027-03-31 | Boyne |  |  | 120 |  |  | Identify any necessary relaying required for the protection at Boyne HE Pos |  | MI |  |  | Proposed | 600000 | Engineering |  |  |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | South | CLECO | 24033 |  |  | 27724 | 44833 | GEN | 2025-04-01 | Manuel |  |  | 138 |  |  | Expand Manuel Substation to interconnect J1286 |  | LA |  |  | M4_Pre-Construction | 2831239 | Engineering |  |  |  |  | Cleco Power LLC | N | N | N
A in MTEP23 | C | South | CLECO | 24112 |  |  | 27741 | 44848 | GEN | 2023-10-31 | Centennial | West Bay | 1 | 138 |  |  | New Substation Perkins tapped into Centennial to West Bay 138 kV line |  | LA |  |  | M1_Final SPM or OOC | 2607000 | GIA |  |  | Customer is self-building the substation. Cost only reflect Cleco's portion of the work funded by the customer. |  | Cleco Power LLC | N | N | N
A in MTEP23 | C | Central | DEI | 23886 |  | M220302 | 27726 | 44936 | GEN | 2023-12-31 | J1234-1235 IN Solar 1 | Gen and POI Subs |  | 138 |  | 150 | J1234 - J1235 IN Solar 1, LLC (Wheatland Solar (?) - 150MW net (100 MW for J1234 and 50 MW for J1235); generating substation with 200 feet+/- 138kV generator lead line; new POI sub with 3-CB ring bus located in the 13856 line |  | IN |  |  | Planned | 11181000 | Engineering Preliminary |  | 2022 |  | 150 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23637 |  | TP1717 | 27404 | 44943 | LNrl | 2024-06-01 | Hennepin | Putnam |  | 138 |  |  | Raise existing PUTN-HKOK-1556, PUTN-HENN-1771, PUTN-HENN-1765, PUTN-ESK-1757, and PUTN-BURE-1552 transmission lines. |  | IL |  |  | Planned | 1800000 | GIA |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22870 |  | TP1525 | 26892 | 44948 | LNrl | 2025-06-01 | Carrollton |  |  | 138 |  |  | Split the ~2 mile Mason-Carrollton-8/Carrollton-Sioux-8 138 kV lines into two separate circuits to avoid the loss of a single structure causing a long-term outage on both Carrollton supplies. |  | MO |  |  | Proposed | 5000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | West | ATC | 25262 |  | PR08874 | 28376 | 45182 | RLY | 2023-11-08 | North Monroe |  |  | 138 |  |  | North Monroe SS New Protection Panel |  | WI |  |  | Planned | 195742 | GIA |  | 2020 | WO #604899 |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 25262 |  | PR08874 | 28375 | 45182 | RLY | 2023-11-08 | Bass Creek |  |  | 138 |  |  | Bass Creek SS Relay Panel Improvements |  | WI |  |  | Planned | 156123 | GIA |  | 2020 | WO #604898 |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | B | East | METC | 15752 |  | METC_18_066 | 27541 | 44937 | RLY | 2027-06-01 | Redstone |  |  | 138 |  |  | Terminate OPGW at Redstone position WM6. |  | MI |  |  | Proposed | 100000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 22147 |  |  | 26713 | 45001 | RLY | 2024-10-01 | Stable |  |  | 138 |  |  | Upgrade relaying at Stable 138kV to accommodate system changes |  | MI |  |  | M2a_Pre-Project Approval | 69216 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 22147 |  |  | 26712 | 45001 | RLY | 2024-10-01 | Blackstone |  |  | 138 |  |  | Upgrade relaying at Blackstone to accommodate system changes. |  | MI |  |  | M2a_Pre-Project Approval | 69216 | Engineering |  | 2023 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 22165 |  |  | 26719 | 44935 | RLY | 2023-08-01 | Stable |  |  | 138 |  |  | Upgrade relays at Stable 138kV station. |  | MI |  |  | M2a_Pre-Project Approval | 60924 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 22165 |  |  | 26718 | 44935 | RLY | 2023-08-01 | Mud Lake |  |  | 138 |  |  | Upgrade relays at Mud Lake 138kV station |  | MI |  |  | M2a_Pre-Project Approval | 72264 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 22165 |  |  | 26717 | 44935 | RLY | 2023-08-01 | Marshall |  |  | 138 |  |  | Upgrade relays at Marshall 138kV |  | MI |  |  | M2a_Pre-Project Approval | 60924 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 22165 |  |  | 26716 | 44935 | RLY | 2023-08-01 | Brooks Industrial |  |  | 138 |  |  | Upgrade relays at Brooks Industrial |  | MI |  |  | M2a_Pre-Project Approval | 60924 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23709 |  | METC_22_078 | 27761 | 44897 | RLY | 2027-06-01 | Blendon |  |  | 138 |  |  | Replace Section 30 Line Relaying at Blendon |  | MI |  |  | Proposed | 248766 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23709 |  | METC_22_078 | 27760 | 44897 | RLY | 2027-06-01 | Campbell |  |  | 138 |  |  | Replace 138kV Pos. 188 Relaying at Campbell |  | MI |  |  | Proposed | 321430 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23872 |  | METC_22_070 | 27730 | 44897 | RLY | 2026-12-31 | Spaulding |  |  | 138 |  |  | Install relay panel at Spaulding Pos. BM36, 36B7 & 36M9 |  | MI |  |  | Proposed | 499016 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23872 |  | METC_22_070 | 27729 | 44897 | RLY | 2026-12-31 | Broadmoor |  |  | 138 |  |  | Upgrade relay equipment at Spaulding |  | MI |  |  | Proposed | 233311 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24295 |  |  | 28082 | 45026 | RLY | 2025-11-30 | Stable | Substation |  | 138 | 138 |  | Install SEL-2506 relaying at Stable to mitigate islanding scenarios. |  | MI |  |  | Proposed | 44963 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24419 |  |  | 27889 | 45002 | RLY | 2025-12-10 | Coldwater |  |  | 138 |  |  | Remove X-phase and Z-phase wavetraps at Coldwater Section 20. Upgrade Coldwater Section 20 relays. Install Orion I/O for J1320 status points. Install Nokia SAR-8. |  | MI |  |  | M3_Long Lead Materials | 313776 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24419 |  |  | 27888 | 44939 | RLY | 2025-12-10 | Batavia |  |  | 138 |  |  | Remove X-phase and Z-phase wavetraps at Batavia position WM39. Upgrade Batavia WM39 relays. Install OrionLX RTU and I/O for J1320 status points. Replace Cisco Router with Cisco 4331 and Cisco 2520 (or equivalent). Install Nokia SAR-8. |  | MI |  |  | M3_Long Lead Materials | 208138 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24455 |  |  | 27899 | 44943 | RLY | 2024-12-23 | Verona |  |  | 138 |  |  | Upgrade 588 and 388 relaying. |  | MI |  |  | M3_Long Lead Materials | 94905 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24455 |  |  | 27898 | 44942 | RLY | 2024-12-23 | Mud Lake |  |  | 138 |  |  | Upgrade BM8 and WM10 relaying. |  | MI |  |  | M3_Long Lead Materials | 83659 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24673 |  |  | 28058 | 44987 | RLY | 2024-05-31 | Highfield |  |  | 138 |  |  | Install Anti-Islanding relaying At Highfield sub. |  | MI |  |  | Planned | 73125 | Engineering |  | 2023 |  |  | METC | N | N | N
A in MTEP23 | C | East | WPSC | 23616 |  |  | 27360 | 44806 | RLY | 2026-12-31 | Gaylord |  |  | 138 |  |  | Upgrade existing electromechanical relays with digital relays. |  | MI |  |  | Proposed | 800000 | Planning |  | 2026 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | East | WPSC | 23618 |  |  | 27362 | 44806 | RLY | 2024-12-31 | Lake County |  |  | 138 |  |  | Minor control system upgrade for communication assisted protection scheme with METC’s Pere Marquette substation. |  | MI |  |  | Proposed | 75000 | Planning |  | 2024 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | West | MEC | 23723 |  | H01B4, H01B5, T92LM, T92LP | 27436 | 45125 | COM | 2027-12-31 | Edgington |  |  | 161 |  |  | New fiber communication paths from Edgington substation to remote end substations for communication and protective relaying. Combination of new OPGW on 161 kV transmission line and new underground fiber. |  | IL |  |  | Proposed | 5400000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | B | Central | AmerenMO | 23430 |  | TP1699 | 27083 | 45056 | LNrl | 2025-12-01 | Appanoose | Zachary |  | 161 |  |  | Reroute Appanoose - Adair -161 kV to Appanoose - Zachary. |  | MO |  |  | Planned | 1200000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | HMPL | 24172 |  |  | 27759 | 44866 | LNrl | 2023-07-01 | HMPL SUB 4 161 kV | HMPL Sub 4 Tap 161 kV | 1 | 161 |  |  | Extending the line by 0.26 miles |  | KY |  |  | Proposed | 155000 | Budgetary |  |  |  |  | Henderson Municipal Power & Light | N | N | N
A in MTEP23 | C | West | XEL | 23513 |  |  | 27285 | 44792 | Remove | 2025-06-15 | Pine Lake |  |  | 161 | 115 |  | Retire Pine Lake 161kv to 115kv yard. |  | WI |  |  | Planned | 1000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | MEC | 23592 |  | T929V | 27338 | 45156 | RLY | 2024-12-31 | Floyd | Emery |  | 161 | 69 |  | Add 69 kV Bus PTs; remove wave trap and employ fiber for Floyd-Emery 161 kV line relaying |  | IA |  |  | Planned | 350000 | Budgetary |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MDU | 24978 |  |  | 28151 | 45155 | COM | 2023-12-01 | Tatanka South |  |  | 230 |  |  | Communication equipment replacement |  | SD,ND |  |  | Proposed | 0 | [5 empty] | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | South | CLECO | 24113 |  |  | 27742 | 44848 | GEN | 2024-09-15 | Cole | Penton | 1 | 230 |  |  | Tap the future Cole to Penton 230 kV line and build a new Substation Singer |  | LA |  |  | Proposed | 2967565 | GIA |  |  | Customer is self-building the substation. Cost only reflect Cleco's portion of the work funded by the customer. |  | Cleco Power LLC | N | N | N
A in MTEP23 | C | South | CLECO | 24114 |  |  | 27743 | 44848 | GEN | 2024-09-29 | Caneland |  |  | 230 |  |  | Expand Caneland Substation to interconnect J1367 Generation Plant |  | LA |  |  | Proposed | 5163000 | GIA |  |  |  |  | Cleco Power LLC | N | N | N
A in MTEP23 | C | Central | DEI | 23887 |  |  | 27722 | 44833 | GEN | 2024-11-15 | J1378 Crosroads Solar | Gen Sub |  | 230 |  | 200 | J1378 Crossroads Solar, LLC - 200MWs - Generation equipment; Approx. 0.097 mile of 230 kV generator lead line @ 795AL kcmil |  | IN |  | 0.1 | Planned | 0 |  |  |  |  | 200 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | West | GRE | 23920 |  | 207531 | 27636 | 45068 | LNrl | 2023-10-13 | Stanton |  |  | 230 |  |  | Replace/relocate 5 towers and reconductor the river crossing to avoid structure/line segments from falling into Missouri river. |  | MN | 0.25 |  | Proposed | 3122886.14 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23946 |  | 23-ELS-005 | 27869 | 44938 | Remove | 2023-12-31 | Snakefarm |  |  | 230 |  |  | Remove Snakefarm 115 kV capacitor bank |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | Central | NIPS | 24562 |  |  | 28045 | 44965 | COM | 2024-06-01 | Schahfer | Hinshaw |  | 345 |  |  | Replacing shield wire on 345kV line with OPGW between Hinshaw and Schahfer, and between Hinshaw and Starke. |  | IN |  |  | Planned | 3374514 | GIA |  | 2023 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP23 | C | West | XEL | 24902 |  |  | 28132 | 45062 | COM | 2024-09-01 | Brookings County | Lyon County | 1 | 345 |  |  | Replace aging OPGW on Brookings - Lyon County 345kV line. |  | MN,SD |  |  | Proposed | 2305464 | Planning Preliminary |  |  | Being performed in conjunction with Brookings - Lyon County 2nd circuit addition project |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 24902 |  |  | 28133 | 45062 | COM | 2025-09-01 | Hampton Corner | Helena | 1 | 345 |  |  | Replace aging OPGW on the Hampton Corner - Helena 345kV line. |  | MN |  |  | Proposed | 1701856 | Planning Preliminary |  |  | Project being performed in conjunction with Hampton - Helena 2nd circuit installation project. |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23367 |  | TP1671 | 27036 | 44943 | GEN | 2024-12-01 | Austin |  |  | 345 |  |  | Project will connect a 1165 combined cycle generator to the existing Austin substation this requires a new 345 kV breaker position. |  | IL |  |  | Planned | 2700000 | GIA |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23983 |  | TP1722 | 27718 | 45069 | GEN | 2024-11-01 | Turner |  |  | 345 |  |  | A 200 MW wind project interconnecting the Ameren Illinois system |  | IL |  |  | Planned | 12000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 24133 |  | TP1725 | 27754 | 45056 | GEN | 2024-06-01 | Goose Creek |  |  | 345 |  |  | 300 MW Wind Farm |  | IL |  |  | Planned | 0 | [5 empty] | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 23388 |  | TP1704 | 27030 | 45056 | GEN | 2024-06-01 | Spencer |  |  | 345 |  |  | 380 MW Wind Farm Connected Spencer Creek. |  | MO |  |  | Planned | 1700000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 23470 |  | TP1701 | 27242 | 45160 | GEN | 2024-06-01 | Fabius |  |  | 345 |  |  | Construct the new 345 kV Fabius substation in Knox County, Missouri to provide a Point of Interconnection for the Generating Facility with a terminal that will consist of all necessary terminal equipment to connect the J1025 leadline to 345kV Fabius substation bus. J1025 is a 300 MW Wind project interconnecting to the Zachary-Maywood 345 kV line |  | MO |  |  | Proposed | 11000000 | GIA |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 23500 |  | TP1702 | 27243 | 44789 | GEN | 2024-11-01 | Zachary |  |  | 345 |  |  | One 345 kV terminal in the Zachary substation. The terminal will consist of all necessary terminal equipment to connect the J1182 leadline to the Zachary substation bus. J1182 is a 250 MW Solar project interconnecting to the Zachary substation 345 kV bus |  | MO |  |  | Proposed | 2593000 | GIA |  | 2021 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | DEI | 23967 |  | M210469 | 27717 | 44833 | GEN | 2024-06-01 | J1295 Gibson Solar | Gen Sub |  | 345 |  | 280 | J1295 Gibson Solar (280MW +/-) |  | IN |  |  | Planned | 0 |  |  |  |  | 280 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | East | ITCT | 23880 |  |  | 27672 | 44819 | LNrl | 2023-12-31 | blanket |  |  | 345 | 120 |  | Relocation portions of transmission lines located in public right of way at the government entities mandate. |  | MI |  |  | Proposed | 2400000 | Planning Preliminary |  |  |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | West | MEC | 24999 |  |  | 28164 | 45086 | LNrl | 2026-06-03 | CBEC | Overland Trail | 1 | 345 |  |  | Reroute the CBEC-Overland Trail 345 kV line into new line terminal at Overland Trail Substation |  | IA |  |  | Proposed | 2000000 | Planning |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | East | METC | 23950 |  |  | 27681 | 44819 | LNrl | 2023-12-31 | blanket |  |  | 345 | 138 |  | Relocation of portions of transmission lines located in public right of way at the government entity’s mandate. |  | MI |  |  | Proposed | 2400000 | Planning |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | West | ATC | 24758 |  | PR09191 | 28080 | 45182 | RLY | 2026-06-03 | Columbia |  |  | 345 |  |  | J1410 J1411 Columbia SS Relay Panel |  | WI |  |  | Planned | 283940 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24758 |  | PR09191 | 28079 | 45182 | RLY | 2026-06-03 | North Madison |  |  | 345 |  |  | J1410 J1411 North Madison Relay Panel |  | WI |  |  | Planned | 242888 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24799 |  | PR09198 | 28089 | 45182 | RLY | 2026-11-12 | Rockdale |  |  | 345 |  |  | Rockdale SS Relay |  | WI |  |  | Planned | 239432 | GIA |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | East | ITCT | 24333 |  |  | 27787 | 44944 | RLY | 2025-12-29 | Milan | Substation |  | 345 | 345 |  | Upgrade relaying at Milan 345kV position CI. |  | MI |  |  | Proposed | 420320 | Facility Study |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24417 |  |  | 27882 | 44939 | RLY | 2025-05-16 | Milan |  |  | 345 |  |  | Upgrade relaying at position CQ. |  | MI |  |  | M3_Long Lead Materials | 293184 | GIA |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | Central | NIPS | 24562 |  |  | 28044 | 44965 | RLY | 2024-06-01 | Schahfer | Burr Oak |  | 345 |  |  | Remote end communication and protection upgrades at Burr Oak, Schahfer, Starke, and Schrader Ditch. |  | IN |  |  | Planned | 2319299 | GIA |  | 2023 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP23 | C | South | Entergy-AR | 23898 |  | 22-EAL-006 | 27580 | 45050 | RLY | 2026-12-01 | Mcneil 500kV |  |  | 500 |  |  | • Ensure the McNeil – El Dorado 500 kV line, the McNeil 500/115 kV auto and the McNeil – Etta 500 kV line have redundant high-speed protection. • Ensure protection schemes have independent CT and PT winding inputs. • Ensure dual battery installations or monitoring sufficient to FERC 754 guidelines. |  | AR |  |  | Planned | 3970000 | Planning |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP23 | C | West | OTP | 23866 |  | 7523 | 27645 | 44819 | SUB | 2023-12-31 | Veblen 41.6 kV |  |  | 41.6 |  |  | Veblen 41.6 kV breaker replacement. |  | SD |  |  | Proposed | 450000 | Planning |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23955 |  | 7311 | 27662 | 45125 | SUB | 2024-12-31 | Wilton 41.6 kV |  |  | 41.6 |  |  | Install a new line sectionalizing 41.6 kV breaker at Wilton, ND. |  | ND |  |  | Proposed | 250000 | Planning |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | ITCM | 23693 |  | J1132 GIA NU | 27431 | 44812 | BUS | 2024-06-01 | Creston Roundhouse | Substation |  | 69 | 69 |  | Expand the 69kV bus at the Creston Roundhouse substation to add a 2nd box structure. |  | IA |  |  | Planned | 316693 | Engineering |  |  |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23924 |  | 23-ELC-003 | 27861 | 44938 | CB | 2024-06-01 | Mossville |  |  | 69 |  |  | Replace underrated 69 kV breaker |  | LA |  |  | Proposed | 3600000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | West | GRE | 23680 |  | 208340 | 27567 | 45156 | CB | 2025-01-31 | Frog Creek |  |  | 69 |  |  | Replace Circuit Switcher FC161-10 at Frog Creek substation with breaker and add disconnect switches. Replacement of Panel #2 relaying to also be included. |  | MN |  |  | Proposed | 1030196.45 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23717 |  | 208340 | 27532 | 45156 | CB | 2025-04-09 | Deer River |  |  | 69 |  |  | Replace breakers 21NB1,2 & 3. Oil containment and SSVT relocation project is be combined with this project to create more efficiencies with project execution. Replace bus PTs as well due to relay prioritization recommendation. Replace single phase 115kV CCVT with 3 single-phase CCVTs. Move Zemple line relays to the 115kV CTs (current transformers) and CCVTs. Replace EEE and internal equipment, address bus work and jumper issues, and fix wood high side dead-end. |  | MN |  |  | Proposed | 3823670.01 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23782 |  | 209267 | 27546 | 45068 | CB | 2026-07-18 | Dotson Corners |  |  | 69 |  |  | Replace 69kv oil breakers 860, 861, and 862 and associated equipment. |  | MN |  |  | Proposed | 778017 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23783 |  | 209168 | 27536 | 44995 | CB | 2025-02-28 | Maple Lake |  |  | 69 |  |  | Replace 69kV relaying & Breakers 1NB4 & 5 at the Maple Lake sub and associated equipment. |  | MN |  |  | Proposed | 1158346 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | MEC | 23571 |  | T90W4, T90W7, T90W8, T90WA | 27328 | 45156 | CB | 2027-12-01 | Humboldt East |  |  | 69 |  |  | Replace 69 kV breaker 6890 and modify 69 kV line relaying on breakers 6890 and 7130 to accommodate lines from Humboldt Central Substation and Weaver Switching Station, respectively. |  | IA |  |  | Planned | 2300000 | Budgetary |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23571 |  | T90W4, T90W7, T90W8, T90WA | 27331 | 45156 | CB | 2027-12-01 | Humboldt Central |  |  | 69 |  |  | Replace 69 kV breakers 7110 and 7120 and add 69 kV line relaying on breakers 7110 and 7120 to accommodate lines from Corn Belt's Humboldt Substation and Humboldt East Substation, respectively. Add 69 kV bus and 69-13 kV transformer differential relaying. None of this is Transmission. |  | IA |  |  | Planned | 0 | Budgetary |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23593 |  | H00GK | 27342 | 45156 | CB | 2027-12-31 | Charles City North |  |  | 69 |  |  | Charles City North Add 69 kV Breakers |  | IA |  |  | Planned | 800000 | Budgetary |  | 2022 | Revised cost includes only Transmission costs. |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23628 |  | T926Y | 27334 | 44805 | CB | 2024-06-01 | Waverly Junction |  |  | 69 |  |  | Reconfigure 69 kV line terminals to eliminate tapped substation transformer |  | IA |  |  | Planned | 1300000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23655 |  |  | 27396 | 44938 | CB | 2024-12-01 | Shenandoah |  |  | 69 |  |  | Replace to 69 kV breakers at Shenandoah Substation |  | IA |  |  | Planned | 600000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23683 |  |  | 27412 | 44938 | CB | 2024-10-01 | Sheldon |  |  | 69 |  |  | Replace Sheldon 69 kV Breakers 7730, 7740, 7880 and 7890 and associated disconnect switches and relaying |  | IA |  |  | Planned | 2800000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | Central | DEI | 23833 |  | M220179 | 27569 | 45168 | Dist | 2025-06-01 | Edinburgh Industrial Park |  |  | 69 | 12 |  | DEI to construct high-side and loop 69kV lines into a new IMPA-owned Edinburgh Industrial Park substation; one 69/12kV 20MVA transformer; SCADA controlled MOLB 69kV line switches; two 69kV buses with a manually operated 69kV bus tie switch; 69kV connections from the 6950 and 69146 ckts. |  | IN |  | 1.3 | Proposed | 4570000 | Engineering w/AFUDC |  | 2023 | cost estimate is for DEI 69kV facilities only |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23968 |  | DIN2387 | 27703 | 45168 | Dist | 2028-08-08 | Greensfork East | new sub |  | 69 | 12 |  | Greensfork East 69/12kV - 22.4MVA Sub: looped-through feed from 69100 ckt. |  | IN |  |  | Proposed | 1440000 | Engineering w/AFUDC |  | 2023 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23969 |  | M180235 | 27704 | 45168 | Dist | 2026-10-02 | Williamsport | new sub |  | 69 | 12 |  | Williamsport new 69/12kV - 22.4MVA sub: looped-through feed from the 6936 ckt. |  | IN |  |  | Proposed | 3152000 | Engineering w/AFUDC |  | 2023 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | West | GRE | 23761 |  | 209316 | 27557 | 45068 | Dist | 2027-01-04 | NW Litchfield |  |  | 69 |  |  | Tap Xcel’s Grove City – Litchfield Mun 69 kV line and Construct about 3 miles of 69 kV radial line to the high side of Meeker’s new NW Litchfield distribution substation. Install metering and telecom at the new sub. |  | MN |  | 3 | Proposed | 2969551 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23762 |  | 208815 | 27555 | 45156 | Dist | 2024-04-30 | Trimont |  |  | 69 |  |  | Retire GRE assets in the Trimont SMEC distribution substation. |  | MN |  |  | Proposed | 243446.12 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23802 |  | 209310 | 27560 | 45068 | Dist | 2025-10-31 | West Otsego | West Otsego Tap | 1 | 69 |  |  | Install a 3-way 69 kV switch on GRE’s Otsego to Albertville 69 kV line and construct about 0.5 miles of 69 kV tap line to the high side of Wright Hennepin’s West of Otsego area substation. |  | MN |  | 0.5 | Proposed | 1283329 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23804 |  | 209185 | 27558 | 45068 | Dist | 2025-07-29 | Kimball | Kimball Tap | 1 | 69 |  |  | Install a 3-way 69 kV, 1200 A switch on Xcel Energy’s Kimball – Watkins 69 kV line and construct about 2 miles of 69 kV line with 477 ACSR conductor to the high side of Meeker’s new Kimball area distribution substation. |  | MN |  | 2 | Proposed | 1036304.63 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | B | South | SMEPA | 12222 |  |  | 22353 | 44979 | Dist | 2023-06-01 | Maxie |  |  | 69 |  |  | Replace the member distribution transformer and high side breaker/circuit switcher. |  | MS |  |  | Proposed | 1765000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | West | XEL | 23528 |  |  | 27266 | 44791 | Dist | 2025-10-15 | Gaiter Lake |  |  | 69 |  |  | Build new Gaiter Lake substation in Waseca to pick up load off of Clarks Grove, Meridan, and Waseca substations. |  | MN |  |  | Planned | 7800000 | Planning Preliminary |  |  | Distribution project with Substation work to support, DCP $5M SUB $2.8M. |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | ATC | 23875 |  | PR09194 | 27596 | 45182 | SUB | 2026-12-01 | Walnut GIS |  |  | 69 |  |  | Walnut GIS Asset Renewal |  | WI |  |  | Planned | 4372716 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23875 |  | PR09194 | 27961 | 45182 | SUB | 2026-12-01 | Wingra SS |  |  | 69 |  |  | Asset Renewal |  | WI |  |  | Planned | 1093179 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23875 |  | PR09194 | 27960 | 45182 | SUB | 2026-12-01 | Ruskin SS |  |  | 69 |  |  | Asset Renewal |  | WI |  |  | Planned | 1093179 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23875 |  | PR09194 | 27958 | 45182 | SUB | 2026-12-01 | East Campus |  |  | 69 |  |  | Asset Renewal |  | WI |  |  | Planned | 4372716 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23875 |  | PR09194 | 27957 | 45182 | SUB | 2026-12-01 | Blount SS |  |  | 69 |  |  | Asset Renewal |  | WI |  |  | Planned | 5502315 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23913 |  | PR09242 | 27610 | 45182 | SUB | 2027-05-01 | Colburn |  |  | 69 |  |  | New Substation |  | WI |  |  | Planned | 39900000 | Planning |  | 2027 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | B | Central | AmerenMO | 21927 |  |  | 26534 | 44453 | SUB | 2025-02-06 | Kinsey 69kV |  |  | 69 | 12 | 7MVA | New 5/7 mVA 69-12.5 kV substation |  | MO |  |  | Planned | 1200000 | Planning |  |  |  | 7MVA | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP23 | C | Central | DEI | 23867 |  | WVPA-2023-1 | 27646 | 45168 | SUB | 2024-08-07 | WVPA Anderson Grain |  |  | 69 |  |  | WVPA Rebuilding Anderson Grain 69/12kV Sub: Relocate transmission and add in & out with SCADA switches for new Anderson Grain substation. Install 69kV ckt switcher and relaying for high side protection. |  | IN |  |  | Proposed | 1750000 | Engineering |  | 2023 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23871 |  | WVPA-2023-7 | 27655 | 45167 | SUB | 2026-10-31 | WVPA NSC Lick Creek | new sub |  | 69 | 12 | 150 | WVPA NSC (Ninestar Connect) Lick Creek 69/12kV Substation: 22.4MVA |  | IN |  | 3.5 | Proposed | 6923547 | Planning Preliminary |  | 2022 |  | 150 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23922 |  | WVPA-2023-2 | 27647 | 45168 | SUB | 2024-04-03 | WVPA Bringhurst |  |  | 69 |  |  | WVPA Bringhurst 69/12kV Sub Rebuild Project: 4.5MVA loading on 6.25MVA existing bank. Possibly bring #1 & #2 sectionalizing line switches inside of substation for an in&out. WVPA owns the loop through portion of the substation. |  | IN |  |  | Proposed | 5800000 | Engineering |  | 2023 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23923 |  | WVPA-2023-6 | 27654 | 44819 | SUB | 2024-07-15 | WVPA Vandalia | new sub |  | 69 | 12 |  | WVPA Vandalia (Fillmore) Substation: 69/12kV Vandalia Substation - Incorporate SCADA operated 69 kV flow-through switches into 6996 line between Greensboro and Amo. |  | IN |  |  | Proposed | 5450000 | Planning Preliminary |  | 2022 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23953 |  | WVPA-2023-8 | 27656 | 44819 | SUB | 2024-05-31 | WVPA Greencastle |  |  | 69 | 12 |  | WVPA Greencastle 69/12kV Substation Rebuild: Rebuild the existing 69-12.47 kV Greencastle Substation with 69 kV flow-through in another location due to size of site. Replace bank with 14.4 MVA. |  | IN |  |  | Proposed | 4828000 | Planning Preliminary |  | 2022 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23980 |  | M200372 | 27694 | 45168 | SUB | 2023-12-29 | Glenwood West (new) |  |  | 69 | 12 |  | Glenwood West (new) - Install 10.5MVA, 69-12kV non-LTC transformer; build/re-route the existing 6920 line to loop through the new substation with ATO/TLS switches |  | IN |  |  | Under Construction | 1400000 | Engineering w/AFUDC |  | 2023 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23981 |  | M200398 | 27695 | 45168 | SUB | 2025-11-06 | Saint Paul Northwest (new) |  |  | 69 | 12 |  | Saint Paul Northwest (new) - Install 10.5MVA, 69-12kV non-LTC transformer; build/re-route the existing 6937 line to loop through the new substation with ATO/TLS switches |  | IN |  |  | Proposed | 1377000 | Engineering w/AFUDC |  | 2023 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | West | GRE | 23682 |  | 209291 | 27565 | 45156 | SUB | 2024-06-21 | Princeton |  |  | 69 |  |  | Add breaker and relaying to address incomplete topology and relaying load limit issue at Princeton. The plan to accommodate this work is to bring the OL line around to the west bay of the four structure and place breaker in PT occupied bay. Bus PT’s will be replaced and relocated to a different location on site to accommodate the breaker addition in west bay. This project will also require that we rebuild to OL line tapping into the north by bringing it in to the west bay with the characteristics of the new line rebuild plan of the OL line. |  | MN |  |  | Proposed | 763118.2 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23764 |  | 209168 | 27540 | 44995 | SUB | 2025-09-02 | Stinson |  |  | 69 |  |  | Add low side breaker and SEL-487E secondary transformer relay. Move 69kV line relays to the 69kV CTs. New panel will be installed with SEL-487E and breaker controls. |  | MN |  |  | Proposed | 664368 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23781 |  | 208675 | 27537 | 45068 | SUB | 2024-10-15 | Shannon |  |  | 69 |  |  | Add low side breaker and SEL-487E secondary transformer relay. Move 69kV line relays to the 69kV CTs. New panel will be installed with SEL-487E and breaker controls. Replace RTU. Replace two (2) 69kV Bus PTs (G.E. Superbute) |  | MN |  |  | Proposed | 596069 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23784 |  | 209330 | 27545 | 44995 | SUB | 2025-09-01 | Blackberry |  |  | 69 |  |  | Remove existing switch 20NSM1 from Blackberry and replace with a circuit breaker and disconnect. OR Retain existing switch 20NSM1 at Blackberry and add a circuit breaker between the 115/69 kV transformer and switch 20NSM1. |  | MN |  |  | Proposed | 704466 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23824 |  | 208670 | 27539 | 45068 | SUB | 2024-11-11 | Virginia |  |  | 69 |  |  | Add low side breaker and SEL-487E secondary transformer relay. Move 69kV line relays to the 69kV CTs. New panel will be installed with SEL-487E and breaker controls. Replace RTU. Replace three (3) 69kV Bus Pts (G.E. Superbute) |  | MN |  |  | Proposed | 555894.89 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | ITCM | 23511 |  | Grinnell South | 27275 | 44945 | SUB | 2025-12-15 | Grinnell South | Substation |  | 69 | 69 |  | Rebuild the Grinnell South sub in a new location directly south of the existing sub and add a new 20MVAR cap bank. |  | IA |  |  | Proposed | 4691139 | Engineering |  | 2022 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 23511 |  | Grinnell South | 27276 | 44945 | SUB | 2025-12-31 | Grinnell South | Substation |  | 69 | 69 |  | Retire the old Grinnell South sub after completion of the new one. |  | IA |  |  | Proposed | 631261 | Engineering |  | 2022 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 23684 |  | Kittyhawk Sub Rebuild | 27413 | 44945 | SUB | 2025-12-31 | Kittyhawk | Substation |  | 69 | 69 |  | Rebuild the Kittyhawk 69kV substation to allow for a 2nd distribution transformer and 2 line breakers and a bus tie breaker. |  | IA |  |  | Proposed | 3652741 | Engineering |  | 2022 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 23701 |  | J1135 GIA TOIF | 27437 | 45140 | SUB | 2027-06-01 | Huntwoods | Substation |  | 69 | 69 |  | Install equipment dedicated to the J1135 generating facilities. The J1135 line will be connected to a new breaker position on the Huntwoods 69 kV bus. This work is to install a new 69kV terminal. TOIF cost to include the new breaker, switches, relay panel and any new associated equipment. |  | IA |  |  | Planned | 558384 | Engineering |  |  |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 24740 |  | Commercial 69kV Sub | 28072 | 45015 | SUB | 2024-06-01 | Commercial (JCE) | Substation |  | 69 | 69 |  | ITC’s portion of the Commercial Substation ITC will install a new 69 kV substation with 2 69 kV line breakers, one distribution transformer position, and one mobile transformer position. All the ITC equipment will be capable of 600A or greater. |  | IL |  |  | Proposed | 3076869 | Engineering |  | 2023 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | MEC | 23608 |  | T92F4, T92F6 | 27323 | 45156 | SUB | 2024-06-01 | E. 29th & Hubbell |  |  | 69 |  |  | Expand steel, install 69 kV line breakers, and install a new 69 kV line tap |  | IA |  |  | Planned | 500000 | Budgetary |  | 2022 | Updated cost estimate to include only Transmission components. |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23629 |  | T9048; T92A2; T929X | 28093 | 45159 | SUB | 2025-12-01 | Charles City South |  |  | 69 |  |  | Replace 69 kV line breaker 6210, line breaker 6350 and associated line relaying, and 69 kV bus differential relaying. |  | IA |  |  | Planned | 1600000 | Budgetary |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23720 |  |  | 27419 | 44812 | SUB | 2025-06-01 | Sioux Center |  |  | 69 |  |  | Construct new 69 kV line from Hickory Avenue Substation to Sioux Center Substation. Expand Hickory Avenue and Sioux Center Substations to install new 69 kV line terminals |  | IA |  |  | Planned | 3000000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23720 |  |  | 27418 | 44812 | SUB | 2025-06-01 | Hickory Avenue |  |  | 69 |  |  | Construct new 69 kV line from Hickory Avenue Substation to Sioux Center Substation. Expand Hickory Avenue and Sioux Center Substations to install new 69 kV line terminals |  | IA |  |  | Planned | 2000000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | East | WPSC | 23615 |  |  | 27359 | 44806 | SUB | 2026-12-31 | Copemish |  |  | 69 |  |  | Replace the circuit breaker and its associated controls and protective relaying, bringing the station to Wolverine’s standard for 138kV transmission operation. |  | MI |  |  | Proposed | 1500000 | Planning |  | 2026 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | West | XEL | 23728 |  |  | 27464 | 44813 | SUB | 2026-10-15 | Owen Area Substation |  |  | 69 |  |  | Install new Owen Area Substation and convert Owen Distribution to 23.9 kV. |  | WI |  |  | Planned | 7854000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | ITCM | 23722 |  | J1132 GIA TOIF | 27434 | 44812 | SUBmisc | 2024-06-01 | Creston Roundhouse | Substation |  | 69 | 69 |  | TOIF includes facilities and equipment dedicated to the Generating Facility including; 69kV switch |  | IA |  |  | Planned | 40968 | Engineering |  |  |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | MEC | 23739 |  | T92LC | 27428 | 45156 | SUBmisc | 2027-12-31 | Sub 42 |  |  | 69 |  |  | Sub 42: Install 69 kV Line Switches |  | IL |  |  | Planned | 800000 | Budgetary |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | Central | DEI | 23978 |  | M190253 | 27692 | 45168 | SwSta | 2025-12-31 | Bargersville North Switching Station | new sub - ring bus |  | 69 |  |  | Build new Bargersville North 69kV three breaker ring bus switching station in the 69102 line |  | IN |  |  | Proposed | 11659302 | Planning Preliminary |  | 2022 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23979 |  | M190256 | 27693 | 45168 | SwSta | 2026-03-03 | Trafalgar | ring bus |  | 69 |  |  | Convert the existing Trafalgar 69 kV switching station to a three breaker ring bus |  | IN |  |  | Proposed | 9980000 | Engineering w/AFUDC |  | 2023 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | East | WPSC | 23612 |  |  | 27356 | 44806 | SwSta | 2026-12-31 | Altona |  |  | 69 |  |  | Replace the control building to install modern digital relays and install an additional circuit breaker to increase reliability on Altona to Morley transmission line. |  | MI |  |  | Proposed | 1500000 | Planning |  | 2026 |  |  | Wolverine Power Supply Cooperative, Inc. | N | N | N
A in MTEP23 | C | West | XEL | 23463 |  |  | 27268 | 44791 | SwSta | 2024-06-01 | Nighthawk |  |  | 69 |  |  | New 4-line terminal breaker station connecting to Minnesota Valley – Troy 69 kV transmission line (0724), Crook’s substation, and the SMBSC plant. |  | MN |  |  | Planned | 5000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | SMMPA | 25252 |  |  | 28348 | 45155 | Dist | 2023-03-01 | Fairmont Energy Station |  |  | 69 | 12500 |  | New 69/12.5kV breaker station. |  | MN |  |  | Proposed | 3720000 | Engineering Preliminary |  | 2023 |  |  | Southern Minnesota Municipal Power Agency | N | N | N
A in MTEP23 | C | West | SMMPA | 25252 |  |  | 28346 | 45155 | Dist | 2026-03-01 | West Industrial Park Substation |  |  | 69 | 12500 |  | New 69/12.5kV distribution substation being built west of Fairmont, MN to meet new distribution needs. |  | MN |  |  | Proposed | 800000 | Engineering Preliminary |  | 2023 |  |  | Southern Minnesota Municipal Power Agency | N | N | N
A in MTEP23 | C | West | XEL | 23450 |  |  | 27211 | 44785 | BUS | 2024-12-15 | Stockyards |  |  | 115 |  |  | Install new 115kV bus tie and associated disconnect switches and bus work and re-terminate 0818/5529 at Rogers Lake Sub. |  | MN |  |  | Planned | 5300000 | Planning Preliminary |  |  | Distribution project with Transmission work to support. DCP $3.3M TAM $2M |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23453 |  |  | 27224 | 44788 | BUS | 2022-12-31 | Riverside |  |  | 115 |  |  | Replace switches 5M330B, 5M331B, 5M329A, 5M330A, 5M329B, 5M331A, aux current transformers on 5M304 and 5M305, and two sections of busbar. |  | MN |  |  | Proposed | 900000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23454 |  |  | 27225 | 44788 | BUS | 2022-12-31 | Red Rock |  |  | 115 |  |  | Replace bushing current transformers on breaker K2, switches K2B1, 946B, K2B2, 946A, and meters on 946 and K2. |  | MN |  |  | Planned | 650000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23468 |  |  | 27215 | 44788 | BUS | 2022-08-01 | Chisago County |  |  | 115 |  |  | Replace primary and secondary 115 kV bus 1 differential relays for TR05 and TR06 |  | MN |  |  | Planned | 200000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23469 |  |  | 27219 | 44788 | BUS | 2022-12-31 | Scott County |  |  | 115 |  |  | Replace busbar. |  | MN |  |  | Planned | 200000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23479 |  |  | 27282 | 44791 | BUS | 2024-06-01 | Iron River |  |  | 115 | 34.5 |  | Rebuild the existing Iron River substation to include a 115 kV ring bus and new 115/34.5 kV transformer. |  | WI |  |  | Planned | 7000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23486 |  |  | 27216 | 44788 | BUS | 2023-03-01 | Inver Hills |  |  | 115 |  |  | Replace busbar. |  | MN |  |  | Planned | 200000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23487 |  |  | 27217 | 44788 | BUS | 2022-12-31 | Kohlman Lake |  |  | 115 |  |  | Replace meter on breaker 5P106. |  | MN |  |  | Planned | 50000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23488 |  |  | 27218 | 44788 | BUS | 2022-12-31 | Prairie |  |  | 115 |  |  | Replace meter on breaker 5G8. |  | ND |  |  | Planned | 50000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23489 |  |  | 27221 | 44788 | BUS | 2022-12-31 | Wilmarth |  |  | 115 |  |  | Replace bushing current transformer on breaker 5S11 as well as switches 8S26B1, 8S25B, 8S25A, 8S26B1. |  | MN |  |  | Planned | 550000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | B | South | Entergy-MS | 15708 |  | 19-EMI-001 | 23715 | 44999 | CB | 2025-12-15 | North Jackson |  |  | 115 |  |  | Install Transmission Breakers at North Jackson 115 kV substation. |  | MS |  |  | Proposed | 7300000 | [5 empty] | Entergy Mississippi | N | N | N
A in MTEP23 | C | West | GRE | 23679 |  | 207331 | 27513 | 45064 | CB | 2023-11-01 | Cromwell |  |  | 115 |  |  | Replace 115 kV circuit breakers 13L and 26L. |  | MN |  |  | Proposed | 1359267.96 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23681 |  | 208397 | 27566 | 45064 | CB | 2024-06-30 | Riverton |  |  | 115 |  |  | This project will remove 69kV bus differential relaying, replace GE-T60 with SEL-487E using existing panel 7, protect the 69kV bus zone with the transformer relays, replace Riverton IR8600 RTU with Cybectec RTU, replace Westinghouse 3-phase 115kV PT with 3 single phase CCVTs on 115kV bus, and replace the 115-kV 25WB1 oil breaker. In addition to this work there will also be some 69-kV and 115-kV bus work and jumper modifications. |  | MN |  |  | Proposed | 849708.75 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23799 |  | 208459 | 27563 | 45068 | CB | 2023-11-16 | Benton County |  |  | 115 |  |  | Replace 115kv breakers 5N52 and 5N53 |  | MN |  |  | Proposed | 526695.97 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 24285 |  | 209696 | 27955 | 45068 | CB | 2025-08-01 | Benton County |  |  | 115 |  |  | The existing 115kV Benton County substation is built as a two row breaker-and-a-half breaker station. A new breaker and a half row would be built out to accommodate the interconnection of the 100 MW solar farm for J1426. The network upgrades at the substation will include the installation of a new 115kV Breaker, Line arrestors, line CCVTs, Primary/Secondary Relay Panels, Metering, new metering CTs, and disconnects in the breaker-and-a-half row. |  | MN |  |  | Proposed | 2386979 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | South | Entergy-MS | 23820 |  |  | 27514 | 45065 | Dist | 2024-06-01 | Gloster |  |  | 115 | 13.8 |  | A new 13.8kV feeder breaker will be added at the Entergy Mississippi LLC owned Gloster substation in order to serve Cooperative Energy's distribution member's new customer. |  | MS |  |  | Planned | 193520 |  |  |  | All cost will be funded by member distribution cooperative. |  | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | South | Entergy-MS | 23820 |  |  | 27738 | 45065 | Dist | 2024-06-01 | Gloster |  |  | 115 | 13.8 |  | A new 13.8kV feeder breaker will be added at the Entergy Mississippi LLC owned Gloster substation in order to serve Cooperative Energy's distribution member's new customer. |  | MS |  |  | Planned | 290280 |  |  |  | Entergy Cost |  | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | West | GRE | 23763 |  | 209529 | 27548 | 45156 | Dist | 2028-09-26 | Laketown | Laketown Tap | 1 | 115 |  |  | Install 3-way MOD 2000 A 115 kV switch on GRE’s MV-VTT and construct about 3 mile 115 kV transmission line from the three way switch to the high side of MVEC’s Laketown distribution substation. |  | MN |  | 3 | Proposed | 6308542 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23801 |  | 206783 | 27561 | 45068 | Dist | 2023-09-29 | Cotton | Cotton Tap | 1 | 115 |  |  | LCP is rebuilding the existing Cotton Distribution site to the north, the 115 kV (TT Line) will need to adjust to terminate on LCP’s new high side structure. The EEE from Goodland distribution substation will be placed at the new Cotton substation. |  | MN |  |  | Proposed | 468450.72 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23819 |  | 209373 | 27534 | 45068 | Dist | 2024-11-22 | Eidswold |  |  | 115 |  |  | New 115/12.47 kV substation for Dakota Electric Association (DEA) in the Elko New Market area. |  | MN |  |  | Proposed | 207813.44 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | MRES | 24232 |  |  | 27765 | 44893 | Dist | 2025-12-31 | ALEXNOKO | ALEXAND7 |  | 115 |  |  | Alexandria Light & and Power (ALP) will build a new distribution substation on the southeast part of town. The substation will tap and existing 115 kV line with an in and out substation. The substation will have a 115 kV to distribution transformer. |  | MN |  |  | Proposed | 1358000 | Budgetary |  |  |  |  | Missouri River Energy Services (MRET) | N | N | N
A in MTEP23 | C | South | SMEPA | 23941 |  |  | 27677 | 45175 | Dist | 2024-06-01 | Silver Creek |  |  | 115 |  |  | In order to serve the Silver Creek delivery point economically and reliably, service will be established by tapping the Cooperative Energy owned Line 571 115kV line. A 115kV GOAB will be installed at the tap point and a new 115kV tap line will be constructed to the delivery point. |  | MS |  |  | Proposed | 1725000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | West | XEL | 24315 |  |  | 27778 | 44910 | Dist | 2025-06-16 | Elm Creek | South Dayton | 1 | 115 | 34.5 |  | Install new 115/34.5kV substation in Dayton area to meet area load growth. |  | MN |  |  | Planned | 12400000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | South | Entergy-AR | 24697 |  |  | 28067 | 45009 | INT | 2024-11-27 | Aurelle 115kV |  |  | 115 |  |  | New point of interconnection for J1612 100 MW solar project. |  | AR |  |  | Planned | 13031000 | GIA |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP23 | C | South | Entergy-LA | 24985 |  | 23-ELN-001 | 28183 | 45089 | INT | 2026-04-01 | Batrop Tap |  |  | 115 |  |  | GIA 1827 |  | LA |  |  | Proposed | 18500000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 25143 |  | 23-ELN-002 | 28214 | 45120 | INT | 2024-10-25 | Rilla |  |  | 115 |  |  | Facilities required for the interconnection of J1602 at Rilla 115 kV. The J1602 battery will be interconnected behind the main step up transformer for J1239 (Rilla 115 kV POI) |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | West | ATC | 24475 |  |  | 27902 | 45182 | SUB | 2025-12-31 | Tommy's Turnpike SS |  |  | 115 |  |  | Construct a new 115 kV loop through bus and disconnect switches on White Ave – Okray 115 kV line (B-106) to interconnect a distribution transformer |  | WI |  |  | Planned | 7700000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24783 |  | PR09241 | 28112 | 45182 | SUB | 2024-12-31 | Hodag |  |  | 115 |  |  | Add additional transformer, expand and reconfigure substation to a loop through straight bus configuration |  | WI |  |  | Planned | 2700000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | B | South | Entergy-AR | 12055 |  | 17-EAI-008 | 22136 | 45167 | SUB | 2026-06-01 | Gum Springs |  |  | 115 |  |  | Create a new substation by tapping the Arkadelphia North – Richwood 115kV and the Arkadelphia West – Dalark 115kV line sections. |  | AR |  |  | Planned | 14950800 | Planning |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP23 | C | South | Entergy-MS | 23348 |  | 22-EML-005 | 27037 | 45028 | SUB | 2024-12-01 | 337104 |  |  | 115 |  |  | Entergy will construct a new (4) breaker ring bus substation with (1) – 40 MVA, LTC 115/13.8 kV transformer. The new substation will have (1) main and (3) feeder breakers. The new substation will cut into the current Grenada – Tillatoba 115 kV line. |  | MS |  |  | Proposed | 32610000 | [5 empty] | Entergy Mississippi | N | N | N
A in MTEP23 | C | West | GRE | 23921 |  | 207418 | 27640 | 45156 | SUB | 2027-05-21 | Pilot Knob |  |  | 115 |  |  | Rebuild the Pilot Knob Substation to a breaker and a half configuration due to age and condition of the current equipment. Upgrade the DA-PD line from Deerwood to Pilot Knob substation to increase the capacity. Upgrade to be built to 115kV standards but operated at 69kV. Retire the underground portion of the DA-PLX at Pilot Knob and replace with overhead Retire the DA-RE line from Pilot Knob road to Black Hawk Road Retire the DA-PKX from Pilot Knob to Cliff Road Retire SS-2820 and replace with a turning structure. Retire SS-2819 |  | MN |  |  | Proposed | 18553424 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | MP | 23707 |  | Maturi Substation Expansion | 27487 | 45183 | SUB | 2025-12-31 | Maturi |  |  | 115 |  |  | Rebuild and expand existing Maturi Substation. Project will add three breaker to allow for the transmission line to be looped in and out of the substation. |  | MN |  |  | Planned | 3580000 | Engineering |  | 2023 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP23 | C | West | MP | 23708 |  | Mahtowa Substation Expansion | 27488 | 45183 | SUB | 2027-12-31 | Mahtowa |  |  | 115 |  |  | Add three 115 kV Breakers to reconfigure the Mahtowa Substation into a 3 position ring bus. |  | MN |  |  | Planned | 2500000 | Planning |  | 2023 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP23 | C | West | OTP | 23806 |  |  | 27570 | 45058 | SUB | 2024-12-31 | Brookings County (603192) |  |  | 115 |  |  | Add a new position at Brookings County (Xcel) 115 kV to except a new 115 kV line from the Lake Preston 115 kV substation. |  | SD |  |  | M1_Final SPM or OOC | 500000 | Planning |  | 2023 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23806 |  |  | 27554 | 45058 | SUB | 2024-12-31 | Lake Preston 115/34.5 kV (new) |  |  | 115 | 34.5 |  | New Lake Preston 115/34.5 kV substation. A 115 kV ring bus will be built to accommodate two 115 kV transmission line terminations, two 115/34.5 kV transformers, and the addition of 115 kV capacitor banks. |  | SD |  |  | M1_Final SPM or OOC | 9500000 | Engineering |  | 2023 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23806 |  |  | 27553 | 45058 | SUB | 2024-12-31 | Hetland 115 kV (620209) |  |  | 115 |  |  | Expand the existing Hetland 115 kV substation to add a new termination for a new 115 kV line that will extend from Hetland 115 kV to a new Lake Preston 115 kV substation. |  | SD |  |  | M1_Final SPM or OOC | 1100000 | Engineering Preliminary |  | 2023 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23936 |  |  | 27657 | 45058 | SUB | 2024-12-31 | Big Stone (620214) |  |  | 115 |  |  | Expand the 115 kV bus to accommodate a new 115 kV line position. |  | SD |  |  | M1_Final SPM or OOC | 2300000 | Engineering Preliminary |  | 2023 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 23936 |  |  | 27659 | 45058 | SUB | 2024-12-31 | Milbank 115/12.5 kV (new) |  |  | 115 |  |  | Construct a new Milbank 115/12.5 kV substation |  | SD |  |  | M1_Final SPM or OOC | 6300000 | Engineering Preliminary |  | 2023 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | XEL | 23509 |  |  | 27267 | 44791 | SUB | 2024-06-01 | Junction Mill |  |  | 115 | 69 |  | Build new Junction Mill substation near 3-terminal 115kV connection with Glenmont, River Falls and Crystal Cave lines. In addition, this substation will install a new 115/69kv transformer and change the operating voltage of the River Falls tap to 69kV. The transformation at the River Falls substation will be removed as well any 115kV equipment. |  | WI |  |  | Planned | 12000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | OTP | 25256 |  |  | 28398 | 45169 | SUB | 2024-06-01 | Jamestown 345 kV |  |  | 115 | 41.6 |  | Expansion of the 115 kV bus at the Jamestown 345 kV substation; addition of a new 115/41.6 kV transformer; addition of a 41.6 kV bus with breakers and a tie to the existing 41.6 kV system. |  | ND |  |  | M1_Final SPM or OOC | 3250000 | Engineering Preliminary |  | 2023 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | South | Entergy-MS | 23786 |  |  | 27526 | 44946 | SwSta | 2026-06-01 | Rawhide |  |  | 115 |  |  | Tap the Entergy MS owned Flowers - Tinsley 115kV line and construct a new Cooperative Energy owned 115kV breaker switching station near Rawhide Road in Warren, MS. |  | MS |  |  | Proposed | 2860000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | South | Entergy-MS | 23786 |  |  | 27524 | 44946 | SwSta | 2026-06-01 | Ft Redwood |  |  | 115 |  |  | Construct a new 115kV line from the Entergy Mississippi LLC owned Flowers 115kV station to a new Cooperative Energy owned 115kV switching station near the FT Redwood substation. |  | MS |  |  | Proposed | 2860000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | West | OTP | 23936 |  |  | 27660 | 45058 | SwSta | 2026-12-31 | New 115 kV Switching Station |  |  | 115 |  |  | New 115 kV switching station along the Big Stone - Marietta 115 kV line |  | SD |  |  | M1_Final SPM or OOC | 5800000 | Engineering Preliminary |  | 2023 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | B | East | ITCT | 22847 |  | ITC_22_001 | 26845 | 45027 | SUB | 2027-03-31 | New 120kV Substation |  |  | 120 |  |  | Construct Kings Point 120kV station as a straight bus station with one 40kA section breaker and two 40kA line breakers |  | MI |  |  | Proposed | 4200000 | Engineering |  |  |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 23947 |  |  | 27673 | 44924 | SUB | 2026-12-31 | ITCT Facilitates |  |  | 120 |  |  | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2 Million that have an in service date within the year 2026 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2 Million a separate project will be submitted for approval. |  | MI |  |  | Proposed | 2500000 | Budgetary |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24280 |  |  | 27804 | 44944 | SUB | 2025-02-28 | Greenwood | Substation |  | 120 | 120 |  | Install Row P at Greenwood 120kV. Install breakers PT and PM. Install disconnect switches PV, PR, PO, and PD. |  | MI |  |  | M3_Long Lead Materials | 2881189 | GIA |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24593 |  |  | 28048 | 45077 | SUB | 2024-04-30 | Sunbird |  |  | 120 |  |  | Install a 120 kV Section Breaker, 3-120 kV line breakers, and create Bus 103 at Sunbird substation. |  | MI |  |  | Planned | 7650000 | Engineering |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24593 |  |  | 28053 | 44970 | SUB | 2025-05-31 | Pontiac |  |  | 120 |  |  | Install 1-120 kV line breaker, replace existing 120 kV station equipment, and bypass the 120 kV reactor at the Pontiac 120 kV substation. |  | MI |  |  | Planned | 961000 | Engineering |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP23 | B | East | ITCT | 24072 |  | ITCT_22_043 | 27731 | 44935 | SUBmisc | 2026-12-31 | Resource |  |  | 120 |  |  | Remove transmission equipment at Resource substation. |  | MI |  |  | Proposed | 460000 | Engineering |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24441 |  |  | 27930 | 44945 | SUBmisc | 2025-02-28 | Greenwood |  |  | 120 |  |  | Install position PQ to interconnect J1331 generator. |  | MI |  |  | M3_Long Lead Materials | 0 | GIA |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24593 |  |  | 28052 | 44970 | SUBmisc | 2024-04-30 | Bloomfield |  |  | 120 |  |  | Upgrade relaying at Bloomfield to accommodate the changes at Sunbird substation. |  | MI |  |  | Planned | 524000 | Engineering |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP23 | B | Central | DEI | 23406 |  | M220242 | 27033 | 44819 | BUS | 2027-06-01 | Bedford 345 KV | bus upgrade |  | 138 |  | 511 | Bedford 345 KV - Upgrade 138KV Bus 9 from (1)954acsr@120C (overhead line rating) to (2)954ACSR@120C |  | IN |  |  | Proposed | 532500 | Planning Preliminary |  | 2022 |  | 511 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23862 |  | M220320 | 27619 | 45168 | BUS | 2032-04-01 | Bedford 345 KV | bus upgrade |  | 138 |  | 747 | Bedford 345 KV Sub 138-138 bus tie path - Upgrade 138kV bus (increase to 2-1590AL), CTs (reconnect at 2000A:5A ratio), and (2) switches (replace with 3000A) |  | IN |  |  | Proposed | 667000 | Engineering w/AFUDC |  | 2023 |  | 747 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23937 |  | 23-ELB-007 | 27856 | 45015 | BUS | 2023-03-10 | Willow Glen |  |  | 138 |  |  | Construct rigid bus to tie in the Willow Glen 138 kV southwest bus and southeast bus together. |  | LA |  |  | M5_In Service | 2900000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | Central | IPL | 23825 |  |  | 27520 | 44832 | BUS | 2024-12-01 | Rockville |  |  | 138 |  |  | Conversion to Ring Bus |  | IN |  |  | Proposed | 8500000 | Planning |  | 2022 |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP23 | C | Central | NIPS | 23472 |  |  | 27245 | 45180 | BUS | 2026-12-31 | Leesburg |  |  | 138 |  |  | Add a breaker and move terminal to convert ring bus to breaker-half configuration. |  | IN |  |  | Proposed | 2392215 | Engineering Preliminary |  | 2022 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP23 | C | Central | DEI | 23861 |  |  | 27618 | 44819 | CB | 2026-12-31 | Columbus 345 | CBs |  | 138 |  |  | Columbus 345 Sub Breaker Upgrades: Replace (3) 138kV CBs on Xfmr Banks 1, 2, and 3 with higher fault interrupting capacity |  | IN |  |  | Proposed | 1500000 | Planning Preliminary |  | 2022 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | South | Entergy-TX | 24152 |  | 22-ETI-017 | 27757 | 44882 | CB | 2023-06-30 | Moscow |  |  | 138 |  |  | Add two 138 kV Circuit breakers to the Moscow substation |  | TX |  |  | Proposed | 10470000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | Central | IPL | 23568 |  |  | 27319 | 44804 | CB | 2025-12-31 | Southwest |  |  | 138 |  |  | Replacement of one (1) 138 kV breaker #6 at Southwest |  | IN |  |  | Proposed | 900000 | Scoping |  |  |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP23 | C | Central | DEI | 3382 |  | AMIN0341 | 6255 | 44822 | Dist | 2026-07-14 | Vincennes Vigo St. | convert distribution sub | 1 | 138 | 12 | 301 | Build new radial 138kV line and add breaker at Vincennes 138kV sub to convert Vigo St. sub from 34kV to 138kV |  | IN |  | 2.3 | Proposed | 10932000 | Engineering w/AFUDC |  | 2022 |  | 301 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | South | Entergy-TX | 24460 |  |  | 27939 | 44945 | Dist | 2023-05-31 | Coldspring |  |  | 138 |  |  | Phase I - Reconductor a 4.25-mile distribution circuit from the Coldspring Substation to the customer facility. |  | TX |  |  | Planned | 1275000 | Construction |  |  |  |  | East Texas Electric Cooperative Inc. | N | N | N
A in MTEP23 | C | West | ATC | 24445 |  | PR09069 | 27953 | 45182 | INT | 2024-08-01 | Ebenezer SS |  |  | 138 |  |  | J1374 Ebenezer SS Interconnection Facilities |  | WI |  |  | Planned | 375518 | GIA |  |  |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24446 |  | PR09162 | 27966 | 45182 | INT | 2025-06-12 | Summer Meadows Swt Station |  |  | 138 |  |  | Interconnection Facilities |  | MI |  |  | Planned | 378915 | GIA |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24802 |  | PR09208 | 28111 | 45182 | INT | 2023-12-27 | Sunrise |  |  | 138 |  |  | J1460 Sunrise SS Interconnection Facilities |  | WI |  |  | Planned | 400108 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | Central | AmerenIL | 24878 |  | TP1736 | 28120 | 45056 | INT | 2025-12-01 | Ashley-IL |  |  | 138 |  |  | This project will tap into the existing Ashley 138 kV 3-position ring bus to serve as the Point of Interconnection for the Interconnection Customer's Generating Facility, Ashley Solar, LLC |  | IL |  |  | Planned | 1000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 24900 |  | TP1740 | 28128 | 45061 | INT | 2025-12-01 | Ipava |  |  | 138 |  |  | Interconnection Facilities shall consist of one 138 kV terminal in the Ipava substation to connect the J1383 leadline. |  | IL |  |  | Planned | 1000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 24901 |  | TP1741 | 28129 | 45061 | INT | 2025-12-01 | Morganfield |  |  | 138 |  |  | Add 138 kV terminal in the Morganfield substation to connect the J1302 and J1096 leadline to the Morganfield substation |  | IL |  |  | Planned | 1000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | South | Entergy-LA | 24254 |  | 23-ELF-005 | 27769 | 44894 | INT | 2025-06-01 | New Sub |  |  | 138 |  |  | This project is to support the interconnection of J1465 on 138 kV line between existing Livonia and Colonial Springs stations. |  | LA |  |  | Proposed | 14400000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 24862 |  | 23-ELF-006 | 28125 | 45057 | INT | 2024-12-15 | Champagne | Plaisance |  | 138 |  |  | Solar Interconnection station |  | LA |  |  | Proposed | 4329000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 24986 |  | 23-ELF-007 | 28184 | 45089 | INT | 2025-12-04 | Richard | Bayou Cove |  | 138 |  |  | GIA J1795 |  | LA |  |  | Proposed | 17700000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 25083 |  | 23-ELF-008 | 28208 | 45119 | INT | 2025-05-06 | Richard | Scott |  | 138 |  |  | This construction of a new station on the Richard to Scott 138 kV line to accommodate the interconnection of a solar facility (J1794) |  | LA |  |  | Proposed | 12840000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 25140 |  | 23-ELC-004 | 28209 | 45119 | INT | 2025-12-04 | Lake Charles Bulk | Henning |  | 138 |  |  | Facilities required to interconnect J1669 Lake Charles Bulk to Henning 138 kV |  | LA |  |  | Proposed | 16910000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-TX | 24298 |  | 23-ETI-013 | 27874 | 44938 | INT | 2025-05-01 | Rich | Livingston |  | 138 |  |  | Project to support interconnection of J1442 on the Livingston to Rich 138 kV line. |  | TX |  |  | Proposed | 15590000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-TX | 25102 |  | 23-ETI-019 | 28215 | 45120 | INT | 2025-02-01 | Grimes |  |  | 138 |  |  | Facilities to accommodate new storage facility |  | TX |  |  | Proposed | 7212000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | Central | NIPS | 24032 |  |  | 27710 | 44830 | INT | 2024-05-01 | Springboro | Monticello |  | 138 |  |  | Tap in / tap out facilities from Monticello – Springboro 138kV line to new substation |  | IN |  |  | Planned | 2096068 | Facility Study |  | 2022 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP23 | B | West | ATC | 19963 |  | PR09137 | 25648 | 45181 | SUB | 2026-12-31 | Kirkwood SS |  |  | 138 |  |  | Asset Renewal |  | WI |  |  | Planned | 14100000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23875 |  | PR09194 | 27959 | 45182 | SUB | 2026-12-01 | Blackhawk(MGE) |  |  | 138 |  |  | Asset Renewal |  | WI |  |  | Planned | 1093179 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23875 |  | PR09194 | 27956 | 45182 | SUB | 2026-12-01 | Sycamore SS |  |  | 138 | 69 |  | Asset Renewal |  | WI |  |  | Planned | 4372716 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23895 |  | PR09085 | 27578 | 45182 | SUB | 2026-12-01 | McCue SS |  |  | 138 | 69 |  | Control House and Relay Asset Renewal |  | WI |  |  | Planned | 9500000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23897 |  | PR09086 | 27579 | 45182 | SUB | 2026-12-01 | Ohmstead SS |  |  | 138 |  |  | Control House and Relay Asset Renewal |  | WI |  |  | Planned | 5700000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23901 |  | PR09135 | 27586 | 45182 | SUB | 2026-12-01 | Shoto SS |  |  | 138 | 69 |  | Replace T1 |  | WI |  |  | Planned | 6200000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23903 |  | PR09176 | 27589 | 45182 | SUB | 2026-12-01 | North Beaver Dam |  |  | 138 | 69 |  | Asset Renewal |  | WI |  |  | Planned | 16100000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23912 |  | PR09258 | 27609 | 45182 | SUB | 2027-12-31 | East Krok |  |  | 138 |  |  | Transformer Replacement |  | WI |  |  | Planned | 8700000 | Planning |  | 2027 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23915 |  |  | 27612 | 45182 | SUB | 2027-01-31 | Delta County |  |  | 138 | 69 |  | Delta County DIC Upgrades |  | MI |  |  | Planned | 21000000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24296 |  |  | 27823 | 45182 | SUB | 2028-07-31 | Valders SS |  |  | 138 | 69 |  | Construct New Substation |  | WI |  |  | Planned | 24200000 | Planning |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24373 |  | PR09181 | 27830 | 45182 | SUB | 2025-08-01 | Manogue Rd SS |  |  | 138 |  |  | New Substation |  | WI |  |  | Planned | 7100000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24446 |  | PR09162 | 27962 | 45182 | SUB | 2025-06-12 | Summer Meadow Switching Station |  |  | 138 |  |  | J1251 Summer Meadow Swt Station Network Upgrade |  | MI |  |  | Planned | 6349774 | GIA |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24784 |  | PR09256 | 28113 | 45182 | SUB | 2025-06-01 | Ellisville |  | M-39 | 138 |  |  | 138 kV loop through substation with line breakers on Highway V – East Krok 138 kV (M-39) |  | WI |  |  | Planned | 10200000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24801 |  | PR09207 | 28105 | 45182 | SUB | 2027-11-12 | Progress |  |  | 138 |  |  | Progress SS Network Upgrades |  | WI |  |  | Planned | 749813 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24801 |  | PR09207 | 28104 | 45182 | SUB | 2027-11-12 | North Fond Du Lac |  |  | 138 |  |  | North Fond Du Lac SS Network Upgrades |  | WI |  |  | Planned | 576824 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24801 |  | PR09207 | 28103 | 45182 | SUB | 2027-11-12 | Ellinwood |  |  | 138 |  |  | Ellinwood SS Network Upgrades |  | WI |  |  | Planned | 1115722 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24801 |  | PR09207 | 28102 | 45182 | SUB | 2027-11-12 | Aviation |  |  | 138 |  |  | Aviation SS Network Upgrades |  | WI |  |  | Planned | 1876952 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24802 |  | PR09208 | 28109 | 45182 | SUB | 2025-12-27 | Sunrise |  |  | 138 |  |  | J1460 Sunrise SS Network Upgrades |  | WI |  |  | Planned | 3274790 | GIA |  | 2023 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | B | Central | AmerenIL | 22728 |  | TP1491 | 26826 | 45159 | SUB | 2025-06-01 | Decatur North 27th Street |  |  | 138 |  |  | Rebuild this station to a 7 position BAAH, minimum 8 position ultimate BAAH |  | IL |  |  | Planned | 19800000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22789 |  | TP1530 | 26901 | 45159 | SUB | 2026-06-01 | Canton |  |  | 138 |  |  | New Ring bus |  | IL |  |  | Planned | 3250000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22868 |  | TP1522 | 26889 | 45092 | SUB | 2024-12-01 | Quincy south |  |  | 138 |  |  | Replace 1753 and 1823 BKRs, Replace 1751 line switch. |  | IL |  |  | Planned | 3000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22946 |  | TP1534 | 26944 | 44756 | SUB | 2025-12-01 | Pioneer |  |  | 138 |  |  | Rebuild Pioneer 138 kV substation as a 5-positon ring bus |  | IL |  |  | Proposed | 8500000 | Budgetary |  |  |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22946 |  | TP1534 | 26905 | 45158 | SUB | 2025-12-01 | Alta |  |  | 138 |  |  | Rebuild Alta 138 kV substation as a 4-position initial, 6-position ultimate 138 kV ring bus |  | IL |  |  | Proposed | 9200000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22947 |  | TP1538 | 26909 | 45027 | SUB | 2025-12-01 | Lakeshire |  |  | 138 |  |  | Add line breaker to Pos. J (Baum-Wat-1) |  | IL |  |  | Proposed | 3400000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23026 |  | TP1570 | 26941 | 45158 | SUB | 2025-12-01 | Reifen |  |  | 138 |  |  | Construct a new 138 kV substation as an ultimate six-position ring bus requiring one 3000 A 138 kV breaker initially adjacent to the Continental Tire facility. Add breaker position to Mt Vernon 42 2nd street substation |  | IL |  |  | Planned | 9250000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23505 |  | TP1345 | 27255 | 45158 | SUB | 2025-06-01 | Bosco |  |  | 138 |  |  | Relocate station due to the contamination, build a ring bus at a new location. |  | IL |  |  | Planned | 14400000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23632 |  | TP1027 | 27373 | 44987 | SUB | 2024-12-01 | Beehive |  |  | 138 |  |  | Add Breakers for new 138 kV line connection to Dupo Ferry |  | IL |  |  | Planned | 1200000 | Construction |  |  |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23632 |  | TP1027 | 27372 | 44987 | SUB | 2024-12-01 | Dupo Ferry |  |  | 138 |  |  | Add breakers to new line connection to Beehive |  | IL |  |  | Planned | 1100000 | Construction |  |  |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23637 |  | TP1717 | 27403 | 44943 | SUB | 2024-06-01 | Hennepin |  |  | 138 |  |  | Install one 138 kV terminal in the Putnam substation. The terminal will consist of all necessary terminal equipment to connect the J1200 leadline to the Putnam substation 138 kV bus. Install upgrades at Putnam substation. Raise existing PUTN-HKOK-1556, PUTN-HENN-1771, PUTN-HENN-1765, PUTN-ESK-1757, and PUTN-BURE-1552 transmission lines |  | IL |  |  | Planned | 0 | [5 empty] | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23676 |  | TP1715 | 27398 | 44943 | SUB | 2024-06-01 | Coffeen |  |  | 138 |  |  | Install one 138 kV terminal in the Coffeen North substation. The terminal will consist of all necessary terminal equipment to connect the J1201 leadline to the Coffeen North substation 138 kV bus |  | IL |  |  | Planned | 1100000 | GIA |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23846 |  | TP1718 | 27631 | 44819 | SUB | 2026-12-31 | Grand Tower |  |  | 138 |  |  | Add line Terminal at Grand Tower for new Grand Tower to Wittenberg line |  | IL |  |  | Proposed | 0 | [5 empty] | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 24780 |  | TP1733 | 28094 | 45056 | SUB | 2025-12-01 | Fayetteville Bee Hollow |  |  | 138 |  |  | The Fayetteville Bee Hollow Substation will be rebuilt to a 4 position (6 position ultimate) 138kV ring bus for J1311 |  | IL |  |  | Planned | 8000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22787 |  | TP1526 | 26893 | 45176 | SUB | 2026-12-01 | Warson |  |  | 138 |  |  | Line BKRs on 4 line terminals, High Side interrupting devices on XFMRs 1,2,3,4 Add bus tie 2-3 BKR |  | MO |  |  | Planned | 8000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22846 |  | TP1498 | 26872 | 44948 | SUB | 2026-12-01 | Sioux |  |  | 138 |  |  | Add interrupting device on 14H (Starting XFMR 1) Upgrade 15H posn to higher ampacity to increase available capacity of the 700MVA Auto XFMR |  | MO |  |  | Planned | 10500000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22890 |  | tp1524 | 26891 | 45158 | SUB | 2025-12-01 | Selma |  |  | 138 |  |  | Add line breakers to Selma-Rivermines-2 & DPFE-Selma-1 Add High Side Interrupting devices to XFMR 1 & 2 |  | MO |  |  | Planned | 3000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22926 |  | TP1529 | 26899 | 45158 | SUB | 2027-12-01 | Dardenne |  |  | 138 |  |  | Add Breakers to Dardenne |  | MO |  |  | Proposed | 5000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 23152 |  | TP1593 | 26990 | 45012 | SUB | 2024-12-01 | Copley |  |  | 138 |  |  | Build a new four position 138 kV Ring bus needed to connect two 13/12 kV transformers |  | MO |  |  | Planned | 20000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | South | CLECO | 24416 |  |  | 27875 | 44938 | SUB | 2027-07-15 | Rosepine |  |  | 138 |  |  | Tap the existing Leesville to Cooper 138 kV line 11.4 miles from Leesville with a new Rosepine Substation |  | LA |  |  | Proposed | 20585000 | Budgetary |  |  |  |  | Cleco Power LLC | N | N | N
A in MTEP23 | C | South | CLECO | 24416 |  |  | 27877 | 44938 | SUB | 2027-07-15 | Deridder |  |  | 138 |  |  | Add a new 138 kV Terminal at Deridder |  | LA |  |  | Proposed | 3000000 | Budgetary |  |  |  |  | Cleco Power LLC | N | N | N
A in MTEP23 | C | Central | DEI | 23886 |  | M220302 | 27727 | 44936 | SUB | 2023-12-31 | Wheatland Solar Sw Sta | POI misc. TO work |  | 138 |  |  | DEI POI work scope - 13856 line work and Relay work req'd at Edwardsport, Washington Muni, and Peabody Coal |  | IN |  |  | Planned | 6051683 | Engineering Preliminary |  | 2022 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23892 |  | TIN1581 | 27568 | 45168 | SUB | 2026-06-30 | Shelbyville Northeast |  |  | 138 | 69 |  | Shelbyville Northeast: build 138kV ring bus; replace CIR 6946, 6976, 69183, 13803, 13865 relays, replace OCBs 6946, 6976, 69183, 69138-1, 13803, replace Bank 1 ground switch with circuit switcher, and station battery. |  | IN |  |  | Proposed | 10800000 | Engineering w/AFUDC |  | 2023 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23966 |  | M220271 | 27702 | 44823 | SUB | 2023-06-01 | Greensburg 138 | ring bus |  | 138 |  |  | Greensburg 138kV expand sub and configure to (4) breaker ring bus |  | IN |  |  | Proposed | 5884000 | Planning Preliminary |  | 2022 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | South | Entergy-TX | 24134 |  | 22-ETI-018 | 27758 | 44876 | SUB | 2024-10-30 | Mustang |  |  | 138 |  |  | Cut Mustang 138 kV substation into the existing Orange to Bunch Gully 138 kV line. |  | TX |  |  | Proposed | 28000000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-TX | 24920 |  | 23-ETI-015 | 28142 | 45161 | SUB | 2024-10-31 | Cole Road |  |  | 138 |  |  | Cole Road Substation will be cut into the Jacinto to Splendora 138 kV line |  | TX |  |  | Proposed | 29600000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | Central | IPL | 23766 |  |  | 27638 | 44819 | SUB | 2023-12-31 | Mill Street | Edison |  | 138 | 13.2 |  | New 138 kV, two 40 MVA transformer, three-breaker straight bus substation to serve customer load |  | IN |  |  | Under Construction | 15000000 | Engineering |  | 2022 |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP23 | C | Central | IPL | 23831 |  |  | 27635 | 44819 | SUB | 2024-11-01 | Stout North | Gardner Lane |  | 138 | 13.2 |  | New 138 kV, two 40 MVA transformer, three-breaker straight bus substation to serve customer load |  | IN |  |  | Planned | 15000000 | Engineering |  | 2022 |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP23 | C | Central | IPL | 23832 |  |  | 27634 | 44819 | SUB | 2023-11-01 | Thompson |  |  | 138 | 13.2 |  | One new 138/13.2 kV 40 MVA distribution transformer with one new 138 kV breaker |  | IN |  |  | Under Construction | 16000000 | Engineering |  | 2022 |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP23 | C | Central | IPL | 23834 |  |  | 27575 | 44818 | SUB | 2024-12-31 | Edison | Brookwood | 36 | 138 | 13.2 |  | New 138 kV, two 40 MVA transformer, three-breaker straight bus substation to serve customer load |  | IN |  |  | Under Construction | 15000000 | Planning |  | 2022 |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP23 | C | Central | IPL | 23893 |  |  | 27625 | 44819 | SUB | 2024-12-31 | Sunnyside | German Church |  | 138 | 13.2 |  | New 138 kV, two 40 MVA transformers, 8 breaker, breaker and a half substation to serve AES-IPL customer load and provide transmission service to TOs whom have requested as such |  | IN |  |  | Planned | 15000000 | Planning |  | 2022 |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP23 | C | Central | IPL | 24273 |  |  | 27773 | 45167 | SUB | 2026-12-31 | Thompson | United MOC | 77 | 138 | 12.47 |  | New 138kV, two 20 MVA transformer, three-breaker substation |  | IN | 0 | 0 | Planned | 10700000 | Planning |  | 2022 |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP23 | C | Central | IPL | 24293 |  |  | 27774 | 44904 | SUB | 2025-12-31 | Winding Ridge |  |  | 138 | 12.47 |  | New 138 kV, two 40 MVA transformers, 4 breaker, ring bus substation to serve WVPA load |  | IN |  |  | Planned | 10000000 | Planning |  | 2022 |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP23 | C | East | METC | 22147 |  |  | 26710 | 45001 | SUB | 2024-10-01 | J1310 |  |  | 138 |  |  | Construct a new 138kV station as a breaker and half station with three 40kA breakers in a ring bus configuration. |  | MI |  |  | M2a_Pre-Project Approval | 5785696 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 22165 |  |  | 26714 | 44935 | SUB | 2023-08-01 | J1430 Interconnection |  |  | 138 |  |  | Build J1430 as a breaker and half station with three 40kA breakers in a ring bus configuration. |  | MI |  |  | M2a_Pre-Project Approval | 5998873 | Engineering |  | 2021 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23709 |  | METC_22_078 | 27491 | 44897 | SUB | 2027-06-01 | Tyler |  |  | 138 |  |  | Extend White and Blue Buses and install (5) 138 kV, 3000 A continuous, 50 kA min. interruptible breakers at Tyler 138kV |  | MI |  |  | Proposed | 4371321 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23785 |  |  | 27515 | 45001 | SUB | 2025-03-03 | New J1550 Interconnection Station |  |  | 138 |  |  | Construct the J1550 POI Interconnection station as a 138kV breaker and half station with three 40A breakers in a ring bus configuration. |  | MI |  |  | Planned | 9430612 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23865 |  | METC_22_071 | 27684 | 44841 | SUB | 2025-03-01 | Elephant |  | 1 | 138 |  |  | Construct new 138 kV, 3-row breaker and a half substation. |  | MI |  |  | Proposed | 18300000 | Engineering Preliminary |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23865 |  | METC_22_071 | 27721 | 44841 | SUB | 2025-03-01 | Chase |  | 1 | 138 |  |  | Sub work |  | MI | 7.8 |  | Proposed | 150000 | Engineering Preliminary |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23865 |  | METC_22_071 | 27721 | 44841 | SUB | 2025-03-01 | Mecosta |  | 1 | 138 |  |  | Sub work |  | MI | 7.8 |  | Proposed | 275000 | Engineering Preliminary |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23872 |  | METC_22_070 | 27550 | 44897 | SUB | 2026-12-31 | Kraft |  |  | 138 |  |  | Upgrade existing 500 circuit switcher, 2 line switches with new breakers at Kraft 138kV station |  | MI |  |  | Proposed | 5226528 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24276 |  |  | 27793 | 44943 | SUB | 2025-12-31 | Hawley | Substation |  | 138 | 138 |  | Construct a new 138kV station as a breaker and half station with three breakers in a ring bus configuration. |  | MI |  |  | Proposed | 6393380 | Facility Study |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24277 |  |  | 27796 | 44943 | SUB | 2025-12-31 | Peddler | Substation |  | 138 | 138 |  | Construct a new 138kV station as a breaker and half station with three breakers in a ring bus configuration. |  | MI |  |  | M3_Long Lead Materials | 6393380 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24279 |  |  | 27798 | 45001 | SUB | 2026-01-28 | Hathon | Substation |  | 138 | 138 |  | Construct a new 138kV station as a breaker and half station with five 40kA breakers in a ring bus configuration. |  | MI |  |  | Proposed | 8318370 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24279 |  |  | 27802 | 45001 | SUB | 2026-01-28 | Goss | Substation |  | 138 | 138 |  | Upgrade Position WM13 relays at the Goss substation. |  | MI |  |  | Proposed | 199390 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24279 |  |  | 27800 | 45001 | SUB | 2026-01-28 | Cornell | Substation |  | 138 | 138 |  | Upgrade Positions 177 relays at the Cornell Substation. |  | MI |  |  | Proposed | 256477 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24282 |  |  | 27822 | 45154 | SUB | 2025-03-31 | Vargo | Substation |  | 138 | 138 |  | Construct the new 138kV station as a breaker and half station with three breakers in a ring bus configuration. |  | MI |  |  | Proposed | 6648067 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24294 |  |  | 27780 | 44944 | SUB | 2025-03-31 | Quarry | Substation |  | 138 | 138 |  | Install a new 138 kV station with 5-138kV 40KAIC breakers and associated disconnects in a ring bus configuration. |  | MI |  |  | M3_Long Lead Materials | 7133994 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24294 |  |  | 27783 | 44944 | SUB | 2025-03-31 | Twining | Substation |  | 138 | 138 |  | Remove sparing from Twining breaker position 177. Upgrade position 177 line relays. Upgrade RTU, router, and switch. Extend T1 telecom service from Twining to J1210 Station. |  | MI |  |  | M3_Long Lead Materials | 354342 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24295 |  |  | 27789 | 44943 | SUB | 2025-11-30 | Bearcat | Substation |  | 138 | 138 |  | Construct the New Station as a breaker and half station with three 40kA breakers in a ring bus configuration |  | MI |  |  | Proposed | 6421627 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24295 |  |  | 27792 | 44943 | SUB | 2025-11-30 | Brook Industrial | Substation |  | 138 | 138 |  | Upgrade Brooks Industrial position WM14 Relaying |  | MI |  |  | Proposed | 37218 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24295 |  |  | 27791 | 44943 | SUB | 2025-11-30 | Marshall | Substation |  | 138 | 138 |  | Upgrade Marshall section 30 relaying. |  | MI |  |  | Proposed | 37218 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24317 |  |  | 27805 | 44944 | SUB | 2025-05-12 | J1375 New Station | Substation |  | 138 | 138 |  | Install a new 138 kV station with 3-138kV 40KAIC breakers and associated disconnects in a ring bus configuration. |  | MI |  |  | M3_Long Lead Materials | 6115758 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24317 |  |  | 27808 | 44944 | SUB | 2025-05-12 | White Lake | Substation |  | 138 | 138 |  | Upgrade Bus 1, install new Bus 2, install 138kV tie-breaker, install two 138kV line breakers, reconnect CE Trans 2 at Bus 2. |  | MI |  |  | M3_Long Lead Materials | 5622349 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24318 |  |  | 27810 | 44944 | SUB | 2024-05-31 | J1379 New Station | Substation |  | 138 | 138 |  | Install a new 138 kV station with 4-138kV 40KAIC breakers and associated disconnects in a ring bus configuration. |  | MI |  |  | M3_Long Lead Materials | 7382677 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24318 |  |  | 27813 | 44944 | SUB | 2024-05-31 | North Belding | Substation |  | 138 | 138 |  | Remove sparing from North Belding breaker positions 177. Upgrade position 177 line relays. Install Blue bus and 500 tie breaker. |  | MI |  |  | M3_Long Lead Materials | 2997076 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24318 |  |  | 27812 | 44944 | SUB | 2024-05-31 | Eureka | Substation |  | 138 | 138 |  | Remove sparing from Eureka breaker positions 288 and 277. Upgrade positions 288 and 277 line relays. Install 2 138kV line CCVTs for line positions 288 and 277. |  | MI |  |  | M3_Long Lead Materials | 1688183 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24319 |  |  | 27818 | 44944 | SUB | 2025-12-31 | Edgar | Substation |  | 138 | 138 |  | Extend the Delhi-Tompkins #2 138kV line to loop in the station. |  | MI |  |  | Proposed | 7446364 | Facility Study |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24419 |  |  | 27886 | 44939 | SUB | 2025-12-10 | Byers |  |  | 138 |  |  | Install a new 138 kV station with 3-138kV 40KAIC breakers and associated disconnects in a ring bus configuration. |  | MI |  |  | M3_Long Lead Materials | 6304819 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24438 |  |  | 27923 | 44946 | SUB | 2024-04-05 | Wagner |  |  | 138 |  |  | Install breaker 9B7 and associated disconnects switches at Wagner 138kV. |  | MI |  |  | M3_Long Lead Materials | 1053802 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24673 |  |  | 28056 | 44987 | SUB | 2024-05-31 | Charge |  |  | 138 |  |  | New 138 kV, 3-row, breaker and a half substation |  | MI |  |  | Planned | 14100000 | Engineering |  | 2023 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 25038 |  | METC_23_070 | 28187 | 45155 | SUB | 2025-03-31 | Orr Road |  |  | 138 |  |  | Install a new 3000 A, 63 kA breaker at Orr Road Pos. 6B7 and associated equipment and connect OPGW at Orr Road substation. |  | MI |  |  | Proposed | 1400000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 25038 |  | METC_23_070 | 28186 | 45092 | SUB | 2025-03-31 | Murphy |  |  | 138 |  |  | Install a new 3000 A, 63 kA breaker at Murphy Pos. 4B7 and associated equipment and connect OPGW at Murphy station. |  | MI |  |  | Proposed | 1400000 | Engineering |  |  |  |  | METC | N | N | N
A in MTEP23 | C | Central | NIPS | 24032 |  |  | 27711 | 44830 | SUB | 2024-05-01 | J1482 |  |  | 138 |  |  | New double breaker double bus 138kV station that will be placed adjacent to Transmission Owner’s Monticello – Springboro 138kV line |  | IN |  |  | Planned | 15796226 | Facility Study |  | 2022 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP23 | C | Central | WVPA | 23846 |  | TP1718 | 27627 | 44819 | SUB | 2025-12-31 | Seminary |  |  | 138 |  |  | Rebuild the 138kV Seminary bus to a ring, the 69 kV to a breaker and a half, and install a cap bank. |  | MO |  |  | Proposed | 25000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | WVPA | 23846 |  | TP1718 | 27628 | 44819 | SUB | 2026-12-31 | Wittenberg |  |  | 138 |  |  | Install new relaying and breakers for the new 138 kV line to Seminary. |  | MO |  |  | Proposed | 1000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | South | CLECO | 24415 |  |  | 27871 | 44938 | SUB | 2024-07-17 | Turps |  |  | 138 |  |  | Tap Longville to Nelson 13.1 miles from Longville and build a new Turps substation. |  | LA |  |  | Proposed | 10000000 | Budgetary |  |  |  |  | Cleco Power LLC | N | N | N
A in MTEP23 | C | South | CLECO | 24415 |  |  | 27873 | 44938 | SUB | 2024-07-15 | Ragley |  |  | 138 |  |  | Build a new 138 kV substation at the end of the Turps to Ragley 138 kV line. |  | LA |  |  | Proposed | 14200000 | Budgetary |  |  |  |  | Cleco Power LLC | N | N | N
A in MTEP23 | C | West | ATC | 24445 |  | PR09069 | 27954 | 45182 | SUBmisc | 2024-08-01 | Ebenezer SS |  |  | 138 |  |  | J1374 Ebenezer SS Network Upgrades |  | WI |  |  | Planned | 1201495 | GIA |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24446 |  | PR09162 | 27965 | 45182 | SUBmisc | 2025-06-12 | Perkins SS |  |  | 138 |  |  | Remote End Work |  | MI |  |  | Planned | 141280 | GIA |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24473 |  | PR09182 | 27900 | 45182 | SUBmisc | 2024-07-01 | Rock River SS |  |  | 138 |  |  | : Expanding Rock River 138kV Bus 3 to interconnect a distribution transformer |  | WI |  |  | Planned | 3000000 | Planning |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 25262 |  | PR08874 | 28374 | 45182 | SUBmisc | 2023-11-08 | Norwegian Creek |  |  | 138 |  |  | J1305 Norwegian Creek SS Network Upgrades |  | WI |  |  | Planned | 6707061 | GIA |  | 2020 | WO #604897 |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 25262 |  | PR08874 | 28378 | 45182 | SUBmisc | 2023-11-08 | Norwegian Creek |  |  | 138 |  |  | J1305 Norwegian Creek SS Interconnection Facilities |  | WI |  |  | Planned | 366366 | GIA |  | 2020 | WO #604901 |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22806 |  | TP1493 | 26935 | 45158 | SUBmisc | 2024-04-01 | Rush |  |  | 138 |  |  | Upgrade the Rush Island 345 kV bus to 3000A capability |  | MO |  |  | Proposed | 1500000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 23971 |  | TP5228 | 27736 | 44951 | SUBmisc | 2024-12-01 | Hannibal West |  |  | 138 |  |  | Upgrade Terminal Equipment at Hannibal West - Retap CT's and install new meter |  | MO |  |  | Planned | 450000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | East | METC | 23785 |  |  | 27517 | 45028 | SUBmisc | 2024-10-04 | Batavia |  |  | 138 |  |  | Upgrade Position WM37 relays |  | MI |  |  | Proposed | 245596 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 23885 |  |  | 27682 | 44924 | SUBmisc | 2026-12-31 | METC Faciltiies |  |  | 138 |  |  | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in service date within the year 2026 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million a separate project will be submitted for approval |  | MI |  |  | Proposed | 2500000 | Planning |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24277 |  |  | 27795 | 44943 | SUBmisc | 2025-12-31 | Gains | Thompson Road | 1 | 138 | 138 |  | Extend the Thompson Road - Gaines 138kV line to loop in the J1292 |  | MI |  |  | Proposed | 541200 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24300 |  |  | 27890 | 44946 | SUBmisc | 2025-12-10 | Byers |  |  | 138 |  |  | Install line entrance structures and install position WM14 at Byers to interconnect J1320 generator. |  | MI |  |  | M3_Long Lead Materials | 0 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24301 |  |  | 27894 | 45001 | SUBmisc | 2024-11-29 | Vargo |  |  | 138 |  |  | Install position WM13 for the J1472 generator to connect. |  | MI |  |  | M3_Long Lead Materials | 0 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24319 |  |  | 28061 | 44994 | SUBmisc | 2025-12-31 | Tompkins |  |  | 138 |  |  | Remove fiber connections from Nokias to Churchill MOABs |  | MI |  |  | Proposed | 58713 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24319 |  |  | 28060 | 44994 | SUBmisc | 2025-12-31 | Delhi |  |  | 138 |  |  | Remove fiber connections from Nokias to Churchill MOABs |  | MI |  |  | Proposed | 48580 | Engineering |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24377 |  |  | 27885 | 44946 | SUBmisc | 2024-12-23 | Coldwater |  |  | 138 |  |  | Replace line drops for Section 20 at Coldwater. |  | MI |  |  | M3_Long Lead Materials | 66394 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24396 |  |  | 27893 | 44946 | SUBmisc | 2025-03-31 | Quarry |  |  | 138 |  |  | Install position WM14 at Quarry to interconnect J1210 generator. |  | MI |  |  | M3_Long Lead Materials | 0 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24433 |  |  | 27895 | 45001 | SUBmisc | 2025-12-31 | Hawley |  |  | 138 |  |  | Install position WM12 at the new station for J1255 generator to connect. |  | MI |  |  | M3_Long Lead Materials | 0 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24436 |  |  | 27911 | 44946 | SUBmisc | 2025-05-12 | Lamos |  |  | 138 |  |  | Install position WM8 to interconnect J1375 generator. |  | MI |  |  | M3_Long Lead Materials | 0 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24437 |  |  | 27922 | 45071 | SUBmisc | 2025-12-31 | Edgar |  |  | 138 |  |  | Install position BM14 to connect the J1399 generator |  | MI |  |  | M3_Long Lead Materials | 0 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24439 |  |  | 27924 | 44944 | SUBmisc | 2024-04-05 | Wagner |  |  | 138 |  |  | Install entrance structure and disconnect. |  | MI |  |  | M3_Long Lead Materials | 0 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24453 |  |  | 27907 | 44943 | SUBmisc | 2025-12-31 | Peddler |  |  | 138 |  |  | Expand J1292 station by installing breakers 8B7 and 8W8. terminate the J1255-J1292 #1 line at position BM6. Terminate the J1255-J1292 #2 line at position BM8. |  | MI |  |  | M3_Long Lead Materials | 1758504 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24453 |  |  | 27906 | 44943 | SUBmisc | 2025-12-31 | Hawley |  |  | 138 |  |  | Expand J1255 station by installing breakers 8W2 and 10B7. terminate the J1255-J1292 #1 line at position WM8. Terminate the J1255-J1292 #2 line at position BM10. |  | MI |  |  | M3_Long Lead Materials | 1758504 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24456 |  |  | 27910 | 44946 | SUBmisc | 2025-11-30 | Bearcat |  |  | 138 |  |  | Install position WM14 as TOIF for the J1248 generator to connect. |  | MI |  |  | Proposed | 0 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24459 |  |  | 27929 | 44945 | SUBmisc | 2024-05-31 | Hornet |  |  | 138 |  |  | Install a 138 kV entrance structure and 177 disconnect switch at the J1379 PCO at J1379 Station position WM14. |  | MI |  |  | M3_Long Lead Materials | 0 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24493 |  |  | 27913 | 44946 | SUBmisc | 2026-01-31 | Hathon |  |  | 138 |  |  | Install position BM10 as TOIF for J1297 to connect. |  | MI |  |  | Proposed | 0 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22186 |  | TP1472 | 26740 | 45158 | SwSta | 2025-06-01 | South Ottawa |  |  | 138 |  |  | Create a 5 position 6 ultimate ring bus at the existing South Ottawa substation |  | IL |  |  | Planned | 9300000 |  |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22667 |  | TP1489 | 26823 | 44846 | SwSta | 2025-12-01 | Havana | Cincinnati |  | 138 |  |  | Construct a new 138 kV substation in ring bus configuration on the existing Ameren Havana-Cincinnati-1352 138 kV line. A position will feed PPI Forest City 138/69 kV |  | IL |  |  | Planned | 8500000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23026 |  | TP1570 | 27312 | 45158 | SwSta | 2027-06-01 | Kays |  |  | 138 |  |  | New Kays Substation |  | IL |  |  | Planned | 16000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23088 |  | TP1510 | 26960 | 44948 | SwSta | 2024-06-01 | Quincy East |  |  | 138 |  |  | Replace BKR 1442 Replace switch 1456. |  | IL |  |  | Planned | 1500000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23286 |  | TP1598 | 27011 | 44943 | SwSta | 2025-06-01 | Pana |  |  | 138 |  |  | Add interconnection point to the Pana substation for PPI's new bulk substation which will be called Panther. |  | IL |  |  | Planned | 900000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 24052 |  | TP1721 | 28119 | 45056 | SwSta | 2025-12-01 | Nile |  |  | 138 |  |  | Construct a ring bus arrangement with four-line terminal positions and provisions for two additional future terminal positions. Cut existing Crab Orchard-Muddy 138 kV transmission line. |  | IL |  |  | Planned | 9250000 | Budgetary |  | 2025 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 24779 |  | TP1732 | 28092 | 45030 | SwSta | 2025-12-01 | Hoot |  |  | 138 |  |  | J1266 |  | IL |  |  | Planned | 10500000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 24781 |  | TP1734 | 28095 | 45142 | SwSta | 2025-12-01 | Greenwave |  |  | 138 |  |  | The J1232 Generating Facility will interconnect at the Greenwave substation cutting the Mattoon West-Arland-1539 138 kV Transmission Line. |  | IL |  |  | Planned | 8000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | South | Entergy-AR | 23900 |  | 23-EAL-010 | 27583 | 45050 | CB | 2025-06-01 | Dell 161kV |  |  | 161 |  |  | Upgrade Dell 161 kV Breakers B2240, B2205 and B2235 to 63kA |  | AR |  |  | Planned | 2515000 | Planning |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP23 | C | West | MEC | 23572 |  | T929Y | 27333 | 45169 | CB | 2023-12-01 | Franklin |  |  | 161 |  |  | Replace Franklin breaker 9210 and associated terminal equipment |  | IA |  |  | Under Construction | 500000 | Construction |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23675 |  |  | 27397 | 45156 | CB | 2025-12-01 | Avoca |  |  | 161 | 69 |  | Install a 69 kV breaker on the low-side of Avoca 161-69 kV Transformer 8T3, replace/rolocate Avoca Breakers 622 and 623 to accommodate new 69 kV breaker and replace Breakers 801, 802 and 620 due to condition |  | IA |  |  | Planned | 4100000 | Budgetary |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23692 |  | H00V5 | 27430 | 45125 | CB | 2027-12-31 | Sub 28 |  |  | 161 |  |  | Sub 28: Add 161 kV line breakers and install new control building. |  | IL |  |  | Planned | 3700000 | Budgetary |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23727 |  | T92K5 | 27452 | 44819 | CB | 2027-09-01 | Sub 56 |  |  | 161 |  |  | Network Upgrades for J1131 Solar |  | IA |  |  | Planned | 2025000 | GIA |  | 2020 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23740 |  |  | 27438 | 44936 | CB | 2026-12-31 | Webster |  |  | 161 |  |  | Replace 161 kV breaker 9250 in Webster substation |  | IA |  |  | Planned | 300000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MRES | 23710 |  |  | 27490 | 44816 | CB | 2024-01-01 | ATLANTC5 |  |  | 161 |  |  | Replace two 161 kV oil filled breakers. |  | IA |  |  | Proposed | 800000 | Budgetary |  |  |  |  | Missouri River Energy Services (MRET) | N | N | N
A in MTEP23 | C | South | SMEPA | 23126 |  |  | 27010 | 44952 | CB | 2021-11-01 | Morrow |  |  | 161 |  |  | Non-Stand Alone Network Upgrades: Install substation bay and two 161kV gas circuit breakers for new 161kV bundled line. |  | MS |  |  | M5_In Service | 710000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | South | SMEPA | 23126 |  |  | 27006 | 44952 | CB | 2021-11-01 | Morrow |  |  | 161 |  |  | Interconnection Facilities: Install substation bay and two gas circuit breakers at Plant Morrow switchyard for ST and CT GSU connections. |  | MS |  |  | M5_In Service | 710000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | Central | WVPA | 23715 |  |  | 27509 | 45124 | CB | 2024-02-28 | Charmin Bulk |  |  | 161 |  |  | Add breakers to Charmin Bulk to have 2 separate 161kV feeds from Trail of Tears. |  | MO |  |  | Under Construction | 4485000 |  |  | 2023 |  |  | Wabash Valley Power Association, Inc. | N | N | N
A in MTEP23 | B | South | SMEPA | 12210 |  |  | 22357 | 44957 | Dist | 2025-06-01 | South Hattiesburg Industrial |  |  | 161 |  |  | A new distribution station will be constructed adjacent to the 161kV switching station and the existing distribution feeders from both delivery points will be routed to the new station. |  | MS |  |  | Proposed | 8762200 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | Central | AmerenMO | 24860 |  | TP1739 | 28122 | 45056 | INT | 2025-12-01 | Bullion |  |  | 161 |  |  | This project will construct a new Point of Interconnection for the Interconnection Customer's Generating Facility, Kelso 2 Solar LLC, to the Buillion Switching Station. The 161 kV lead line from Kelso 2 Solar LLC will terminate into the fourth position. |  | MO |  |  | Planned | 1000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | South | Entergy-AR | 24879 |  |  | 28127 | 45058 | INT | 2025-11-01 | Prairie Creek |  |  | 161 |  |  | A new 3 breaker ring bus switching station for J1816 solar project |  | AR |  |  | Planned | 12604000 | GIA |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP23 | C | South | Entergy-AR | 24898 |  |  | 28126 | 45057 | INT | 2025-01-31 | Flat Lake |  |  | 161 |  |  | New POI for Forgeview Solar J1562 project. |  | AR |  |  | Planned | 5161000 | GIA |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP23 | C | South | Entergy-AR | 24918 |  |  | 28138 | 45068 | INT | 2024-10-31 | Hamrick 161kV |  |  | 161 |  |  | New ring bus switching station for J1842 interconnection. |  | AR |  |  | Planned | 2073000 | GIA |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP23 | B | Central | AmerenMO | 22790 |  | TP1533 | 26903 | 45158 | SUB | 2026-12-01 | Moreau |  |  | 161 |  |  | Construct a four position (six ultimate) 161 kV ring bus at Moreau |  | MO |  |  | Planned | 8500000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22791 |  | TP1541 | 26912 | 45158 | SUB | 2026-12-01 | Mcbaine Tap |  |  | 161 |  |  | New switching station at McBaine tap off LYMT-OVRT-3 |  | MO |  |  | Planned | 14400000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22814 |  | TP1505 | 26875 | 44948 | SUB | 2024-12-01 | Guthrie |  |  | 161 |  |  | Add a 161 kV line breaker to the 161 kV GUTH-LYMT-3 line at Guthrie. |  | MO |  |  | Proposed | 2000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22815 |  | TP1506 | 26876 | 44945 | SUB | 2025-12-01 | Hunter |  |  | 161 |  |  | Maintenance: BKR H7 Bus Tie 2-3, Line relays on H6 and H2 Bus Relays on Bus 2 BKR relays on bus ties 1-2 and 2-3 Operations: Line breakers on H2 and H10 High Side Interrupting Devices on XFMR 1, 2, 3 |  | MO |  |  | Planned | 3000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22869 |  | TP1523 | 26890 | 45158 | SUB | 2027-06-01 | Clark |  |  | 161 | 138 |  | Rebuild Clark 138/161 kV Substation to have a 138 kV BAAH bus with 8 positions (4 existing lines, 2 XFMRs, bring in RIV-ALFM-6636) and a 161 kV ring bus with 6 positions (2 existing lines, 2 XFMRs, and new line position to Viburnum). Rebuild the existing Clark-Viburnum 161 kV line to be double circuit 161 kV lines. Add a 161 kV terminal at Viburnum Substation. Route the RIV-ALFM-6636 138 kV line into the new Clark 138 kV BAAH bus. |  | MO |  |  | Planned | 10000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22873 |  | TP1535 | 26906 | 45027 | SUB | 2026-06-01 | Oran |  |  | 161 |  |  | Add 161 kV ring bus to split the Kelso- Morley-3 line into two lines |  | MO |  |  | Planned | 7800000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22927 |  | TP1532 | 26902 | 44948 | SUB | 2024-12-01 | Viaduct |  |  | 161 | 115 |  | Convert 115 kV facilities at Viaduct to 161 kV. Eliminate Viaduct 161 to 115kV transformer T1 by bypassing it, and by changing the taps on Viaduct XFMR 1 from 115 to 161kV. Replace 115kV OCB #5210 with a 161kV puffer breaker. |  | MO |  |  | Proposed | 5000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | B | Central | AmerenMO | 23006 |  | tp1509 | 26879 | 44948 | SUB | 2025-12-01 | Pilot Knob |  |  | 161 |  |  | Add circuit switcher for XFMR 1 and line breaker for 161 kV FLET –PKNB -2 |  | MO |  |  | Planned | 4000000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 23526 |  | TP1672 | 27256 | 45160 | SUB | 2024-12-01 | Warrenton |  |  | 161 |  |  | Install a 161kV 4 pos ring bus at Warrenton Substation. |  | MO |  |  | Planned | 15000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | West | ITCM | 23546 |  | Jefferson Co 161kV Ring | 27271 | 44816 | SUB | 2025-12-31 | Jefferson County | Substation |  | 161 | 161 |  | Rebuilding the 161 kV bus into a ring bus configuration will increase the reliability of the system reliability of the area and modernize the existing substation originally built in 1970 without a full substation replacement. In addition, the project will replace some existing infrastructure at the substation which is at the end of its useful life and in need or replacement. A ring bus configuration will increase operational flexibly for the area by allowing increased ability to reconfigure the system during certain outage conditions. |  | IA |  |  | Proposed | 6443395 | Engineering |  |  |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 24449 |  | Nevada Area Load Interconnections | 27978 | 45063 | SUB | 2024-12-31 | Prairieview Industrial | Substation |  | 161 | 161 |  | Construct ITC portion of new Prairieview Industrial Substation. |  | IA |  |  | Proposed | 11381150 | Engineering |  | 2023 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 24449 |  | Nevada Area Load Interconnections | 27981 | 45063 | SUB | 2024-12-31 | Fernald | Substation |  | 161 | 161 |  | Expand Fernald substation with new 161 kV line terminal. |  | IA |  |  | Proposed | 983818.75 | Engineering |  | 2023 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 24449 |  | Nevada Area Load Interconnections | 27980 | 45063 | SUB | 2024-12-31 | Ames | Substation |  | 161 | 161 |  | Rebuild 161 kV portion of Ames transmission substation into a ring bus. |  | IA |  |  | Proposed | 7757340 | Engineering |  | 2023 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 24449 |  | Nevada Area Load Interconnections | 27979 | 45063 | SUB | 2024-12-31 | Teller | Substation |  | 161 | 161 |  | Construct new Teller 161 kV substation. |  | IA |  |  | Proposed | 9615583.75 | Engineering |  | 2023 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | MEC | 23570 |  | H00YH, T91Y8 | 27326 | 44805 | SUB | 2026-06-01 | Valley Trail |  |  | 161 |  |  | Construct new 161 - 13.2 kV substation |  | IA |  |  | Planned | 9500000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23590 |  | T92JD | 27327 | 45156 | SUB | 2027-12-01 | Granger |  |  | 161 |  |  | Install 161 kV line breakers and associated relaying |  | IA |  |  | Planned | 2100000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23609 |  | T92DV | 27324 | 44805 | SUB | 2025-06-01 | Delaware |  |  | 161 |  |  | Install 161 kV line breakers and associated relaying |  | IA |  |  | Proposed | 1900000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23686 |  |  | 27423 | 44812 | SUB | 2026-12-01 | Hospers |  |  | 161 | 69 |  | Construct new 161 kV line from Obrien County Substation to Hospers Substation, expand Obrien County Substation to install 345-161 kV, 560 MVA transformer and 161 kV bus and expand Hospers Substation to install 161-69 kV, 167 MVA transformer and 161 kV bus |  | IA |  |  | Proposed | 5000000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23691 |  | H014F, H014H, T928G | 27429 | 45156 | SUB | 2026-12-31 | Riverdale |  |  | 161 |  |  | Construct new 161-13.2 kV substation |  | IL |  |  | Proposed | 3200000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23699 |  |  | 27408 | 45126 | SUB | 2026-09-01 | Gifford Road |  |  | 161 |  |  | Construct Gifford Road 161-13.2 kV Sub and Line Taps |  | IA |  |  | Proposed | 3000000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23723 |  | H01B4, H01B5, T92LM, T92LP | 27433 | 45125 | SUB | 2027-12-31 | Edgington |  |  | 161 | 13.2 |  | Construct new 161-13.2 kV substation |  | IL |  |  | Planned | 4200000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23724 |  |  | 27441 | 45156 | SUB | 2023-12-31 | Pomeroy |  |  | 161 | 69 |  | Pomeroy 161 kV Substation 69 kV Breaker Replacement and Addition |  | IA |  |  | Under Construction | 600000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | South | SMEPA | 23126 |  |  | 27008 | 44952 | SUB | 2022-07-01 | Purvis Bulk |  |  | 161 |  |  | Non-Stand Alone Network Upgrades: Replace all 161kV breakers and relaying equipment at Purvis Bulk. |  | MS |  |  | M5_In Service | 2470000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | South | SMEPA | 23126 |  |  | 27007 | 44952 | SUB | 2021-11-01 | Morrow |  |  | 161 |  |  | Stand Alone Network Upgrades: Completely rebuild the Morrow 161kV switchyard with new bus work, breakers, relaying, and station equipment. |  | MS |  |  | M5_In Service | 7550000 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | West | XEL | 23513 |  |  | 27283 | 44792 | SUB | 2025-06-15 | Emerald |  |  | 161 | 115 |  | Line W3209 – Replace 3 way switch with new 161kv to 115kv substation. |  | WI |  |  | Planned | 9000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | MEC | 23690 |  | T92LB | 27427 | 45156 | SUBmisc | 2025-12-31 | Quad Cities Enron |  |  | 161 |  |  | Quad Cities Enron Substation: Install 161 kV Line Switches |  | IA |  |  | Planned | 500000 | Budgetary |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | Central | GLH | 23827 |  |  | 27527 | 45030 | SwSta | 2026-12-31 | Heath |  |  | 161 |  |  | Build a new 3-ring breaker switching station near Health, KY bisecting Joppa - Shawnee Ckt 1 and allowing 1-161 kV terminal for connection with Big Rivers Electric McCracken station. |  | KY |  |  | Proposed | 15900000 | Planning |  |  |  |  | Gridliance | N | N | N
A in MTEP23 | B | South | SMEPA | 12210 |  |  | 27675 | 44957 | SwSta | 2025-06-01 | South Hattiesburg Industrial |  |  | 161 |  |  | In order to serve the South Hattiesburg and Hattiesburg Industrial delivery points economically and reliably, service will be established by constructing a 161kV breaker switching station. |  | MS |  |  | Proposed | 3789500 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | West | XEL | 23512 |  |  | 27279 | 44791 | SwSta | 2026-06-01 | Prairie View |  |  | 161 |  |  | Rebuild the Wheaton Substation on a new location with a 4-row breaker and a half 161 kV configuration in order to separate it from the Generation facility. |  | WI |  |  | Planned | 17000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | B | Central | DEI | 23407 |  | M220243 | 27034 | 44824 | BUS | 2024-06-01 | Bloomington 230 | bus upgrade |  | 230 | 138 | 160 | Bloomington 230 - Upgrade Bk1 138KV Bus - from 300CU to 954AL; Summer xfmr ratings will increase to 160/165MVA; Summer 13836 line ratings will increase to 178/178MVA |  | IN |  |  | Proposed | 387100 | Planning Preliminary |  | 2022 |  | 165 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | South | Entergy-LA | 24253 |  | 23-ELB-019 | 27768 | 44894 | CB | 2025-08-09 | Willow Glen |  |  | 230 |  |  | Replace 12 230 kV breakers |  | LA |  |  | Proposed | 16510000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 24272 |  | 23-ELB-020 | 27771 | 44894 | CB | 2025-07-15 | Moler |  |  | 230 |  |  | add four breakers to Moler to create a four breaker ring bus. |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | West | GRE | 23869 |  | 208998 | 27651 | 44995 | CB | 2024-06-28 | Ramsey |  |  | 230 |  |  | Replace breaker 33RB1 |  | MN |  |  | Proposed | 471468 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 24053 |  | 23-ELS-007 | 27725 | 44833 | INT | 2024-05-01 | Vacherie |  |  | 230 |  |  | This construction at the existing Vacherie 230 kV substation is to accommodate the interconnection of a solar facility (J1431) |  | LA |  |  | Planned | 1420000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 24094 |  | 23-ELB-018 | 27740 | 44847 | INT | 2023-11-01 | Bueche |  |  | 230 |  |  | All facilities required for interconnection of J1463 at the Bueche 230 kV station |  | LA |  |  | Proposed | 128000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 24272 |  | 23-ELB-020 | 27770 | 44894 | INT | 2026-03-01 | J1421 |  |  | 230 |  |  | Construct station for new interconnect customer |  | LA |  |  | Proposed | 32259000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 24861 |  | 23-ELS-009 | 28123 | 45057 | INT | 2025-06-01 | Evergreen | Donaldsonville |  | 230 |  |  | Interconnection facilities for J1583 |  | LA |  |  | Proposed | 5000000 |  |  |  | ISD is back feed date |  | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 25101 |  | 23-ELS-011 | 28211 | 45120 | INT | 2025-12-22 | Bogalusa | Talisheek |  | 230 |  |  | This construction of a new station on the Bogalusa to Talisheek 230 kV line to accommodate the interconnection of a solar facility (J1564) |  | LA |  |  | Proposed | 18820000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 25122 |  | 23-ELS-011 | 28210 | 45119 | INT | 2026-06-01 | Vacherie | Chackbay |  | 230 |  |  | This construction of a new station on the Vacherie to Chackbay 230 kV line to accommodate the interconnection of a solar facility (J1542) |  | LA |  |  | Proposed | 19300000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-MS | 24880 |  |  | 28137 | 45068 | INT | 2024-07-31 | Cotton Blossom |  |  | 230 |  |  | The generation facility intends to connect adjacent to the current solar facility located at Cotton Blossom 230 kV substation. |  | MS |  |  | Proposed | 724000 | GIA |  | 2022 |  |  | Entergy Mississippi | N | N | N
A in MTEP23 | C | South | Entergy-MS | 24899 |  |  | 28136 | 45068 | INT | 2024-07-31 | Twinkletown |  |  | 230 |  |  | The generation facility intends to connect adjacent to the current solar facility located at Twinkletown 230 kV substation. |  | MS |  |  | Proposed | 672000 | GIA |  | 2022 |  |  | Entergy Mississippi | N | N | N
A in MTEP23 | C | South | Entergy-MS | 25086 |  |  | 28254 | 45141 | INT | 2025-11-16 | Tinnin Road |  |  | 230 |  |  | The generation facility intends to connect to the existing Tinnin Road 230 kV station. |  | MS |  |  | Proposed | 5529000 | GIA |  | 2022 |  |  | Entergy Mississippi | N | N | N
A in MTEP23 | C | South | Entergy-TX | 24839 |  | 23-ETI-014 | 28124 | 45057 | INT | 2025-12-04 | Rocky Creek | Veteran |  | 230 |  |  | Interconnection for J1671 |  | TX |  |  | Proposed | 18847000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-TX | 24984 |  | 23-ETI-018 | 28182 | 45089 | INT | 2026-06-01 | Plum Grove | Colony |  | 230 |  |  | GI on Plum Grove to Colony |  | TX |  |  | Proposed | 16300000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | Central | DEI | 23887 |  |  | 27723 | 45168 | SUB | 2024-11-15 | Veedersburg West | POI CB |  | 230 |  |  | J1378 Crossroads Solar POI - 230kV line termination interconnection facilities including metering equipment; Veedersburg West sub - add 230kV breakers and complete a 4-breaker ring |  | IN |  |  | Planned | 5992933 | Engineering Preliminary |  | 2022 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23964 |  | M220168 | 27700 | 45183 | SUB | 2025-06-01 | Kokomo Fusion - Phase 1 | new sub |  | 230 | 69 | 300 | Kokomo Project Fusion Phase 1: new 230/69kV substation for new large customer load inserted in the 23022 ckt. with breaker and 1/2 layout (between Greentown and Kokomo Webster St.); (2) 150MVA -230/69kV transformers; (14) 69kV breakers in a breaker and one half layout; loop 69172 ckt. (between Kokomo East and Kokomo Chrysler North) through new sub; also loop the 69174 ckt. (between Kokomo Touby Pike Tap 1 and Chrysler North Jct.); (3) 60MVA - 69/34.5kV transformers; add second parallel 230/69kV xfmr at Kokomo Webster St. |  | IN |  |  | Proposed | 92073454 | Planning Preliminary |  | 2023 | cost/scope increases for phase 2 prep (additional CBs; land; 2nd Webster St. 230/69kV xfmr, etc.) | 300 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | West | GRE | 23718 |  | 208732 | 27564 | 45156 | SUB | 2025-03-27 | Rush City |  |  | 230 |  |  | This project will establish a 230 kV ring bus topology at Rush City. For GRE to address the rating exceedances experienced with the current shared breaker position, GRE will add breakers and associated equipment/relaying/etc. to the 230-kV Rush City bus between the Linwood, Red Rock, and Rock Creek lines |  | MN |  |  | Proposed | 4013958.83 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | MDU | 23596 |  |  | 27378 | 45183 | SUB | 2025-10-31 | Glenham |  |  | 230 |  |  | Rebuild of current Glenham substation 230/115/41.6 kV. |  | SD |  |  | Planned | 19000000 | Planning Preliminary |  | 2022 |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 23634 |  |  | 27386 | 44943 | SUB | 2025-12-31 | Wishek |  |  | 230 | 41.6 |  | Rebuild of 115 and 41.6 kV and building out 230 kV for new wind farm |  | ND |  |  | Planned | 14300000 | Planning Preliminary |  | 2022 |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | MDU | 24092 |  |  | 27734 | 45183 | SUBmisc | 2023-12-31 | Baker |  |  | 230 |  |  | Re-adjust breaker CT ratios and remove wave trap at Baker terminal for line going to Little Missouri. |  | ND |  |  | Planned | 50000 | Budgetary |  | 2022 |  |  | Montana-Dakota Utilities Company | N | N | N
A in MTEP23 | C | West | GRE, MP | 23877 |  | Nelson Lake 230 kV | 27668 | 44819 | SwSta | 2026-06-01 | Nelson Lake |  |  | 230 |  |  | New 230 kV Substation, 5 position breaker+half |  | ND | 0 | 0 | Proposed | 18000000 | Planning |  | 2022 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP23 | C | West | XEL | 23712 |  |  | 27503 | 44816 | BUS | 2023-09-01 | Lyon County |  |  | 345 | 115 |  | Replace 5N130 actuator secondary current limitation to increase TR9 rating back up to it's transformer limits. |  | MN |  |  | Planned | 300000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23760 |  |  | 27502 | 44816 | BUS | 2023-09-01 | Nobles County |  |  | 345 | 115 |  | Upgrade flexible busbar to increase ratings of TR9 and TR10. |  | MN |  |  | Planned | 450000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | Central | AmerenIL, AmerenMO | 23845 |  |  | 27624 | 45015 | CB | 2025-12-01 | Various |  |  | 345 | 138 |  | Replace Breakers as needed |  | IL,MO |  |  | Planned | 5000000 | Budgetary |  | 2025 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | West | MEC | 23689 |  | T92LA | 27426 | 45125 | CB | 2023-04-07 | Sub 93 (Louisa) |  |  | 345 |  |  | Replace Sub 93 (Louisa) 345 kV breaker 934 |  | IA |  |  | M5_In Service | 390000 | Actual |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23725 |  | T92K4 | 27442 | 44819 | CB | 2025-07-01 | Palo Alto |  |  | 345 |  |  | Network Upgrades for J877 Palo Alto Solar |  | IA |  |  | Planned | 3800000 | GIA |  | 2020 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | ATC | 24447 |  | PR09172 | 27967 | 45182 | INT | 2026-09-01 | Hill Valley SS |  |  | 345 | 138 |  | Interconnection Facilities |  | WI |  |  | Planned | 639848 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24613 |  | PR09165 | 28055 | 45182 | INT | 2025-06-01 | Rockdale SS |  |  | 345 | 138 |  | Interconnection Facilities |  | WI |  |  | Planned | 1350240 | GIA |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24758 |  | PR09191 | 28081 | 45182 | INT | 2026-06-03 | North Arlington Swt St |  |  | 345 |  |  | J1410 J1411 North Arlington Swt St Interconnection Facilities |  | WI |  |  | Planned | 1229118 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24799 |  | PR09198 | 28091 | 45182 | INT | 2026-11-12 | Blitz |  |  | 345 |  |  | J1377 Blitz SS Interconnection Facilities |  | WI |  |  | Planned | 637088 | GIA |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24801 |  | PR09207 | 28106 | 45182 | INT | 2027-03-19 | El Dorado |  |  | 345 |  |  | J1253 El Dorado Interconnection Facilities |  | WI |  |  | Planned | 629915 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | Central | AmerenIL | 24859 |  | TP1737 | 28121 | 45056 | INT | 2025-12-01 | Casey West |  |  | 345 |  |  | A new 345 kV position will be constructed at Casey West Substation to serve as the Point of Interconnection for Union Center Solar, LLC under GIA J1204. The CSYW-NWTY-1 line position will also be moved from the southwest corner of the substation to the southeast corner to avoid line crossing with the IC. |  | IL |  |  | Planned | 1200000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22706 |  | TP1490 | 26824 | 44948 | INT | 2024-06-01 | Spencer Creek |  |  | 345 |  |  | Connect a 200MW solar farm via 345 kV lead line from Interconnection Customer collector substation to existing Spencer Creek switching station. |  | MO |  |  | Planned | 4200000 | Budgetary |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | NIPS | 24562 |  |  | 28043 | 44965 | INT | 2024-06-01 | Schahfer | Burr Oak |  | 345 |  |  | Tap-in / Tap-out facilities to cut, then connect existing Schahfer – Burr Oak 345kV line. |  | IN |  |  | Planned | 7855659 | GIA |  | 2023 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP23 | B | West | ATC | 20201 |  | WO 604551 | 26316 | 45182 | SUB | 2026-06-30 | Various Sites |  |  | 345 | 69 |  | Small Capital Project and Asset Renewal |  | WI,MI |  |  | Planned | 47000000 | Budgetary |  |  |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 20204 |  | WO 604549 | 26319 | 45182 | SUB | 2025-06-30 | Various Sites |  |  | 345 | 69 |  | Load Interconnection |  | WI,MI |  |  | Planned | 16000000 | Budgetary |  |  |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 23906 |  | PR09177 | 27592 | 45182 | SUB | 2026-12-01 | South Fond du Lac |  |  | 345 | 69 |  | South Fond du Lac Asset Renewal |  | WI |  |  | Planned | 9500000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24093 |  | PR09266 | 27733 | 45182 | SUB | 2027-06-01 | Rocky Run SS |  |  | 345 | 115 |  | Planning Scope: o Remove Rocky Run 345/115kV transformers T2 and T4. Replace with on-site spare 500MVA 345/115kV transformer in the T4 position. o Upgrade two (2) 345kV bus switches and five (5) 115kV bus switches. o Remove breaker 4-2 and shorten 345kV ring bus. o Purchase new 500MVA 345/115kV system spare. Asset Renewal Scope: o Replace W-8 secondary relay SEL-321 (component replacement). o Replace all physical security cameras. |  | WI |  |  | Planned | 17600000 | Planning |  | 2027 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24447 |  | PR09172 | 27968 | 45182 | SUB | 2026-09-01 | Hill Valley SS |  |  | 345 | 138 |  | Substation Modifications |  | WI |  |  | Planned | 1613040 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24613 |  | PR09165 | 28054 | 45182 | SUB | 2025-06-01 | Rockdale SS |  |  | 345 | 138 |  | J1214_J1326 Network Upgrades |  | WI |  |  | Planned | 2719697 | GIA |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24758 |  | PR09191 | 28077 | 45182 | SUB | 2026-06-03 | North Arlington Swt St |  |  | 345 |  |  | J1410 J1411 North Arlington Swt St Network Upgrades |  | WI |  |  | Planned | 15552396 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24799 |  | PR09198 | 28088 | 45182 | SUB | 2026-11-12 | Blitz |  |  | 345 |  |  | J1377 Blitz SS Network Upgrades |  | WI |  |  | Planned | 10516164 | GIA |  | 2024 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24801 |  | PR09207 | 28108 | 45182 | SUB | 2027-03-19 | El Dorado |  |  | 345 |  |  | J1253 El Dorado Network Upgrade |  | WI |  |  | Planned | 10705127 | GIA |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | Central | AmerenIL | 22888 |  | TP1513 | 26851 | 45158 | SUB | 2027-06-01 | edwards |  |  | 345 |  |  | New 345 kV ring Bus |  | IL |  |  | Planned | 32000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23635 |  | TP1714 | 27395 | 44943 | SUB | 2024-06-01 | Baldwin |  |  | 345 |  |  | Install one 345 kV terminal in the Baldwin substation. The terminal will consist of all necessary terminal equipment to connect the J1202 leadline to the Baldwin substation 345 kV bus. |  | IL |  |  | Proposed | 150000 | GIA |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23678 |  | TP1716 | 27400 | 44943 | SUB | 2024-06-01 | Duck Creek |  |  | 345 |  |  | Install one 345 kV terminal in the Duck Creek substation. The terminal will consist of all necessary terminal equipment to connect the J1199 leadline to the Duck Creek substation 345 kV bus. Upgrade control and relay fiber panel at the Duck Creek substations as well as the remote end substati |  | IL |  |  | Planned | 2500000 | GIA |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 23982 |  | TP1719 | 27697 | 45159 | SUB | 2025-12-01 | Newton |  |  | 345 |  |  | Install one 345 kV terminal in the Newton substation. The terminal will consist of all necessary terminal equipment to connect the J1198 leadline. |  | IL |  |  | Planned | 1500000 | GIA |  | 2022 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 24133 |  | TP1725 | 27755 | 45056 | SUB | 2024-06-01 | Goose Creek |  |  | 345 |  |  | Add 345kV Breaker Position for J1360 to connect at Goose Creek. |  | IL |  |  | Planned | 4200000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22866 |  | TP1675 | 26880 | 45158 | SUB | 2027-06-01 | St. Francois |  |  | 345 | 138 |  | Install a new circuit breaker at St. Francois Sub position V43 to complete the ring bus. Add a new breaker at position V45. |  | MO |  |  | Planned | 12700000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | DEI | 23864 |  |  | 27621 | 44819 | SUB | 2028-06-01 | West of Bloomington 345 (new) |  |  | 345 | 138 | 525 | Build new 345/138kV substation located in the IPL Petersburg to Frances Crk 345kV line. |  | IN |  |  | Proposed | 21000000 | Planning Preliminary |  | 2022 |  | 600 | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | DEI | 23925 |  |  | 27707 | 44880 | SUB | 2029-12-31 | Slugger 138 load |  |  | 345 | 138 |  | (1) 12kV construction load up to 12MWS at River Ridge S. 6955 circuit; (2)138 radial tap from 13898 str. 817-4275 to feed up to 146MWs; (3) build 345/138kV substation to feed up to 407MWs |  | IN |  | 16 | Proposed | 123500000 | Planning Preliminary |  | 2022 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | Central | IPL | 23107 |  |  | 27014 | 44739 | SUB | 2023-12-01 | DEI Whitestown | DEI Hortonville |  | 345 | 138 |  | J993 Substation |  | IN |  |  | Proposed | 16000000 | GIA |  | 2022 |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP23 | C | Central | IPL | 23852 |  |  | 27630 | 45184 | SUB | 2025-12-31 | R1011 |  |  | 345 | 34.5 |  | The Interconnection Customer’s collector substation shall contain one (1) generator step-up transformer 34.5/345 kV, 168/280 MVA, one (1) 345 kV, 1200 A circuit breaker and transmission line/bus protection |  | IN |  |  | Planned | 15000000 | Planning |  | 2022 |  |  | Indianapolis Power & Light Company | N | N | N
A in MTEP23 | C | West | ITCM | 23483 |  | J1174 TOIF | 27308 | 44806 | SUB | 2025-06-30 | Bluebill | Switch Station |  | 345 | 345 |  | A new Bluebill 345 kV switching station will be constructed to interconnect projects J1174 and J1175. The Bison – Colby 345 kV line will be tapped and re-routed to new positions in the Bluebill station. The TOIF will include dead-end, disconnect switch, arresters, PT’s, relay panel, and associated equipment. |  | IA |  |  | Planned | 864989 | Engineering |  | 2022 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | ITCM | 23484 |  | J1175 TOIF | 27309 | 44806 | SUB | 2025-06-30 | Bluebill | Switch Station |  | 345 | 345 |  | A new Bluebill 345 kV switching station will be constructed to interconnect projects J1174 and J1175. The Bison – Colby 345 kV line will be tapped and re-routed to new positions in the Bluebill station. The TOIF will include dead-end, disconnect switch, arresters, PT’s, relay panel, and associated equipment. |  | IA |  |  | Planned | 864989 | Engineering |  | 2022 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | East | ITCT | 23884 |  |  | 27678 | 44924 | SUB | 2025-12-31 | ITCT Facilities |  |  | 345 | 120 |  | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. |  | MI |  |  | Proposed | 44250000 | Budgetary |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24313 |  |  | 27776 | 44944 | SUB | 2025-03-31 | Wedge | Substation |  | 345 | 345 |  | J1196 is a generation interconnection request for a 200 MW Solar Power Plant proposing to connect to the ITCT Greenwood - Rapson (Banner) 345 kV circuit.J1196 generation is queued within the DPP 2019 Cycle 1. |  | MI |  |  | Proposed | 11387184 | GIA |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24333 |  |  | 27784 | 44944 | SUB | 2025-12-29 | Neblo | Substation |  | 345 | 345 |  | Construct the new station as a 345kV station breaker and half station with three 40kA breakers in ring bus station. |  | MI |  |  | Proposed | 10631002 | Facility Study |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24333 |  |  | 27786 | 44944 | SUB | 2025-12-29 | Majestic | Substation |  | 345 | 345 |  | Upgrade relaying at Majestic 345kV position AQ. |  | MI |  |  | Proposed | 426272 | Facility Study |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24417 |  |  | 27880 | 44939 | SUB | 2025-05-16 | Ostrander |  |  | 345 |  |  | Construct a new 345kV station as a breaker and half station with three breakers in a ring bus configuration. |  | MI |  |  | M3_Long Lead Materials | 11346966 | GIA |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | West | MEC | 23686 |  |  | 27422 | 44812 | SUB | 2026-12-01 | Obrien County |  |  | 345 | 161 |  | Construct new 161 kV line from Obrien County Substation to Hospers Substation, expand Obrien County Substation to install 345-161 kV, 560 MVA transformer and 161 kV bus and expand Hospers Substation to install 161-69 kV, 167 MVA transformer and 161 kV bus |  | IA |  |  | Proposed | 10000000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23703 |  | T92K7, T92K8 | 27443 | 45029 | SUB | 2025-06-01 | J982 Sub |  |  | 345 |  |  | Network Upgrades for J982 Generator (345 kV Interconnection Sub) |  | IA |  |  | Planned | 12750000 | GIA |  | 2020 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 24212 |  |  | 27762 | 44896 | SUB | 2025-12-01 | Arbor Hill | Raccoon Trail | 1 | 345 |  |  | New 345 kV ring bus substation bisecting the existing Arbor Hill-Raccoon Trail 345 kV line. |  | IA |  |  | Planned | 0 | Planning |  | 2022 | Estimated Cost: $0 ($59.5m is estimated 100% customer reimbursement as a contribution in aid of construction) |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 24999 |  |  | 28161 | 45083 | SUB | 2024-05-31 | Southland |  |  | 345 |  |  | Expand 345 kV bus at existing Southland Substation to serve new customer load. |  | IA |  |  | Proposed | 20000000 | Planning |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 24999 |  |  | 28165 | 45086 | SUB | 2026-06-03 | Overland Trail |  |  | 345 |  |  | Expand existing Overland Trail 345 kV bus to install a new 345 kV line terminal. |  | IA |  |  | Proposed | 9000000 | Planning |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 24999 |  |  | 28162 | 45083 | SUB | 2025-02-01 | Southland |  |  | 345 |  |  | Expand 345 kV bus at existing Southland Substation to serve new customer load. |  | IA |  |  | Proposed | 5000000 | Planning |  | 2023 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | East | METC | 23948 |  |  | 27679 | 44924 | SUB | 2025-12-31 | METC Facilities |  |  | 345 | 120 |  | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. |  | MI |  |  | Proposed | 41750000 | Budgetary |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24275 |  |  | 27788 | 44944 | SUB | 2024-06-06 | Morocco | Substation |  | 345 | 345 |  | Complete 345kV rows 34 and 36. Install 345kV breakers 34R8, 36R8, and 36F7. Install 345kV disconnects 34R2, 36R4, 36H6, and 36F1. |  | MI |  |  | Proposed | 4260888 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24314 |  |  | 27779 | 44943 | SUB | 2025-05-05 | Thetford | Substation |  | 345 | 345 |  | Complete Thetford 345kV Row 29. Install breakers 29F7, 29H9, and 29R8 including any required disconnects for new breakers. |  | MI |  |  | Proposed | 4245703 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24448 |  |  | 27973 | 45114 | SUB | 2025-10-31 | Murphy | Styx |  | 345 |  |  | Install a new 345kV 3 Breaker ring station laid out in a breaker and a half configuration. |  | MI |  |  | Proposed | 11202000 | Facility Study |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | Central | NIPS | 22809 |  |  | 26840 | 45043 | SUB | 2025-06-01 | NEW J1058 |  |  | 345 |  |  | New double breaker double bus 345kV sub on the Schahfer to St. John line |  | IN |  |  | Planned | 20996953 | Facility Study |  | 2024 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP23 | C | Central | NIPS | 24562 |  |  | 28042 | 44965 | SUB | 2024-06-01 | Hinshaw |  |  | 345 |  |  | Greenfield 345kV double breaker double bus station named Hinshaw. Hinshaw will have 5 bays, with 4 built out under a MPFCA. |  | IN |  |  | Planned | 33739046 | GIA |  | 2023 |  |  | Northern Indiana Public Service Company | N | N | N
A in MTEP23 | C | West | ATC | 23902 |  | PR09112, PR08623, PR09166, PR09222, PR09240, F5971 | 27588 | 45182 | SUBmisc | 2025-12-01 | Various Sites |  |  | 345 | 69 |  | o Replace the existing Cisco 2520 switches at approximately 28 substation control house locations including dedicated firewall additions at the enhanced security sites o Replace the existing Cisco 3750/3850 physical security switches at approximately 56 control house locations o Install station wi-fi functionality at approximately 67 control house locations o Replace the existing network speakers and network door video stations at approximately 67 control house locations o Migrate mission critical equipment from AC inverted power to the station DC power at approximately 67 control house locations o Implement rogue device detection at approximately 67 control house locations |  | WI,MI |  |  | Planned | 10000000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24446 |  | PR09162 | 27964 | 45182 | SUBmisc | 2025-06-12 | Arnold SS |  |  | 345 | 138 |  | Remote End Work |  | MI |  |  | Planned | 150718 | GIA |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24838 |  | PR09216 | 28117 | 45182 | SUBmisc | 2028-12-29 | Fox River |  |  | 345 |  |  | Fox River SS Jumper Replacement |  | WI |  |  | Planned | 85375 | GIA |  | 2027 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | East | ITCT | 24299 |  |  | 27878 | 44939 | SUBmisc | 2025-03-31 | Wedge |  |  | 345 |  |  | Install position DI at Wedge to interconnect J1196 generator. |  | MI |  |  | M3_Long Lead Materials | 0 | GIA |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24376 |  |  | 27879 | 44939 | SUBmisc | 2025-12-29 | Neblo |  |  | 345 |  |  | Install entrance structure and disconnect as TOIF to interconnect J1224 & J1329 |  | MI |  |  | M3_Long Lead Materials | 0 | GIA |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 24418 |  |  | 27883 | 44939 | SUBmisc | 2025-05-16 | Ostrander |  |  | 345 |  |  | Install position CI at Ostrander to interconnect J1350 generator. |  | MI |  |  | M3_Long Lead Materials | 0 | GIA |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | METC | 24434 |  |  | 27908 | 44946 | SUBmisc | 2025-05-05 | Thetford |  |  | 345 |  |  | Install position RH29 to interconnect J1203 generator. |  | MI |  |  | M3_Long Lead Materials | 0 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24435 |  |  | 27909 | 44946 | SUBmisc | 2024-06-06 | Morocco |  |  | 345 |  |  | Install position RH36 to interconnect J1226 generator. |  | MI |  |  | M3_Long Lead Materials | 0 | GIA |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24448 |  |  | 27976 | 45114 | SUBmisc | 2025-10-31 | Murphy |  |  | 345 |  |  | Install C37.94 in Nokia router, Change SFP’s at Murphy in Nokia, Install Orion I/O module. |  | MI |  |  | Proposed | 39600 | Facility Study |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24448 |  |  | 27975 | 45114 | SUBmisc | 2025-10-31 | Slate |  |  | 345 |  |  | Install fiber jumpers at Slate for OPGW Fiber, Change SFP’s at Slate in Nokia. |  | MI |  |  | Proposed | 13200 | Facility Study |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | East | METC | 24514 |  |  | 27977 | 44950 | SUBmisc | 2024-01-29 | Palomino |  |  | 345 |  |  | Install 177 disconnect switch and required entrance structures at position RH31 as TOIF |  | MI |  |  | Proposed | 0 | Facility Study |  | 2022 |  |  | METC | N | N | N
A in MTEP23 | C | Central | AmerenIL | 24695 |  | TP1729 | 28065 | 45056 | SwSta | 2025-12-01 | Fauna |  |  | 345 |  |  | 125 MW solar electric generation project. That will interconnect at Fauna sub on Xenia - Mt Vernon West 345 kV Line 4591 |  | IL |  |  | Planned | 11000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 24718 |  | TP1730 | 28075 | 45019 | SwSta | 2025-12-01 | Quotient |  |  | 345 |  |  | Construct a new 345¿kV Quotient switching station in Jefferson County, IL to provide a Point of Interconnection for the Generating Facility. The new J1241 Interconnection Switching Station will split the existing Xenia – Mt Vernon West 345 kV transmission line |  | IL |  |  | Planned | 11000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenIL | 24840 |  | TP1742 | 28130 | 45061 | SwSta | 2025-12-01 | Zeke |  |  | 345 |  |  | New switching station for J1263 generator |  | IL |  |  | Planned | 10000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | AmerenMO | 24696 |  | TP1727 | 28066 | 45004 | SwSta | 2025-06-01 | Vanhorn |  |  | 345 |  |  | Construct the Interconnection Facilities at the J1352 Interconnection Switching Station, line cut-in and relay upgrades. Vanhorn sub on Montgomery-Spencer Creek 345 kV line. |  | MO |  |  | Planned | 11000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | Central | DEI | 23967 |  | M210469 | 27716 | 45168 | SwSta | 2024-06-01 | Douglas 345KV Switching Station | POI Sub |  | 345 |  |  | J1295-Gibson Solar 345kV (34516 ckt.) Switching Station (3-CB ring) |  | IN |  |  | M3_Long Lead Materials | 17700000 | Engineering w/AFUDC |  | 2023 |  |  | Duke Energy Corporation | N | N | N
A in MTEP23 | C | West | ITCM | 23485 |  | J1174 & J1175 NU | 27310 | 44806 | SwSta | 2025-06-30 | Bluebill | Switch Station |  | 345 | 345 |  | A new Bluebill 345 kV switching station will be constructed to interconnect projects J1174 and J1175. ITC will TO self-fund the Network Upgrades and will earn a return of and return on investment under a FSA for 90% of the cost. 10% of the Network Upgrades costs will be recovered under Attachment GG. |  | IA |  |  | Planned | 13816106 | Engineering |  | 2022 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | South | Entergy-LA | 23957 |  | 23-ELB-004 | 27915 | 45145 | SUB | 2026-06-30 | Conway |  |  | 500 |  |  | Construct Conway 500 kV station, 3 breaker ring and Autotransformer. Construct new control house. |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 25242 |  | 23-ELS-002 | 28277 | 45166 | SUB | 2028-07-01 | Churchill |  |  | 500 | 230 |  | 500 kV Station and two 500-230 kV Autos |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-LA | 25242 |  | 23-ELS-002 | 28276 | 45166 | SUB | 2028-07-01 | Commodore |  |  | 500 | 230 |  | 500-230 kV substation, including 500-230 kV Auto |  | LA |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-MS | 23932 |  | 23-EML-001 | 27852 | 44938 | SUB | 2024-12-31 | Multiple |  |  | 500 |  |  | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. |  | MS |  |  | Proposed | 50427385 | [5 empty] | Entergy Mississippi | N | N | N
A in MTEP23 | C | South | Entergy-TX | 23952 |  | 23-ETI-004 | 27941 | 44946 | SUB | 2030-12-19 | Babel |  |  | 500 |  |  | Construct 500 kV Babel station on the Hartburg to Layfield 500 kV line. Install 500 kV reactors at station |  | TX |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-TX | 23952 |  | 23-ETI-004 | 27942 | 44950 | SUB | 2030-12-19 | Running Bear |  |  | 500 | 138 |  | Construct 500-230-138 kV Running Bear Station. Install 500-230 kV and 230-138 kV Autotransformer. Cut in three 138 kV lines and two 230 kV lines. |  | TX |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | South | Entergy-AR | 23855 |  | 23-EAL-001 | 27581 | 45076 | SwSta | 2027-12-01 | Keo |  |  | 500 |  |  | Reconfigure the Keo 500 kV substation so that the Keo – White Bluff & Keo - Wrightsville 500kV lines are not lost for a P2.3 internal breaker fault. |  | AR |  |  | Planned | 15015000 | Planning |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP23 | C | Central | SIGE | 23751 |  | 2022-8 | 27475 | 44813 | TX | 2024-12-31 | Maryland | Maryland | T1 | 69 | 12 |  | Replace existing 69/12 kV T1 |  | IN |  |  | Planned | 1400000 | Budgetary |  | 2022 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP23 | C | Central | SIGE | 23751 |  | 2022-8 | 27476 | 44813 | TX | 2024-12-31 | Maryland | Maryland | T2 | 69 | 12 |  | Add new 69/12 kV T2 for distribution system support |  | IN |  |  | Planned | 2500000 | Budgetary |  | 2022 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP23 | C | Central | SIGE | 23755 |  | 2022-12 | 27480 | 44813 | TX | 2024-12-31 | Point | Point | D1 | 69 | 12 |  | Replace 69/12 kV T1 due to age and condition |  | IN |  |  | Planned | 12257000 | Budgetary |  | 2022 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP23 | C | Central | SIGE | 23756 |  | 2022-13 | 27481 | 45125 | TX | 2025-12-31 | Yankeetown | Yankeetown | T1 | 69 | 12 |  | Replace 69/12 kV T1 due to age and condition |  | IN |  |  | Planned | 1102500 | Budgetary |  | 2022 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP23 | C | Central | SIGE | 23757 |  | 2022-14 | 27482 | 44813 | TX | 2024-12-31 | Garvin | Garvin | T2 | 69 | 12 |  | Add second 69/12 kV transformer |  | IN |  |  | Planned | 2500000 | Budgetary |  | 2022 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP23 | C | West | XEL | 23456 |  |  | 27237 | 44788 | TX | 2026-12-31 | Lake Yankton |  |  | 115 | 69 |  | Replace Lake Yankton 115/69 kV TR02. |  | MN |  |  | Planned | 1500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23457 |  |  | 27240 | 44788 | TX | 2026-12-31 | Hydro Lane |  |  | 115 | 69 |  | Replace Hydro Lane 115/69 kV TR05. |  | WI |  |  | Planned | 3000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23495 |  |  | 27233 | 44788 | TX | 2024-12-31 | Pipestone |  |  | 115 | 69 |  | Replace Pipestone TR05 and TR06 115/69 kV transformers. |  | MN |  |  | Planned | 3000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23496 |  |  | 27234 | 44788 | TX | 2025-12-31 | Inver Grove |  |  | 115 | 69 |  | Replace Inver Grove 115/69 kV TR02. |  | MN |  |  | Planned | 2500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23497 |  |  | 27236 | 44788 | TX | 2026-12-31 | Lake Pulaski |  |  | 115 | 69 |  | Replace Lake Pulaski 115/69 kV TR05. |  | MN |  |  | Planned | 2500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23498 |  |  | 27238 | 44788 | TX | 2027-12-31 | Minnesota Valley |  |  | 115 | 69 |  | Replace Minnesota Valley 115/69 kV TR11. |  | MN |  |  | Planned | 2500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23499 |  |  | 27241 | 44788 | TX | 2027-12-31 | Osprey |  |  | 115 | 69 |  | Replace Osprey 115/69 kV TR05. |  | WI |  |  | Planned | 3500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23506 |  |  | 27239 | 44788 | TX | 2025-12-31 | Gingles |  |  | 115 | 69 |  | Replace Gingles 115/69 kV TR05. |  | WI |  |  | Planned | 2500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | South | Entergy-TX | 24460 |  |  | 27940 | 44945 | TX | 2024-07-31 | Coldspring |  |  | 138 |  |  | Phase II - Adds power transformer and distribution bay. |  | TX |  |  | Planned | 2465960 | Construction |  |  |  |  | East Texas Electric Cooperative Inc. | N | N | N
A in MTEP23 | C | Central | SIGE | 23758 |  | 2022-15 | 27483 | 44813 | TX | 2024-12-31 | Bergdolt | Bergdolt | T2 | 138 | 12 |  | Add second 138/69 kV T2 |  | IN |  |  | Planned | 2500000 | Budgetary |  | 2022 |  |  | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | N | N | N
A in MTEP23 | C | West | ITCM | 23510 |  | Rock Creek T3 | 27274 | 44945 | TX | 2025-12-31 | Rock Creek | Transformer | T3 | 161 | 69 | 150 MVA | Replacing the existing unit with a new 150 MVA unit will allow the system to continue to serve the Equistar customer load in a similar fashion. |  | IA |  |  | Proposed | 4267194 | Engineering |  | 2022 |  |  | ITC Midwest | N | N | N
A in MTEP23 | C | West | MEC | 23573 |  | T909B | 27341 | 45030 | TX | 2025-12-01 | Black Hawk |  |  | 161 | 69 |  | Replace existing 161-69 kV, 50 MVA Transformer with a 161-69 kV, 167 MVA Transformer |  | IA |  |  | Planned | 9000000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23610 |  | T90BH; T92A0 | 27339 | 45030 | TX | 2026-12-01 | Washburn |  |  | 161 | 69 |  | Replace existing 161-69 kV, 50 MVA Transformer with a 161-69 kV, 125 MVA Transformer |  | IA |  |  | Planned | 7500000 | Budgetary |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | MEC | 23721 |  |  | 27420 | 44812 | TX | 2025-12-01 | Monona |  |  | 161 | 69 |  | Replace the existing Monona 161-69 kV transformer with a 125 MVA unit. Convert Monona 161 kV bus to a ring bus configuration. Also, replace two 69 kV breakers and upgrade associated terminal equipment. |  | IA |  |  | Planned | 7000000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | South | SMEPA | 23126 |  |  | 27004 | 44952 | TX | 2022-01-27 | Morrow |  |  | 161 | 22 |  | New 161/22kV, 520 MVA GSU for new natural gas fired combustion turbine (CT). |  | MS |  |  | M5_In Service | 0 | [5 empty] | South Mississippi Electric Power Association | N | N | N
A in MTEP23 | C | West | XEL | 23490 |  |  | 27227 | 44788 | TX | 2024-12-31 | Crystal Cave |  |  | 161 | 115 |  | Replace Crystal Cave 161/115 kV TR01. |  | WI |  |  | Planned | 3500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23492 |  |  | 27229 | 44788 | TX | 2027-12-31 | Pine Lake |  |  | 161 | 115 |  | Replace Pine Lake 161/115 kV TR03. |  | WI |  |  | Planned | 3500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | South | Entergy-AR | 21807 |  | 22-EAL-001 | 26375 | 45009 | TX | 2023-03-01 | Brinkley East |  |  | 230 | 115 |  | Change tap setting on the Brinkley East 230/115kV Auto. |  | AR |  |  | M5_In Service | 15000 | Planning |  |  |  |  | Entergy Arkansas | N | N | N
A in MTEP23 | C | South | Entergy-TX | 23933 |  | 23-ETI-002 | 27870 | 44938 | TX | 2026-06-01 | Sabine |  |  | 230 | 138 |  | Replace Sabine 230-138 kV Auto with a larger 500 MVA transformer |  | TX |  |  | Proposed | 15500000 | [5 empty] | Entergy | N | N | N
A in MTEP23 | C | Central | AmerenMO | 22066 |  | TP5142 | 26704 | 45158 | TX | 2026-12-01 | Mason |  |  | 345 | 138 |  | Replace Mason 345/138 kV xfmr #1 with a 700 MVA unit |  | MO |  |  | Planned | 7800000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | B | Central | AmerenMO | 23430 |  | TP1699 | 27081 | 45056 | TX | 2025-12-01 | Zachary |  |  | 345 | 161 |  | Install a 2nd Zachery 345/161 KV 560 MVA Transformer |  | MO |  |  | Planned | 14300000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | B | East | ITCT | 23853 |  | ITCT_22_019 | 27549 | 45071 | TX | 2026-12-31 | Wayne |  |  | 345 | 120 |  | Replace 345/120kV transformer 301 at Wayne with a new transformer rated at least 750 MVA for summer emergency. |  | MI |  |  | Proposed | 5635000 | Engineering |  | 2022 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | ITCT | 23894 |  | ITCT_22_028 | 27571 | 44935 | TX | 2026-12-31 | Jewell |  |  | 345 | 230 |  | Replace the 345/230 KV transformer #301 at Jewell with a new, standard transformer of similar size. |  | MI |  |  | Proposed | 6600000 | Engineering |  |  |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | East | METC | 23829 |  |  | 27535 | 45000 | TX | 2026-12-31 | Tompkins |  |  | 345 | 138 |  | Replace the 345/138 KV transformer #1 at Tompkins with a new, standard transformer of similar size. |  | MI |  |  | Proposed | 5231640 | [5 empty] | METC | N | N | N
A in MTEP23 | C | East | METC | 23835 |  | METC_22_064 | 27573 | 44943 | TX | 2026-12-31 | Pere Marquette |  |  | 345 |  |  | Replace 345/138KV transformer 2 at Pere Marquette with a new, standard transformer of similar size. Install a 345 kV breaker and associated switch on the high side of the transformer. Also, install a 138 kV switch on the low side of the transformer. |  | MI |  |  | Proposed | 8500000 | Engineering |  | 2023 |  |  | METC | N | N | N
A in MTEP23 | C | West | XEL | 23455 |  |  | 27235 | 44788 | TX | 2025-12-31 | Parkers Lake |  |  | 345 | 115 |  | Replace Parkers Lake 345/115 kV TR09 (3 phases). |  | MN |  |  | Planned | 6000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23491 |  |  | 27228 | 44788 | TX | 2022-12-31 | Parkers Lake |  |  | 345 | 115 |  | Replace Parkers Lake 345/115 kV TR10 with a single 3 phase transformer. |  | MN |  |  | Planned | 3500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23493 |  |  | 27230 | 44788 | TX | 2024-09-15 | Monticello |  |  | 345 | 230 |  | Replace Monticello 345/230 kV TR06. |  | MN |  |  | Planned | 3500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23493 |  |  | 27231 | 44788 | TX | 2025-09-16 | Monticello |  |  | 345 | 115 |  | Replace Monticello 345/115 kV TR10. |  | MN |  |  | Planned | 3500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23494 |  |  | 27232 | 44788 | TX | 2024-12-15 | Prairie Island |  |  | 345 | 161 |  | Replace Prairie Island 345/161 kV TR10. |  | MN |  |  | Planned | 3500000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | West | XEL | 23515 |  |  | 27288 | 44792 | TX | 2025-06-01 | Eau Claire |  |  | 345 | 161 |  | Upgrade Eau Claire TR09. |  | WI |  |  | Planned | 8000000 | Planning Preliminary |  |  |  |  | Northern States Power (Xcel Energy) | N | N | N
A in MTEP23 | C | South | Entergy-LA | 24252 |  | 23-ELS-008 | 27766 | 44894 | TX | 2025-09-20 | Bayou Labutte |  |  | 500 | 230 |  | Install 2nd 500-230 kV transformer |  | LA |  |  | Proposed | 45202000 |  |  |  | Total cost of project |  | Entergy | N | N | N
A in MTEP23 | C | West | ATC | 23856 |  | PR09084 | 27587 | 45182 | SVC | 2026-12-01 | Benson Lake |  |  | 20.5 |  |  | Replace hardware and software of the Benson Lake SVC plant System Control and Monitoring (SCM) Layer with supported hardware and software with a design life of 10 years. |  | WI |  |  | Planned | 4500000 | Planning |  | 2026 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | GRE | 23805 |  | 209202 | 27533 | 45068 | CAP | 2023-08-31 | Searles |  |  | 69 |  |  | Retire the 5.4 MVar Searles Capacitor Bank and associated components. |  | MN |  |  | Proposed | 116968.65 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23821 |  | 209307 | 27531 | 45068 | CAP | 2023-08-18 | Penelope |  |  | 69 |  |  | Retire the 5.4 MVar Penelope Capacitor Bank and associated components. |  | MN |  |  | Proposed | 121351 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | GRE | 23823 |  | 208667 | 27538 | 45068 | CAP | 2025-12-31 | Burnsville |  |  | 69 |  |  | Historically, the capacitor bank at Burnsville was presenting high transient voltage upon switching. It was taken out of service around 5 years ago and has not been needed since. A study was performed by planning, and it has been determined due to new system configuration that the capacitor bank is no longer required. |  | MN |  |  | Proposed | 1022278 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | MEC | 23719 |  |  | 27409 | 45126 | CAP | 2026-06-01 | Oakland |  |  | 69 |  |  | Install 69 kV, 12 MVAR capacitor bank and install 69 kV line breakers at Oakland Substation. |  | IA |  |  | Proposed | 5000000 | Planning |  | 2022 |  |  | MidAmerican Energy Company | N | N | N
A in MTEP23 | C | West | GRE | 23803 |  | 207408 | 27559 | 45068 | CAP | 2024-11-01 | Big Swan |  |  | 115 |  |  | Add a new 40 MVAr capacitor on the extended 115-kV bus and replace 69-kV bus relaying, station power, and battery bank. |  | MN |  |  | Proposed | 2633876.19 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N
A in MTEP23 | C | West | MP | 22885 |  | Brainerd Crypto | 26858 | 45163 | CAP | 2025-12-31 | Brainerd |  |  | 115 |  | 20 | Add a second 115 kV 20 MVAR switched capacitor bank |  | MN | 0 | 0 | Proposed | 750000 | Planning |  | 2022 |  |  | Minnesota Power (Allete, Inc.) | N | N | N
A in MTEP23 | C | West | OTP | 23129 |  |  | 26970 | 44701 | CAP | 2024-06-01 | Casselton 115 kV (620180) |  |  | 115 |  |  | Expand the existing 115 kV bus at OTP's Casselton, ND substation with two additional 115 kV breakers to allow for another position in the bus. Add a new 115 kV 15 MVAR capacitor and breaker into the new position created in the Casselton 115 kV bus. |  | ND |  |  | Planned | 1200000 | Planning |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | C | West | OTP | 24457 |  |  | 27926 | 44944 | CAP | 2024-07-31 | Bagley Jct. 115 kV (620239) |  |  | 115 |  |  | Add a 20 MVAR 115 kV capacitor at Bagley Jct. 115 kV switching station. |  | MN |  |  | M3_Long Lead Materials | 1153145 | Engineering |  | 2022 |  |  | Otter Tail Power Company | N | N | N
A in MTEP23 | B | East | ITCT | 23828 |  |  | 27529 | 44993 | CAP | 2025-06-01 | Hurst |  |  | 120 |  |  | Install a 33.3 MVAR capacitor at bus 102, position HJ, with a new 120 kV, 40 kA synchronous breaker and associated disconnect switch. Install a 3000 A, 40 kA breaker at position HK on the Hurst – Genoa 120 kV circuit. |  | MI |  |  | Proposed | 3125000 | Engineering |  | 2023 |  |  | ITC Transmission | N | N | N
A in MTEP23 | C | Central | AmerenMO | 23351 |  | TP1470 | 27074 | 45158 | CAP | 2024-12-01 | Bugle |  |  | 138 |  |  | 120 MVAR 138 kV Capacitor at Bugle |  | MO |  |  | Proposed | 26000000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | South | Entergy-TX | 24152 |  | 22-ETI-017 | 27756 | 44859 | CAP | 2023-06-30 | Moscow |  |  | 138 |  |  | In order to serve the new load at the Moscow substation, a new 138 kV capacitor bank will be installed |  | TX |  |  | Proposed | 0 | [5 empty] | Entergy | N | N | N
A in MTEP23 | B | Central | AmerenIL | 22966 |  | TP1562 | 26932 | 45158 | SVC | 2025-12-01 | Turkey Hill |  |  | 138 |  |  | Add 250 MVAR STATCOM at Turkey Hill |  | IL |  |  | Planned | 42500000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | B | Central | AmerenIL | 22966 |  | TP1562 | 27345 | 45158 | SVC | 2025-12-01 | Granite City 23rd street |  |  | 138 |  |  | Add 250 MVAR STATCOM to Centerville 138 kV substation |  | IL |  |  | Planned | 42500000 | Budgetary |  | 2023 |  |  | Ameren Services Company | N | N | N
A in MTEP23 | B | Central | AmerenIL | 22966 |  | TP1562 | 27344 | 45127 | SVC | 2027-06-01 | Jarvis |  |  | 138 |  |  | Add 250 MVAR STATCOM at Jarvis 138 kV |  | IL |  |  | Planned | 42500000 | Budgetary |  |  |  |  | Ameren Services Company | N | N | N
A in MTEP23 | B | Central | AmerenIL | 22966 |  | TP1562 | 27343 | 45127 | SVC | 2027-06-01 | Moro |  |  | 138 |  |  | Add 250 MVAR STATCOM at Moro |  | IL |  |  | Planned | 42500000 | Budgetary |  |  |  |  | Ameren Services Company | N | N | N
A in MTEP23 | C | West | ATC | 24785 |  | PR09224 | 28114 | 45182 | CAP | 2025-06-30 | Pleasant Prairie |  |  | 345 |  |  | Install four 75 Mvar 345 kV Capacitor Banks |  | WI |  |  | Planned | 7600000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | ATC | 24819 |  | PR09225 | 28115 | 45182 | CAP | 2025-06-30 | Racine |  |  | 345 |  |  | Install two 75 Mvar 345 kV Capacitor Banks |  | WI |  |  | Planned | 8400000 | Planning |  | 2025 |  |  | American Transmission Co. LLC | N | N | N
A in MTEP23 | C | West | GRE | 23883 |  | 209381 | 27674 | 45068 | CAP | 2024-05-31 | Cedar Mountain |  |  | 345 |  |  | Installation of (2) 75 MVar capacitor banks, installation of 3 new 345kV breakers to complete the breaker and a half |  | MN |  |  | Proposed | 4025164 | Planning Preliminary |  |  |  |  | Great River Energy | N | N | N