## Summary
MTEP Year | Planning Region | Utility/TO | Project ID | Project Name | State | Project Type | Other Type | Classification | Evidence | Data Center Flag | Load (MW) | Max kV | Estimated Cost ($) | System Need / Rationale | Report Notes
MTEP20 | West | ITCM | 18847 | Big Cedar Load Interconnection | IA | Other | Load Growth | Direct LG | Driver: Large Industrial |  | 450 MVA | 345 | 104627788.2 | New load at Big Cedar Industrial Park in Cedar Rapids, IA; new 345 kV substation, 345/161 kV transformers, underground 161 kV to customer substations | Big Cedar Industrial Park, Cedar Rapids IA. New 345 kV switching station ($105M). EPR project
MTEP20 | South | Entergy-TX | 18248 | Millbend 138 kV: New Distribution Station | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 56.5 MVA | 138 | 65400000 | Area load growth 56.5 MVA to start, 35.2 MVA from New Caney Sub and 21.3 MVA from Heights Sub
MTEP20 | South | Entergy-LA | 13925 | Choudrant: New distribution substation | LA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 230 | 56225000 | New 230 kV distribution substation in southern Lincoln parish for load growth | ELL $56.2M
MTEP20 | South | Entergy-TX | 15648 | Castle 230 kV: New Distribution Station | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 18.5 MVA | 230 | 50510000 | Distribution load growth, 18.5 MVA to start
MTEP20 | South | Entergy-LA | 18233 | Start 115 kV: Construct New Substation | LA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 39505305
MTEP20 | South | Entergy-LA | 18227 | Norris Road 138 kV: New Distribution Station | LA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 39200000
MTEP20 | South | Entergy-TX | 13943 | Southern Point 138 kV: New Substation | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 7.0 MVA | 138 | 22000000 | Distribution system load growth, 7.0 MVA to start
MTEP20 | West | ATC | 14907 | Load Interconnection Program 2021 | WI,MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 20124594
MTEP20 | South | Entergy-AR | 18103 | Screeton 115kV: Construct new substation | AR | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 40 MVA | 115 | 15132530
MTEP20 | West | MEC | 18129 | 25th Street NW 161 KV Substation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 12935000
MTEP20 | West | ATC | 18052 | Barneveld SS, DIC, new substation | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 69 | 12300000
MTEP20 | West | MEC | 18137 | South Waukee 161-13.2 kV Substation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 11988000
MTEP20 | South | Entergy-AR | 18101 | Hot Springs Plemmons 115kV: Construct new substation | AR | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 40 MVA | 115 | 10904173
MTEP20 | Central | AmerenIL | 19045 | New Rivian Load Interconnection | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 10100000 |  | Rivian EV plant at Diamond Star, IL (Normal). Two 138kV lines. EPR project
MTEP20 | South | Entergy-MS | 17086 | Brandon Area Loop Project | MS | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 9952989
MTEP20 | West | ITCM | 18061 | Mason City Industrial 161kV Substation Interconnection | IA | Other | Load Growth | Direct LG | Driver: Large Industrial |  | 18 | 161 | 9747847 | Mason City Industrial distribution substation; ~18MW initial load
MTEP20 | Central | AmerenIL | 9734 | New North Utica 138 kV substation | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 8400000
MTEP20 | West | ATC | 18051 | Sheboygan County SS, DIC, substation rebuild | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 138 | 8000000
MTEP20 | West | ITCM | 18846 | Creston Roundhouse 69kV Substation Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 7863016
MTEP20 | West | ATC | 18053 | Waupaca SS, DIC, transformer addition | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 138 | 6900000
MTEP20 | Central | AmerenIL | 16556 | New Bueller 138 kV substation (formerly Grove) | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 6600000
MTEP20 | Central | PPI | 18148 | New Riggston 138 kV substation | IL | Other | Load Growth | Direct LG | Driver: Data Center | Y |  | 138 | 6400000 | Establish 138 kV ring bus to serve proposed Data Center in IL Electric Cooperative territory | Data Center for IL Electric Cooperative between Jacksonville Industrial Park and Winchester
MTEP20 | East | METC | 18055 | Riverview Interconnection | MI | Other | Load Growth | Direct LG | Driver: Large Industrial |  | 40 | 138 | 6270000 | Dedicated customer substation ~1.25 miles west of Riverview; service 40MW of new load | EPR project
MTEP20 | West | XEL | 18132 | Cottage Grove Airgas Load Interconnection | MN | Other | Load Growth | Direct LG | Driver: Large Industrial (Airgas) |  |  | 115 | 5000000 | New 115 kV substation on Chemolite-Cottage Grove 115 kV line to serve new Airgas load
MTEP20 | East | ITCT | 17504 | Abrams Interconnection | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 120 | 4519000
MTEP20 | West | ITCM | 17705 | Madrid North 69kV Substation Rebuild Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 4144344
MTEP20 | Central | DEI | 18308 | New Hunts Creek 138/12 kV substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 3807000
MTEP20 | West | ITCM | 17734 | Clinton Perrin 69/24kV Substation Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 33 MVA | 69 | 3787788
MTEP20 | Central | DEI | 18307 | New Westfield East 69/12 kV substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 4 MVA | 69 | 3767000
MTEP20 | West | ITCM | 17704 | Cedar Rapids Hunter Field Substation Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 50 MVA | 69 | 3578790
MTEP20 | West | ATC | 17628 | Preble SS, DIC, add 4th transformer and substation rebuild | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y | 22 MVA | 138 | 3498694
MTEP20 | Central | AmerenIL | 18626 | New Delhi 69 kV substation | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 3000000
MTEP20 | Central | DEI | 18325 | New NSA Crane ULTF 69/12 kV substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 17 | 69 | 2800000
MTEP20 | West | ITCM | 17736 | Waukon Snakeskin 69kV Substation Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 2507447
MTEP20 | West | MP | 17184 | Nemadji Transformer Addition | WI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 2500000
MTEP20 | West | ITCM | 17741 | ITCM Customer Interconnects with short lead time 2023 | IA,MN,IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 2400000
MTEP20 | South | AECC | 18805 | NUCOR Cap Bank | AR | BRP |  | Hidden LG (BRP) | Driver: Large Industrial (NUCOR) |  |  | 161 | 2000000 | Mitigate low voltages for N-1 contingency; feeds Hickman North / NUCOR II steel plant | NUCOR steel plant load
MTEP20 | East | CETO | 18886 | Jaguar 138 kV Lines | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 2000000
MTEP20 | East | ITCT | 17744 | ITCT Customer Interconnections - Year 2023 | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 120 | 2000000
MTEP20 | East | METC | 17745 | METC Customer Interconnections - Year 2023 | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 2000000
MTEP20 | West | XEL | 17989 | EREPC Wellington Interconnection | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 1320000
MTEP20 | West | GRE | 18025 | Cannon River Park 115 kV Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 1000000
MTEP20 | East | WPSC | 18015 | Cadillac Substation Line Modifications | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 1000000
MTEP20 | East | WPSC | 14005 | Hammond Bay Interconnection Line | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 900000
MTEP20 | Central | DEI | 18306 | New H.E. Batesville 138/12 kV new substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 500000
MTEP20 | West | XEL | 18033 | Hydro Lane Expansion | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 350000
MTEP20 | West | ITCM | 17738 | Thompson MacTavish 69kV Substation Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 20 MVA | 69 | 346800
MTEP20 | West | ITCM | 17739 | Calmar Prairie Farmer 69kV Substation Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 205200
MTEP20 | West | ITCM | 17735 | Clinton South 69kV Substation Retirement | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 161873
MTEP20 | Central | AmerenMO | 17224 | New Pershall 138/12 kV distribution Substation | MO | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138
MTEP20 | Central | AmerenMO | 17665 | New Barrett Station 138/12 kV Transformer No. 2 | MO | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138
MTEP20 | Central | AmerenMO | 17685 | New Creve Coeur 138/12 kV substation | MO | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138
MTEP20 | Central | AmerenMO | 17686 | New Dougherty Ferry 138/12 kV substation | MO | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138
MTEP20 | Central | AmerenMO | 17945 | New Highway M 138/12 kV substation | MO | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138
MTEP20 | Central | AmerenMO | 17947 | New Fountain Lakes 138/12 kV transformer No. 2 | MO | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138
MTEP21 | South | Entergy | 20045 | Northline 230 kV: New Substation | LA | Other | Load Growth | Direct LG | Driver: Large Industrial |  | 50 | 230 | 42800000 | Distribution System Load Growth. | Northline 230kV: 50MW new load. $42.8M
MTEP21 | South | Entergy | 20067 | Southline 138 kV: New Substation | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 34800000 | Distribution system load growth
MTEP21 | West | Great River Energy | 20148 | Appleton - Benson (AG-AB) 115 kV Line | MN | Other | Reliability | Hidden LG | Keywords: load growth |  |  | 115 | 34773673 | This project is needed for the following reasons: 1. Accommodate future load growth in the Benson and other areas along the 115-kV transmission system 2. Improve load serving capability of the 41.6 kV and 115 kV transmission system 3. Address future NERC standard reliability violations, such as contingency low voltage concerns in the 115-kV system 4. Address existing N-2 contingency voltage collapse cases it the 115-kV system | GRE West Region; classified Local Reliability but serves load growth
MTEP21 | East | ITC Transmission | 20036 | Sebewaing 345kV_Installation | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 10 | 345 | 32544000 | The city of Sebewaing in anticipating a load increase and is seeking to move up to 10MW to the new interconnection.
MTEP21 | South | Entergy Mississippi | 13995 | Mannsdale 230kV Substation | MS | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 40 MVA | 230 | 32200000 | The service area of the planned Mannsdale substation is a portion of west Madison county experiencing growth rates of 3% or more with several known block load subdivisions planned in the near future and multiple tracks for potential build out. It is currently being served by circuits from Flora, Bozeman, and Lake Castle substations at 3 to 7 line miles away. There is some transfer capability between circuits for contingency conditions but it is limited by voltage decay due to heavy loading and distance. Beginning in 2020 feeder configurations will have to be switched to non-optimal reliability configurations due to load growth in the area.
MTEP21 | West | American Transmission Co. LLC | 14968 | Load Interconnection Program 2022 | WI,MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 27586994 | Load Interconnection
MTEP21 | South | Entergy | 21525 | Sullivan 230 kV: New Station, Southport to Sullivan 230 kV Line upgrade | LA | BRP |  | Hidden LG (BRP) | Driver: Large Industrial |  |  | 230 | 27100000 | The Sullivan station will be dedicated to serve New Orleans Sewerage and Water Board load. The Southport to Sullivan 230 kV upgrade is driven by NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. In 2023 summer the P2.3 Internal Breaker Fault of a Ninemile breaker will cause overloads on the Southport to Sullivan 230kV line. | BRP; New Orleans Sewerage & Water Board customer
MTEP21 | Central | City of Columbia, MO | 19805 | New UMC 69 kV Substation | MO | Other | Reliability | Hidden LG | Keywords: load growth |  |  | 69000 | 26000000 | Improve reliability for University of Missouri-Columbia (UMC) due to expected load growth. | CWLD Local Reliability; university load growth
MTEP21 | West | MidAmerican Energy Company | 19994 | Marcus East to Hospers 69 kV Line and Rebuild Marcus East Substation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 25400000 | Serves new customer load, resolves low voltage that could occur following contingencies by providing a second source into Marcus East Substation
MTEP21 | West | MidAmerican Energy Company | 20626 | Se Soteria Substation & 161 kV Line Taps | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 25300000 | Distribution substation is needed to serve new, large customer load
MTEP21 | West | MidAmerican Energy Company | 20627 | Johnson Creek Substation & 161 kV Line Taps | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 25300000 | Distribution substation is needed to serve new, large customer load
MTEP21 | South | Entergy | 20073 | Ponderosa 230 kV: Install Power Transformer | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 230 | 23500000 | Distribution system load growth
MTEP21 | South | Entergy | 21085 | Sugar House 230 kV: New Station | LA | Other | Load Growth | Direct LG | Driver: Large Industrial |  | 50 | 230 | 20100000 | Entergy has received a request from a customer interested in adding new load to a new station on the transmission system. | Sugar House 230kV: 50MW industrial customer. $20.1M
MTEP21 | East | ITC Transmission | 21105 | Apollo Interconnection | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 120 | 17147252 | DTE has requested a new 120 kV interconnection on the ITCT Hunters Creek-Lapeer 120kV circuit. The interconnection request is to feed two DTE transformers, and a future third transformer.
MTEP21 | West | MidAmerican Energy Company | 20173 | Quick-Sub 701 161 kV Line and Line Terminals | IA | Other | Reliability | Hidden LG | Keywords: load growth, customer load |  |  | 161 | 17000000 | Reliability improvement. Serves existing and expanding customer loads. Provides an additional 161 kV line into the Council Bluffs area. Increases reliability. | MEC West Region; local reliability with load growth component
MTEP21 | West | MidAmerican Energy Company | 19999 | Booneville: Second 345-161 kV Xfmr | IA | BRP |  | Hidden LG (BRP) | Driver: Area Load Growth (BRP) |  |  | 345 | 16700000 | Load growth in West Des Moines area increasing demand on Booneville 345-161 kV autotransformer after P6 N-1-1 contingencies | BRP driven by West Des Moines load growth; NERC P6/P23
MTEP21 | West | American Transmission Co. LLC | 19961 | Wells St. DIC – New West Marinette-Wells St. 69 kV line | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 69 | 16100000 | Load Interconnection
MTEP21 | Central | Ameren Services Company | 19852 | New Sikeston 161 kV Substation | MO | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 15200000 | Business development
MTEP21 | East | ITC Transmission | 21170 | Lenox-Stephens- Henry Ford MH - Shrine | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 7 | 345 | 14563912 | DTE interconnection for Henry Ford Macomb Hospital. Hospital is expanding, projecting an increase of 2.7 MW of load. Station will serve new load, in addition 3.7 MW of load will be transferred to Shrine from existing DTE distribution stations.
MTEP21 | South | Entergy Arkansas | 19907 | Moreland 161kV: Rebuild Substation | AR | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 20 MVA | 161 | 13400000 | There is approximately 20 MVA of load at risk for the loss of the single transformer at Moreland substation. Currently there is load shifted from Moreland to Russellville to eliminate a real time overload on the existing transformer.
MTEP21 | West | MidAmerican Energy Company | 20000 | Bondurant Substation: Add 345-161 Xfmr | IA | BRP |  | Hidden LG (BRP) | Driver: Area Load Growth (BRP) |  |  | 345 | 11900000 | Mitigate thermal overloads for Category P6 N-1-1 contingencies observed in MTEP20 summer peak models | BRP driven by Altoona load growth; NERC P6
MTEP21 | Central | Big Rivers Electric Corporation | 21165 | New Maxon Load Addition | KY | Other | Load Growth | Direct LG | Driver: Large Industrial |  | 30-60 | 161 | 11400000 | Phase I: Expand 69 kV substation for 30 MW industrial load; Phase II: increase to 60 MW | Maxon Load Addition: 30MW industrial (expandable to 60MW) in BREC KY. $11.4M
MTEP21 | Central | Ameren Services Company | 19085 | New Shelbyville S. 138 kV Ring Bus for PPI ISHI Load Addition | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 10000000 | Customer load addition
MTEP21 | West | MidAmerican Energy Company | 19998 | NW 2nd Street Substation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 10000000 | Serve new customer load and provide for substation expansion
MTEP21 | South | Entergy Arkansas | 19908 | Cave City 161kV: Add 2nd Transformer | AR | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 40 MVA | 161 | 8054670 | The existing 14 MVA transformer and regulator is projected to be loaded to 109% in the winter of 2023.
MTEP21 | West | ITC Midwest | 20037 | Carbide-Viele 161kV Rebuild | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 6200000 | Customer requested interconnection.
MTEP21 | West | MidAmerican Energy Company | 20003 | Highway 6 161/13.2 kV Substation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 6000000 | Serve new customer load
MTEP21 | West | MidAmerican Energy Company | 18890 | Clarksville-Donald Feldman 69 kV Line | IA | Other | Reliability | Hidden LG | Keywords: load growth |  |  | 69 | 5389340 | Convert MidAmerican’s Clarksville East-Shell Rock 34.5 kV line to 69 kV. Also, Corn Belt is constructing a new switching station northwest of Shell Rock, Donald Feldman Switching Station; Corn Belt is experiencing rapid load growth in the area. With the additional load, Corn Belt’s 69 kV system needs voltage support during contingencies. Corn Belt has obtained approval from SPP for a 69 kV interconnection between the new Donald Feldman Switching Station and MidAmerican’s Clarksville East Substation. MidAmerican’s Clarksville East-Shell Rock 34.5 kV line is in the vicinity of the new switching station. MidAmerican is pursuing options for a MidAmerican 69 kV line between Clarksville East Substation and the new Donald Feldman Switching Station.
MTEP21 | West | MidAmerican Energy Company | 20154 | 69 kV Substation Line Tap Blanket 2021-2024 | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 5150000 | Three-year "blanket project" to install 69 kV line taps into several new or existing substations to serve customer loads and/or increase system reliability. Specific project locations and scope of work to be determined on an ongoing basis as determined by need.
MTEP21 | West | ITC Midwest | 21429 | Tiffin Crossroads Substation Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 20 MVA | 69 | 5132408 | Customer requested interconnection
MTEP21 | West | ITC Midwest | 21625 | Keokuk Geode 69kV Substation Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 33 MVA | 69 | 4764418 | Interstate Power and Light Company (IPL) has requested to connect a new substation in Keokuk, IA.
MTEP21 | West | Central Minnesota Municipal Power Agency | 20169 | Delano_Municipal_Utilities_New_69_kV_Industrial_Park_Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 8 | 69 | 4100000 | System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. The downtown substation does not have room for expansion. A new substation next to the GRE Crow River 115/69kV substation will need the future load growth needs of Delano.
MTEP21 | West | Northern States Power (Xcel Energy) | 19892 | Elm Creek TR4 | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 4070000 | Extended outage duration under Transformer N-1 contingency to mitigate overloads. New customer load interconnecting to substation.
MTEP21 | West | American Transmission Co. LLC | 20925 | Lancaster Transformer Replacement & Substation Rebuild | WI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 3700000 | Load Interconnection
MTEP21 | West | American Transmission Co. LLC | 19806 | Bonnie Road SS, DIC, New Substation | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 69 | 3504413 | Load Interconnection
MTEP21 | West | Northern States Power (Xcel Energy) | 19891 | Replace Green Isle Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 3500000 | Addition of industrial load is planned. Existing TR1 has contingency risk post load addition. Existing substation is 4kV and needs to be converted to conform with standards, existing site not sized to fit
MTEP21 | West | Northern States Power (Xcel Energy) | 19890 | Watkins - Kimball Line Rebuild | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 3200000 | 83 year old poles. Age and condition do not support repairs. Load growth requires upgrade of small conductor. Potential for increased outage frequency and duration. Failure could provide risk to public
MTEP21 | West | Central Minnesota Municipal Power Agency | 20168 | Delano_Municipal_Utilities_Substation_B_Transformer_Upgrade | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 8 | 69 | 2500000 | System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. Delano currently has two 10 MVA 69/12.47kV transformer. The Sub B transformer was original in 1970 and rewound in 1999. There has been another project submitted into MTEP 21 for the substation A transformer upgrade. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers in 2022 extra capacity is needed. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers by 2022, extra capacity is needed.
MTEP21 | West | ITC Midwest | 20180 | ITCM Customer Interconnects with short lead time 2024 | IA,MN,IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 2400000 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request.
MTEP21 | Central | Ameren Services Company | 20365 | New Normal East 138/69 kV transformer | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 112 MVA | 138 | 2000000 | Local load serving need
MTEP21 | East | ITC Transmission | 20044 | ITCT Customer Interconnections - Year 2024 | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 120 | 2000000 | Customer Requests are often in need of interconnection on an expedited basis. This blanket allows interconnection requests of smaller nature to be quickly studied and connected by ITC.
MTEP21 | East | METC | 20047 | METC Customer Interconnections - Year 2024 | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 2000000 | Customer Requests are often in need of interconnection on an expedited basis. This blanket allows interconnection requests of smaller nature to be quickly studied and connected by METC.
MTEP21 | West | Central Minnesota Municipal Power Agency | 20166 | Delano_Municipal_Utilities_Substation_A_Transformer_Upgrade | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 8 | 69 | 1750000 | System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. Delano currently has two 10 MVA 69/12.47kV transformers. The Sub A transformer is 27 years old built in 1993, rewound once, and reaching the end of its life. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers by 2022, extra capacity is needed.
MTEP21 | West | MidAmerican Energy Company | 20002 | Waukee: Add 69 kV Capacitor Bank | IA | Other | Reliability | Hidden LG | Keywords: customer load |  |  | 69 | 1600000 | Increase reliability and allow for additional customer load.
MTEP21 | Central | Ameren Services Company | 9843 | New Normal East 138/34.5 kV transformer | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 112 MVA | 138 | 1500000 | Local load serving need
MTEP21 | West | Montana-Dakota Utilities Company | 19205 | Tioga Loop | ND | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 60 | 1480722 | Load growth
MTEP21 | Central | Duke Energy Corporation | 20196 | New Rosston 69/12 kV substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 1337000 | Distribution load growth
MTEP21 | West | MidAmerican Energy Company | 20012 | Sub 17: Add 161-13.2 kV Transformer | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 1000000 | Serve expanding customer load
MTEP21 | West | MidAmerican Energy Company | 20008 | Hampton West –Latimer 69 kV Line Uprate | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 925000 | Increases line rating to accommodate new customer load
MTEP21 | East | Wolverine Power Supply Cooperative, Inc. | 20885 | Cimmaron Interconnection | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 600000 | New Load Interconnection
MTEP21 | West | Great River Energy | 20151 | Milaca Breaker Addition 69 kV | MN | Other | Reliability | Hidden LG | Keywords: load growth |  |  | 69 | 419407.71 | The Milaca – Ogilvie 69 kV line is 12.7 miles, 170°F, 36.2/55.6 MVA line that is limited by jumpers (30.1/45.7 MVA). During summer peak loading, the “PG” (Milaca – Ogilvie 69 kV) line will overload when Milaca 5NB1 trips. This is based off existing summer peak loads and does not depend on load growth to achieve the need.
MTEP21 | West | Northern States Power (Xcel Energy) | 19905 | 2589 - Barnes Grove Interconnection | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 350000 | GRE interconnecting new Barnes Grove substation to serve new customer load
MTEP21 | West | MidAmerican Energy Company | 20006 | DPS 161 kV Strain Bus Uprate | IA | BRP |  | Hidden LG (BRP) | Driver: Area Load Growth (BRP) |  |  | 161 | 300000 | Mitigates thermal overload in near term summer peak model following P6 N-1-1 contingency event. | BRP driven by Altoona load growth; NERC P6
MTEP22 | South | Entergy Arkansas | 22530 | Sandy Bayou 500/230kV: New substation | AR | Other | Load Growth | Direct LG | Driver: Large Industrial |  | 250 MVA | 500 | 122000000 | This project is needed to serve a new industrial customer locating in Mississippi county, AR near the Driver - Shelby 500kV transmission line. | EAL $122M; massive industrial customer
MTEP22 | South | Entergy | 21851 | Falcon: New 138 kV Distribution Station | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 113800000 | Distribution load growth.
MTEP22 | Central | Duke Energy Corporation | 22425 | New West Lafayette Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 300 | 345 | 100000000 | New Customer load of 300MW/186MVAR with capacity factor of 50%
MTEP22 | South | Entergy | 21850 | District: New 138 kV Distribution Station | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 85200000 | Distribution load growth.
MTEP22 | South | Entergy | 15649 | Texas 138 kV: New Distribution Station | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 69400000 | Distribution load growth.
MTEP22 | South | Entergy | 21847 | Galaxy: New 138 kV Distribution Station | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 65900000 | Distribution load growth.
MTEP22 | South | Entergy | 13910 | Calhoun: New distribution substation | LA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 230 | 56800000 | Area distribution load
MTEP22 | Central | Hoosier Energy REC, Inc. | 22648 | New HE_Prescott_161kV_Line | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 400 | 345 | 45000000 | Expand DEI Prescott ring-bus and construct new 345/161 substation. Construct 161kV line from Prescott to new Decatur-Napoleon Station (22646). Required to accommodate up to 400 MW load, and maintain N-2 reliability, at new Decatur-Napoleon 161kV station.
MTEP22 | Central | Hoosier Energy REC, Inc. | 22666 | New HE_Batesville_161kV_Line | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 400 | 345 | 45000000 | Expand DEI Batesville ring-bus and construct new 345/161 substation. Construct new 161kV line from DEI Batesville to new 161kV station between Decatur and Napoleon. Required to accommodate up to 400 MW load, and maintain N-2 reliability, at new Decatur-Napoleon 161kV station.
MTEP22 | South | Cleco Power LLC | 20163 | Many Area Transmission Expansion | LA | BRP |  | Hidden LG (BRP) | Driver: Large Industrial (BRP) |  |  | 230 | 38100000 | In 2025 a P6 contingency on Many to Fisher 138 kV line followed by a contingency on Carroll to Red River 138 kV line causes an overload greater than 125 % on South Shreveport to Wallace lake 138 kV line. Also voltage violation exist for this contingency. Load shed is the only mitigation for this P6 contingency. With projected industrial load growth in this area this project has been modified to account for the additional load. The original alternative is in the Alternative notes. | BRP driven by projected industrial load growth
MTEP22 | Central | Hoosier Energy REC, Inc. | 22628 | New HE_Sleepy_Hollow 345/161 Sub | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 400 | 345 | 38000000 | Construct new 345kV ring bus station with 345/161 transformation between DEI Prescott and DEI Columbus. Construct new 161kV transmission line to new 161kV station between Decatur and Napoleon. Required to accommodate up to 400 MW load, and maintain N-2 reliability, at new Decatur-Napoleon 161kV station.
MTEP22 | Central | Hoosier Energy REC, Inc. | 22646 | New Decatur-Napoleon 161KV Station | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 25 | 161 | 26000000 | New customer request interconnection to 161kV line. Construct new 161kV station about 1.5 miles south of Decatur station to accommodate interconnection. Initial load about 25 MW, growing up to 400 MW through 2032.
MTEP22 | West | American Transmission Co. LLC | 21925 | Plymouth #5 - New DIC | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 138 | 21500000 | Load Interconnection
MTEP22 | Central | Big Rivers Electric Corporation | 21685 | New Pratt Paper Load Addition | KY | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 30-60 | 161 | 20200000 | Conversion of existing switching structure into a switching station and construction of a 8 mile radial transmission line to serve new industrial load. | Pratt Paper mill load 30MW (expandable 60MW). 8 mi radial 161kV line (BREC, KY)
MTEP22 | West | ITC Midwest | 21982 | Southern Dubuque 161/69kV Source & Bunker Hill 69kV Loop | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 150 MVA | 161 | 19306266 | Alliant Energy has requested that ITC provide a network feed for the radial Dubuque 8th Street-Bunker Hill 69 kV line. The Bunker Hill site is centrally located with all other transmission lines more or less bordering the edges of the city of Dubuque. The Bunker Hill substation can not serve existing distribution load during summer months and Alliant Energy must move several distributions feeders to other distribution sources. The new 69kV source will initially be just the new 69 kV loop to Bunker Hill, but will also be effective at serving future load along the Southwest Arterial, a recently completed 4 lane bypass connecting the major highways heading south and west from Dubuque.
MTEP22 | South | Cleco Power LLC | 22205 | Cole Substation | LA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 230 | 18764954 | This new substation is needed to serve a new industrial customer.
MTEP22 | West | American Transmission Co. LLC | 16770 | Load Interconnection Program 2023 | WI,MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 18045914 | Load Interconnection - Coordination with LDC
MTEP22 | Central | Duke Energy Corporation | 22208 | Rebuild Bedford to Mitchell Lehigh 138kV - 13822 Line | IN | BRP |  | Hidden LG (BRP) | Keywords: new load |  |  | 138 | 17960000 | MTEP21 results show line overload for multiple Cat. P6 pairings; interim operating mitigation to reduce Gibson/Petersburg station gens by 500MWs; if necessary, load shed up to 40MWs from bus 249932 (proposed new load in MTEP19) | BRP with new load driver
MTEP22 | South | Cleco Power LLC | 23327 | Marthaville Substation | LA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 230 | 15697000 | New industrial load
MTEP22 | South | Cleco Power LLC | 23328 | Vernon Substation | LA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 13650000 | New industrial load
MTEP22 | West | ITC Midwest | 21929 | Forks Switching Station & Forks-Rost 161kV Circuit | MN | BRP |  | Hidden LG (BRP) | Driver: Area Load Growth (BRP) |  |  | 161 | 13456200 | Part of a joint study to serve load expansion in Worthington, MN. MRES submitted a load addition on the Southeast side of the city of Worthington, MN. As part of this load addition study, GRE and ITC Midwest analyzed the existing operation and reliability concerns/violations. | BRP; part of Worthington load expansion
MTEP22 | West | Great River Energy | 22030 | Rost 161/69 kV Substation and Lorain - Rost 69 kV Line | MN | BRP |  | Hidden LG (BRP) | Driver: Area Load Growth (BRP) |  |  | 161 | 13368000 | Missouri River Energy Services (MRES), Great River Energy (GRE), and ITC Midwest (ITCM) performed a joint study of the Worthington area in southwestern Minnesota. Existing operational and reliability issues in this area have existed for some time. Various options have been considered for the Worthington load center, approximately 60 MW, and other loads that surround the area. At present, single contingency bus outages at Elk 161/69 kV substation cause the Worthington load to drop. In addition, there is a challenge to take maintenance outages on the 161 kV system from Split Rock to Lakefield Junction, some portions of the 69 kV system, and some portions of the neighboring 345 kV system due to voltage concerns across the area. Reconfiguration of the 69 kV system is a normal occurrence and puts area load at risk if an event were to occur in this temporary configuration. With the load growth occurring in Worthington for Worthington Public Utilities (WPU) over the next few years, the above issues are being exacerbated, and the proposal of a new substation in the Worthington area, prompted a deeper look into the area resulting in the following project need: Phase 1: Approximately 9 mile, 69-kV line from existing MRES Lorain breaker station to new Rost 69 kV breaker substation: Necessity: Establish alternative source beyond Elk to serve the Worthington load center Allow redundant 161/69 kV sources to be connected (Heron Lake and Elk) Lower reliability exposure to multiple 69 kV loads and wind farm connections on long 69 kV corridors Establish new relaying point to enhance relay settings with consideration for the wind farm sources and allow for future wind connections into the substation Benefits: Reduces the dependence of the Worthington load pocket on ITCM’s Elk Substation Increased operational flexibility for Worthington load for prior outages Additional 69-kV source to the Federated Rural Electric Association service territory including breaking up a highly exposed 69 kV line Enhanced relaying for line protection that consist of long distance 69 kV line with many radial taps and four wind farms, all without breaker protection Phase 2: Establish 161/69 kV at Rost with new 161 kV line from new ITC 161 KV Lakefield Corners breaker station Necessity: Low voltage - any outage on the 161-kV between Split Rock Substation (Xcel Energy) and Magnolia Substation leaves the system susceptible to low voltages for faults anywhere between Lakefield Junction and Elk 161-kV. Eliminate considerable operational concerns for prior-outage situation with a second event in the area. 161 kV prior outages of concern from Split Rock to Lakefield Junction including 161 kV substation on the corridor of Magnolia, Elk, Brewster, and Heron Lake. Reduce temporary operating guide and system reconfiguration due to voltage issues caused by a second contingency event. Eliminate significant risk of load loss within a broad area of southwestern Minnesota Benefits: New 161-kV source to the Worthington load pocket, via Rost 69 kV development allowing continued load expansion in the Worthington area Projects address voltage collapse and allows 69-kV system to remain in normal configuration during critical prior outages New Rost 161/69 kV source allows simplification of work at Heron Lake thus resulting in reduced cost at that substation. | BRP; serves Worthington area load growth
MTEP22 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 22008 | New Kaiser Aluminum 138 kV Sub | IN | Other | Load Growth | Direct LG | Driver: Large Industrial (Kaiser Aluminum) |  |  | 138 | 12000000 | New large industrial customer interconnection at Kaiser Aluminum 138 kV
MTEP22 | West | Minnesota Power (Allete, Inc.) | 21686 | Mesaba Junction 137 Line Extension | MN | BRP |  | Hidden LG (BRP) | Keywords: industrial load |  |  | 115 | 9000000 | Provides redundancy to an industrial load pocket that requires near-constant availability. Improves reliability by providing to independent sources to the Babbitt area. Enables asset renewal by allowing the existing Embarrass-Babbitt 115kV Line to be taken out of service and improved.
MTEP22 | West | American Transmission Co. LLC | 22989 | Columbus SS, DIC, Transformer Replacement | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 69 | 8782156 | Load Interconnection
MTEP22 | West | Montana-Dakota Utilities Company | 20946 | Poplar2 115/60 kV | MT | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 8525000 | Load growth; extend 115 kV to Poplar Oil Field to support load growth on the 60 kV system and mitigate 60 kV voltage violations under Poplar 60 kV line-end outage contingency or loss of existing 115/60 kV transformer at Poplar.
MTEP22 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 22006 | New Anderson Road 69/12 kV Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 8500000 | Address load growth
MTEP22 | Central | Ameren Services Company | 21306 | New Whitetail 138 kV Substation | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 8000000 | Customer interconnection
MTEP22 | Central | Ameren Services Company | 21326 | New Duff 138 kV Substation | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 8000000 | Customer interconnection
MTEP22 | West | Missouri River Energy Services (MRET) | 23346 | Hutchinson Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 8000000 | There are existing operational concerns in the area that require generation to be ran system intact. The City of Hutchinson expects a large expansion of existing customer load over the next couple of years, which will exacerbate the operational concern.
MTEP22 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 22009 | New Midwest Fertilizer 138 kV Sub | IN | Other | Load Growth | Direct LG | Driver: Large Industrial (Midwest Fertilizer) |  |  | 138 | 8000000 | Large industrial customer - Midwest Fertilizer 138 kV
MTEP22 | West | ITC Midwest | 21937 | Chariton North 69kV Substation Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 33 MVA | 69 | 6836817 | Customer Interconnection
MTEP22 | West | MidAmerican Energy Company | 21896 | NE 94th Avenue 161-13.2 kV Substation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 6700000 | Reliability improvement and serve load
MTEP22 | West | MidAmerican Energy Company | 21897 | Berwick 161-13.2 kV Substation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 6700000 | To serve growing load.
MTEP22 | East | METC | 21505 | Houghton Lake Interconnection | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 5 | 138 | 6161060 | Consumers Energy has provided notification for a new 138kV substation to be located approximately 12.5 miles west of the METC Bard Rd - Higgins point of interconnection. Houghton Lake station will serve 13.5 MW and 7.9 MVAR of load transferred from the CE Houghton Heights Substation. The new switching station is needed to service the new CE substation.
MTEP22 | West | MidAmerican Energy Company | 23366 | Powell Creek 161-13 kV Substation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 5500000 | Serve new customer load
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21950 | New Timmons 69/12 kV substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 4 MVA | 69 | 5301167 | Build new substation to serve member load
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21956 | New Yellow River 69 kV Sub | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 4 MVA | 69 | 5255244 | New Ind park load
MTEP22 | Central | Duke Energy Corporation | 22246 | New IMPA Frankfort 300W 69/12kV Distribution Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 5018000 | Distribution load growth: wholesale obligation to serve load via IMPA for Frankfort Municipal
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21964 | Upgrade Colfax 138/69/12 kV substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 4 MVA | 69 | 5000000 | Added load in area
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21954 | New Rosebud 69/12kV Sub | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 4947000 | Transfer of load from Old substation
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21961 | New Marco 69/12 kV substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 4 MVA | 69 | 4947000 | Backup of existing load and added load.
MTEP22 | South | Entergy | 23209 | Legend 230 kV New Customer Connection | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 230 | 4250000 | Entergy has received a request from a customer interested in adding new load to a new station on the transmission system.
MTEP22 | Central | Ameren Services Company | 21426 | Reconductor S. Bloomington-W. Washington 138 kV lines (1334 & 1544) | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 4200000 | Customer load
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21962 | New Berthaville 69/12 kV sub | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 4 MVA | 69 | 4200000 | New Berthaville substation needed south of Goodland for new dairy farm and added load in area.
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21955 | Upgrade Fair Oaks 2nd bank 138/69/12 kV transformer | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 4 MVA | 69 | 4176754 | Add second 138/69/12kV 22.4MVA transformer to Fair Oaks substation to handle new load in area
MTEP22 | West | Central Minnesota Municipal Power Agency | 21975 | Blue Earth Light and Water- New Northeast 69/12.47 kV Sub | MN | Other | Reliability | Hidden LG | Keywords: load growth, new load |  |  | 69 | 4100000 | Following a PSS/E AC Contingency Calculation (ACCC) analysis of the Blue Earth Light & Water (BELW) transmission system, numerous voltage violations (< 0.93 per unit) were noted on BELW facilities as a result of a few different contingencies. The analysis included various load and generation forecasts, and these violations were noted in several years and seasons. The Rice St. and West 69/12.47kV substations do not have enough capacity to add additional load growth in the city. With a potential 3.5 MW approximately new load scheduled to come online, there is a need to build a new North East 69/12.47kV substation to accommodate load growth, load transfers, support transmission system voltage, and add reliability to the BELW transmission and distribution systems. The new substation would connect to the existing 69kV transmission system via a 3-way switch and would be designed to include room for future In/Out circuit breakers. | Reliability with load growth driver
MTEP22 | Central | Prairie Power, Inc. | 21748 | Rebuild Barry-E. Hannibal Tap 69 kV line to double circuit | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 3762000 | Provide network service to Barry substation.
MTEP22 | West | ITC Midwest | 21936 | Centerville Cooper Creek 69kV Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 20 MVA | 69 | 3708274 | Load serving, future conversion and retirement of existing Centerville North substation.
MTEP22 | East | METC | 22001 | Westwood 138 kV Interconnection | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 3700000 | Wolverine Power Cooperative requests for a new 138 kV interconnection to METC’s Plum station.
MTEP22 | West | MidAmerican Energy Company | 23516 | Enterprise Way South Substation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 3500000 | Serve new customer load
MTEP22 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 22007 | Rebuid Warrick North 138 kV switching station | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 3500000 | Create new terminal for transmission line to large industrial customer.
MTEP22 | East | Wolverine Power Supply Cooperative, Inc. | 21665 | Day Interconnection | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 3500000 | Interconnection Request
MTEP22 | West | American Transmission Co. LLC | 22987 | Northview SS, DIC, New Substation | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 138 | 3220000 | Other - Load Interconnection
MTEP22 | West | American Transmission Co. LLC | 22988 | Gaston Road SS, DIC, Additional Transformer | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 69 | 3000000 | Load Interconnection
MTEP22 | West | American Transmission Co. LLC | 23007 | Cambria SS, DIC, New Substation | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 69 | 3000000 | Load Interconnection
MTEP22 | West | American Transmission Co. LLC | 23520 | Johnstown SS, DIC, New Substation | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 69 | 3000000 | Other - Load Interconnection
MTEP22 | West | Northern States Power (Xcel Energy) | 21892 | West Shakopee Interconnection | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 3000000 | Needed to accommodate the rapidly developing load growth along the western edge of the City of Shakopee’s territory.
MTEP22 | Central | Duke Energy Corporation | 22212 | Rebuild Morgantown to Samaria Jct 69kV Line | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 2901158 | Transmission Planning identified contingency overload due to Load Growth; Contingency: Bloomington 230 to Needmore Jct. 6949 Line Outage
MTEP22 | West | Great River Energy | 22445 | Cedar 115 kV Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 2773049.09 | Cedar Substation – This is a new site located near the intersection of Cedar Ave and Lakeville Blvd. in Lakeville. DEA has talked to engineering and land rights at GRE about the feasibility as this now has passed city council and DEA is purchasing the land and would likely build out this site in 2023. Load growth within the city limits of Lakeville, between Dodd Boulevard, Flagstaff Avenue, and the area south of the existing Dodd Park substation, are forecasted to exceed the available capacity of neighboring Dodd Park, Vermillion River, and Ritter Park substations. Much of the developable land within Lakeville’s 2040 comprehensive plan is proposed as either low density or low/medium density residential housing. Area adjacent to Cedar Avenue, between County Road 50 and 190th Street West, is proposed to be developed as commercial, mixed use, and residential density at or above medium density housing units. The Cedar substation is required to supply new and existing members within both the Lakeville and Farmington city limits an adequate voltage supply during both normal system configurations. The new Cedar substation is also required to provide an adequate contingency supply to southern circuits of the Dodd Park substation, as well as northern and western feeders leaving the Vermillion River substation. Feeders are proposed to be constructed as part of the new Cedar substation as new loads continue to come into the area surrounding the site; specifically residential and mixed use to the north and largely commercial and industrial to the south of the substation location.
MTEP22 | Central | Ameren Services Company | 18063 | New Mt. Pleasant 345 kV substation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 2600000 | Customer-Driver Request
MTEP22 | East | ITC Transmission | 22013 | ITCT Pole Top Switch Additions/Replacement Program 2023 | MI | Other | Reliability | Hidden LG | Keywords: industrial load, load interconnect |  |  | 138 | 2400000 | The ITCT system has many 120 kV load interconnection taps that do not have pole-top switches installed on either one or both sides of the tap or have switches that are not operable. Without pole-top switches, this reduces the flexibility to isolate faults or planned outages of a section of the line (for repair work or maintenance purposes. As a consequence, all distribution or industrial load that is tapped and served from the line will be out of service along with it until the faulted section can be repaired. Since there are no switches installed at these junctions or the switches are not operable, it is impossible to sectionalize a faulted part of the circuit to restore power to customers while the crew is working on bringing that section of the line back in-service again. The transmission circuits are often long transmission lines which have more exposure to weather related forces (e.g. ice, snow, wind, extreme temperatures, and lightning strikes).
MTEP22 | East | METC | 21984 | METC Pole Top Switch Additions/Replacement Program 2023 | MI | Other | Reliability | Hidden LG | Keywords: industrial load, load interconnect |  |  | 138 | 2400000 | The METC system has many 138 kV load interconnection taps that do not have pole-top switches installed on either one or both sides of the tap or have switches that are not operable. Without pole-top switches, this reduces the flexibility to isolate faults or planned outages of a section of the line (for repair work or maintenance purposes. As a consequence, all distribution or industrial load that is tapped and served from the line will be out of service along with it until the faulted section can be repaired. Since there are no switches installed at these junctions or the switches are not operable, it is impossible to sectionalize a faulted part of the circuit to restore power to customers while the crew is working on bringing that section of the line back in-service again. The transmission circuits are often long transmission lines which have more exposure to weather related forces (e.g. ice, snow, wind, extreme temperatures, and lightning strikes).
MTEP22 | East | METC | 21993 | METC Pole Top Switch Additions/Replacement Program 2024 | MI | Other | Reliability | Hidden LG | Keywords: industrial load, load interconnect |  |  | 138 | 2400000 | The METC system has many 138 kV load interconnection taps that do not have pole-top switches installed on either one or both sides of the tap or have switches that are not operable. Without pole-top switches, this reduces the flexibility to isolate faults or planned outages of a section of the line (for repair work or maintenance purposes. As a consequence, all distribution or industrial load that is tapped and served from the line will be out of service along with it until the faulted section can be repaired. Since there are no switches installed at these junctions or the switches are not operable, it is impossible to sectionalize a faulted part of the circuit to restore power to customers while the crew is working on bringing that section of the line back in-service again. The transmission circuits are often long transmission lines which have more exposure to weather related forces (e.g. ice, snow, wind, extreme temperatures, and lightning strikes).
MTEP22 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 22011 | New Warrick N. - Kaiser 138 kV Line | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 2300000 | New customer
MTEP22 | West | Otter Tail Power Company | 22606 | OTP Jamestown, ND Load Addition | ND | Other | Load Growth | Direct LG | Driver: Load Growth |  | 24 MVA | 115 | 2268000 | The new 115/41.6 kV transformer will serve the existing 41.6 kV load, allowing additional capacity on the 41.6 kV tertiaries of the Jamestown 345/115/41.6 kV transformers to serve the new customer. | OTP EPR project
MTEP22 | East | ITC Transmission | 22016 | 2025 ITCT Customer Interconnections | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 120 | 2000000 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. These projects are strictly in response to customer interconnection requests. They are not being proposed to address any specific ITCT system reliability concerns.
MTEP22 | East | METC | 21995 | 2025 METC Customer Interconnections | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 2000000 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. These projects are strictly in response to customer interconnection requests. They are not being proposed to address any specific ITCT system reliability concerns.
MTEP22 | South | South Mississippi Electric Power Association | 22345 | East Winstonville Delivery Point | MS | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 1862800 | Member has requested a new load delivery point near Winstonville, MS.
MTEP22 | East | METC | 21706 | Mill Creek Interconnection | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 62 | 138 | 1822800 | WPSC has provided a formal interconnection request for transmission service tapped from the Mcgulpin - Riggsville 138kV line. WPSC will construct Mill Creek substation as a 138/13.08 kV distribution station with a single transformer and high-side protection. Mill Creek station will serve 1.62 MW and 0.7 MVAR of new load and 1.39 MW of transferred load from the WPSC Cheboygan Station.
MTEP22 | West | Great River Energy | 20865 | Shamrock 69 kV Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 1709484.43 | Accommodate a second transformer in the near future (~2023). The existing Corcoran substation is locked with roads that are close to the substation and there is no room to accommodate expansions to meet fast growing electric demand in the area.
MTEP22 | Central | Prairie Power, Inc. | 21747 | New Barry 69 kV Substation | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 1600000 | Provide service to new load (Cannibis facility) at Barry Distribution substation.
MTEP22 | West | Central Minnesota Municipal Power Agency | 21974 | Blue Earth Light and Water- West Sub Transformer Replacement | MN | Other | Age and Condition | Hidden LG (Age+LG) | Keywords: load growth |  |  | 69 | 1500000 | Blue Earth Light and Water has a West sub which carries a 10/14 MVA 69/12.47 kV Transformer. The transformer is showing signs of age as it is 32 years old and needs to be replaced because of potential load growth.
MTEP22 | West | MidAmerican Energy Company | 21902 | Anthon Substation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 1500000 | Serve load
MTEP22 | West | Great River Energy | 21829 | South Dayton 115 kV Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth | Y | 23 | 115 | 1485000 | Connexus Energy’s distribution planning group has calculated the 5-year load projection for Connexus Energy substations in Hennepin County, starting with the South Dayton #1 bank being installed in 2023, as well as a projection of the Connexus Energy load south of the river at the end of the current City of Dayton planning time horizon. This is based on the Metro Council’s “2015 System Statement” for the City of Dayton dated 17 SEP 2015, and CE’s understanding of the City of Dayton area that lies within the Connexus Energy service area. Page 4 of this document shows a household count of 4,400 in 2040 vs. 2,200 in 2020, and most of this increase falls within the Connexus Energy service area. The City of Dayton “2040 Future Land Use Draft” shows Commercial, Mixed Use, and Business Park use within the Connexus Energy service further justifying the load projections. In addition, the City of Maple Grove shows that the Hennepin #4 feeder area adjacent to the substation serves commercial property, which has the potential to re-develop to higher load density as it sits on the Highway 610 corridor. Connexus Energy anticipates both the Hennepin and the South Dayton substations to have a strong potential to double their load over the time window between 2023 and 2040, bringing Connexus Energy’s south of the river load to 23 MW. Project Alternatives: Connexus Energy investigated adding a 2nd transformer at Hennepin Substation, but that substation is remote from the growth area and has severely restricted feeder routes, due to the Elm Creek Park Reserve, and cannot adequately serve the growth area. Connexus Energy studied additional river crossings from Energy Park or Daytonport Substations, but the distances are too long and expensive, and the process to construct additional Mississippi River crossings is very complex. The existing Energy Park Substation river crossing has recently been re-built, and it is dedicated to loads south of the river, but it has limited reach into the growth areas. Overall, the distance from source to load on CE’s 12.47 kV system requires a new delivery point situated in the heart of the load growth area
MTEP22 | East | Michigan Public Power Agency | 21761 | Zeeland Riley Transformer Addition | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 3 MVA | 138 | 1465000 | With the voltage conversion of the Wolverine transmission system to 138kV, there should be a focus on maintaining sufficient backup capacity in the 138kV:69kV connection. With the loss of one of the two 138kV:69kV transformers in the 2021 projected load scenario, internal generation would be needed to maintain load levels below rated capacity for the remaining transformer. An additional 83.3MVA 138kV:69kV transformer installed at Riley Substation would provide sufficient capacity for an N-1 contingency through 2035 load projections.
MTEP22 | Central | Duke Energy Corporation | 22207 | New WVPA Hendricks Belle Union 138/12kV Distribution Sub | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 4 MVA | 138 | 1408403 | WVPA distribution load growth
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21957 | Upgrade Oregon 69 kV Sub | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 7 MVA | 69 | 1338591 | Substation needs to supply new load in area.
MTEP22 | West | Central Minnesota Municipal Power Agency | 21973 | Blue Earth Light and Water- Rice Street Transformer Replacement | MN | Other | Age and Condition | Hidden LG (Age+LG) | Keywords: load growth |  |  | 69 | 1250000 | The Rice street transformer is showing signs of age which is 28 years old and needs tp be replaced. Rice Street carries almost 60% of BELW load. | Age & Condition with load growth component
MTEP22 | Central | Hoosier Energy REC, Inc. | 23266 | New HE_AboutBit 115 MVA Load | IN | Other | Load Growth | Direct LG | Driver: Large Industrial |  | 115 MVA | 69 | 1200000 | Hoosier Energy has received a request from a customer to add 115 MVA load to the 69kV transmission system, about 1 mile south of Merom station. An agreement targeting an in-service date of January 2023 was reached between Hoosier Energy and the customer in June 2022. The project is to be constructed prior to the MTEP23 cycle. | 115 MVA industrial load ~1mi from Merom (Hoosier Energy, IN)
MTEP22 | East | METC | 23246 | CE - Riverbend Tap (Saginaw River - Twining 138 kV) | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 25 | 138 | 1160000 | Consumers Energy requested to tap METC's Saginaw-Twining 138 kV line to connect its new Riverbend substation. The new Riverbend substation will serve 4.25 MW load, 1.35 MW of it is being transferred from the existing Bessinger substation (46kV).
MTEP22 | East | METC | 22627 | Day - New WPSC Interconnection | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 1132000 | WPSC interconnection request for transmission service tapped from the Deja Jct. – Derby Jct. section of Eureka – Vestaburg 138kV line. WPSC will construct Day substation as a distribution station with a single transformer and associated high-side protection. Wolverine has submitted the following MTEP project into the portal database for the WPSC owned portion of facilities: Day Interconnection – MTEP21 Target A, project #21665
MTEP22 | East | Wolverine Power Supply Cooperative, Inc. | 21425 | Mills Creek Interconnection | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 1000000 | New interconnection/Load growth
MTEP22 | South | Entergy | 23307 | Flare Hill 230 kV New Customer Substation | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 230 | 980000 | Entergy has received a request from a customer interested in adding new load to a new station on the transmission system.
MTEP22 | West | Great River Energy | 21830 | Shamineau Lake 115 kV Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 792000 | Crow Wing Power has served the southern Motley / Lincoln area from the Ward delivery point for a while and Crow Wing Power is noticing that it is becoming more difficult to maintain end of the line voltage for its customers. The Ward substation is in Todd-Wadena’s service territory and Crow Wing Power must go 6 miles before they enter their own service territory which makes the voltage issue even more challenging. Having a source closer to their load pocket and within their own service territory will lower the miles per feeder, lowering the exposure for each circuit resulting in better reliability. Additionally, the new source will be closer to the growing load pocket and end of the line voltage will be met. The addition of regulators and capacitor banks isn’t viable since the distribution system already has two sets of regulation. The regulators on the feeders from Ward have been working overtime to keep up with the 34.5kV voltage fluctuations.
MTEP22 | West | MidAmerican Energy Company | 21904 | Sioux Center Substation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 600000 | Serve load
MTEP22 | Central | Big Rivers Electric Corporation | 20766 | New Easton Rd 69 kV line | KY | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 500000 | The distribution cooperative is constructing a new delivery point to serve member load.
MTEP22 | West | Minnesota Power (Allete, Inc.) | 21606 | West Cohasset Project | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 500000 | New customer load interconnection to 23 kV system
MTEP22 | West | Great River Energy | 22528 | Matter 69 kV Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 5 | 69 | 402407 | Delano Municipal Utilities (DMU) desires to establish a distribution substation tapping GRE’s DX line to serve about 5 MW peak load and provide a backup service to its existing Delano Muni distribution substation. DMU will be responsible to install a metering package per GRE’s requirement to allow metering data transfer between DMU’s new substation and GRE.
MTEP22 | West | Otter Tail Power Company | 21427 | OTP Max Water Treatment Plant 41.6 kV | ND | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 41.6 | 350000 | A new water treatment plant is interconnecting to OTP's system in Max, ND. This new load addition is driving the need for transmission upgrades in the Max, ND and Parshall, ND 41.6 kV areas.
MTEP23 | Central | Duke Energy Corporation | 23925 | New Slugger 138kV Load | IN | Other | Load Growth | Direct LG | Driver: Large Industrial |  |  | 345 | 123500000 | Large new customer load - early phases from 138 kV, then 345/138 kV as load grows | DEI $123.5M; ISD 12/31/2029; major new industrial customer
MTEP23 | Central | Duke Energy Corporation | 23964 | New Kokomo Fusion Phase 1 - 230/69 kV Sub | IN | Other | Load Growth | Direct LG | Driver: Large Industrial (Stellantis/EV) |  | 110 | 230 | 92073454 | Kokomo Project Fusion - new 230/69 kV substation for large new customer load; (2) 150MVA 230/69 kV transformers, (14) 69 kV breakers | DEI $92.1M; ISD 6/1/2025; likely Stellantis EV manufacturing
MTEP23 | West | MidAmerican Energy Company | 24999 | Southland Expansion & Upgrades | IA | Other | Load Growth | Direct LG | Driver: Large Industrial |  |  | 345 | 58000000 | Expand 345 kV bus at Southland to serve new customer load; new 345 kV line from Overland Trail to Pony Creek | Southland Expansion: 345kV bus expansion for new customer (MEC IA). $58M
MTEP23 | West | ITC Midwest | 24449 | Nevada Area Load Interconnections | IA | Other | Load Growth | Direct LG | Driver: Area Load Growth |  |  | 161 | 56519142.5 | New transmission substations networked to existing 161 kV at Ames, NE Ankeny, Fernald; load interconnections in Ames/Nevada area | ITCM $56.5M; major load interconnection
MTEP23 | West | Otter Tail Power Company | 23806 | OTP Lake Preston, SD Load Addition | SD | Other | Load Growth | Direct LG | Driver: Large Load |  |  | 115 | 42600000 | Serve new customer load in SD by extending 115 kV from Hetland to new Lake Preston 115/34.5 kV; then 45-mi 115 kV to Brookings County 345/115 kV | Lake Preston: new customer load in SD, ~55mi new 115kV line (OTP). $42.6M
MTEP23 | South | Cleco Power LLC | 24415 | Ragely Substation | LA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 40000000
MTEP23 | West | American Transmission Co. LLC | 23913 | Northern Adams County Area Network Improvement Project | WI | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 187 MVA | 69 | 39900000
MTEP23 | South | Entergy Mississippi | 23348 | Grenada Industrial 115 kV: New Station | MS | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 10 | 115 | 32610000
MTEP23 | West | Otter Tail Power Company | 23936 | OTP Milbank, SD Load Addition | SD | Other | Load Growth | Direct LG | Driver: Load Growth + Electrification |  | 9.5 | 115 | 32300000 | Serve new 4.5 MW load at Milbank SD plus 9.5 MW electric boiler conversion; new 12.5-mi 115 kV line; new Milbank 115/12.5 kV substation | Milbank: 9.5MW electric boiler, expand Big Stone 115kV (OTP). $32.3M
MTEP23 | South | Entergy | 24920 | Cole Road 138 kV New Customer Station | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 10 | 138 | 29600000
MTEP23 | South | Entergy | 24134 | Mustang 138 kV New Customer Substation | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 150 | 138 | 28000000
MTEP23 | East | ITC Transmission | 24593 | GM Orion Plant Expansion | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 120 | 25796000
MTEP23 | West | American Transmission Co. LLC | 23915 | Delta County, DIC, Upgrades | MI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 138 | 21000000
MTEP23 | East | ITC Transmission | 22847 | Kings Point - New DTE 120kV Interconnection | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 120 | 20000000
MTEP23 | Central | Ameren Services Company | 23152 | New Copley 138-12 kV Substation | MO | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 20000000
MTEP23 | East | METC | 24673 | Project Hickory Load connection | MI | Other | Other Local Needs | Hidden LG | Keywords: load connection |  |  | 138 | 16623125
MTEP23 | West | American Transmission Co. LLC | 20204 | Load Interconnection Program 2024 | WI,MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 16000000
MTEP23 | Central | Indianapolis Power & Light Company | 23832 | New 138/13.2 Transformer at Thompson Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 40 MVA | 138 | 16000000
MTEP23 | Central | Indianapolis Power & Light Company | 23766 | New IU Health Substation 138 kV | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 40 MVA | 138 | 15000000
MTEP23 | Central | Indianapolis Power & Light Company | 23831 | New Gillette 138 kV Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 40 MVA | 138 | 15000000
MTEP23 | Central | Indianapolis Power & Light Company | 23834 | New Valley Avenue 138 kV Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 40 MVA | 138 | 15000000
MTEP23 | Central | Indianapolis Power & Light Company | 23893 | New Winding Ridge 138 kV Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 40 MVA | 138 | 15000000
MTEP23 | West | Northern States Power (Xcel Energy) | 24315 | Dubay Lake Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 12400000
MTEP23 | West | American Transmission Co. LLC | 24575 | DPC Clearfield Jct Tap, New T-T | WI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 11100000
MTEP23 | Central | Indianapolis Power & Light Company | 24273 | New - 138kV - Airtech Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 20 MVA | 138 | 10700000
MTEP23 | South | Entergy Arkansas | 24938 | Driver - Hybar 230kV: New transmission line | AR | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 230 | 10632090
MTEP23 | South | Entergy | 24152 | Moscow 138 kV Customer Load Addition Project | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 10470000
MTEP23 | West | American Transmission Co. LLC | 24784 | Ellisville SS, DIC, New Substation | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 138 | 10200000
MTEP23 | Central | Indianapolis Power & Light Company | 24293 | New - 138 kV - New Pleasant Acres Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 4 MVA | 138 | 10000000
MTEP23 | West | MidAmerican Energy Company | 23570 | Valley Trail 161 kV Substation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 9500000
MTEP23 | West | Southern Minnesota Municipal Power Agency | 25252 | Fairmont, MN Area 69kV Transmission Expansion | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 8920000
MTEP23 | West | Northern States Power (Xcel Energy) | 23728 | Owen Area Substation | WI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 7854000
MTEP23 | West | American Transmission Co. LLC | 24475 | Tommy's Turnpike DIC, New Sub | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y | 38 MVA | 115 | 7700000
MTEP23 | West | American Transmission Co. LLC | 24373 | Manogue Rd SS DIC, New Substation | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y | 3 MVA | 138 | 7100000
MTEP23 | Central | Duke Energy Corporation | 23871 | New WVPA NSC Lick Creek 69/12kV Sub. | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 4 MVA | 69 | 6923547
MTEP23 | West | Great River Energy | 23763 | Laketown Substation Tap | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 6308542
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 24414 | WPSC Elephant Interconnection (Project 23865 Partial Alternative) | MI | Other | Other Local Needs | Direct LG | Driver: Large Industrial |  | 103-206 | 138 | 6000000 |  | 103MW expanding to 206MW industrial near Mecosta (Consumers Energy/METC)
MTEP23 | West | ITC Midwest | 23511 | Grinnell South 69kV Substation & 20MVAR Cap | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 5637400
MTEP23 | West | MidAmerican Energy Company | 23699 | Gifford Road 161-13.2 kV Substation and 161 kV Line Taps | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 5500000
MTEP23 | West | Northern States Power (Xcel Energy) | 23547 | 21829 - South Dayton Interconnection | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 5000000
MTEP23 | Central | Duke Energy Corporation | 23833 | New Edinburgh Industrial Park 69/12kV sub | IN | Other | Reliability | Hidden LG | Driver: Industrial Park |  | 20 MVA | 69 | 4570000 | DEI to construct high-side and loop 69 kV lines into new IMPA-owned Edinburgh Industrial Park substation; one 69/12 kV 20MVA transformer
MTEP23 | West | ITC Midwest | 23684 | Kittyhawk 69kV Substation Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 3902741
MTEP23 | West | ITC Midwest | 24740 | Commercial (JCE) 69 kV Substation | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 3801869
MTEP23 | South | East Texas Electric Cooperative Inc. | 24460 | Coldspring Load Addition | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 2 | 138 | 3740960
MTEP23 | West | ITC Midwest | 23636 | ITCM Customer Interconnects (short lead time) 2025 | IA,MN,IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 3600000
MTEP23 | West | Otter Tail Power Company | 25256 | OTP Jamestown, ND Load Addition #2 | ND | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 3250000
MTEP23 | Central | Duke Energy Corporation | 23969 | New Williamsport 69/12kV Sub | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 4 MVA | 69 | 3152000
MTEP23 | West | Montana-Dakota Utilities Company | 23633 | Ellendale load addition | ND | Other | Load Growth | Direct LG | Driver: Data Center | Y | 180 | 34.5 | 3060359.76 | MDU new customer requesting service at Ellendale ND for total demand of 180 MW; served from existing Ellendale 2 transformer 34.5 kV tertiary | Ellendale: new 180MW customer (MDU ND). $3M. Precursor to data center projects
MTEP23 | West | American Transmission Co. LLC | 24473 | Rock River SS, DIC, Additional Transformer | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 138 | 3000000
MTEP23 | West | Great River Energy | 23761 | NW Litchfield Substation Tap | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 2969551
MTEP23 | West | Minnesota Power (Allete, Inc.) | 22885 | Brainerd Crypto | MN | Other | Load Growth | Direct LG | Driver: Crypto Mining |  | 70 | 115 | 2750000 | Mitigation for 70 MW cryptocurrency mining load at Brainerd 115 kV bus; second 20 MVAR capacitor bank and thermal upgrade of Brainerd-Riverton 115 kV line | Cryptocurrency mining 70 MW load at Brainerd 115 kV (Minnesota Power). EPR project
MTEP23 | West | American Transmission Co. LLC | 24783 | Hodag SS, DIC, Add Additional Transformer | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 115 | 2700000
MTEP23 | East | ITC Transmission | 23947 | 2026 ITCT Customer Interconnections | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 120 | 2500000
MTEP23 | West | Cedar Falls Utilities | 23993 | Streeter-Wida Rebuild | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 2000000
MTEP23 | West | Otter Tail Power Company | 23896 | OTP Devils Lake, ND 115 kV Delivery | ND | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 1550000
MTEP23 | Central | Duke Energy Corporation | 23968 | New Greensfork East 69/12kV Sub | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 4 MVA | 69 | 1440000
MTEP23 | West | Missouri River Energy Services (MRET) | 24232 | ALP SE Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 1358000
MTEP23 | West | Great River Energy | 23802 | West Otsego Substation Tap | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 1283329
MTEP23 | West | Otter Tail Power Company | 23129 | OTP Casselton 115 kV Capacitor Addition | ND | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 1200000
MTEP23 | Central | Big Rivers Electric Corporation | 19007 | Upgrade Kansas 69 kV line | KY | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 900000
MTEP23 | Central | Ameren Services Company | 23286 | New [PPI] Paragon 138 kV substation | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 900000
MTEP23 | West | Northern States Power (Xcel Energy) | 23514 | Sauk Centre North Interconnection | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 800000
MTEP23 | West | MidAmerican Energy Company | 23687 | Storm Lake Industrial 69 kV Line Taps | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 800000
MTEP23 | South | South Mississippi Electric Power Association | 23820 | Gloster 13.8kV Delivery Point | MS | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 483800
MTEP23 | Central | Duke Energy Corporation | 23863 | Upgrade Cayuga to Nucor 34501 Line Terminal 345 kV | IN | BRP |  | Hidden LG (BRP) | Keywords: nucor |  |  | 345 | 320000
MTEP23 | West | Great River Energy | 23819 | Eidswold Substation Tap | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 207813.44
MTEP23 | South | Arkansas Electric Coopertive Corporation | 24192 | UIG | AR | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 20 | 0
MTEP23 | West | Montana-Dakota Utilities Company | 24978 | Tatanka Load Addition | SD,ND | Other | Load Growth | Direct LG | Driver: Large Industrial |  | 100 | 230 |  | MDU serving 100 MW of load at Tatanka Wind Farm collector substation off Tatanka South | Tatanka: 100MW load at wind farm collector sub (MDU). $0
MTEP24 | South | ENTERGY SERVICES, LLC. | 25432 | Cypress to Legend 500 kV line | TX | BRP |  | Hidden LG (BRP) | Driver: Load Growth (BRP) |  |  | 500 | 405900001 | Cypress to Legend 500 kV line; selected because superior performance under future load growth; P3 overloads | ETI BRP $406M; load growth drove selection over alternatives
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50138 | Dodge County, DIC, New Substation | WI | Other | Load Growth | Direct LG | Driver: Data Center/DIC Campus | Y |  | 138 | 161000000 | Dodge County DIC New Substation for Data Innovation Campus | Dodge County Manhattan: new 138kV sub near Beaver Dam (ATC WI). $161M
MTEP24 | South | ENTERGY MISSISSIPPI, LLC. | 25215 | Andes 500/230 kV Substation | MS | Other | Load Growth | Direct LG | Driver: Large Load |  | 720 MVA | 500 | 158000005 | Andes 500/230 kV Substation; large load EPR | EML EPR $158M
MTEP24 | South | ENTERGY ARKANSAS, LLC | 50093 | Galet 500/230kV New Substation | AR | Other | Load Growth | Direct LG | Driver: Load Growth |  | 1200 MVA | 500 | 142000000 | Galet 500/230 kV New Substation for load growth | Galet 500/230kV: 2x1200 MVA autotransformers, new customer (EAL AR). $142M
MTEP24 | South | ENTERGY SERVICES, LLC. | 24958 | Sandling 230 kV Customer Load Addition Project | TX | Other | Load Growth | Direct LG | Driver: Large Industrial |  |  | 230 | 114200000 | Sandling 230 kV Customer Load Addition; large industrial load | New industrial customer near Port Arthur TX. Sandling 230 kV. $114M
MTEP24 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 50089 | Aetna Synchronous Condenser | IN | Other | Local Reliability | Hidden LG | Driver: Load Growth (Voltage Support) |  |  | 138 | 91000000 | Synchronous condenser for voltage support driven by EPR load growth | Central region EPR $91M
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25299 | Racine County, DIC, Nimbus Substation | WI | Other | Load Growth | Direct LG | Driver: Data Center/DIC Campus | Y |  | 138 | 89000000 | Racine County Data Innovation Campus Nimbus Substation; EPR | Racine County Nimbus: new 138/24.9kV BAAH sub (ATC WI). $89M. Precursor to DIC campus
MTEP24 | South | ENTERGY MISSISSIPPI, LLC. | 25214 | Virlilia 230 kV Substation | MS | Other | Load Growth | Direct LG | Driver: Large Load |  | 150 MVA | 230 | 79500003 | Virlilia 230 kV Substation; large load EPR | EML EPR $80M
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 24274 | New - 138 kV Maloney-Reservoir Loop | IN | Other | Load Growth | Direct LG | Driver: Load Growth |  |  | 138 | 71400000 |  | Maloney-Reservoir Loop: 138kV loop with 2 new subs for growing customer load (IPL IN). $71.4M
MTEP24 | West | ITC MIDWEST | 50106 | Big Cedar Interconnection | IA | Other | Load Growth | Direct LG | Driver: Large Industrial |  |  | 345 | 63743317 | Big Cedar Interconnection - large new load in Cedar Rapids IA area | Big Cedar Load Expansion Phase 2: new 345kV switching station + 2nd 345kV line (ITCM). $64M
MTEP24 | Central | HOOSIER ENERGY | 25350 | New Waynesville 345kV Station | IN | Other | Local Reliability | Hidden LG | Driver: Load Growth + Reliability |  |  | 345 | 58160000 | New Waynesville 345kV Station for load growth and reliability | Labeled Local Reliability but desc says "support load growth and reliability in the Walesboro Area"
MTEP24 | East | METC | 50038 | Project Phoenix-Husky Substation | MI | Other | Local Needs | Direct LG | Driver: Large Load |  |  | 345 | 50252000 | Project Phoenix-Husky Substation; large new load | METC EPR $50M
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 24778 | Grant County, DIC, New Substation | WI | Other | Load Growth | Direct LG | Driver: Data Center/DIC Campus | Y |  | 69 | 50100000 | Grant County DIC New Substation for Data Innovation Campus | Grant County DIC: new load interconnection in SW Wisconsin. $50M
MTEP24 | South | ENTERGY MISSISSIPPI, LLC. | 25229 | Costas 230 kV Substation | MS | Other | Load Growth | Direct LG | Driver: Large Load |  | 150 MVA | 230 | 44500002 | Costas 230 kV Substation; large load EPR | EML EPR $45M
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25526 | Terre Haute Project Tonic Water | IN | Other | Load Growth | Direct LG | Driver: Large Industrial |  | 130 | 138 | 35777500 |  | Project Tonic Water: 130MW north of Vigo Co Industrial Park, Terre Haute
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25372 | New 345-138 kV Monrovia Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 500 MVA | 345 | 35348000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25507 | Umore Park 115 kV Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 35000000
MTEP24 | East | METC | 50151 | Sphinx 138 kV Station | MI | Other | Load Growth | Direct LG | Driver: Load Growth |  | 255 MVA | 138 | 32810000 | Sphinx 138 kV Station; new load station | METC EPR $33M
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25335 | Add new Thorntown 69kV ckt and rebuild 6943 ckt | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 31200000
MTEP24 | South | CLECO POWER LLC | 50011 | WeeksIsland Sub | LA | Other | Local Reliability | Hidden LG | Driver: New Industrial Load |  |  | 138 | 21224064 | New industrial load requiring substation at Weeks Island | Labeled Local Reliability but desc says "serve a new industrial load". Tap Ivanhoe-Bayou Warehouse 138kV for industrial customer
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25428 | New Shenandoah Substation and 69 kV lines | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 19100000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 22911 | Load Interconnection Program 2025 | MI; WI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 19000000
MTEP24 | West | MONTANA-DAKOTA UTILITIES CO. | 50037 | Ellendale load 2 addition | ND | Other | Load Growth | Direct LG | Driver: Data Center | Y | 225 | 230 | 16776939 | Ellendale load 2 addition; 225MW data center EPR | 2nd data center load at Ellendale ND, 225 MW total. New Data Center Sub with 230 kV line from 345 kV sub
MTEP24 | Central | AMEREN ILLINOIS | 25153 | New Moyer 138 kV Ring Bus for One Earth Energy Interconnection | IL | Other | Load Growth | Direct LG | Driver: Ethanol Plant |  | 30 | 138 | 16700000 |  | One Earth Energy 30MW ethanol plant interconnection (AmerenIL)
MTEP24 | South | ENTERGY ARKANSAS, LLC | 50013 | Grand Prairie 115kV: New substation | AR | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 3 MVA | 115 | 15626062
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25461 | Johnson Creek - Maffitt Lake 161 kV line | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 15300000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25367 | New 138 kV Hawthorne Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 40 MVA | 138 | 15000000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25332 | WVPA Pike 69kV Line Rebuild | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 15000000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25525 | Kokomo Project Fusion Phase 2 - 230/69kV Sub | IN | Other | Load Growth | Direct LG | Driver: Battery Mfg (StarPlus) |  | 155 | 230 | 14000000 |  | StarPlus Energy battery mfg Phase 2: 155MW in Kokomo IN
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25448 | Browns Woods Substation and 161 kV lines | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 13400000
MTEP24 | West | MONTANA-DAKOTA UTILITIES CO. | 50152 | Ellendale load 3 addition | ND | Other | Load Growth | Direct LG | Driver: Data Center | Y | 125 | 230 | 12575738 | Ellendale load 3 addition; 125MW data center EPR | 3rd data center load at Ellendale ND, 125 MW. Served from Ellendale Data Center Sub (MTEP 50037)
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25347 | WVPA Lebanon Industrial 69/12kV Sub | IN | Other | Load Growth | Direct LG | Driver: Pharmaceutical (Eli Lilly) |  |  | 69 | 12215000 |  | WVPA Lebanon Industrial sub for new Eli Lilly facility
MTEP24 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 50174 | New Customer X 138kV Substation | IN | Other | Load Growth | Direct LG | Driver: Large Load |  | 200 | 138 | 12000000 | New Customer X 138kV Substation; new large customer EPR | 200MW Customer X on Roxana-StatelineB circuit (NIPSCO)
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25226 | Union Townline, DIC, Sub Expansion | WI | Other | Load Growth | Direct LG | Driver: Data Center/DIC Campus | Y |  | 69 | 11600000 | Union Townline DIC Sub Expansion | ATC $11.6M
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25220 | Cuba City South, DIC, Sub Expansion | WI | Other | Load Growth | Direct LG | Driver: Data Center/DIC Campus | Y |  | 69 | 11000000 | Cuba City South DIC Sub Expansion | ATC $11M
MTEP24 | South | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | 50164 | Woodberry Load Addition | AR | Other | Load Growth | Direct LG | Driver: Load Growth |  | 26 | 69 | 10200000 | Woodberry Load Addition EPR | AECC EPR $10M
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25331 | WVPA Blacketor 69/12kV Sub | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 8753000
MTEP24 | West | OTTER TAIL POWER COMPANY | 16289 | Bemidji 115/12.5 kV Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 37 MVA | 115 | 8000000
MTEP24 | South | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | 50094 | Northstar | AR | Other | Load Growth | Direct LG | Driver: Load Growth |  | 20 MVA | 115 | 7000000 | Northstar load growth EPR | AECC EPR $7M
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25424 | NE 6th St Substation and 161 kV line taps | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 6500000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25460 | Southridge Substation and 161 kV line taps | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 6500000
MTEP24 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25520 | South Lucedale 69kV Delivery Point | MS | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 6477100
MTEP24 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25489 | North Lucedale 69kV Delivery Point | MS | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 6399100
MTEP24 | Central | AMEREN ILLINOIS | 24034 | Coffeen N. XFMR 2 Replacement | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 700 MVA | 345 | 6000000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 50029 | SE Soteria Add 161 kV Breakers | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 6000000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 50030 | Johnson Creek Add 161 kV Breakers | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 6000000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 24555 | New - Waverly - 138 kV Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 5 MVA | 138 | 6000000
MTEP24 | West | ITC MIDWEST | 25308 | ITCM Leon Rodeo 69 kV Substation Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 4860742
MTEP24 | South | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | 50099 | Lewisville West Capacity Increase | AR | Other | Load Growth | Direct LG | Driver: Load Growth |  | 100 MVA | 115 | 4500000 | Lewisville West Capacity Increase EPR | AECC EPR $5M
MTEP24 | West | ITC MIDWEST | 25188 | ITCM Boone South 69 kV Substation Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 33 MVA | 69 | 4363663
MTEP24 | Central | AMEREN MISSOURI | 50057 | Vessel Bulk Sub - Add 2nd 138/34 kV Transformer | MO | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 84 MVA | 138 | 4000000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 50031 | Maffitt Lake Add 161 kV Breakers | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 4000000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25147 | Mead Johnson 69/12kV Transformer Replacement | IN | Other | Age and Condition | Hidden LG (Age+LG) | Driver: Load Growth + Age |  |  | 69 | 3800000 | Mead Johnson transformer replacement driven by load growth and age | Labeled Age&Condition but desc adds "and to support local load growth"
MTEP24 | West | ITC MIDWEST | 25211 | ITCM Customer Interconnects with short lead time 2026 | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 3750000
MTEP24 | West | MONTANA-DAKOTA UTILITIES CO. | 25301 | Leola load addition | SD | Other | Load Growth | Direct LG | Driver: Load Growth |  | 50 | 115 | 3600000 | Leola load addition EPR | MDU EPR $4M
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25309 | Substation Technology Package #2 - 2024 | WI | Other | Local Needs | Hidden LG | Keywords: data center | Y |  | 0 | 3600000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25333 | Westfield 156th St 69/12kV Sub | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 3442000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 50014 | West Grand Add 161 kV Line Breakers | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 3000000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50136 | Baraboo SS, DIC, Substation Relocation | WI | Other | Load Growth | Direct LG | Driver: Data Center/DIC Campus | Y |  | 69 | 3000000 | Baraboo SS DIC Substation Relocation | ATC $3M
MTEP24 | West | ITC MIDWEST | 25307 | ITCM State Center Rural 69 kV Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 5 MVA | 69 | 2910514
MTEP24 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25416 | Lucedale 69kV Switching Station | MS | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 2860000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50091 | Milwaukee County, New DIC | WI | Other | Load Growth | Direct LG | Driver: Data Center/DIC Campus | Y |  | 138 | 2600000 | Milwaukee County New DIC expansion | ATC $2.6M
MTEP24 | Central | AMEREN MISSOURI | 50086 | Load addition at Montgomery 161 kV Substation | MO | Other | Load Growth | Direct LG | Driver: Data Center | Y | 250 | 161 | 2500000 | Load addition at Montgomery 161 kV Substation; 250MW data center EPR | 250 MW datacenter at Montgomery 161 kV Substation (Ameren Missouri)
MTEP24 | East | METC | 25277 | METC Customer Interconnections - 2027 | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 2500000
MTEP24 | East | ITC | 25364 | ITCT Customer Interconnections - 2027 | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 2500000
MTEP24 | West | ITC MIDWEST | 25253 | ITCM Flint Ridge Control Enclosure & 69 kV Tie Breaker Addition | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 33 MVA | 69 | 2160171
MTEP24 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25501 | County Line 115kV Delivery Point | MS | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 2160000
MTEP24 | West | ITC MIDWEST | 25306 | ITCM Burlington 4th Street Control Enclosure & 69 kV Tie Breaker Addition | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 33 MVA | 69 | 1984333
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25411 | Second 69 kV Line into Rock Valley Town Substation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 1600000
MTEP24 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 25290 | Sprott 69/12kV Substation | MO | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 1200000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 50068 | HE Taylorsville 69/12kV Sub | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 3 | 69 | 900000
MTEP24 | West | GREAT RIVER ENERGY | 50101 | Hodges Substation Tap | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 750116
MTEP24 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25540 | State Line 69kV Delivery Point | MS | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 725000
MTEP24 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25419 | Hermanville 115kV Delivery Point | MS | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 700000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25377 | DPC North Wal Interconnection | WI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 500000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50539 | Cargas 500 kV and Smalling 500-230 kV stations | LA | Other | Load Growth | Direct LG | Driver: Large Load (EPR) |  | 500 MVA | 500 | 1210000001 | Entergy received request from customer adding new load in Holly Ridge LA. Two new 500/230kV stations, 27mi new 500kV, four 1500MVA 500/230kV autotransformers, eight 230kV lines | Cargas/Smalling 500-230kV: $1.21B for new customer in Holly Ridge LA
MTEP25 | South | ENTERGY SERVICES, LLC. | 50350 | Babel to Webre 500 kV New Line | LA | BRP |  | Hidden LG (BRP) | Keywords: load growth |  |  | 500 | 1066000000 | Loss of the 500 kV path between Hartburg and Webre along with generation in South Louisiana overloads multiple facilities during high west to east or east to west transfers across the southern portion of Entergy’s system. This project also increases the load serving capability for the Amite South region of the Entergy service territory which is critical to maintaining reliability while accommodating expected load growth. The project will also increase operational flexibility and enhance resiliency by creating a geographically diverse EHV transmission path which is especially important during extreme weather events. | BRP: Babel-Webre 500kV new line ($1.066B). Loss of 500kV path thermal overloads in South LA
MTEP25 | South | ENTERGY SERVICES, LLC. | 50540 | Sarepta to Mount Olive 500 kV Project | LA | BRP |  | Hidden LG (BRP) | Driver: Large Industrial (BRP) |  |  | 500 | 470100002 | Entergy received a request from a customer adding new load in Holly Ridge, LA. These facilities were identified as needed to maintain NERC compliance during Entergy’s studies. Entergy is observing the following thermal violations which require the need for this project: • P6 loss of Sterlington to El Dorado 500 kV and MT Olive to El Dorado 500 kV lines. o Marion – Huttig 115 kV line o Marion – Sterlington 115 kV line o El Dorado E – T.E.P S/F 115 kV line o El Dorado E – El Dorado 115 kV line o J1612 – Strong 115 kV line o J1612 – Huttig115 kV line o El Dorado D – El Dorado M 115 kV line o T.E.P S/F – Strong 115 kV line o Vienna – Bernice 115 kV line o Sarepta – Minden 115 kV line o Minden LG – Minden LA 115 kV line o Bernice – Junction City 115 kV line o Upland – Junction City 115 kV line o Parnell – Newell 115 kV line o Newell – Upland 115 kV line o Wyatt – Parnell 115 kV line o El Dorado Mon – El Dorado | BRP: Sarepta-Mt Olive 500kV ($470M) mitigating thermal violations from Cargas load in Holly Ridge LA
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 24919 | Mill Road – Granville Project | WI | BRP |  | Hidden LG (BRP) | Driver: Data Center/DIC Campus (BRP) | Y |  | 345 | 423705000 | Reliability. Address MTEP and TYA reliability P6 (N-1-1) issues, future sensitivities identify N-1 issues. Significant market congestion has been an issue for many years and is expected to become more severe with load interconnections and generation related changes, Portions of the existing 138 kV facilities are within the Asset Life Cycle Program window to replace, Portions of the corridor (line 3453, 3443 and 5041) are required to be rebuilt due to Generator Interconnection queue study limitations. | ATC BRP; Racine DIC CAP $424M
MTEP25 | West | ITC MIDWEST | 50157 | Big Cedar Load Expansion | IA | Other | Load Growth | Direct LG | Driver: Large Industrial (EPR) |  |  | 345 | 380549625 | In order to reliably serve the two new requested loads, upgrades on the ITC Midwest transmission system are required. These upgrades include expansion of the Big Cedar Switching Station, an additional 345 kV line/source into the Cedar Rapids area, and reactive power compensation at Big Cedar to support system contingent voltages. In addition to the upgrades included here the Morgan Valley - Twinkle (Marshalltown) Tranche 1 LRTP project and Beverly - Sub 92 Tranche 1 LRTP project are also required to ensure system reliability with these load additions. | Big Cedar Load Expansion: two new loads in Cedar Rapids area, 345kV upgrade. $381M. EPR
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50628 | Upgrade LEAP Transmission Network Phase 2 | IN | Other | Load Growth | Direct LG | Driver: Data Center | Y | 600 | 345 | 345000000 | Additional load committed to LEAP District. Total demand estimated 1200MW. 600MW increase. New 345kV ring bus, 12mi 345kV, new 345/138kV sub, 15mi 345kV. | LEAP Phase 2: additional 600 MW data center load. Total LEAP ecosystem ~$852M+
MTEP25 | South | ENTERGY MISSISSIPPI, LLC. | 50602 | Green Acres 500/230 kV New Substation | MS | Other | Load Growth | Direct LG | Driver: Large Load |  | 1200 MVA | 500 | 312000002 | Entergy received a request from a customer adding new load in Madison County, MS. Upgrades, including this facility, have been identified as needed due to the load growth. | Green Acres 500/230kV: $312M for new customer in Madison County MS
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50167 | Racine County, DIC, Jupiter Substation | WI | Other | Load Growth | Direct LG | Driver: Data Center/DIC Campus | Y | 500 MVA | 345 | 295000000 | Racine County DIC Jupiter Substation; part of Racine DIC CAP | Racine County Jupiter Sub: 4x500MVA 345/138kV transformers, STATCOM. Part of Data Innovation Campus
MTEP25 | South | ENTERGY SERVICES, LLC. | 50671 | RiverPlex 500-230 kV Station | LA | Other | Load Growth | Direct LG | Driver: Large Load (EPR) |  | 1200 MVA | 500 | 284000000 | Entergy received a request from a customer adding new load near Donaldsonville, LA. Upgrades, including this facility, have been identified as needed due to the load growth. | RiverPlex 500-230kV: $284M for new customer near Donaldsonville LA
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50208 | New LEAP Transmission Network | IN | Other | Load Growth | Direct LG | Driver: Data Center | Y | 600 | 345 | 222200000 | Large customer committed to LEAP District, Innovation district west of Lebanon IN. Data center customer ramping to 600 MW total demand. New 345/138kV sub, ~10mi double-circuit 345kV, two 138kV stations, ~25mi 138kV. | LEAP Innovation District data center, Lebanon IN. 600 MW Phase 1. Total district demand 1200 MW (Phase 1+2)
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50543 | Racine County, DIC, Cosmos Substation | WI | Other | Load Growth | Direct LG | Driver: Data Center/DIC Campus | Y | 500 MVA | 345 | 195000000 | Racine County DIC Cosmos Substation; DIC campus project | Racine County Cosmos Sub: 4x500MVA 345/138kV transformers. Part of DIC cluster ~$850M+
MTEP25 | South | ENTERGY MISSISSIPPI, LLC. | 50600 | Oak Bend 230 kV station | MS | Other | Load Growth | Direct LG | Driver: Large Load |  | 150 MVA | 500 | 150000002 | Entergy received a request from a customer adding new load in Warren County, MS. Upgrades, including this facility, have been identified as needed due to the load growth. | Oak Bend 230kV: $150M for new customer in Warren County MS
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50168 | Racine County Western Feed Transmission Line Project | WI | Other | Load Growth | Direct LG | Driver: Data Center/DIC Campus | Y |  | 345 | 124000000 | Racine County Western Feed Transmission Line; part of Racine DIC CAP | Racine County Western Feed: two new 345kV double circuit lines for DIC campus
MTEP25 | West | GREAT RIVER ENERGY | 50481 | LG - 2 | MN | Other | Load Growth | Direct LG | Driver: Large Load |  |  | 345 | 120000000 | Load growth in area exceeds capacity of existing substations and requires installation of new load serving distribution substations in the area. | GRE LG-2: $120M for load growth exceeding capacity in MN area
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50166 | Racine County, DIC, Mount Pleasant Substation Expansion | WI | Other | Load Growth | Direct LG | Driver: Data Center/DIC Campus | Y | 500 MVA | 345 | 117000000 | Racine County DIC Mount Pleasant Substation Expansion; part of Racine DIC CAP | Racine County Mt Pleasant expansion: 500MVA 345/138kV transformer, STATCOM for DIC campus
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50718 | Rebuild Cayuga to Nucor 345 kV line | IN | BRP |  | Hidden LG (BRP) | Driver: Data Center (BRP) | Y |  | 345 | 95529061 | This project is driven by recent EPR submission of Project LEAP load, and future adjacent loads. | BRP: Rebuild Cayuga-Nucor 345kV driven by LEAP data center EPR submission
MTEP25 | Central | AMEREN ILLINOIS | 50190 | New Peru-Princeton 138 kV line | IL | Other | Load Growth | Direct LG | Driver: Large Load (EPR) |  |  | 138 | 90000000 | Rebuild Princeton sub, new 4-position 138kV sub near Peru, new 23mi 138kV line; submitted through EPR | AMIL EPR $90M
MTEP25 | South | ENTERGY SERVICES, LLC. | 50199 | Rhodair 230 kV New Substation and Transmission Lines | TX | Other | Load Growth | Direct LG | Driver: Large Industrial (EPR) |  |  | 230 | 85000000 | Entergy has received requests from customers adding new load in the Port Arthur, TX area. Upgrades, including this facility, have been identified as needed due to the load growth. | ETI EPR $85M
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50165 | Racine County, DIC, Stratus Substation | WI | Other | Load Growth | Direct LG | Driver: Data Center/DIC Campus | Y |  | 138 | 68500000 | Racine County DIC Stratus Substation; part of Racine County Area 2&3 DIC EPR CAP | Racine County Stratus Sub: new 138/24.9kV BAAH sub for DIC campus
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50725 | Rebuild Kokomo HP to Tipton West to Cammack Rd Jct 230kV | IN | BRP |  | Hidden LG (BRP) | Driver: Data Center (BRP) | Y |  | 230 | 65500000 | This project is driven by recent EPR submission of Project LEAP load, and future adjacent loads. | BRP: Rebuild Kokomo-Tipton-Cammack 230kV driven by LEAP data center EPR
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50445 | Sioux Falls 115kV Conversion | SD | Other | Load Growth | Direct LG | Driver: Area Load Growth |  |  | 115 | 60000000 | conversion of the 69kV system from West Sioux Falls-Lincoln-Lawrence to 115kV addresses voltage concerns and overloading associated with future load growth. Line 0730 is at end of life. | Sioux Falls 115kV conversion: voltage concerns from future load growth + end-of-life line
MTEP25 | South | ENTERGY SERVICES, LLC. | 50546 | Bluepoint 230 kV New Substation and line Cut-ins | LA | Other | Load Growth | Direct LG | Driver: Load Growth |  | 150 MVA | 230 | 59600000 | Entergy received a request from a customer adding new load near Donaldsonville, LA. Upgrades, including this facility, have been identified as needed due to the load growth. | ELL $59.6M
MTEP25 | South | ENTERGY SERVICES, LLC. | 50196 | Admiral 138 kV New Substation and Transmission Line | LA | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 67 MVA | 138 | 54400001 | Entergy received a request from a customer adding new load near New Iberia, LA. Entergy is proposing to construct a new 138 kV substation name Admiral that will be cut in on the existing Kirk to Moril 138 kV line to serve the new load.
MTEP25 | South | ENTERGY SERVICES, LLC. | 50528 | Benoit 230 kV Station | LA | Other | Load Growth | Direct LG | Driver: Load Growth |  |  | 230 | 51800001 | Entergy received a request from a customer adding new load south of Lake Charles, LA. Upgrades, including this facility, have been identified as needed due to the load growth. The project is being submitted after the September 2024 cutoff for inclusion into MTEP25. | ELL $51.8M
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50719 | Rebuild Nucor to Wolf Creek 345 kV line | IN | BRP |  | Hidden LG (BRP) | Driver: Data Center (BRP) | Y |  | 345 | 49000000 | This project is driven by recent EPR submission of Project LEAP load, and future adjacent loads. | BRP driven by LEAP data center EPR. Rebuild Nucor to Wolf Creek 345kV
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50691 | LEAP Phase 2 EPR Mitigations | IN | BRP |  | Hidden LG (BRP) | Driver: Data Center (BRP) | Y |  | 345 | 45000000 | Reactive and thermal project mitigations for LEAP Phase 2 area large load | BRP: Reactive/thermal mitigations for LEAP Phase 2 (50208) data center load
MTEP25 | South | ENTERGY MISSISSIPPI, LLC. | 50601 | Andes 230 kV Expansion | MS | Other | Load Growth | Direct LG | Driver: Large Load |  |  | 230 | 40000000 | Entergy received a request from a customer adding new load in Madison County, MS. Upgrades, including this facility, have been identified as needed due to the load growth. | EML $40M
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50722 | New Pond Creek 345 : 138 kV Substation | IN | BRP |  | Hidden LG (BRP) | Driver: Data Center (BRP) | Y |  | 345 | 40000000 | New 345 : 138 kV substation in Pike County, Indiana to address thermal overloads at Petersburg substation | IPL BRP; LEAP 2 CAP $40M; Pike County IN
MTEP25 | Central | AMEREN MISSOURI | 50617 | New 345 kV Lumberjack substation for Load Connection | MO | Other | Load Growth | Direct LG | Driver: Load Growth (EPR) |  |  | 345 | 38500000 | New 345 kV Lumberjack Substation for Load Connection | AMMO EPR $38.5M
MTEP25 | South | ENTERGY SERVICES, LLC. | 50608 | Riparian 115 kV Station | LA | Other | Load Growth | Direct LG | Driver: Load Growth (EPR) |  |  | 115 | 38200000 | Entergy received a request from a customer adding new load in Point Celeste, LA. This facility was identified as needed due to the load growth. | ELL EPR $38.2M
MTEP25 | Central | HOOSIER ENERGY | 50698 | New Scotland 345/69kV Substation | IN | Other | Load Growth | Direct LG | Driver: Data Center (supporting) | Y | 20 | 345 | 38000000 | By late 2029, Hoosier Energy is projecting 20 MW of load growth in the Scotland, IN area. The existing 69kV transmission infrastructure cannot serve the additional load due to thermal and voltage constraints. | New Scotland 345/69kV Sub for 20MW load growth projection in Scotland IN area (HE)
MTEP25 | South | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | 50191 | Beebe North 115kV SS - Nelson 115kV SS | AR | BRP |  | Hidden LG (BRP) | Driver: Area Load Growth (BRP) |  |  | 115 | 37000000 | This project is needed to support voltage and improve the reliability of the Member Coop's system caused by normal load growth in the area. | BRP driven by normal load growth. System Need: "support voltage and improve reliability caused by normal load growth"
MTEP25 | South | ENTERGY ARKANSAS, LLC | 50541 | El Dorado 500/345kV Autotransformer Upgrade | AR | BRP |  | Hidden LG (BRP) | Driver: Large Industrial (BRP) |  |  | 500 | 35725000 | These facilities were identified as needed to maintain NERC compliance during Entergy’s studies with the addition of the Mount Olive to Sarepta 500 kV project. This project is being submitted as an EPR due to the long lead time of Autotransformers and the timing of the submittal being after the September 2024 cutoff for inclusion into MTEP25. | EAL BRP $36M; mitigates Cargas violations
MTEP25 | Central | AMEREN MISSOURI | 50256 | New Tibbe 138/34.5 kV Substation | MO | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 33000000 | Load growth
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50286 | Lebanon Industrial 2nd 69kV Source | IN | Other | Local Reliability | Hidden LG | Driver: Pharmaceutical (Eli Lilly) |  |  | 69 | 30311869 | Lebanon Industrial 2nd 69kV Source; near LEAP district | DEI $30M; likely Eli Lilly manufacturing
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50349 | Crane Naval Base load expansion | IN | Other | Load Growth | Direct LG | Driver: Federal/Military |  | 100 MVA | 138 | 28966000 | Crane Naval Base Load Expansion; federal military facility | Crane Naval Base load expansion with new 138/69kV transformer and 69kV line
MTEP25 | West | GREAT RIVER ENERGY | 50482 | LG - 3 | MN | Other | Load Growth | Direct LG | Driver: Large Load |  |  | 115 | 25000000 | Load growth in area exceeds capacity of existing substations and requires installation of new load serving distribution substations in the area. | GRE $25M
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50440 | West Maple Grove Substation | MN | Other | Load Growth | Direct LG | Driver: Area Load Growth |  |  | 115 | 25000000 | New substation needed in the NW Maple Grove area due to substantial load growth in area | Xcel/NSP $25M
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50280 | New Neuron - Lafayette 27MW load | IN | Other | Load Growth | Direct LG | Driver: Large Industrial |  | 27 | 138 | 24970000 | New Neuron - Lafayette; industrial load addition 27 MW | Project Neuron: 27MW new customer in Lafayette (DEI)
MTEP25 | South | ENTERGY SERVICES, LLC. | 50675 | Cove Ridge 138 kV Station | LA | Other | Load Growth | Direct LG | Driver: Load Growth (EPR) |  |  | 138 | 24100000 | Entergy received a request from a customer adding new load near Vinton, LA. This facility was identified as needed due to the load growth. | ELL EPR $24.1M
MTEP25 | Central | HOOSIER ENERGY | 50614 | New Marble Hill 345 kV Station and Load | IN | Other | Load Growth | Direct LG | Driver: Data Center | Y | 310 | 345 | 20500000 | A new data center customer has plans to construct a 310 MW facility within Hoosier Energy’s service territory, adjacent to the 345kV Trimble-Ghent transmission line. The customer is planning an in-service date of Q4 2027. The full 310 MW load is planned for service by Q1 2029. | 310 MW data center near Trimble County on Trimble-Ghent 345kV. Full load by Q1 2029 (Hoosier Energy)
MTEP25 | Central | HOOSIER ENERGY | 50491 | New Ellettsville 345kV Station | IN | Other | Load Growth | Direct LG | Driver: Large Industrial |  |  | 345 | 20000000 | To serve a new customer load that has requested 345kV service | Ellettsville 345kV for new customer requesting 345kV service (HE)
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 25187 | Load Interconnection Program 2026 | MI; WI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 19000000 | Load Interconnection – Program
MTEP25 | South | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | 50594 | Helena Harbor Load Addition | AR | Other | Load Growth | Direct LG | Driver: Load Growth (EPR) |  | 250 | 230 | 18200000 | A member cooperative has a new customer that will be adding a 250MW load. A new 230kV station (Helena Harbor) will be constructed and served on a new, approximately 6-mile radial off Entergy's existing Ritchie 230kV station. Entergy will add a new 230kV position at their Ritchie station to accommodate this new 230kV radial. | Helena Harbor: 250MW customer via new 230kV station 6mi radial (AECC AR)
MTEP25 | South | ENTERGY ARKANSAS, LLC | 50441 | Wrightsville 115kV: Build two 115kV lines | AR | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 17800000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50497 | MidAmerican Upgrades for MTEP 50157 Big Cedar Load Expansion | IA | BRP |  | Hidden LG (BRP) | Driver: Large Industrial (BRP) |  |  | 345 | 16700000 | MISO MTEP 50157 Big Cedar Load Expansion Expedited Project Review study identified network upgrades to meet NERC TPL-001-5 compliance | MEC BRP $17M; Big Cedar CAP
MTEP25 | East | ITC | 50212 | Avery - New DTE Interconnection | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 120 | 15755000 | Accommodate a new interconnection request from DTE to provide capacity for load growth in Detroit city, MI.
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50459 | Install Stewart TR2 | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 15000000 | Load growth in area is exceeding capability of existing transformer at substation
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50727 | Replace Thompson 345/138/13.75 MVA Autotransformer at Thompson Substation | IN | BRP |  | Hidden LG (BRP) | Driver: Data Center (BRP) | Y |  | 345 | 15000000 | EPR BRP TPL-001 Required, N-1-1 of P1-2 Thompson-Rockville transmission line and P1-3 of Stout autotransformer | IPL BRP; LEAP CAP $15M
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50728 | Add 3rd 345/138kV Bank at Edwards Sub | IN | BRP |  | Hidden LG (BRP) | Driver: Data Center (BRP) | Y |  | 345 | 15000000 | Part of LEAP Phase 2 EPR mitigations; adds 3rd 606MVA bank to Edwards substation | BRP driven by LEAP data center EPR. Add 3rd 345/138kV bank at Edwards Sub
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50298 | Four Corners 69/12kV Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 14052130 | Load growth
MTEP25 | Central | HOOSIER ENERGY | 50490 | Merom Station 345kV Expansion and New 345kV line | IN | Other | Load Growth | Direct LG | Driver: Large Industrial |  |  | 345 | 14000000 | To serve a new customer load southeast of Merom station. | Merom 345kV expansion for new customer SE of Merom (HE)
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50417 | Rebuild 0735 St Bonifacius to Mound | MN | Other | Age and Condition | Hidden LG (Age+LG) | Driver: Load Growth + Age |  |  | 69 | 13157400 | The existing structures are at end of life and have numerous defects. OPGW installation on the line will likely replace more than 50% of existing structures triggering a complete rebuild. Significant load growth is forecasted in the area and increased capacity is needed.
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50424 | Maple Street Substation | SD | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 13000000 | Load growth in area is exceeding capability of existing distribution substations in area
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50421 | Rebuild 0737 Gleason Lake to Mound | MN | Other | Age and Condition | Hidden LG (Age+LG) | Driver: Load Growth + Age |  |  | 69 | 12996320 | The existing structures are at end of life and have numerous defects. OPGW installation on the line will likely replace more than 50% of existing structures triggering a complete rebuild. Significant load growth is forecasted in the area and increased capacity is needed.
MTEP25 | Central | HOOSIER ENERGY | 50599 | New Merom 345 kV Substation Load Addition | IN | Other | Load Growth | Direct LG | Driver: Data Center | Y | 620 | 345 | 12790684 | A new data center customer has plans to construct a 620 MW facility within Hoosier Energy’s service territory, approximately 1-mile from Hoosier Energy’s Merom Transmission Station. The is planning an in-service date of July 2026. The full ramp-up to 620 MW load is planned for service by July 2027. | 620 MW data center at Merom, 1 mi from Merom Transmission Station. 653 MVA at 95% PF. Full load by 7/2027
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50302 | Lacrosse 69/12kV Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 14 MVA | 69 | 12500000 | Load growth
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50428 | Replace Cass County TR1 | ND | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 12200000 | Load growth in area is exceeding capability of existing transformer
MTEP25 | East | ITC | 50597 | DTE New Hudson Interconnection | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 120 | 12163500
MTEP25 | Central | AMEREN MISSOURI | 50226 | New Vulcan 138/34 kV Substation | MO | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 12000000 | Load growth
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50334 | Eagle Grove-Goldfield 69 kV Interconnection and Clarion-Latimer 69 kV Line Rebuild | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 12000000 | Serve load
MTEP25 | West | Central Minnesota Municipal Power Agency | 50261 | Blue Earth - North Transmission Substation Add 84/140 MVA transformer | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 75 MVA | 161 | 11200000 | Load growth is driving this need.
MTEP25 | Central | AMEREN ILLINOIS | 50198 | New Wieland Metals 138 kV Load Addition | IL | Other | Load Growth | Direct LG | Driver: Large Industrial (Wieland Metals) |  |  | 138 | 10700000 | New Wieland Metals 138 kV Load Addition | AMIL EPR $10.7M
MTEP25 | Central | AMEREN ILLINOIS | 50299 | New Wakefield 138 kV switching station | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 10700000 | System Growth
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50300 | Hayworth 69/12kV Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 10249426 | Reliability & load growth
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50458 | Install Avon Area Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 10000000 | Load growth in area is exceeding capability of existing substations
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50371 | Lee Hanna 69/12kV Rebuild | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 6 MVA | 69 | 10000000 | Load growth
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50200 | PLPL81 and W-30 345 kV Line, Uprate | WI | Other | Local Reliability | Hidden LG | Driver: Load Growth |  |  | 345 | 9500000 | PLPL81 and W-30 345 kV Line Uprate; new load
MTEP25 | Central | HOOSIER ENERGY | 50493 | Rebuild Ashland Tap - Cisne Junction 69 kV Line | IL | Other | Local Reliability | Hidden LG | Driver: Load Growth |  |  | 69 | 9500000 | System need is to improve reliability. The upgraded conductor and new switch will allow greater operational flexibility and improve maintainability of the line. The existing line is limited to 13 MVA which severely limits the ability of the line to be used in response to contingency events or accommodate load growth. The lack of a switch at Ashland Junction prevents the line from being deenergized for maintenance which makes maintenance difficult. The project will remedy these issues.
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50145 | Beloit Area DIC, New Substation | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y | 33 MVA | 138 | 9000000 | Load Interconnection
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50324 | 88th Street Substation bus expansion and 161-13 kV transformer installation | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 9000000 | Serve load
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50433 | Install Pine Island Island Area Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 8900000 | Load growth in area is exceeding capability of existing substations
MTEP25 | West | ITC MIDWEST | 50204 | Clinton Rail and Air Park 161 kV Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 8760389 | Customer requested interconnection for a new distribution source.
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50502 | New Brownsburg East 138 kV Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 8600000 | Load-serving / load growth project
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50303 | Jacob Mack 2nd Bank & Source | IN | Other | Local Reliability | Hidden LG | Driver: Load Growth + Reliability |  |  | 69 | 8594249 | Jacob Mack 2nd Bank & Source for load growth and reliability | System Need: "Load growth & reliability"
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50429 | West Byron TR 2 | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 7535000 | Load growth in area is exceeding capability of existing transformer at substation
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50449 | Roughrider Substation | ND | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 7500000 | Load growth in area is exceeding capability of existing transformer at substation
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50457 | Install Montrose TR2 | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 7450000 | Load growth in area is exceeding capability of existing transformer at substation
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50426 | Thunder Substation | ND | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 7300000 | Load growth in area is exceeding capability of existing distribution substations in area
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50547 | East Beloit SS, DIC, Sub Rebuild | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 138 | 7200000 | Load Interconnection
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50435 | Install East Mankato Area Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 6700000 | Load growth in area is exceeding capability of existing substations in the East Mankato area.
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50297 | Milnon 69/12kV Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 6649226 | Load growth
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50434 | Replace Meire Grove TR1 | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 6200000 | Load growth in area is exceeding capability of existing transformer
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50292 | Fishback Creek 69/12kV Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 6000000 | Load Growth
MTEP25 | South | ENTERGY SERVICES, LLC. | 50176 | Audubon 230 kV Load Addition and Line upgrades | LA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 230 | 5900000 | Entergy has received a request from a customer to add new load in the Geismar, LA area. Upgrades, including this facility, have been identified as needed due to the load growth.
MTEP25 | South | ENTERGY SERVICES, LLC. | 50209 | South China 138 kV New Substation | TX | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 5800000 | Entergy has received a request from a customer adding new load in the China, TX area.
MTEP25 | South | ENTERGY ARKANSAS, LLC | 50581 | Fort Mountain 161kV: Build New Substation | AR | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 5727876 | This project is needed to connect a new block load customer.
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50296 | Dover 69/12kV Substation | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 12 | 69 | 5500000 | Load growth
MTEP25 | West | ITC MIDWEST | 50207 | Spirit Lake Anchor 69 kV Interconnection | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 50 MVA | 69 | 5398911 | Spirit Lake Anchor will consolidate and take on the load supported by numerous other substations in the area. ITCMW will build the 69 kV portion of this station and build the tap to ITCMW transmission.
MTEP25 | East | METC | 50317 | New Hagensville Junction Interconnection (METC) | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 5010000
MTEP25 | Central | AMEREN ILLINOIS | 50282 | New Radbourn 345 kV and Leghorn 345 kV Shunt Reactors | IL | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 4800000 | System Growth
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50548 | Juneau Industrial SS, DIC, Transformer Addition | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 69 | 4800000 | Load Interconnection
MTEP25 | West | Central Minnesota Municipal Power Agency | 50269 | Blue Earth Northeast Add 2nd Transformer 20-37.3 MVA | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 3 MVA | 69 | 4800000 | Load growth
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50723 | Uprate IPL Petersburg to Cato 138 kV Equipment | IN | BRP |  | Hidden LG (BRP) | Driver: Data Center (BRP) | Y |  | 138 | 4000000 | EPR BRP Mitigation for LEAP Phase 2 | IPL BRP; LEAP CAP $4M
MTEP25 | West | ITC MIDWEST | 50379 | ITC Midwest Load interconnection blanket | IA; IL; MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 3750000 | These projects are being done at the request of an interconnection customer to facilitate new load, to re-distribute existing load, to improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. These projects are strictly in response to customer interconnection requests and are not being proposed to address any specific ITCM system reliability concerns.
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50223 | Whitewater – Sugar Creek 138 kV (WHIG53), Flow Control Device | WI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 3358000 | Load Growth
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50376 | Rebuild HE Bethany to Charlestown Jct 69kV Line | IN | Other | Load Growth | Direct LG | Driver: Multiple Industrial |  | 7 | 69 | 3305000 | Project Driver: Multiple future proposed Indiana economic development projects such as The Cheesecake Factory, Sazerac in Charlestown, and Canadian Solar that are distribution-fed and interconnected to the 69kV system at River Ridge. 69kV contingency of most concern is the 250363 08CLRKSV to 250593 08INDARS id=1 outage, limiting River Ridge North to a very low future additional capacity of 7.7MW. | Cheesecake Factory, Sazerac, Canadian Solar in Charlestown IN driving 69kV rebuild
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50549 | Wilson St SS, DIC, Transformer Addition | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 69 | 3200000 | Load Interconnection
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50613 | Central SS, DIC, New Substation | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y | 25 MVA | 69 | 3200000 | Load Interconnection
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50285 | New HE Shadow Lake 138/12kV Sub | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 2974000 | HE - transfer load and distribution load growth
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50289 | New Wabash Industrial 69/12kV Sub | IN | Other | Load Growth | Direct LG | Driver: Large Industrial |  | 20+ | 69 | 2968000 | new large customer load | Wabash Industrial: 20+MW customer near Chippewa (DEI)
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 24474 | Winnebago County, New DIC | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 69 | 2900000 | Load Interconnection
MTEP25 | West | Central Minnesota Municipal Power Agency | 50275 | Blue Earth West Sub Transformer Upgrade | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 14 MVA | 69 | 2900000 | Load growth.
MTEP25 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 50404 | Lake Walthall 115kV Delivery Point | MS | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 2830000 | A member distribution cooperative, Magnolia Electric, has requested a new 115kV delivery point south of Tylertown, MS.
MTEP25 | East | ITC | 50468 | ITCT Customer Interconnections - 2028 | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 2500000 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. These projects are strictly in response to customer interconnection requests. They are not being proposed to address any specific ITCT system reliability concerns.
MTEP25 | East | METC | 50466 | METC Customer Interconnections - 2028 | MI | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 345 | 2500000 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. These projects are strictly in response to customer interconnection requests. They are not being proposed to address any specific METC system reliability concerns.
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50598 | Progress SS, DIC, Substation Rebuild | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y |  | 138 | 2500000 | Load Interconnection
MTEP25 | West | Central Minnesota Municipal Power Agency | 50268 | Blue Earth Rice Street Transformer Replacement | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 20 MVA | 69 | 2400000 | Load growth
MTEP25 | West | GREAT RIVER ENERGY | 50587 | Darnen Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 2362888 | Agralite Electric Cooperative requires a new distribution substation to serve power to a new dairy processing plant. Agralite requested transmission service from GRE to serve this new load. In addition to the new industrial load some existing load will be reallocated to this substation from other nearby Agralite substations to better serve their members. Due to the size of the new interconnected load and the potential for multiple distribution transformers served in a double-ended configuration, the transmission line will be configured in-and-out with the transmission path going into the distribution substation and back out, thereby providing redundant service from Morris or Walden.
MTEP25 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 50400 | Ovett 69kV Delivery Point | MS | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 2100000 | A member distribution cooperative, Dixie Electric, has requested a new 69kV delivery point near Ovett in Jones County, MS.
MTEP25 | Central | AMEREN MISSOURI | 50616 | New Rootbeer 345 kV Substation Load Addition | MO | Other | Load Growth | Direct LG | Driver: Load Growth (EPR) |  |  | 345 | 2000000 | New Rootbeer 345 kV Substation Load Addition | AMMO EPR
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50503 | New Pleasant Acres Substation Feed 2 138 kV line | IN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 4 MVA | 138 | 2000000 | Load-serving / load growth project
MTEP25 | West | GREAT RIVER ENERGY | 50472 | Hawick Breaker Station | MN | BRP |  | Hidden LG (BRP) | Driver: Area Load Growth (BRP) |  |  | 69 | 2000000 | As part of a Willmar area study, a breaker station at Hawick was seen to eliminate existing N-1-1 (or N-2 with system adjustments allowed) thermal overloads in the area and provide margin for load growth. This project will be done in conjunction with other Willmar Municipal projects in the area identified as part of the same study | Part of Willmar area study, driven by load growth thermal overloads
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50335 | Johnson Creek Add 161 kV Breakers | IA | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 161 | 2000000 | Serve growing customer load in the area.
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50342 | Rebuild Greencastle Industrial Jct. to WVPA Vandalia 69kV Line | IN | Other | Local Reliability | Hidden LG | Driver: Emerging Load |  |  | 69 | 1984000 | The dominate contingency is the loss of the 34541 Line between Amo (249240) and Qualitech Steel (249518). This triggers automated opening of the Amo bank to avoid overloading of this non-BES bank and extensive overloads on the 69kV system. This results in Greencastle Industrial Jct. (250469) to Vandalia (251002) and Vandalia (251002) to Filmore (250442) to load to 96.4% and 82.3% respectively. This is based on a MISO24 2009 SUM case. The loss of the Amo bank also results in contingency emerging loading issues but to a lesser extent.
MTEP25 | Central | AMEREN MISSOURI | 50531 | New AECI Load Addition at Ameren Fredericktown 138 kV | MO | Other | Load Growth | Direct LG | Driver: Load Growth (EPR) |  | 75 | 161 | 1200000 | New AECI Load Addition at Ameren Fredericktown 138 kV | AMMO EPR
MTEP25 | Central | AMEREN MISSOURI | 50615 | New Central 138 kV Substation Load Addition | MO | Other | Load Growth | Direct LG | Driver: Load Growth (EPR) |  |  | 138 | 1000000 | New Central 138 kV Substation Load Addition | AMMO EPR
MTEP25 | Central | AMEREN MISSOURI | 50696 | New Huster-McClay 138 kV line tap for Hayford load | MO | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 138 | 500000 | Customer request
MTEP25 | West | GREAT RIVER ENERGY | 50392 | Elk River Muni West | MN | Other | Local Reliability | Hidden LG | Driver: Load Growth |  |  | 69 | 68811 | Thermal overloading The short span of 266 ACSR transmission between switches EWSM11 and EWS14 will overload for the loss of Liberty – Thompson Lake 69 kV line in the near-term with very little expected load growth until overloading. Switches EWSM11 and EWS10 will overload for the loss of Liberty – Thompson Lake 69 kV line after the 134 MW subsystem has grown by 40 MW. Assuming a CAGR of 1-2%, the switches will need to be replaced in 14-28 years. The subsystem is described furthermore at the end of the document.
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50494 | Knight Substation | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 115 | 29600 | Required for load growth in the area.
MTEP25 | Central | AMEREN TRANSMISSION COMPANY OF ILLINOIS | 50636 | New Diamond Core Load Addition (RECC Territory) at Mogul 345 kV substation | IL; MO | Other | Load Growth | Direct LG | Driver: Data Center | Y |  | 138 |  | Diamond Core Load Addition at Mogul 345 kV substation; EPR load growth | Diamond Core data center at Mogul 345 kV, RECC territory. Connected to solar line, separately metered
MTEP25 | West | OTTER TAIL POWER COMPANY | 50603 | OTP Big Stone South Load Addition | SD | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 230 |  | A new customer has requested to interconnect to OTP's system. This project is required to serve the new load and maintain transmission system reliability.
MTEP25 (App B) | West | Central Minnesota Municipal Power Agency | 50278 | Blue Earth new North to Northeast 69 kV line | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  |  | 69 | 12800000 | Load growth
MTEP25 (App B) | West | Central Minnesota Municipal Power Agency | 50276 | Blue Earth North Substation Upgrade 1st 161/69 Transformer to 45-60-75 MVA | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 75 MVA | 161 | 3700000 | Load growth
MTEP25 (App B) | West | AMERICAN TRANSMISSION COMPANY | 50346 | Huebner SS, DIC, Transformer Addition | WI | Other | Load Growth | Direct LG | Other Type: Load Growth | Y | 33 MVA | 138 | 3200000 | Load Interconnection
MTEP25 (App B) | West | Central Minnesota Municipal Power Agency | 50277 | Blue Earth Northeast Sub Upgrade 1st transformer to 20-37.3 MVA | MN | Other | Load Growth | Direct LG | Other Type: Load Growth |  | 3 MVA | 69 | 3000000 | Load growth

## MTEP20
MTEP Year | Planning Region | Utility/TO | Project ID | Project Name | Project Description | State | Project Type | Other Type | System Need / Rationale | Project Driver | Data Center Flag | Load (MW) | Expected ISD | Max kV | Min kV | Estimated Cost ($) | Report Notes
MTEP20 | Central | AmerenIL | 11925 | New Massac Substation - Convert Joppa 230 kV substation to 345 kV substation | Install 2-345/161 kV, 560 MVA transformers, remove 230/161 kV equipment. Rebuild Joppa-West Frankfort 230 kV for 345 kV use (Massac-Jordan). | IL | Other | Reliability |  |  |  |  | 2023-06-01 | 345 | 161 | 112400000
MTEP20 | West | ITCM | 18847 | Big Cedar Load Interconnection | A new load will be added at the Big Cedar Industrial Park in Cedar Rapids, IA and ITC will construct a new Big Cedar Substation to connect this new load. The new sub will tap the Beverly – Morgan Valley 345 kV line and create a Morgan Valley – Big Cedar #1 345 kV line and a Big Cedar – Beverly 345 kV line. New line taps should utilize bundled T2-795 ACSR conductor and have OPGW. ITC will also need to add a second 345 kV circuit on the existing Beverly – Morgan Valley 345 kV line to add a 3rd 345 kV feed into the new Big Cedar substation. The new 345 kV line should utilize bundled T2-795 ACSR conductor. The new Big Cedar substation will include a new 3 position 345 kV breaker and half substation with 3 – 345 kV lines and 2 – 345/161 kV transformers (450 MVA nameplate) and all 345 kV substation equipment should be rated 3000 amps summer normal rating. The 161 kV portion of the substation will be folded breaker and ½, with each transformer connected to a dedicated position (double breaker double bus), and the new 161 kV underground feeds to the customer will be connected on breaker and a half positions. All new 161 kV substation equipment should be rated 2000 amps minimum summer normal rating. All new underground 161 kV lines from Big Cedar to the customer substations should be rated 900 amps minimum summer normal rating. ITC will install new 161 kV ring bus substations at each of the new customer substations. All substation equipment should be rated 2000 amps minimum summer normal rating. ITC will build out the Morgan Valley substation to full 4 position breaker and ½ with the addition of this load and the additional line into Morgan Valley. IPL has also requested that the existing 69 kV double circuit line be relocated as part of this project. The Beverly – Fairfax #2 and Fairfax – Oakridge 69 kV line will be moved to follow the railroad tracks up to Edgewood Rd, then follow Edgewood Rd to meet up with the existing line route. | IA | Other | Load Growth | New load at Big Cedar Industrial Park in Cedar Rapids, IA; new 345 kV substation, 345/161 kV transformers, underground 161 kV to customer substations | Large Industrial |  | 450 MVA | 2021-12-31 | 345 | 69 | 104627788.2 | Big Cedar Industrial Park, Cedar Rapids IA. New 345 kV switching station ($105M). EPR project
MTEP20 | Central | AmerenIL | 18249 | New LaSalle Area 138 kV Statcom (100 MVAR) | Install a 100 MVAR Statcom. | IL | BRP | [5 empty] | 2023-12-01 | 138 | 0 | 91400000
MTEP20 | Central | AmerenIL | 18250 | New Robinson 138 kV Statcom (70 Mvar) | Install an 70 Mvar Statcom.a new substation just south of Robinson Marathon. Re locate the Robinson – Newton 138 kV line and the Robinson – Lawrenceville 138 kV line in and out of the new substation. | IL | BRP | [5 empty] | 2023-06-01 | 138 | 0 | 78000000
MTEP20 | Central | AmerenIL | 17910 | Rebuild Grand Tower-Carbondale NW 138 kV line | Rebuild ~36 miles of the Grand Tower-Carbondale NW-W. Frankfort 138 kV line as double circuit 345/138 kV. | IL | Other | Age and Condition |  |  |  |  | 2024-12-01 | 345 | 138 | 75600000
MTEP20 | Central | AmerenIL | 13797 | Rebuild Albion South-Norris City North 138 kV to double circuit | Rebuild the existing 138 kV circuit to 2000A. Double circuit the line for new 3000A 345 kV circuit. | IL | Other | Age and Condition |  |  |  |  | 2022-12-01 | 345 | 138 | 74000000
MTEP20 | Central | AEP | 17684 | Upgrade Greentown 765 kV substation | Rehabilitation and reconfiguration of the 765kV Greentown yard. | IN | Other | Age and Condition |  |  |  |  | 2023-02-15 | 765 | 138 | 70000000
MTEP20 | South | Entergy-TX | 18248 | Millbend 138 kV: New Distribution Station | Build ~ 7miles of new transmission line to cut the new Millbend 138 kV station into the existing New Caney to Parkway 138 kV line. | TX | Other | Load Growth | Area load growth 56.5 MVA to start, 35.2 MVA from New Caney Sub and 21.3 MVA from Heights Sub |  |  | 56.5 MVA | 2024-06-01 | 138 | 0 | 65400000
MTEP20 | South | Entergy-LA | 13925 | Choudrant: New distribution substation | Construct a 230 kV distribution substation named Choudrant in southern Lincoln parish near the town of Choudrant and construct a 230 kV transmission line from the new substation that terminates into the existing Mt Olive substation. | LA | Other | Load Growth | New 230 kV distribution substation in southern Lincoln parish for load growth |  |  |  | 2023-06-01 | 230 | 0 | 56225000 | ELL $56.2M
MTEP20 | Central | AmerenIL | 11926 | New Jordan Substation - Convert West Frankfort 230 kV substation to 345 kV substation | Install 345/138 kV, 560 MVA transformer. Rebuild/reinsulate 19.9 miles of existing 230 kV line between West Frankfort and St. Johns for use at 345 kV. | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 345 | 138 | 56100000
MTEP20 | South | Entergy-TX | 15648 | Castle 230 kV: New Distribution Station | Cut the Castle 230 kV station in and out on the Ponderosa to Grimes 230 kV line. 230 kV breakers will be installed at Castle. | TX | Other | Load Growth | Distribution load growth, 18.5 MVA to start |  |  | 18.5 MVA | 2024-06-01 | 230 | 0 | 50510000
MTEP20 | Central | AmerenMO | 17908 | Rebuild Bland-Franks 345 kV line | Rebuild approximately 44 miles 345kV line to 3000A. | MO | Other | Age and Condition |  |  |  |  | 2024-12-01 | 345 | 0 | 48400000
MTEP20 | East | NIPS | 18986 | Rebuild NIPSCo BES for Reinforcements | Strengthen the NIPSCo transmission system ahead of the anticipated suspension of the [NIPS] Schahfer units 14, 15, 17 and 18. | IN | BRP | [5 empty] | 2023-05-01 | 138 | 0 | 48100000
MTEP20 | Central | AmerenIL, AmerenMO | 16984 | Rebuild Sioux-Meppen North 138 kV line (4) | Rebuild existing river crossing (structures 173-179). | IL,MO | Other | Age and Condition |  |  |  |  | 2021-12-01 | 138 | 0 | 45700000
MTEP20 | East | METC | 15896 | Battle Creek - Morrow (Jaguar) #1 138 kV Rebuild | The proposed solution is to rebuild 19.38 miles from Str #008E57412E to Str #008E8623 of the Battle Creek – Morrow #1 138kV circuit using 954 ACSR conductor with future double-circuit steel structures and leave adjacent side vacant for future circuit and also rebuild 3.3 miles from Str #008E8623 to Morrow station of 477 ACSR conductor to 954 ACSR conductor with double circuit steel structures. | MI | BRP | [5 empty] | 2024-12-31 | 138 | 0 | 41000000
MTEP20 | West | ATC | 16486 | Arcadian SS - Power Transformer and Control House Replacement and Asset Renewal | -Vacate and demolish existing control house buildings and procure new level-8 control house and contents (relay, RTU, etc.) -Remove both Westinghouse LTC transformers (T2 & T3) and replace with one 345/138kV 500MVA transformer -T1 wil be retained and relocated onto proper oil containment -Remove all 3 345kV live tan breakers and associated free standing CTs -Remove all 4 138kV Allis Chalmers BZO oil circuit breakers -Remove both 345kV circuit switchers -Spare 230kV transformer and towers will remain | WI | Other | Age and Condition |  |  |  |  | 2023-12-31 | 345 | 138 | 40000000
MTEP20 | South | Entergy-LA | 18233 | Start 115 kV: Construct New Substation | Build new 115 kV substation named Start along with 2 miles of in-and-out 115 kV line from Alto to new substation site. | LA | Other | Load Growth |  |  |  |  | 2025-06-01 | 115 | 0 | 39505305
MTEP20 | South | Entergy-LA | 18227 | Norris Road 138 kV: New Distribution Station | New distribution station to be cut into the CLECO Youngsville to Segura 138 kV line. | LA | Other | Load Growth |  |  |  |  | 2026-06-01 | 138 | 0 | 39200000
MTEP20 | Central | AmerenMO | 18267 | New Wright City 345 kV substation | Joint project between Ameren Missouri and AECI. Tap the Ameren Missouri Labadie-Montgomery 345kV line via a new 3-breaker, 345kV ring bus near the intersection of the line and the AECI (Central Electric Power Coop) 161kV line west of Charrette. Rebuild the existing 161kV line between the tap point and the AECI Wright City Substation as double-circuit 345/161kV. Install new 345/161kV step down transformer at Wright City. | MO | BRP | [5 empty] | 2023-12-01 | 345 | 161 | 39100000
MTEP20 | West | ATC | 14909 | Small Capital Project and Asset Renewal Program 2021 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2021. | WI,MI | Other | Age and Condition |  |  |  |  | 2024-06-30 | 345 | 69 | 38913412
MTEP20 | Central | AmerenMO, WVPA | 17845 | New Wittenberg-Trail of Tears 138 kV line | Wabash Valley- Install new Wittenberg ring bus switching station on the Grand Tower-Perryville line. Reconfigure Trail of Tears substation to BAAH. Install new 161 kV line from Trail of Tears to Charmin Bulk Substation. Install 2 breakers at Charmin Bulk Substation. Ameren - Install 12 miles of new 138 kV line from Wittenberg Substation to Trail of Tears Substation. Install new 161-138 kV transformer at Trail of Tears Substation. | MO | Other | Reliability |  |  |  |  | 2023-12-01 | 161 | 138 | 38500000
MTEP20 | South | Entergy-AR | 19767 | Heth 500kV: New Substation (J1060) | The Heth 500kV substation is to cut in the J1060 450 MW solar facility. This includes a 500kV cut in to the exiting West Memphis - Keo 500kV line. A new 500kV interconnection substation will be installed. Remote end upgrades at KEO and West Memphis include removing line traps, line tuners, existing relays, and replacing them with new relay panels. | AR | GIP | [5 empty] | 2023-05-01 | 500 | 0 | 38044000
MTEP20 | West | ITCM | 17740 | ITCM Asset Blanket for 2023 | Replace equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance have increased potential for misoperations and higher maintenance costs associated with their ongoing use. | IA,MN,IL | Other | Age and Condition |  |  |  |  | 2023-12-31 | 345 | 69 | 37080000
MTEP20 | Central | AmerenIL | 17904 | New Highland-Aviston 138 kV line | Install new Highland area ring bus. Re-configure Aviston Substation to a ring bus. Install new 16.5 mile 138 kV line between Highland and Aviston. | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 138 | 0 | 35700000
MTEP20 | East | METC | 17844 | Summerton - Bullock cut in to Salt River 138 kV | Extend the Summerton - Bullock 138 kV circuit by extending ~15 miles of double circuit 138 kV construction into Salt River 138 kV station. | MI | GIP | [5 empty] | 2022-10-28 | 138 | 0 | 35493000
MTEP20 | West | XEL | 18345 | Scott County - Helena Line Upgrade | Upgrade Helena - Scott County 345kV line to accommodate additional flow from J587 Blazing Star 2 generation interconnection | MN | GIP | [5 empty] | 2022-09-15 | 345 | 0 | 34000000
MTEP20 | South | Entergy-TX | 19665 | Deer to Indian 138 kV line | Build ~16-19 miles of new 138 kV transmission line from Deer substation to Indian substation. The project will consist of a 795 ACSR Drake single circuit transmission line from Deer substation to Indian Substation, or a 795 ACSR Drake single circuit transmission line from Deer Substation to a new 3 breaker ring bus switching station (cut into existing Indian to Gulf Livingston transmission line) approximately 1 mile to the west of Indian substation. This is contingent on the ability to acquire ROW for the transmission project. | TX | BRP | [5 empty] | 2025-06-01 | 138 | 0 | 33340000
MTEP20 | Central | AmerenMO | 17804 | Rebuild Lutesville-St. Francois 345 kV line | Rebuild 63 miles of 345kV wood H-frame circuit. | MO | Other | Age and Condition |  |  |  |  | 2023-12-01 | 345 | 0 | 32800000
MTEP20 | Central | AmerenIL | 18275 | New Holland NW-Neoga South 345 kV line (4509) | Construct a 345 kV double circuit on the existing Holland Northwest-Neoga South-4509 line R.O.W. replacing structures. Target rating: 3000 A summer emergency. | IL | BRP | [5 empty] | 2023-12-01 | 345 | 0 | 32000000
MTEP20 | West | MEC | 18176 | Circuit Breaker Additions and Replacements 2020-2022 | Blanket project to add and replace new 345 kV circuit breakers to expand to ring bus which will reduce misoperations, increase reliability and operating flexibility. | IA | Other | Reliability |  |  |  |  | 2022-12-01 | 345 | 0 | 31000000
MTEP20 | Central | AmerenIL, AmerenMO | 17905 | New Hull 161/138 kV transformer | Install new 161 kV Finn ring bus (Hannibal area). Convert the Spalding Substation to a ring bus configuration adding a positon for a line to the Hannibal area Substation. Double circuit the PENO-SPLD-2 line from Spalding to the Marion tap and rebuild the Marion Tap 161 kV section of the PENO-SPLD-2 line to the Mississippi River, through the new Hannibal area Substation and the existing Marion Substation. Install new 161 kV bus-tie breaker at Marion Substation. Install new 161-138 kV transformer at Hull substation. Operate the HULL-MRN-1690 line at 161kV. | MO | Other | Reliability |  |  |  |  | 2022-06-01 | 161 | 138 | 30300000
MTEP20 | Central | AmerenIL | 17974 | New Crab Orchard 345/138 kV transformer | Tap the Shawnee-West Frankfort east-4564 line and install 345kV ring bus to make a connection for the installation of a new 345-138 kV transformer. | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 138 | 0 | 28000000
MTEP20 | Central | AmerenMO | 16555 | Relocate Page 138 kV substation to new Bugle 138 kV Substation | Relocate the existing 138 kV Page substation to the new Bugle site. 138 kV to be built as breaker and a half arrangement. | MO | Other | Reliability |  |  |  |  | 2024-06-01 | 345 | 138 | 27500000
MTEP20 | Central | AmerenMO | 9721 | Reconductor Bland-Tegeler 138 kV line | Reconductor line to 1200 A summer emergency capability | MO | BRP | [5 empty] | 2022-12-01 | 138 | 138 | 27200000
MTEP20 | Central | AmerenMO | 16986 | Rebuild Page-Sioux 138 kV line (4) | Rebuild existing Missouri River crossing (Str. 112-117) | MO | Other | Age and Condition |  |  |  |  | 2023-12-02 | 138 | 0 | 26657745
MTEP20 | West | ATC | 18985 | J850/J878 MPFCA East Paris New SS | The purpose of the project is to construct a 345-138 kV substation to the east of the 138kV Paris substation. | WI | GIP | [5 empty] | 2022-12-23 | 345 | 138 | 25525101
MTEP20 | Central | AmerenIL | 18269 | New LaSalle–North Utica 138 kV line | New 138 kV ring bus breaking the North LaSalle–Fox River 138 kV line. Construct a new line between LaSalle 138 kV substation and new ring bus. Add two line breakers at the LaSalle 138 kV substation. | IL | BRP | [5 empty] | 2025-06-01 | 138 | 0 | 25400000
MTEP20 | Central | AmerenIL | 16944 | New Louisville South 345/138 kV Transformer | Install new 345 kV ring bus at the Louisville South Substation location tapping the Newton-Xenia-1 line. Install 560 MVA 345-138 kV transformer and connect to the Louisville South 138 kV bus. | IL | Other | Reliability |  |  |  |  | 2022-12-01 | 345 | 138 | 25200000
MTEP20 | West | ATC | 18568 | Howards Grove SS - Erdman SS 138 kV, new line | Construct approximately 7 miles of new 138 kV line from Howards Grove to Erdman. | WI | BRP | [5 empty] | 2023-11-30 | 138 | 0 | 25000000
MTEP20 | Central | AmerenIL | 16988 | New Fogarty-Limit 138 kV Line | Install new 138 kV line from Fogarty Substation to limit. Install new ring bus at Limit to make the connection | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 138 | 0 | 24600000
MTEP20 | West | ATC | 18017 | Petenwell-Badger-West-Saratoga, (X-43) 138kV, Line Rebuild | 138 kV Line X-43 is 22.7 miles long with pole vintages from the 1940s, 1950s and 1960s The limitations of the system result in voltage collapse for forced outages during planned maintenance The Council Creek SPS no longer fully mitigates market congestion issues due to increased system flows X-43 will be rebuilt with an a maximum rating of 1030 Amps for all seasons. This will resolve system reliability, market congestion and pending asset renewal issues | WI | BRP | [5 empty] | 2022-12-31 | 138 | 0 | 24500000
MTEP20 | West | MDU | 17466 | Heskett Substation Retirement | The Heskett substation will be retired due to age and condition concerns. The existing Mandan substation will be expanded to accommodate the 230 kV and 115 kV facilities currently connected to Heskett. A new Mandan 38th St substation will be constructed to accommodate the 69 and 41.6 kV facilities. | ND | Other | Age and Condition |  |  |  |  | 2020-11-30 | 230 | 41.6 | 24000000
MTEP20 | Central | AmerenIL | 18311 | New Maple Flats Solar (J813) interconnection | Re-configure Louisville South 138 kV substation to BAAH bus. Add terminal facilities for J813 connection. | IL | GIP | [5 empty] | 2021-10-29 | 138 | 0 | 24000000
MTEP20 | East | METC | 18147 | Rebuild Bard Road – Warren 138 kV | Rebuild 16.4 miles of the Bard Road – Clare Junction section of the Bard Road – Warren 138kV circuit and to rebuild 3.3 miles of the Clare Junction – Warren section of the Bard Road – Warren 138kV circuit with 954 ACSR utilizing future 230 kV double circuit construction initially operated as 138 kV single circuit with adjacent side left vacant for future use. | MI | GIP | [5 empty] | 2022-05-01 | 138 | 0 | 23918246
MTEP20 | Central | AmerenIL | 17976 | New Redhawk 345/138 kV transformer | Tap the Coffeen-Roxford-4551 line and install 345kV ring bus to make the connection for a new 345-138 kV transformer at Redhawk Substation. | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 345 | 138 | 22400000
MTEP20 | West | ITCM | 17729 | Savanna-Argo Fay-York Area Rebuilds | ITC will build a new 69kV line approximately 6 miles from the York Substation to the Argo Fay Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. ITC will build a new 69kV line approximately 6.5 miles from the Clay Substation to the Chadwick Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. ITC will rebuild approximately 6.5 miles of the Argo Fay Substation to the Chadwick Substation 34.5kV line to 69kV Standards. The overhead conductor will have an ampacity of 600A or higher. ITC will retire approximately 6 miles of 34.5kV line between Argo Fay and the Clay substation. ITC will retire approximately 6 miles of 34.5kV line between Argo Fay and the Savanna substation. | IL | Other | Age and Condition |  |  |  |  | 2025-12-30 | 69 | 34 | 22350000
MTEP20 | Central | AmerenIL | 13709 | New Putnam breaker-and-a-half 138 kV substation | Build new 138 kV BAAH substation on new site near Hennepin. | IL | Other | Age and Condition |  |  |  |  | 2022-12-01 | 138 | 0 | 22300000
MTEP20 | East | METC | 18238 | Morrow (Jaguar) 138 kV Station Rebuild | Rebuild Morrow 138 kV station at a new site approximately 1.55 miles to the north utilizing new equipment in a five-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called Jaguar. • Acquire new property as necessary and install (15) 138 kV, 3000 A breakers with at least 40 kA interrupting capability in a five-row, breaker-and-a-half scheme configuration for this new station. • Redirect all circuits currently at the Morrow 138 kV station into the new Jaguar 138 kV station and connect CE’s new replacement step-down transformers, and Kalamazoo River Generation Station via radial feeds into the new Jaguar station. • Reconductor Morrow - Jaguar 795 ACSR section of the Morrow – Bradley (V22) 138kV line using 1431 ACSR conductor and utilizing this circuit to create Cork Street – Jaguar 138kV line. | MI | Other | Age and Condition |  |  |  |  | 2024-12-31 | 138 | 0 | 22300000
MTEP20 | West | ATC | 17525 | J870/J871 MPFCA Highland Generator Network Upgrades | A 300 MW solar farm in Grant and Iowa County, Wisconsin. Customer has requested a Point of Interconnection (POI) at Highland Substation that taps the existing X-17 line between Eden and Wyoming Valley Substations. | WI | GIP | [5 empty] | 2020-08-01 | 138 | 69 | 22180519
MTEP20 | South | Entergy-TX | 13943 | Southern Point 138 kV: New Substation | Construct a new 138 kV substation that replaces the existing Speedway 138 kV substation. | TX | Other | Load Growth | Distribution system load growth, 7.0 MVA to start |  |  | 7.0 MVA | 2024-06-01 | 138 | 0 | 22000000
MTEP20 | East | METC | 18190 | Dort 138 kV Station Rebuild | Rebuild Dort 138 kV station with a new control house at a new site approximately 0.5 miles to the south utilizing new equipment in a four-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called Calvary. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance to be performed again in a safe and efficient manner. | MI | Other | Age and Condition |  |  |  |  | 2024-06-01 | 138 | 0 | 21325000
MTEP20 | West | ATC | 19729 | J732 Superior SS Network Upgrades and Interconnection Facilities | Interconnection of about 560 MW the facility composed of one (1) steam turbine unit and one (1) natural gas unit in a 1x1 combined cycle facility interconnecting at the new Superior Substation. | WI | GIP | [5 empty] | 2023-11-30 | 345 | 230 | 21245605
MTEP20 | West | ATC | 14907 | Load Interconnection Program 2021 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2021. | WI,MI | Other | Load Growth |  |  |  |  | 2024-06-30 | 138 | 69 | 20124594
MTEP20 | Central | AmerenIL | 12176 | New West Frankfort East & Norris City 345 kV reactors | Reconfigure West Frankfort East to BAAH and install 345 kV, 50 Mvar shunt reactor. | IL | BRP | [5 empty] | 2023-12-01 | 345 | 0 | 19700000
MTEP20 | Central | DEI | 18284 | J754 Gen. Interconnect | J754 Wind Farm - Gen. Interconnect: 34501 ckt. - 300MW Wind farm; 3-breaker ring bus switching station | IN | GIP | [5 empty] | 2021-03-15 | 345 | 0 | 19655000
MTEP20 | Central | AmerenIL | 18263 | New Fargo–Hines 138 kV line | New line between the Fargo 138 kV substation and the Hines 138 kV substation. | IL | BRP | [5 empty] | 2025-06-01 | 138 | 0 | 18720000
MTEP20 | East | ITCT | 17998 | Build Stone Pool - Temple 120 kV | The proposed solution is to build a new circuit (approximately 1.25 miles) from the Stone Pool 120 kV Station to the Temple 120 kV station utilizing 3200 Kcmil underground cable. | MI | Other | Other Local Needs |  |  |  |  | 2024-06-01 | 120 | 0 | 18670000
MTEP20 | West | GRE | 14366 | Svea Tap - Litchfield Tap Line Rebuild Project | Rebuild GRE’s existing 69 kV transmission line from Willmar to Litchfield Muni Tap with a larger conductor. | MN | Other | Age and Condition |  |  |  |  | 2024-06-14 | 69 | 0 | 18350000
MTEP20 | East | NIPS | 18276 | Rebuild Maple-LNG 138kV Line | Rebuild Maple to LNG 138kV Line | IN | BRP | [5 empty] | 2023-05-01 | 138 | 0 | 18000000
MTEP20 | West | ATC | 14915 | Physical Security Program 2021 | Physical Security projects typically have shorter project life cycles. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2021. | WI,MI | Other | Other Local Needs |  |  |  |  | 2024-06-30 | 345 | 69 | 17908909
MTEP20 | Central | AmerenMO | 16491 | Rebuild Sioux-Meppen-4, Page-Sioux-4, Sioux-Huster-1 138 kV lines | Sioux-Huster-1/Sioux-Meppen North-4: Rebuild ~9 miles of triple circuit 138 kV lattice tower line to double-circuit steel poles. | MO,IL | Other | Age and Condition |  |  |  |  | 2021-12-01 | 138 | 0 | 17100000
MTEP20 | West | MEC | 18117 | Washburn-Hazleton 161 kV Reconductor | Reconductor Washburn-Hazleton 161 kV line. Upgrade Washburn substation terminal equipment. | IA | GIP | [5 empty] | 2020-10-31 | 161 | 0 | 16700000
MTEP20 | West | OTP | 18947 | OTP Ellendale-Oakes-Forman-Hankinson 230 kV Upgrades J302/J503 | This project consists of upgrades to Otter Tail Power Company’s substations and transmission lines to accommodate the interconnection of a wind generators, J302/J503. Four Facility upgrades are needed: • Ellendale to Oakes 230 kV Line Reconductor • Oakes to Forman 230 kV Reconductor • Forman to Hankinson 230 kV Structure Replacements • Forman 230 kV Switch Replacement | ND | GIP | [5 empty] | 2021-03-01 | 230 | 0 | 16500000
MTEP20 | South | Entergy-AR | 18097 | Pleasant Hill 500kV: Add 2 Reactors | Add 2 100 MVAR reactors at Pleasant Hill 500 kV bus | AR | BRP | [5 empty] | 2023-06-01 | 500 | 0 | 16333119
MTEP20 | East | NIPS | 18685 | J883 GIA Network Upgrades | Generator Interconnection. The existing East Winimac – Monticello line will be cut into at the site of the new substation. | IN | GIP | [5 empty] | 2023-04-15 | 138 | 0 | 15990564
MTEP20 | East | WPSC | 18011 | Rebuild Atlanta to Airport 138kV | Rebuild and upgrade 31.5 miles of 138 kV with double circuit steel poles, 795ACSS conductor, and OPGW. | MI | Other | Age and Condition |  |  |  |  | 2023-12-31 | 138 | 0 | 15500000
MTEP20 | South | Entergy-AR | 18103 | Screeton 115kV: Construct new substation | Build a new 115kV substation with a single 40 MVA 115/13.8kV LTC transformer between Hazen and Carlisle 115kV substations near the town of Screeton. | AR | Other | Load Growth |  |  |  | 40 MVA | 2024-06-01 | 115 | 13.8 | 15132530
MTEP20 | West | XEL | 18505 | Jim Falls - Holcombe Rebuild | Rebuild Jim Falls - Holcombe 115kV line to remove overload under contingency | WI | Other | Reliability |  |  |  |  | 2023-03-01 | 115 | 0 | 15000000
MTEP20 | Central | DEI | 18331 | Whitesville to Advance 69kV Rebuild | 69154 rebuild from Whitesville to Advance with 477ACSR and light-duty steel poles | IN | Other | Reliability |  |  |  |  | 2021-12-31 | 69 | 0 | 14410000
MTEP20 | Central | AmerenIL | 17627 | Rebuild Fogarty-Kickapoo 138 kV line (1672) | Rebuild 138 kV line to 2000A | IL | Other | Age and Condition |  |  |  |  | 2022-12-01 | 138 | 0 | 14400000
MTEP20 | South | Entergy-TX | 18255 | Fort Worth to Kolbs 69 kV Rebuild | Rebuild the 69 kV line between Fort Worth and Kolbs stations. | TX | Other | Age and Condition |  |  |  |  | 2023-06-01 | 69 | 0 | 14100000
MTEP20 | East | NIPS | 18278 | Rebuild LNG-Stillwell 138kV Line | Rebuild LNG to Stillwell 138kV line | IN | BRP | [5 empty] | 2023-05-01 | 138 | 0 | 14000000
MTEP20 | West | ATC | 4727 | Winona - Atlantic (Winona69) 69kV, reconductor | System Reliability ($11.9M) i. The Winona - Atlantic (Winona69) 69kV circuit is 22 miles long, uses wood H Frame structures and 1/0 Copper conductor ii. This circuit can be a limiter for the import of energy to Houghton and Keweenaw Counties, MI iii. This project will re-conductor this circuit with 477 kcmil ACSR iv. Add ATC owned and operated OPGW to this circuit providing a redundant path for communication in the region Asset Renewal Component ($2M) i. The condition and performance of the existing line infrastructure requires replacement of the existing insulators and select structures ii. There are resource and cost efficiencies in doing the reliability project work in combination with the needed asset renewal work Non-Transmission Alternative (NTA) i. Mitigation of the reliability project, via and NTA, does not remove the need for necessary condition and performance work nor will it provide the reliability benefit of the communication circuit on this line | MI | Other | Reliability |  |  |  |  | 2024-12-31 | 69 | 0 | 13900000
MTEP20 | Central | AmerenMO | 17624 | Rebuild Pike 161 kV Substation | Rebuild the Pike 161 kV substation to a Ring bus configuration. | MO | Other | Reliability |  |  |  |  | 2023-12-01 | 161 | 0 | 13400000
MTEP20 | Central | DEI | 18290 | Purdue University CHP Generation | Purdue University CHP Generation - 15.5MW gas turbines with HRSG unit - non-MISO queue; non-BES | IN | Other | Reliability |  |  |  |  | 2021-07-16 | 138 | 12 | 13310000
MTEP20 | West | GRE | 17944 | Heron Lake - Round Lake (FE-RH) 69 kV Line Rebuild | Rebuild entire FE-RH line (from Heron Lake substation to Round Lake substation) | MN | Other | Age and Condition |  |  |  |  | 2021-09-30 | 69 | 0 | 13232725
MTEP20 | West | GRE, MP | 17664 | Portage Lake 115/69 kV Project | GRE will interconnect to Minnesota Power’s (MP) 13 Line (Riverton – Cromwell 115 kV) with a 4 position, 115 kV ring bus, to be called Portage Lake, at or near the existing Mille Lacs Electric Cooperative (MLEC) Kimberly substation. The new 115 kV Portage Lake ring bus will have four positions; 115 kV line to Riverton (13 Line), 115 kV line to Cromwell (26 Line), 115/69 kV transformer with a 9.5 mile line to Palisade. AKA Kimberly. | MN | Other | Reliability |  |  |  |  | 2023-09-30 | 115 | 69 | 13201117
MTEP20 | Central | AmerenIL | 16704 | Rebuild Salem West-Mt Vernon West 138 kV line (1332) | Rebuild line to 2000A. Upgrade terminal equipment at Salem West to 2000A including 1272 ACSR bus conductor and switch 1330. | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 138 | 0 | 13200000
MTEP20 | South | Entergy-AR | 18726 | Locust Creek 161kV: Construct Switching Station (J919) | Construct a new 3 breaker switching station 2.62 miles north east of the Newport Air Base substation on the L962 161kV Newport Air Base - Cash 161kV transmission line section. This will be used as the point of interconnection for the 180 MW solar photovoltaic generator project J919. | AR | GIP | [5 empty] | 2023-02-01 | 161 | 0 | 13077000
MTEP20 | Central | AmerenIL | 17285 | New Quiver 138 kV Substation | Install new ring bus installation at the intersection of Mason City West – Fogarty -1346 and San Jose Rail – Interstate – 1318 138 kV line. | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 138 | 0 | 13000000
MTEP20 | West | MEC | 18129 | 25th Street NW 161 KV Substation | Construct a new 161 kV substation and associated 161 kV line work to source customer-owned transformation and new load. | IA | Other | Load Growth |  |  |  |  | 2022-07-01 | 161 | 0 | 12935000
MTEP20 | West | ATC | 19146 | J850 North Creek SS, Generator Interconnection Facilities and Network Upgrades | Interconnection of a 250 MW solar farm located in Walworth County, Wisconsin. | WI | GIP | [5 empty] | 2022-09-30 | 138 | 0 | 12573372
MTEP20 | Central | AmerenIL | 15265 | Reconfigure Carbondale NE 138 kV substation to ring bus | Install initial 3-position ring bus at Carbondale NE Substation | IL | Other | Reliability |  |  |  |  | 2023-06-01 | 138 | 0 | 12500000
MTEP20 | West | ATC | 18052 | Barneveld SS, DIC, new substation | ATC will: -Construct an underbuilt 69 kV (138kV capable) circuit from Hooterville to Wally Road onto the ordered route of the Cardinal - Hickory Creek 345kV project -Connect the new WPL Barneveld substation with a loop through straight bus configuration with 2 line breakers -Connect the new MHU Military Ridge substation with a radial tap with line switches -Reitre the existing Y-128 section from Mt. Horeb to Wally Road | WI | Other | Load Growth |  |  |  |  | 2023-12-31 | 69 | 0 | 12300000
MTEP20 | West | GRE | 17964 | Blue Earth - East Chain - Wilbert Tap (FE-WB) 69 kV Line Rebuild | Rebuild entire FE-WB line (Blue Earth to East Chain to Wilbert Tap) | MN | Other | Reliability |  |  |  |  | 2022-12-31 | 69 | 0 | 12273125
MTEP20 | Central | AmerenIL | 17565 | New Oreana-Decatur N 27th Street 138 kV line | Install new 138 kV line between Oreana and Decatur N 27th Street. | IL | BRP | [5 empty] | 2025-06-01 | 138 | 69 | 12200000
MTEP20 | Central | AmerenIL | 17982 | New Maroa 345 kV substation | Install new Maroa 345 kV ring bus substation. | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 345 | 0 | 12000000
MTEP20 | West | MEC | 18137 | South Waukee 161-13.2 kV Substation | Construct a new 161-13.2 kV distribution substation and associated 161 kV line work to accommodate area growth. | IA | Other | Load Growth |  |  |  |  | 2022-06-01 | 161 | 13.2 | 11988000
MTEP20 | Central | PPI | 18162 | New Kington-Ellisville 69 kV Line | New 18-mile 69 kV line tying McDonough Power Cooperative to Spoon River Electric Cooperative | IL | Other | Reliability |  |  |  |  | 2023-12-31 | 69 | 69 | 11925000
MTEP20 | Central | AmerenIL | 15504 | New Dempsey (Blue Mound) 138 kV ring bus addition | Install new ring bus at the tap to Blue Mound on the Pana-Route 51 Decatur-1462 line. | IL | Other | Reliability |  |  |  |  | 2022-06-01 | 138 | 0 | 11700000
MTEP20 | East | METC | 15809 | Four Mile (Northridge) - North Belding 138 kV Rebuild | The proposed solution is to rebuild 8.38 miles Alpine Jct. – Rogue River Jct. and Rogue River Jct. – Cannon Jct. sections of the Four Mile – North Belding 138kV line using 954 ACSR conductor. | MI | BRP | [5 empty] | 2024-12-31 | 138 | 0 | 11700000
MTEP20 | Central | AmerenIL | 13793 | New El Paso 138 kV substation ring bus | Install initial 4-postion ring bus at El Paso Substation for in/out supply. | IL | Other | Reliability |  |  |  |  | 2022-12-01 | 138 | 0 | 11400000
MTEP20 | South | Entergy-MS | 19286 | Cotton Blossom 230 kV: Construct switching station (J830) | This project will construct a new 230 kV switching station cut into the Canton South - Yandell Road line. | MS | GIP | [5 empty] | 2022-03-01 | 230 | 0 | 11367000
MTEP20 | South | Entergy-LA | 18787 | J697 Interconnection: Expand Oak Ridge 115 kV Substation | This project shall consist of transforming the existing 115 kV yard from single bus to dual bus, expanding the existing substation site, installing a new control house, and installing shielding and light fixtures to accommodate the connection of the Interconnection Customer’s transmission line. | LA | GIP | [5 empty] | 2022-10-15 | 115 | 0 | 11314000
MTEP20 | Central | AmerenMO | 17605 | Reconductor Page-Berkeley 138 kV lines 1/2 | Reconductor the Page-Berkeley-1&2 circuits with ACCR conductor | MO | Other | Age and Condition |  |  |  |  | 2022-12-01 | 138 | 0 | 11300000
MTEP20 | South | Entergy-AR | 18946 | Kuhn Road 161kV: Expand Station and Line Rebuild (J934) | The Kuhn Road 161kV bus will be expanded to provide a point of interconnection for J934 solar generating facility. Upgrades will include two 161kV dead end structures, two 161kV 3000 A vertical break disconnects switches, one 161kV 3000 A gas circuit breaker, three 161kV rated surge arresters, three metering accuracy coupling capacitor voltage transformers, revenue accuracy meter, relaying panel and revenue metering panel. Three surge arresters on the incoming line L940 will be installed. Relay settings updates are required for the 161kV bus differential relay, and the Kuhn Road - Parkin and Kuhn Road - Ebony 161kV transmission lines. The existing Ebony - Kuhn Road 161kV transmission line will be rebuilt to support 666.6 kcmil ACSR Flamingo conductor at a minimum rating of 229 MVA. | AR | GIP | [5 empty] | 2022-06-01 | 161 | 0 | 11160000
MTEP20 | East | ITCT | 15890 | Pontiac - Walton 120 kV Rebuild | Rebuild approximately 4.8 miles of 477 ACSR X2 and 1431 ACSR conductors from Pontiac to Giddings 2 Tap to Walton using 2156 ACSR. Also, upgrade station equipment at Pontiac 120kV and Walton 120 kV. | MI | BRP | [5 empty] | 2025-12-31 | 120 | 0 | 11027000
MTEP20 | West | ITCM | 16864 | J475 Generator Interconnection | The Poweshiek to Irvine 161 kV line is to be rebuilt on existing ROW with a conductor having a minimum summer rating of 1,595A. Upgrades at the Poweshiek 161 kV substation will also be required. | IA | GIP | [5 empty] | 2020-10-01 | 161 | 161 | 11000000
MTEP20 | Central | AmerenIL | 17975 | New Rising 345/138 kV transformer No. 2 | Install 2nd 345-138 kV transformer at Rising Substation | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 345 | 138 | 11000000
MTEP20 | West | ATC | 14911 | Communication Reliability Program 2021 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2021. | WI,MI | Other | Other Local Needs |  |  |  |  | 2024-06-30 | 345 | 69 | 10927208
MTEP20 | South | Entergy-AR | 18101 | Hot Springs Plemmons 115kV: Construct new substation | Build a new 115kV substation with a single 40 MVA 115/13.8 kV LTC transformer. | AR | Other | Load Growth |  |  |  | 40 MVA | 2024-06-01 | 115 | 13.8 | 10904173
MTEP20 | West | ITCM | 17728 | Savanna-Metform-York 34kV to 69kV Rebuild | ITC will rebuild approximately 6 miles of the Savanna – Metform – York 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 1200A or higher. ITC will need to investigate the Danisco to York 34.5kV to determine if the insulators are capable of 69kV operation. If not, ITC will reinsulate the Danisco to York 34.5kV line with 69kV insulators. The existing conductor is 954 ACSR and does not need to be replaced due to ampacity needs. The static is 3/8 steel. | IL | Other | Age and Condition |  |  |  |  | 2020-12-30 | 69 | 69 | 10749600
MTEP20 | West | ITCM | 16844 | J495 Generator Interconnection | ITCM and EDF have entered into an engineering and procurement agreement for the acquisition of materials and design of a 3-terminal, 3 breaker, 345 kV switching station to be constructed roughly 7 miles east of the Ledyard 345 kV station and connected to the Ledyard to Colby 345 kV line. The E&P agreement will cover the design and material acquisition for the 345 kV station, and construction work will occur under the GIA. | IA | GIP | [5 empty] | 2019-10-18 | 345 | 345 | 10662026
MTEP20 | South | Entergy-LA | 15645 | Nelson 138 kV: Install transmission breakers | Nelson – Lake Charles Bulk 138 kV L-654 should be re-terminated at the open bay east of Nelson to Deridder bay and L-698 should be moved to the bay L-654 currently occupies. Breaker 7920 and one new IPO breaker (3000A continuous rating, 80 kA interrupting rating) would be needed to re-terminate L-654 in double-bus-double-breaker scheme. | LA | BRP | [5 empty] | 2022-06-01 | 230 | 0 | 10600000
MTEP20 | Central | AmerenIL | 9723 | New Fishhook 138 kV substation | Construct 138 kV breaker station in East Quincy-Meredosia-2 138 kV line. | IL | Other | Reliability |  |  |  |  | 2019-06-01 | 138 | 138 | 10500000
MTEP20 | West | ITCM | 17731 | Savanna City Loop 34kV to 69kV Rebuild | ITC will rebuild approximately 1.66 miles of the Savanna – Eaton 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. ITC will rebuild approximately 0.85 miles of the Bowen – Eaton 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. ITC will rebuild approximately 3.80 miles of the Bowen – Savanna 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. | IL | Other | Age and Condition |  |  |  |  | 2025-12-30 | 69 | 69 | 10478146
MTEP20 | East | METC | 18728 | Cobb (Chopin) - Sternberg 138kV Line Rebuild | The proposed solution is to rebuild approximately 8 miles of the Cobb - Sternberg 138kV circuit using 954 ACSR conductor with single circuit steel structures. | MI | BRP | [5 empty] | 2024-12-31 | 138 | 0 | 10450000
MTEP20 | West | GRE | 17970 | Howard Lake - Highland - Maple Lake Line Rebuild | Rebuild the 69 kV transmission line from Howard Lake to Highland to Maple Lake. | MN | Other | Age and Condition |  |  |  |  | 2023-12-29 | 69 | 0 | 10402000
MTEP20 | West | XEL | 18029 | West St Cloud - Millwood 69kV Rebuild | Rebuild 24 miles of 69kV line from West St. Cloud - Millwood to remediate aging condition issues | MN | Other | Reliability |  |  |  |  | 2021-06-01 | 69 | 0 | 10400000
MTEP20 | South | Entergy-TX | 18251 | Alligator Bayou to Fort Worth 69 kV Rebuild | Rebuild and reconductor the Alligator Bayou to Fort Worth 69 kV line. | TX | Other | Age and Condition |  |  |  |  | 2022-03-01 | 69 | 0 | 10400000
MTEP20 | Central | AmerenIL | 19045 | New Rivian Load Interconnection | Provide 2 separate 138kV lines from West Washington St 138kV BAAH Expansion to serve all load at Diamond Star. | IL | Other | Load Growth |  | EV Manufacturing (Rivian) |  |  | 2021-02-01 | 138 | 0 | 10100000 | Rivian EV plant at Diamond Star, IL (Normal). Two 138kV lines. EPR project
MTEP20 | West | XEL | 15877 | East Metro Area Upgrades | To remediate overloads and voltage concerns in the East metro, line connections will be reconfigured at Red Rock, 115kV line from Baytown - Long Lake will be upgraded. | MN | BRP | [5 empty] | 2022-06-15 | 115 | 0 | 10000000
MTEP20 | West | XEL | 18007 | Prentice - Phillips 115kV Rebuild | Complete wreck out and rebuild of 14.8 miles of 115kV line from Prentice to Phillips Tap to remediate aging condition issues. | WI | Other | Reliability |  |  |  |  | 2023-01-31 | 115 | 0 | 10000000
MTEP20 | Central | AmerenIL | 17324 | New Mason 138 kV Ring bus (J1055) Glacier Sands interconnection | Interconnection for new 144 MW wind farm at Mason (IL) substation. Tap existing bus at Mason to provide connection. | IL | GIP | [5 empty] | 2020-10-15 | 138 | 0 | 10000000
MTEP20 | Central | AmerenIL | 17978 | Rebuild Belleville 17th Street 138 kV substation | Rebuild the Belleville 17th street 138 kV substation to a ring bus configuration. | IL | Other | Reliability |  |  |  |  | 2022-12-01 | 138 | 0 | 10000000
MTEP20 | South | Entergy-TX | 18259 | Lacon 138 kV: Breaker and feeders | Install a 138 kV breaker at Lacon in the bay looking toward the LNG tap. Also included in this project are distribution feeder additions. | TX | Other | Reliability |  |  |  |  | 2023-06-01 | 138 | 0 | 10000000
MTEP20 | South | Entergy-MS | 17086 | Brandon Area Loop Project | Tap L540A (East Whitfield to South Brandon) with a 115kV GOAB and build a new 115kV transmission line from the South Brandon tap to East Brandon delivery point GOAB. | MS | Other | Load Growth |  |  |  |  | 2022-12-01 | 115 | 0 | 9952989
MTEP20 | West | ITCM | 17727 | York Substation 69kV Expansion | ITC will be expanding the York Substation to include a 161/69kV 150MVA transformer. All new 69kV equipment will be capable of 2000A. A tie switch will be added to the 161kV. All new 161kV equipment will be capable of 2000A or greater. See page 2 for the electrical layout of the York Substation. ITC will be retiring the 34.5kV out of the York Substation. No additional 161kV equipment will be needed to accommodate this work. All new 69kV equipment will be capable of 1200A or greater. | IL | Other | Age and Condition |  |  |  |  | 2021-12-31 | 161 | 69 | 9776400
MTEP20 | West | ITCM | 18061 | Mason City Industrial 161kV Substation Interconnection | ITCM will interconnect Alliant Energy’s Mason City Industrial 161/24.9kV distribution substation with in/out taps to the Emery-Lime Creek 161kV line and install four (4) 161kV breakers in a ring bus configuration at the 161kV distribution substation. IPL will install a single distribution transformer initially to serve a load of ~18MW. IPL will install a second distribution transformer in the future to accommodate load growth and load moved from 69kV distribution substations. | IA | Other | Load Growth | Mason City Industrial distribution substation; ~18MW initial load | Large Industrial |  | 18 | 2022-05-30 | 161 | 24.9 | 9747847
MTEP20 | East | ITCT | 17364 | J793 Generator Interconnection | ITCT will install a new 345 kV station with 3-345 kV breakers and associated disconnects in a ring bus configuration. ITCT will loop the Belle River - Fitz #2 345kV circuit into the new J793 substation. ITCT will upgrade relay panels at the Fitz and Belle River Power Plant Stations to accommodate the new generator J793. | MI | GIP | [5 empty] | 2021-05-14 | 345 | 0 | 9734993
MTEP20 | East | ITCT | 15880 | Navarre - River Rouge 120 kV Rebuild | Rebuild the 2.9 miles of 954 ACSR conductor to 2156 ACSR on the Navarre – River Rouge 120 kV line and upgrade station equipment at both ends. | MI | BRP | [5 empty] | 2025-12-31 | 120 | 0 | 9728000
MTEP20 | Central | DEI | 18334 | Rebuild Connersville to Glenwood 69 kV | 6920 rebuild from Connersville to Glenwood with 477ACSR and light-duty steel poles | IN | Other | Reliability |  |  |  |  | 2021-12-31 | 69 | 0 | 9665000
MTEP20 | East | ITCT | 15959 | Hager - Sunset 120 kV Rebuild | The proposed solution is to rebuild 4.33 miles of the Sunset – Hager 120kV circuit using 2156 ACSR conductor with single circuit steel structures and upgrade station equipment at Hager and Sunset stations. | MI | BRP | [5 empty] | 2025-12-31 | 120 | 0 | 9657000
MTEP20 | West | ITCM | 17726 | Savanna 69kV Substation Expansion | ITC will be expanding the Savanna 69kV Substation to a Ring Bus capable of 6-positions. Most new 69kV equipment will be capable of 1200A or greater. ITC will install a 161/69kV 150MVA transformer at Savanna. The 161/69kV transformer position and the Metform position will be capable of 2000A or greater. There will be several phases for the 69kV. | IL | Other | Age and Condition |  |  |  |  | 2021-12-31 | 69 | 69 | 9535800
MTEP20 | South | Entergy-MS | 19287 | Webb 115 kV: Substation Expansion (J908) | This project will expand the 115 kV Webb substation to facilitate the generation interconnection project J908. | MS | GIP | [5 empty] | 2023-06-01 | 115 | 0 | 9417000
MTEP20 | Central | AmerenIL | 17644 | Upgrade Decatur Route 51 138 kV substation | Install initial 138 kV 4-position (ultimate 6-position) ring bus at the Decatur Route 51 substation location | IL | Other | Reliability |  |  |  |  | 2022-06-01 | 138 | 0 | 9400000
MTEP20 | Central | AmerenMO | 17830 | Upgrade Gasconade-Osage 161 kV line | Replace both shield wires and replace structures as needed. | MO | Other | Age and Condition |  |  |  |  | 2021-12-01 | 138 | 0 | 9400000
MTEP20 | Central | AmerenIL | 17825 | Reconfigure Lawrenceville South 138 kV substation | Reconfigure the Lawrenceville South substation to a 6-position ultimate ring bus. | IL | Other | Age and Condition |  |  |  |  | 2023-12-01 | 138 | 0 | 9200000
MTEP20 | East | ITCT | 15883 | Bismarck-Stephens #2 120 kV Rebuild | Rebuild approximately 3.61 miles of 795 ACSS and 954 ACSR conductors to 2156 ACSR on the Bismarck – Stephens #2 120 kV line. | MI | BRP | [5 empty] | 2024-12-31 | 120 | 0 | 9100000
MTEP20 | Central | PPI | 18163 | New Ursa-Big Neck 69 kV Line | New 12.4-mile 69 kV line in Adams Electric Cooperative | IL | Other | Reliability |  |  |  |  | 2023-12-31 | 69 | 69 | 9024000
MTEP20 | West | ATC | 18848 | Blount - East Campus, 69kV, (6907), Replace Damaged Underground Cable | -Replace 1.9 miles of damaged High Pressure Fluid Filled (HPFF) cable with new HPFF using existing pipe. -Damage caused by Blount SS event in July of 2019. | WI | Other | Age and Condition |  |  |  |  | 2020-09-30 | 69 | 0 | 9000000
MTEP20 | East | METC | 18424 | J758 Generator Interconnection (Network Upgrades) - Mud Lake | Build a new 138 kV 3 Breaker ring substation cut in from the Verona - Foundry 138 kV circuit. Changes will require upgraded relaying at Verona 138kV station. | MI | GIP | [5 empty] | 2022-04-08 | 138 | 0 | 8995000
MTEP20 | Central | PPI | 18155 | New Burton-Ursa 69 kV Line | New 16.3-mile 69 kV line in Adams Electric Cooperative | IL | Other | Reliability |  |  |  |  | 2021-12-31 | 69 | 69 | 8945250
MTEP20 | Central | DEI | 18287 | Terre Haute S. Vigo to HE Middletown Jct 69kV Rebuild | Rbld 6901 circuit from TH Haute S. Vigo sub, pole 802-1158, to HE Middletown Jct, pole 802-1315, using light-duty steel poles, 477ACSR conductor & OPGW static. Rpl switch #64LB with two 2000A switches | IN | Other | Reliability |  |  |  |  | 2022-06-01 | 69 | 0 | 8768000
MTEP20 | Central | AmerenMO | 18319 | Upgrade Fredericktown-Heritage 161 kV line (7011) | Replace poles for OPGW installation. Structure replacements will increase the rating to 120 degrees C. | MO | Other | Age and Condition |  |  |  |  | 2021-06-01 | 161 | 0 | 8700000
MTEP20 | West | ITCM | 17725 | Savanna 161kV Substation Expansion | TC will be expanding the Savanna Substation to a Ring Bus capable of 6-positions. The new 161kV equipment will be capable of 2000A. There will be several phases for the 161kV. | IL | Other | Age and Condition |  |  |  |  | 2021-12-31 | 161 | 161 | 8695200
MTEP20 | Central | PPI | 18166 | New Virginia-Saidora 69 kV Line | New 14.9-mile 69 kV line in Menard Electric Cooperative | IL | Other | Reliability |  |  |  |  | 2023-12-31 | 69 | 69 | 8640000
MTEP20 | East | METC | 19545 | Grand Rapids Area Project | Construct two 138kV circuits (~ 2 miles, new ROW on new double circuit structures) to cut in the Chopin – Northridge 138kV line into Meyer 138kV. Install (3) new 138kV breaker at Myer to facilitate new lines come into Meyer and remediate sag limit on the Chopin – Meyer, Meyer – Northridge and Meyer – Tallmadge #2 138kV lines. | MI | BRP | [5 empty] | 2025-06-01 | 138 | 0 | 8540000
MTEP20 | West | XEL | 18006 | Osprey - Hawkins 115kV Rebuild | Wreck out and rebuild of approximately 11.36 miles of 115kV line between Osprey and Hawkins substations for aging conditions | WI | Other | Reliability |  |  |  |  | 2022-06-15 | 115 | 0 | 8500000
MTEP20 | Central | AmerenIL | 16987 | New Benton NW 138 kV Ring bus | Install 6 position ultimate ring bus. | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 138 | 0 | 8500000
MTEP20 | Central | AmerenIL | 17981 | Rebuild North Champaign 138 kV substation | Rebuild the North Champaign 138 kV substation to a ring bus configuration. | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 138 | 0 | 8500000
MTEP20 | Central | AmerenIL | 9734 | New North Utica 138 kV substation | Construct 138 kV breaker station in North LaSalle-Fox River-1646 138 kV line. | IL | Other | Load Growth |  |  |  |  | 2023-12-01 | 138 | 34.5 | 8400000
MTEP20 | Central | AmerenIL | 13708 | New Athens Dutch Hill 138 kV substation ring bus | Add 138 kV ring Bus. Initial 3-position (ultimate 4-position) | IL | Other | Reliability |  |  |  |  | 2022-12-01 | 138 | 0 | 8376000
MTEP20 | Central | DEI | 18286 | Rebuild Brownstown Sw Sta to Pumpkin Center 69 kV | 6952 Rbld Pt 2 Brownstown Sw Sta to Pumpkin Center; 10.7 mi. - 477acsr ; Replace the 6952-69123 tie switch on pole #813-1535-02 located just outside Pumpkin Center substation | IN | Other | Reliability |  |  |  |  | 2021-12-31 | 69 | 0 | 8361000
MTEP20 | West | ITCM | 17730 | Savanna-Clay 34kV to 69kV Rebuild | ITC will rebuild approximately 7.75 miles of 34.5kV to 69kV standards from Savanna Substation to Clay Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. | IL | Other | Age and Condition |  |  |  |  | 2025-12-30 | 69 | 69 | 8262000
MTEP20 | East | METC | 17365 | J717_J728 Generator Interconnection | Build a new 138 kV 3 Breaker ring substation cut in from the Bullock - Warren 138 kV circuit. Install OPGW from the new station to Warren 138 kV sub. | MI | GIP | [5 empty] | 2020-07-30 | 138 | 0 | 8191000
MTEP20 | Central | DEI | 18328 | Rebuild Greencastle N. to Morton Jct. 69 kV | 6933 rebuild from Greencastle N. to Morton Jct. with 477ACSR and light-duty steel poles | IN | Other | Reliability |  |  |  |  | 2021-07-22 | 69 | 0 | 8084000
MTEP20 | Central | DEI | 18845 | Greenwood Clark Twnshp 230kV Ring bus | Greenwood Clark Twnshp: add (2) CBs to complete a 3-position 230kV Ring bus; replace misc. 230kV and 69kV equipment in-kind | IN | Other | Reliability |  |  |  |  | 2021-12-31 | 230 | 69 | 8053000
MTEP20 | South | Entergy-AR | 18725 | Searcy Price 161kV: Expand 161kV Station (J893) | The Searcy Price 161kV substation will be upgraded to incorporate a new POI for J893, a 100 MW photovoltaic generator project. Transmission Network Upgrades for this interconnection include two new 161kV circuit breakers, 161kV disconnect switches, expanding the existing 161kV operating bus, substation yard, control house, and additional relay control panels. | AR | GIP | [5 empty] | 2021-08-01 | 161 | 0 | 8045000
MTEP20 | Central | AmerenIL | 17973 | Rebuild Centerville 138 kV substation | Rebuild the Centerville 138 kV substation to a Ring bus configuration. | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 138 | 0 | 8000000
MTEP20 | Central | AmerenIL | 17977 | New Mt. Vernon West 345/138 kV transformer No. 2 | Install 2nd 345-138 kV transformer at Mt. Vernon West Substation | IL | Other | Reliability |  |  |  |  | 2023-06-01 | 345 | 138 | 8000000
MTEP20 | Central | AmerenIL | 17983 | Rebuild South Belleville 138 kV substation | Rebuild the South Belleville 138 kV substation to a ring bus configuration. | IL | Other | Reliability |  |  |  |  | 2023-06-01 | 138 | 0 | 8000000
MTEP20 | Central | PPI | 18161 | New Bluff Springs-Virginia 69 kV Line | New 13.8-mile 69 kV line in Menard Electric Cooperative | IL | Other | Reliability |  |  |  |  | 2023-12-31 | 69 | 69 | 8000000
MTEP20 | West | ATC | 18051 | Sheboygan County SS, DIC, substation rebuild | Sheboygan County SS, DIC, substation rebuild | WI | Other | Load Growth |  |  |  |  | 2022-12-31 | 138 | 0 | 8000000
MTEP20 | West | ITCM | 17732 | Eddyville Industrial Complex 161kV Substation Expansion | ITC will expand the Eddyville Industrial Complex 161kV substation to the north. ITC will construct a five position 161kV ring bus North of the existing Eddyville Industrial Complex substation. All new terminal equipment will be capable of 2000A minimum. ITCM will terminate the Beacon – Tri County and EIC – Tri County 161kV circuits into these breakers. | IA | Other | Reliability |  |  |  |  | 2023-05-31 | 161 | 161 | 7956038
MTEP20 | West | ITCM | 18846 | Creston Roundhouse 69kV Substation Interconnection | Per Alliant’s request, ITC will construct a 3-terminal straight bus with tie breaker at the proposed Creston Roundhouse substation. All ITC terminal equipment will be capable of 2000A minimum and Alliant will own the land and joint use assets. In addition, ITC line equipment will use T2-4/0. | IA | Other | Load Growth |  |  |  |  | 2022-12-15 | 69 | 69 | 7863016
MTEP20 | Central | AmerenIL | 13705 | New North Nashville 138 kV substation | Install initial 3 position 138 kV ring bus (ultimate 4 position) at North Nashville Substation. | IL | BRP | [5 empty] | 2021-12-01 | 138 | 0 | 7810000
MTEP20 | East | ITCT | 15900 | Rebuild Wayne - Newburgh #1 120 kV | Rebuild approximately 2.7 miles of 795 ACSS conductor to 2156 ACSS on the Wayne – Newburgh #1 120 kV circuit. Also, upgrade station equipment at both Wayne and Newburgh 120 kV. | MI | BRP | [5 empty] | 2025-12-31 | 120 | 0 | 7720000
MTEP20 | Central | AmerenMO | 16552 | Replace Tyson 345/138 kV Transformer | Replace XFMR 1 with a hardened unit and replace the 138kV XFMR 1 breaker and Replace XFMR 3 breaker. | MO | Other | Age and Condition |  |  |  |  | 2022-12-01 | 345 | 138 | 7600000
MTEP20 | Central | AmerenMO | 18309 | New Fredericktown 138 kV substation | Install 138 kV ring bus at Fredericktown Substation | MO | Other | Reliability |  |  |  |  | 2022-12-01 | 138 | 0 | 7500000
MTEP20 | Central | PPI | 18160 | New Arenzville-Bluff Springs 69 kV Line | New 10.3-mile 69 kV line tying Illinois Electric Cooperative to Menard Electric Cooperative | IL | Other | Reliability |  |  |  |  | 2023-12-31 | 69 | 69 | 7459000
MTEP20 | Central | PPI | 18157 | New Kuhlman 138/69 kV Substation | "1) Establish 138 kV substation connecting to the Ameren Meredosia to Frederick 138 kV line 2) New PPI Kuhlman 138/69 kV substation" | IL | Other | Reliability |  |  |  |  | 2022-12-31 | 138 | 69 | 7425000
MTEP20 | Central | DEI | 2864 | Reconductor Centerton to Martinsville 69kV - 69163 ckt. | Reconductor the 69kV-69163 ckt - 3.47 miles of 366ACSR 80C and 0.23 miles of 477ACSR 80C to 954ACSR 100C | IN | Other | Reliability |  |  |  |  | 2023-06-01 | 69 | 0 | 7400000
MTEP20 | Central | DEI | 18304 | Batesville 345kV and 138kV breaker replacements | Batesville 345: Replace (1) 345kV circuit switcher with 345kV SF6 gas circuit breaker ; replace 345kv WT ; Replace (6) 138kV oil circuit breakers with SF6 gas circuit breakers - 13831, 13833, 13839, 13864, 13874, 138345-3 ; replace 13833 and 13874 WTs ; | IN | Other | Reliability |  |  |  |  | 2022-06-01 | 345 | 138 | 7334000
MTEP20 | West | MEC | 18124 | Sub T FD-Boone Jct 161 kV Reconductor | Reconductor MidAmerican's portion of the Sub T FD-Boone Jct 161 kV line and upgrade substation terminal equipment at Sub T FD. | IA | GIP | [5 empty] | 2020-12-31 | 161 | 0 | 7322500
MTEP20 | West | ATC | 18567 | J821 GIC Zenith SS - Generator Interconnection Facilities and Network Upgrades | A 99.9 MW wind farm in Marathon County, Wisconsin. Customer has requested a Point of Interconnection (POI) at a new Zenith Substation. | WI | GIP | [5 empty] | 2021-08-27 | 115 | 0 | 7235132
MTEP20 | Central | DEI | 18332 | Knightstown to Carthage 69kV Rebuild | 69140 rebuild from Knightstown to Carthage with 477ACSR and light-duty steel poles | IN | Other | Reliability |  |  |  |  | 2021-12-31 | 69 | 0 | 7201000
MTEP20 | Central | AmerenIL | 15266 | Reconfigure Fayetteville Bee Hollow 138 kV substation to ring bus | Install initial 3-position ring bus at the existing Fayetteville Bee Hollow substation location. | IL | Other | Reliability |  |  |  |  | 2023-06-01 | 138 | 0 | 7200000
MTEP20 | Central | AmerenIL | 16707 | New Kazad 138 kV Substation in St. Joseph area | Install new ring bus substation at the intersection of VERM-NCMP-1396 and GIFF-SDNY-1588. Install 4 positions initial, 6-positions ultimate. Rebuild the existing Vermillion-N. Champaign-1396 138 kV line to 2000A in both directions from the new substation. Upgrade terminal equipment at Vermillion to 2000A including switch 1328, bus conductor and relay load limit. Upgrade terminal equipment at North Champaign to 2000A including 795 AAC bus conductor and re-tap 1 CT. | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 138 | 0 | 7200000
MTEP20 | Central | DEI | 18327 | Rebuild Dresser to S. Vigo 69 kV | 6901 rebuild from Dresser to S. Vigo with 477ACSR and light-duty steel poles | IN | Other | Reliability |  |  |  |  | 2021-07-16 | 69 | 0 | 7162000
MTEP20 | East | ITCT | 18184 | Rebuild Red Run – Logan 2 – Sloan 120 kV | Rebuild approximately 2.8 miles utilizing 954 ACSR on double circuit structures and upgrade terminal equipment at Sloan. | MI | BRP | [5 empty] | 2024-06-01 | 120 | 0 | 7095000
MTEP20 | Central | AmerenIL | 17972 | Rebuild Salem West 138 kV substation | Rebuild the Salem West 138 kV substation to a ring bus configuration. | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 138 | 0 | 7000000
MTEP20 | West | ATC | 18053 | Waupaca SS, DIC, transformer addition | ATC to expand the Waupaca Substation to accommodate a new 138-kV bus section, new bus-tie breaker, add two line breakers, reposition ATC’s 14-Mvar capacitor banks, and replace power-line carrier with optical ground wire (OPGW) from Waupaca – Harrison North. | WI | Other | Load Growth |  |  |  |  | 2022-06-01 | 138 | 0 | 6900000
MTEP20 | Central | DEI | 18326 | Poseyville to HE Winfield 69kV Rebuild | 69139 Rebuild Part 2: Poseyville to HE Winfield TDSIC ; 4.4 miles - N.O. tie line | IN | Other | Reliability |  |  |  |  | 2021-12-31 | 69 | 0 | 6818000
MTEP20 | Central | AmerenIL | 18321 | New Ford County Wind (J845) interconnection | Install new ring bus (Oswald) on the Gibson City South-Paxton East 138 kV line to make the interconnection for J845. | IL | GIP | [5 empty] | 2021-06-01 | 138 | 0 | 6800000
MTEP20 | Central | AmerenIL | 18323 | New Cass County Solar (J859) interconnection | Install a new ring bus (Flanigan) on the Meredosia East-Ipava South 138 kV line to make the interconnection for J859. | IL | GIP | [5 empty] | 2022-05-31 | 138 | 0 | 6800000
MTEP20 | Central | AmerenMO | 17969 | Replace Mason 345/138 kV Transformer | Replace 345/138 kV, 560 MVA Transformer #2 with a 700 MVA unit | MO | BRP | [5 empty] | 2022-12-01 | 345 | 138 | 6700000
MTEP20 | Central | AmerenIL | 16556 | New Bueller 138 kV substation (formerly Grove) | Tap the Macomb West-Niota 138 kV line to install a new ring bus station to supply the PPI Disco Substation. | IL | Other | Load Growth |  |  |  |  | 2022-06-01 | 138 | 0 | 6600000
MTEP20 | Central | AmerenIL | 18320 | New Bennington Wind (J715) interconnection | Install new 138 kV ring bus (Rutland) on the McLean-Oglesby line to make the interconnection for J715. | IL | GIP | [5 empty] | 2021-05-01 | 138 | 0 | 6600000
MTEP20 | West | MDU | 18260 | Greenway Tap-Herried Rebuild | Rebuild Greenway Tap-Herried 41.6 kV line | SD | Other | Age and Condition |  |  |  |  | 2021-12-31 | 41.6 | 0 | 6600000
MTEP20 | East | METC | 18425 | Verona - Marshall cut into Mud Lake (J758 Stability Upgrade) | Cut in and extend the Verona - Marshall 138kV line by adding 0.6 miles of 954 ACSR DCT to loop in J758. Add two 138kV 40kA breakers at positions 8M9 and 8W8 at the J758 substation 138kV. | MI | GIP | [5 empty] | 2022-04-08 | 138 | 0 | 6510000
MTEP20 | West | MDU | 17304 | G359, Ellendale 345 Network Upgrades | G359 Network Upgrades at Ellendale 345: four 230 kV 50 Mvar fast-switched capacitors and a new switcher for the 345 kV line reactor on the Big Stone South line | ND | GIP | [5 empty] | 2020-02-28 | 345 | 0 | 6431000
MTEP20 | Central | PPI | 18148 | New Riggston 138 kV substation | Establish 138 kV ring bus to serve proposed Data Center in Illinois Electric Cooperative new load between Jacksonville Industrial Park and Winchester. | IL | Other | Load Growth | Establish 138 kV ring bus to serve proposed Data Center in IL Electric Cooperative territory | Data Center | Y |  | 2021-12-31 | 138 | 138 | 6400000 | Data Center for IL Electric Cooperative between Jacksonville Industrial Park and Winchester
MTEP20 | South | LAFA | 14105 | Bonin 69kV Reconfiguration | A reconfiguration of the Bonin 69kV station. | LA | Other | Reliability |  |  |  |  | 2021-09-30 | 69 | 0 | 6400000
MTEP20 | East | METC | 18243 | Battle Creek Transformer 2 Replacement | Replace Battle Creek 345/138kV transformer #2 with a new transformer. | MI | Other | Age and Condition |  |  |  |  | 2023-12-31 | 345 | 138 | 6400000
MTEP20 | Central | AmerenIL | 16990 | New Kline 138 kV substation | Install new 6 position ultimate ring bus at Kline Substation (formerly known as Wanda). | IL | Other | Reliability |  |  |  |  | 2022-12-01 | 138 | 0 | 6300000
MTEP20 | West | MEC | 18177 | Webster-Sub T FD 161 kV Reconductor | Reconductor portion of Webster-Sub T Fort Dodge 161 kV line. | IA | GIP | [5 empty] | 2021-12-15 | 161 | 0 | 6300000
MTEP20 | East | METC | 18055 | Riverview Interconnection | Convert METC Riverview substation from a three-breaker straight bus configuration to a six-breaker ring. Install three 138kV breakers, buswork, and associated disconnects. | MI | Other | Load Growth | Dedicated customer substation ~1.25 miles west of Riverview; service 40MW of new load | Large Industrial |  | 40 | 2021-07-02 | 138 | 0 | 6270000 | EPR project
MTEP20 | East | METC | 18244 | Gallagher Transformer #2 Replacement | Replace Gallagher 345/138kV Transformer #2 with a new transformer | MI | Other | Age and Condition |  |  |  |  | 2023-12-31 | 345 | 138 | 6200000
MTEP20 | Central | PPI | 18116 | New Kilbourne-Saidora 69 kV Line | New 9.7-mile 69 kV line in Menard Electric Cooperative | IL | Other | Reliability |  |  |  |  | 2023-12-31 | 69 | 69 | 6195200
MTEP20 | South | Entergy-AR | 19065 | Ritchie 230kV: Add POI (J663) | This project will add a point of interconnection to the existing Ritchie 230kV substation for J663. TOIF upgrades include two 230kV dead end structures, two 230kV 3000A disconnect switches, one 230kV 3000A gas circuit breaker, three surge arresters, metering CT's, and relay panels. Relay settings updates will be required to all transmission lines, auto transformer, transfer breaker, and bus diffs where needed. | AR | GIP | [5 empty] | 2022-05-01 | 230 | 0 | 6114000
MTEP20 | West | GRE | 17971 | Westwood 1 115 kV Conversion | Convert the existing GRE/SEA Westwood 1 substation from 69 kV to 115 kV service. Rebuild the existing 69 kV transmission line from Le Sauk to Westwood 1 to West St. Cloud to 115 kV. | MN | Other | Reliability |  |  |  |  | 2022-12-02 | 115 | 0 | 6020000
MTEP20 | Central | IPL | 18138 | Center Substation | Add a total of three new 138 kV breakers and replace three existing 138 kV breakers. | IN | Other | Age and Condition |  |  |  |  | 2021-12-31 | 138 | 0 | 6000000
MTEP20 | West | ATC | 16488 | Tilden SS - Control House Replacement and Breaker & Relay Asset Renewal | • Replace six, 138kV oil breakers with SF6 gas breakers that utilize high creep bushings for mine dust contamination • Retire six bushing potential devices installed on two breakers and replace them with six bus voltage transformers • Install a new ATC owned control house and replace relays with ATC standard models • Replace other equipment including disconnect switches, arresters and bus voltage transformers and junction boxes | MI | Other | Age and Condition |  |  |  |  | 2023-12-31 | 138 | 138 | 5880000
MTEP20 | East | METC | 18164 | Amber - Pere Marquette #2 138 kV | Construct a new line from Amber to Pere Marquette utilizing existing rights of way. Rebuild 0.62 miles from Amber to the Pere Marquette – Stronach 138 kV line with 954 ACSR utilizing future 230 kV double circuit construction initially operated as 138 kV single circuit with adjacent side left vacant for future use. Rebuild 0.72 miles of the existing single circuit Pere Marquette – Stronach 138 kV line with double circuit 138 kV construction and install 954 ACSR conductor on one side for the new Amber – Pere Marquette #2 138 kV line and 795 ACSS conductor on the other side for the existing Pere Marquette – Stronach 138 kV line. | MI | BRP | [5 empty] | 2024-06-01 | 138 | 0 | 5815000
MTEP20 | Central | AmerenMO | 17046 | Upgrade Kelso 345/161 kV substations | Install new 3000 A circuit breaker and motor-operated disconnect switch on 345 kV position V3. Replace the existing Kelso substation 336 MVA auto transformer #1 with a 560 MVA transformer. Replace the existing Kelso substation 161 kV bus tie 1-2 position H7 circuit breaker and bus disconnect switches. Replace the existing Kelso substation 161 kV position H6 circuit breaker and disconnect switch, upgrade the bus conductor of position H6 to achieve a minimum current carrying capability of 3000 A. Replace the existing Kelso substation H3 and H4 161 kV circuit breakers and disconnect switches in the CAPE-KEL-2 and KEL-MINR-2 terminals. Upgrade Kelso substation positions H3 and H4 bus conductors to achieve a minimum current carry capability of 2000 A. Replace the existing Kelso substation 161 kV disconnect switch on position H10. Replace the existing Kelso substation H11 and H12 161 kV disconnect switches (line and bus) in the CAPE-KEL-3) and KEL-MORLEY-3 terminals. | MO | Other | Age and Condition |  |  |  |  | 2022-12-01 | 345 | 161 | 5800000
MTEP20 | East | ITCT | 18179 | Rebuild of Hood – Lily 120 kV | Rebuild approximately 2.6 miles of 3/0 Cu X2 of the Hood – Lily 120 kV circuit utilizing 954 ACSR on 230kV, double circuit structures. | MI | BRP | [5 empty] | 2024-06-01 | 120 | 0 | 5780000
MTEP20 | Central | DEI | 18329 | Dover to Thorntown 69kV Rebuild | 69134 rebuild from Dover to Thorntown with 477ACSR and light-duty steel poles | IN | Other | Reliability |  |  |  |  | 2021-12-31 | 69 | 0 | 5776000
MTEP20 | Central | DEI | 18330 | Westland Jct. to Westland 69kV Rebuild | 69166 rebuild from Westland Jct. to Westland with 477ACSR and light-duty steel poles | IN | Other | Reliability |  |  |  |  | 2021-12-31 | 69 | 0 | 5770000
MTEP20 | Central | AmerenIL | 18030 | New Meredosia 345 kV shunt reactive device | Install a shunt Reactive device to control voltages at IL-Meredosia 345 kV. | IL | Other | Reliability |  |  |  |  | 2021-04-01 | 345 | 0 | 5700000
MTEP20 | East | METC | 18426 | Mud Lake - Brewer St Tap Rebuild (J758) | Rebuild the 4.4 miles of 336 ACSR from J758 Substation to Convis and Brewer St. Taps with 954 ACSR. | MI | GIP | [5 empty] | 2022-04-08 | 138 | 0 | 5700000
MTEP20 | West | ATC | 19145 | J947 Tennyson SS, Generator Interconnection Facilities and Network Upgrades | Interconnection of a 188 inverter solar farm in Green County, Wisconsin with a 200MW capacity. | WI | GIP | [5 empty] | 2021-09-30 | 138 | 0 | 5608810
MTEP20 | Central | AmerenIL | 18034 | Upgrade Tazewell 138 kV substation | Replace 14 138 kV breakers at Tazewell Substation including: TAZW-138KV BKR 1321-73, TAZW-138KV BKR 1340, TAZW-138KV BKR 1354, TAZW-138KV BKR 1323, TAZW-138KV BKR 1340-63 (TIE), TAZW-138KV BKR 1350 (XFMR 2), TAZW-138KV BKR 1363, TAZW-138KV BKR 1375, TAZW-138KV BKR 1353, TAZW-138KV BKR 1322, TAZW-138KV BKR 1367, TAZW-138KV BKR 1375-53, TAZW-138KV BKR 1327, TAZW-138KV BKR 1321 (XFMR 1) | IL | Other | Age and Condition |  |  |  |  | 2022-12-01 | 138 | 0 | 5600000
MTEP20 | Central | AmerenMO | 18016 | Reconductor Berkley South 161 kV lines 1/2 | Reconductor BERK-S-1 & 2 on branches 1004 and 1005 with composite core conductor. | MO | Other | Reliability |  |  |  |  | 2023-12-01 | 138 | 0 | 5600000
MTEP20 | West | ATC | 18665 | J855 GIC Ebenezer SS - Generator Interconnection Facilities and Network Upgrades | J855 is a 100.8 MW, 28 turbine wind farm in Grant County, Wisconsin with a requested point of interconnection at a new 138kV substation named Ebenezer SS tapping the existing 138kV line, X-16. | WI | GIP | [5 empty] | 2020-11-06 | 138 | 0 | 5526333
MTEP20 | South | Entergy-AR | 19005 | Ritchie 230kV: Expand substation (J834) | The J834 generator interconnection project will require network upgrades at the Entergy Arkansas Ritchie 230kV substation. This will include new interconnection facilites that will consist of two 230kV dead end structures, one 230kV 3000A gas circuit breaker, two 230kV vertical break disconnect switches, 230kV surge arrestors, CCVT's, metering CT's, and all associated relaying panels. There will be 0.4 miles of 666.6 ASCR Falmingo conductor, and 0.3 miles of 7#7 alumoweld conductor installed for the interconnection. Relay settings will be required all all remote end locations as well as the Autotransformer, Transfer Breaker, and the East and West Bus diff. | AR | GIP | [5 empty] | 2022-05-15 | 230 | 0 | 5511000
MTEP20 | Central | DEI | 18285 | WVPA McGrawsville to Bunker Hill 69kV alternate source line | WVPA to build McGrawsville to Bunker Hill 69kV alternate source line - 7.1 miles to be operated N.O. | IN | Other | Reliability |  |  |  |  | 2021-06-01 | 69 | 0 | 5510000
MTEP20 | Central | DEI | 18324 | WVPA Delphi South-6988 Tap Line | WVPA to build new 69kV, 6.3 mile, radial, N.O., alternate source to Delphi South (IPC, Indiana Packers Corp.) from the existing 6988 line tapped between Flora and Rockfield | IN | Other | Reliability |  |  |  |  | 2023-06-01 | 69 | 0 | 5510000
MTEP20 | South | Entergy-LA | 13938 | Cheniere 115 kV: Install transmission breakers | Install transmission breakers at the existing Cheniere 115 kV substation, which is located on the Frostkraft - Sterlington 115 kV transmission circuit. | LA | Other | Reliability |  |  |  |  | 2023-12-01 | 115 | 0 | 5390471
MTEP20 | Central | DEI | 18288 | Trafalgar Swi Sta to HE Samaria Jct 69kV Rebuild | Rbld transmission line 6949 from Duke Trafalgar Swi Sta & HE Trafalgar sub to HE Samaria Jct using light duty steel poles, 477 ACSR and OPGW. Approximately 4.9 miles. | IN | Other | Reliability |  |  |  |  | 2021-12-31 | 69 | 0 | 5280000
MTEP20 | Central | PPI | 18152 | Reconductor Andrew-Amos 69 kV Line | Reconductor 8.9-mile 69 kV line from 336.4 MCM ACSR to 795 MCM ACSR | IL | Other | Reliability |  |  |  |  | 2022-12-31 | 69 | 69 | 5239200
MTEP20 | Central | DEI | 18333 | Greencastle to Greencastle N. 69kV Rebuild | 6933 rebuild from Greencastle to Greencastle N. with 477ACSR and light-duty steel poles | IN | Other | Reliability |  |  |  |  | 2021-12-31 | 69 | 0 | 5231000
MTEP20 | South | Entergy-LA | 18146 | Sherwood Forest 115 kV: Install breakers | Install transmission line breakers at the existing Sherwood Forest 115 kV substation. | LA | Other | Reliability |  |  |  |  | 2023-12-01 | 115 | 0 | 5100000
MTEP20 | West | ATC | 18925 | J818 Jefferson SS Generator Interconnection Facilities and Network Upgrades | Interconnection of a 149 MW solar facility located in Jefferson County, Wisconsin. | WI | GIP | [5 empty] | 2022-04-01 | 138 | 0 | 5032559
MTEP20 | Central | AmerenIL | 18044 | Reconfigure Caterpillar quad 138 kV circuits | Reconfigure the Tazewell-Caterpillar 2-1375, Edwards-Caterpillar 1-1374, RS Wallace-Keystone-1396 and the Caterpillar 2-Hines-1357 138 kV circuits on a 1.5 mile section where they share a common structure. | IL | Other | Reliability |  |  |  |  | 2024-12-01 | 138 | 0 | 5000000
MTEP20 | West | XEL | 18130 | Port Wing - Cornucopia 34.5kV Rebuild | Rebuild 9.6 miles of 34.5kV line from Port Wing to Cornucopia to remediate aging condition issues. | WI | Other | Age and Condition |  |  |  |  | 2023-06-15 | 34.5 | 0 | 5000000
MTEP20 | West | XEL | 18131 | Orienta Tap - Iron River 34.5kV Rebuild | Rebuild 9 miles of 34.5kV line from former Orienta tap switch to Iron River to remediate aging condition issues | WI | Other | Age and Condition |  |  |  |  | 2023-06-15 | 34.5 | 0 | 5000000
MTEP20 | West | XEL | 18132 | Cottage Grove Airgas Load Interconnection | New 115kV in and out substation tapped on Chemolite to Cottage Grove 115kV line to serve new Airgas load interconnection | MN | Other | Load Growth | New 115 kV substation on Chemolite-Cottage Grove 115 kV line to serve new Airgas load | Large Industrial (Airgas) |  |  | 2020-10-01 | 115 | 13.8 | 5000000
MTEP20 | West | ITCM | 9100 | Burlington-4th St-Agency 69kV Rebuild | Rebuild a portion of the Burlington-South Burlington 69kV line and upgrade the Burlington 69kV terminal so the Burlington-South Burlington line is conductor limited. Rebuild the Burlington 4th Street-Agency 69kV line to T2-477 ACSR. | IA | Other | Reliability |  |  |  |  | 2021-05-31 | 69 | 69 | 4939417.2
MTEP20 | Central | AmerenIL | 18032 | New Xenia 345 kV shunt Reactive device | Install a shunt Reactive device to control voltages at Xenia 345 kV | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 345 | 0 | 4900000
MTEP20 | Central | AmerenMO | 15268 | Upgrade Selma-Buck Knob 138 kV line (1302) | Upgrade the DPFE-SEL-1302 138 kV line from Selma Substation to the old Buck Knob substation location with conductor capable of 1600A under summer emergency conditions. Upgrade terminal equipment at Selma to 1600A minimum capability. | MO | Other | Age and Condition |  |  |  |  | 2022-06-01 | 138 | 0 | 4900000
MTEP20 | Central | DEI | 18305 | Westwood 345kV / 138kV relays and breakers replacement | Westwood misc station equipment replacement including: upgrade relays on 13806, 13808, 138345-1, Bk2, 138 bus 1 and 2, 138 bus tie ; Replace OCB 13820, 13883 and relays | IN | Other | Reliability |  |  |  |  | 2021-09-02 | 345 | 138 | 4900000
MTEP20 | West | MP | 17869 | Superior Transmission Line Relocations | Relocate transmission lines around industrial site to enable development | WI | Other | Reliability |  |  |  |  | 2021-11-01 | 161 | 0 | 4900000
MTEP20 | Central | AmerenMO | 17829 | New Loose Creek 345 kV shunt reactor | Install 345 kV shunt reactor at Loose Creek | MO | Other | Reliability |  |  |  |  | 2021-12-01 | 345 | 0 | 4800000
MTEP20 | East | ITCT | 18241 | Stephens Transformer 303 Replacement | Replace Stephens 345/120kV Transformer #303 with a new transformer. | MI | Other | Age and Condition |  |  |  |  | 2023-12-31 | 345 | 120 | 4800000
MTEP20 | East | ITCT | 18178 | Rebuild of Hancock – Lily 120 kV | Rebuild approximately 2 miles of 3/0 Cu X2 of the Hancock - Lily 120 kV circuit utilizing 954 ACSR on 230kV, double-circuit structures. | MI | BRP | [5 empty] | 2024-06-01 | 120 | 0 | 4680000
MTEP20 | Central | AmerenIL | 16705 | Rebuild Pana-Shelbyville South 138 kV line (1430) | Install OPGW and replace shield wire. | IL | Other | Reliability |  |  |  |  | 2021-12-01 | 138 | 0 | 4600000
MTEP20 | West | ITCM | 17980 | Hancock T3 161/69kV Transformer Replacement | Replace the Beaver Channel T1 & T2 75MVA 161/69kV transformers with the spare 150MVA 161/69kV transformer (SN: WT03583) currently located at the Ames substation. Also install a high side breaker for the new transformer at Beaver channel and replace switch 1454. Any new high side equipment should be 1200A minimum and any new low side equipment should be 1600A minimum. Replace the Hancock T3 75MVA 161/69kV transformer with the Beaver Channel T1 75MVA 161/69kV Transformer (SN: 70450A). Also replace the high side circuit switcher 1320 with a 161kV circuit breaker. Re-use switch 1320B if feasible. Any other new required high-side equipment should be 1200A minimum. | IA | Other | Age and Condition |  |  |  |  | 2020-04-30 | 161 | 69 | 4589958
MTEP20 | East | ITCT | 17504 | Abrams Interconnection | Install a new 120kV substation. Extend the Northeast-Skylark line by adding 0.1 miles of 954 ACSR conductor to loop in Abrams interconnection station. Add three 120kV breakers and two bus sections. | MI | Other | Load Growth |  |  |  |  | 2022-10-31 | 120 | 0 | 4519000
MTEP20 | Central | AmerenMO | 18056 | New Mason 138 kV shunt reactive device | Install a shunt Reactive device to control voltages at Mason 3 138 kV bus | MO | Other | Reliability |  |  |  |  | 2023-12-01 | 138 | 0 | 4500000
MTEP20 | West | MEC | 18181 | Black Hawk 345 kV Capacitor | Add 345 kV, 150 MVAR capacitor bank at Black Hawk 345 kV. | IA | GIP | [5 empty] | 2022-06-30 | 345 | 0 | 4500000
MTEP20 | East | ITCT | 18242 | Wayne Transformer 303 Replacement | Replace Wayne 345/120kV Transformer #303 with a new transformer. | MI | Other | Age and Condition |  |  |  |  | 2023-12-31 | 345 | 120 | 4400000
MTEP20 | South | Entergy-AR | 18727 | Marston 161kV: Cut In Switching Station (J944) | Entergy will cut in a new 3 breaker ring bus that will be built by the Interconnection Customer on the Portageville - New Madrid 161kV line section. This bisection will occur near the tenth structure from the New Madrid substation. Approximately 4.52 miles of ADSS fiber shall be installed between Marston and New Madrid. At the remote end Hayti South, the OCB B9150 will be replaced with a SF6 gas circuit breaker rated at 3000 A. | MO | GIP | [5 empty] | 2022-10-01 | 161 | 0 | 4382000
MTEP20 | Central | AmerenIL | 18031 | New Ipava 345 kV shunt Reactive device | Install a shunt Reactive device to control voltages at Ipava 345 kV | IL | Other | Reliability |  |  |  |  | 2021-04-01 | 345 | 0 | 4300000
MTEP20 | East | METC | 15939 | Leoni - Beecher 138 kV Sixed Wire | The proposed solution is to sixed wire 0.21 miles of the Mercer – Cement City Jct. section of the Leoni – Beecher circuit using existing 477 ACSR conductor. Also remediate sag limit on the 6-wired conductor section to increase its summer emergency rating to a minimum of 1196 Amps (286 MVA). | MI | BRP | [5 empty] | 2025-06-01 | 138 | 0 | 4300000
MTEP20 | South | Entergy-LA | 18786 | J909 Station Interconnection Project | This project is to support the interconnection of solar facility J909 at the Amite 115 kV station. | LA | GIP | [5 empty] | 2022-02-15 | 115 | 0 | 4254000
MTEP20 | West | ITCM | 17705 | Madrid North 69kV Substation Rebuild Interconnection | IPL has requested ITC to rebuild the Madrid North Substation to a standard single box and double box with a bus tie breaker to accommodate their 25 kV plans which will include two transformers and 25 kV switchgear. ITC will also need to install a new control enclosure, as IPL will be retiring their existing control enclosure to accommodate their new switch gear. The existing 69 kV circuit switcher will be replaced with a new 69 kV breaker, which will allow for future retirement of the bus work associated with the 69/34.5 kV transformer. The existing zig-zag transformer should be removed to allow additional space for the installation of the new ITC owned control enclosure. The 69/34.5 kV transformer will need to remain until the conversion to 69 kV happens between Dawson and Madrid North (covered on EI Sketch ITCMW_16_034). The existing section of 69 kV bus that feeds the 69/34.5 kV transformer, transformer, and low-side breaker should be re-used, and then removed in the future as part of the 69 kV conversion. | IA | Other | Load Growth |  |  |  |  | 2021-12-31 | 69 | 34 | 4144344
MTEP20 | West | ATC | 19268 | J807 J819 J947 MPFCA Common Use Upgrades | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. -J807 is seeking interconnection service for 41.4 MW -J819 is seeking interconnection service for 99.9 MW -J947 is seeking interconnection service for 200 MW | WI | GIP | [5 empty] | 2021-12-31 | 138 | 0 | 4067713
MTEP20 | Central | AmerenIL | 11969 | New Miles-Misissippi 138 kV line | Construct new 138 kV line | IL | Other | Reliability |  |  |  |  | 2020-12-01 | 138 | 0 | 4000000
MTEP20 | West | ATC | 15930 | Pulliam SS, Transformer Retirement and Bus Reconfiguration | -Removal of Transformer T16 coordinated with retirement of Pulliam Generation Station -Bus Reconfiguration, straight bus to ring bus -Additional asset renewal of relays and removal of unnecessary circuit breakers | WI | Other | Age and Condition |  |  |  |  | 2022-12-31 | 138 | 69 | 4000000
MTEP20 | West | ATC | 18020 | Mackinac HVDC System Control Module (SCM) Asset Renewal | The Mackinac HVDC System Control Modules (SCMs) consist of multiple computer Servers which provide programmable control and protection functions - This project replaces the SCM servers following industry standard and OEM recommended life cycle timelines | MI | Other | Age and Condition |  |  |  |  | 2022-12-31 | 138 | 0 | 4000000
MTEP20 | West | MP | 15598 | Badoura Transformer Replacement | Replace existing 230/115 kV transformer at Badoura Substation. Complete 230 kV ring bus with 3 new 230 kV breakers. | MN | BRP | [5 empty] | 2024-10-31 | 230 | 115 | 4000000
MTEP20 | East | MPPA | 18003 | Barlow to Parsons Line Rebuild | Rebuild 2.73 miles of 69kV line between Barlow and Parsons. Replace 2.73 miles of #477 ACSR with .58 miles of twin #1000 MCM copper under airport flight path and 1.42 miles of #795 ACSS. Rebuild requires Switching Station upgrades at Barlow Substation. | MI | Other | Reliability |  |  |  |  | 2020-12-31 | 69 | 69 | 4000000
MTEP20 | Central | DEI | 17484 | Rebuild Wabash River-Water St. 138 kV line (13845) | Wabash River to Water St. 13845 upgrade existing 477ACSR line conductor's maximum operating temperature from 100C to 120C | IN | BRP | [5 empty] | 2024-06-01 | 138 | 0 | 3950400
MTEP20 | East | METC | 18112 | Kenowa 345 kV Breaker Installation | Complete row 33 of the Kenowa substation by adding 3 breakers and associated equipment. This addition creates a breaker-and-a-half scheme at Kenowa. | MI | Other | Reliability |  |  |  |  | 2022-12-31 | 345 | 0 | 3950000
MTEP20 | Central | DEI | 18289 | HE Needmore Jct to HE Needmore 69kV Rebuild | 6949 Part 2B - Rebuild transmission line using light duty steel poles, 477 ACSR and OPGW from “HE Needmore Jct” (pole #825-3379) to the HE Needmore substation (pole #825-3418); approximately 2 miles. | IN | Other | Reliability |  |  |  |  | 2021-12-31 | 69 | 0 | 3881000
MTEP20 | Central | DEI | 18308 | New Hunts Creek 138/12 kV substation | Hunts Creek 138/12 kV substation: new sub to be located in the 13855 ckt between LGE Ghent 138 kV and DEI Fairview 138 kV | IN | Other | Load Growth |  |  |  |  | 2021-06-01 | 138 | 12 | 3807000
MTEP20 | Central | AmerenMO | 18013 | New Montgomery 345 kV shunt reactor | Install 50 Mvar shunt reactor at Montgomery 345 kV substation. | MO | Other | Reliability |  |  |  |  | 2025-12-01 | 345 | 0 | 3800000
MTEP20 | West | ATC | 14913 | Line Clearance Mitigation Program 2021 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2021. | WI,MI | Other | Reliability |  |  |  |  | 2024-06-30 | 345 | 69 | 3791502
MTEP20 | West | ITCM | 17734 | Clinton Perrin 69/24kV Substation Interconnection | IPL requested a new Clinton Perrin 69/24kV substation in Clinton, IA. The new substation in city of Clinton, will provide capacity for industrial load south/west of town and will support retirement of Beaver Channel sub and Mill Creek sub after 25kV conversion. IPL will install a single transformer, 12.5kV substation, 20/33MVA capacity. Transformer will have 25kV option, but will be replaced by a 30/50MVA unit for final 25kV configuration. Installed XFMR will be moved elsewhere at that time. This conversion is estimated to be 10-20 years after completion of this construction. Four feeders will be used from this substation to serve load. Contingency at 12.5kV will be up to max rating of transformer, 33MVA. Contingency at 25kV will be reviewed and updated at a later date, but may be up to future 50MVA top rating of final unit. | IA | Other | Load Growth |  |  |  | 33 MVA | 2023-12-31 | 69 | 24 | 3787788
MTEP20 | Central | DEI | 18307 | New Westfield East 69/12 kV substation | Westfield East: new sub - 69/12kv - 22.4 MVA xfmr bank, single phase regulators SCADA/IVVC, 2 breakers, and space for second bank. Normal feed from 6917 ckt, alternate from 69142. | IN | Other | Load Growth |  |  |  | 4 MVA | 2022-06-01 | 69 | 12 | 3767000
MTEP20 | Central | AmerenIL | 18085 | Replace Tazewell 345/138 kV transformer No. 1 | Replace 345-138 kV transformer with new 560 MVA unit. | IL | Other | Age and Condition |  |  |  |  | 2022-06-01 | 345 | 138 | 3750000
MTEP20 | Central | AmerenIL | 18086 | Replace Tazewell 345/138 kV transformer no. 2 | Replace 345-138 kV transformer with new 560 MVA unit. | IL | Other | Age and Condition |  |  |  |  | 2024-06-01 | 345 | 138 | 3750000
MTEP20 | Central | AmerenIL | 18088 | Replace Neoga South 345/138 kV transformer | Replace 345-138 kV transformer with new 560 MVA unit. | IL | Other | Age and Condition |  |  |  |  | 2023-06-01 | 345 | 138 | 3750000
MTEP20 | Central | AmerenIL | 18089 | Replace Brokaw 345/138 kV transformer | Replace 345-138 kV transformer with new 560 MVA unit. | IL | Other | Age and Condition |  |  |  |  | 2023-12-01 | 345 | 138 | 3750000
MTEP20 | Central | AmerenIL | 18090 | Replace Albion South 345/138 kV transformer No. 3 | Replace 345-138 kV transformer with new 560 MVA unit. | IL | Other | Age and Condition |  |  |  |  | 2024-12-01 | 345 | 138 | 3750000
MTEP20 | Central | AmerenMO | 18312 | New Blue Bird Solar (J817) interconnection | Add terminal facilities at Warrenton 161 kV substation to interconnect J817, | MO | GIP | [5 empty] | 2023-06-01 | 161 | 0 | 3700000
MTEP20 | Central | IPL | 18135 | Rockville Auto Replace | Replace 345-138 auto with like-for-like replacement | IN | Other | Age and Condition |  |  |  |  | 2020-12-31 | 345 | 0 | 3700000
MTEP20 | Central | IPL | 17564 | Rockville 345 kV Ring Bus | Add one 345 kV breaker to form a ring bus at the Rockville substation. | IN | Other | Reliability |  |  |  |  | 2020-12-31 | 345 | 0 | 3600000
MTEP20 | West | ITCM | 17704 | Cedar Rapids Hunter Field Substation Interconnection | IPL will be building a new 69/24.9 kV substation named Cedar Rapids Hunter Field near the existing Viola’s Corner substation. This new substation will replace Viola’s Corner. The new substation will have 1 new 69/24.9 kV 50 MVA transformer installed initially, with a second transformer to be added in the future as load grows in the area. ITC will build a new 69 kV substation with two single box structures and two breakers installed, one line breaker and one bus tie breaker, and will add an additional line breaker in the future when IPL adds a second transformer. | IA | Other | Load Growth |  |  |  | 50 MVA | 2021-12-30 | 69 | 25 | 3578790
MTEP20 | South | Entergy-AR | 18099 | El Dorado 115kV: Underrated Breakers | Replace the 115 kV breaker(s) at El Dorado with 63 kA fault interrupting capability. B5820, B6258, B6758, B7158, and B7658 will be replaced. | AR | BRP | [5 empty] | 2021-06-01 | 115 | 0 | 3562971
MTEP20 | East | WPSC | 17204 | Upgrade Vestaburg Transformer | Wolverine to install transformer with increased capacity at the Vestaburg Transmission station in order to support the J589 generation interconnection. The capacity of the new transformer will be 168MVA. | MI | GIP | [5 empty] | 2020-02-29 | 138 | 0 | 3520000
MTEP20 | Central | AmerenIL | 16708 | Reconductor Hines-Pioneer 138 kV line (1326) | Replace existing 927 ACAR conductor with ACCR conductor | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 138 | 0 | 3500000
MTEP20 | Central | AmerenMO | 16985 | Rebuild Sioux-Meppen 138 kV Line (4) | Rebuild 3.7 mile Missouri side section (Str. 146-173) of the old Page-Keokuk line w/ T2 conductor. Page-Sioux-4: Rebuild Missouri River crossing (Str. 112-117) w/ 2000A rated conductor. | MO | Other | Age and Condition |  |  |  |  | 2021-06-01 | 138 | 0 | 3500000
MTEP20 | West | MDU | 15784 | Zahl-Corinth 60 kV line | Rebuild Zahl-Corinth 60 kV line | ND | Other | Age and Condition |  |  |  |  | 2023-09-30 | 60 | 0 | 3500000
MTEP20 | West | MP | 18060 | 8 Line Relocation | Relocate & rebuild Fond Du Lac - Thomson 115 kV Line. Add a 115 kV breaker at Fond Du Lac. | MN | Other | Age and Condition |  |  |  |  | 2023-12-31 | 115 | 0 | 3500000
MTEP20 | West | ATC | 17628 | Preble SS, DIC, add 4th transformer and substation rebuild | WPS will: • expand Preble Substation and install a new control house • add the 4th 138/24.9 kV, 22 MVA xfmr with a circuit breaker on the high-side • rebuild and relocate Bank 2 xfmr and upgrade the high-side to a circuit breaker • retire and remove Henry St Substation ATC will: • extend 138 kV bus to the north and the south • relocate both 138 kV line terminals for line X-154 (Highway V – Tower Dr) • replace existing 77/88 MODs with 138 kV line breakers • install a 138 KV bus-tie breaker • retire the 69 kV Henry St Tap on line L-64 (Danz Ave – Finger Road) | WI | Other | Load Growth |  |  |  | 22 MVA | 2022-06-01 | 138 | 0 | 3498694
MTEP20 | West | ITCM | 18114 | Adams 161kV Breaker and 1/2 Upgrade | Add a breaker to the 161kV bus between breakers 0681 and 0680 and relocate the Rochester and Harmony 161kV lines to terminal positions in the newly formed breaker and 1/2 row (install switches, bus work, dead-end, CCVTs, relays, and all necessary equipment as needed). Add a breaker to the 161kV bus between breakers 0685 and 0682 (install switches, bus work, dead-end, CCVTs, relays, and all necessary equipment as needed). Add a breaker to the 161kV bus between breakers 0790 and 0686 (install switches, bus work, dead-end, CCVTs, relays, and all necessary equipment as needed). All equipment needs to be capable of a minimum of 2000 amp operation. | MN | Other | Reliability |  |  |  |  | 2021-09-15 | 161 | 161 | 3381530
MTEP20 | Central | PPI | 18154 | New Alsey 138 kV shunt reactor device (40 Mvar) | Alsey 138 kV substation - Addition of 40 Mvar reactor - BRP | IL | BRP | [5 empty] | 2022-12-31 | 138 | 138 | 3240000
MTEP20 | West | ATC | 17585 | Colley Road SS, Transformer Replacement and Asset Renewal | • Replace 1975 vintage 93 MVA 138/69/12.47 kV power transformer with a 100 MVA new purchase • Replace four sets of three-phase 1960’s vintage hook-stick disconnect switches | WI | Other | Age and Condition |  |  |  |  | 2023-12-31 | 138 | 69 | 3150000
MTEP20 | West | XEL | 18344 | J587 Blazing Star 2 | New 200MW wind generation interconnection with new 345kV - 115kV substation and generation facilities. | MN | GIP | [5 empty] | 2020-09-15 | 345 | 115 | 3104000
MTEP20 | Central | AmerenIL | 17626 | Rebuild Kickapoo-Limit 138 kV line (1325) | Rebuild line from Kickapoo to Limit to 2000A. Double circuit from Limit to McGrath to supply McGrath radially from Limit. | IL | Other | Reliability |  |  |  |  | 2024-12-01 | 138 | 0 | 3100000
MTEP20 | West | MDU | 18257 | Greenway Substation | Build three breaker 41.6 kV ring bus on at junction of three terminal Wishek-Bowdle-Glenham 41.6 kV line. | SD | Other | Reliability |  |  |  |  | 2021-12-31 | 41.6 | 0 | 3100000
MTEP20 | South | Entergy-AR | 19068 | Flat Fork 230kV: Cut In Switching Station (J907) | Entergy Arkansas will construct new surge arrestors, protective relays, RTU, and other supporting equipment at Ritchie 230kV. There will be equipment upgrades performed at Brinkley East substation such as disconnect switches, insulators, station service, protective relays, and other supporting equipment. The Brinkley East - Aubrey 230kV transmission line cut in will consist of two new steel dead end structures, new steel tangent structures, and new monopole structures. The Interconnection Customer will construct the three breaker ring bus substation. | AR | GIP | [5 empty] | 2022-06-01 | 230 | 0 | 3094660
MTEP20 | South | SMEPA | 17004 | Benndale Recip Project | The existing Benndale combustion turbine facility will have two 11MW RICE gas-fired engines installed with a new GSU. The Benndale switching station will be rebuilt and all oil circuit breakers will be replaced with gas circuit breakers and updated relaying package. | MS | GIP | [5 empty] | 2019-12-25 | 69 | 0 | 3010000
MTEP20 | Central | AmerenIL | 18626 | New Delhi 69 kV substation | 69 kV line to new MJM-Delhi substation with 69/12 kV transformer tapping 69 kV line near Jerseyville MJM sub | IL | Other | Load Growth |  |  |  |  | 2022-06-01 | 69 | 0 | 3000000
MTEP20 | East | NIPS | 18484 | J837 J838 GIA Network Upgrades | Reynolds 345kV upgrades to accommodate GI | IN | GIP | [5 empty] | 2021-08-01 | 345 | 0 | 2979556
MTEP20 | South | Entergy-AR | 19728 | Driver 230kV: POI Existing Substation (J1155) | The project involves the expansion of the Driver 230kV substation to interconnect J1155 solar generation project. Upgrades will include installing a new 230kV breaker, CCVT's, conductor for the cut-in, surge arrestors, and CT's. | AR | GIP | [5 empty] | 2022-09-01 | 230 | 0 | 2949000
MTEP20 | Central | PPI | 18123 | New Payson 69 kV Breaker Station | Establish 69 kV breaker station in Adams Electric Cooperative | IL | Other | Reliability |  |  |  |  | 2022-12-31 | 69 | 69 | 2940400
MTEP20 | Central | PPI | 18165 | New Virginia 69 kV Breaker Station | New 69 kV breaker station in Menard Electric Cooperative | IL | Other | Reliability |  |  |  |  | 2023-12-31 | 69 | 69 | 2929500
MTEP20 | South | Entergy-AR | 19727 | Falls 161kV: New Cut In (J1125) | The J1125 135 MW solar project will interconnect to the Wynne South - AECC Wynne East 161kV line section. The cut-in will comprise of four new steel dead-end structures one new steel tangent structure and the removal of two existing structures. New conductors and shield wire will also be installed. Relay panels at the remote end substations of Moses and Parkin will be replaced. | AR | GIP | [5 empty] | 2023-03-01 | 161 | 0 | 2870660
MTEP20 | East | METC | 17384 | J796 (Goss) Network Upgrade | Network upgrades required to connect the J796 project. J796 is capable of 239 MW of solar generation. METC's Goss 138kV station will need to be expanded by adding four 138kv breakers to accommodate the interconnection. | MI | GIP | [5 empty] | 2021-09-01 | 138 | 0 | 2810000
MTEP20 | Central | DEI | 18325 | New NSA Crane ULTF 69/12 kV substation | new sub - "Crane Northwest" to feed NSA Crane ULTF - 17 MW new load to be fed from 69193 ckt - located North of existing NSA owned East and West Substations | IN | Other | Load Growth |  |  |  | 17 | 2021-06-01 | 69 | 12 | 2800000
MTEP20 | West | ITCM | 17967 | Bowen Substation 69kV Conversion | ITC will be converting the Bowen Substation to 69kV. All network path 69kV equipment will be capable of 600A or greater. | IL | Other | Age and Condition |  |  |  |  | 2029-12-30 | 69 | 69 | 2754375
MTEP20 | West | ATC | 12175 | West Middleton - Stage Coach 69 kV (6927), partial rebuild | *Replace the underground cable at West Middleton with a overhead line *Replacement of jumpers, switches and other terminal equipment | WI | Other | Reliability |  |  |  |  | 2023-12-31 | 69 | 0 | 2735023
MTEP20 | West | ITCM | 16710 | J233 J514 GIA Amendment Network Upgrades | The J233 GIA has been amended to include J514, a 65 MVW increase in ERIS and 30 MW of NRIS for the Marshalltown Generating Station. Network upgrades include raising spans on the Marshalltown-Blairstown 115kV and the Blairstown-Prairie Creek 115kV. | IA | GIP | [5 empty] | 2019-09-02 | 115 | 115 | 2732821
MTEP20 | Central | AmerenIL | 18315 | New Galesburg Wind (J844) interconnection | Add 1 BAAH 138 kV leg to the Sandburg Substation and add 1 breaker postion to interconnect J844. | IL | GIP | [5 empty] | 2021-05-28 | 138 | 0 | 2700000
MTEP20 | Central | AmerenMO | 9735 | Upgrade Tyson 138 kV substation | Replace overstressed 138 kV breakers | MO | Other | Reliability |  |  |  |  | 2021-12-01 | 138 | 138 | 2700000
MTEP20 | Central | AmerenIL | 16706 | Rebuild Goose Creek 345 kV ring bus | Rebuild the Goose Creek 345 kV ring bus to 3000A capability. Replace all limiting terminal equipment and bus conductors with equipment capable of 3000A. | IL | Other | Reliability |  |  |  |  | 2022-12-01 | 345 | 0 | 2600000
MTEP20 | Central | AmerenIL | 17828 | Upgrade Kren-Porter Road 138 kV line (1432) | Replace ~6 miles of existing 3 #7 Copperweld shield wire for the entire line. | IL | Other | Age and Condition |  |  |  |  | 2020-06-01 | 138 | 0 | 2600000
MTEP20 | West | MDU | 18254 | Tioga Substation Rebuild | Rebuild Tioga substation due to age and condition | ND | Other | Age and Condition |  |  |  |  | 2021-12-31 | 115 | 60 | 2600000
MTEP20 | West | ITCM | 17736 | Waukon Snakeskin 69kV Substation Interconnection | IPL will be constructing the Waukon Snakeskin 2 transformer 69/25kV substation the replace the nearby Waukon substation. ITC will install 2 box structures, 2 line breakers and 1 tie breaker. The cap bank and cap bank breaker at the existing Waukon substation should be moved to the Decorah side of the Waukon Snakeskin substation if possible or a new cap bank and breaker of equivalent effective rating should be installed. All substation equipment should have a minimum rating of 1200A. ITC will also install short in/out tap lines. | IA | Other | Load Growth |  |  |  |  | 2021-12-31 | 69 | 69 | 2507447
MTEP20 | South | Entergy-MS | 19285 | New 230 kV Switching Station Cut-in - J866 POI | Terminal equipment upgrades required to facilitate POI for generation interconnection customer J866. | MS | GIP | [5 empty] | 2021-07-01 | 230 | 0 | 2502660
MTEP20 | Central | AmerenIL | 17345 | Rebuild Auburn North-Jacksonville 138 kV line | Scope is broken into 3 sections: o Structures 644-668 will be a complete rebuild to 1600A with 795 T2 conductor. O Structures 19-49 are single pole wood and will require structure replacements. O Jacksonville-Auburn North – 5 structure raises | IL | Other | Age and Condition |  |  |  |  | 2020-06-01 | 138 | 0 | 2500000
MTEP20 | West | MP | 17184 | Nemadji Transformer Addition | Expand 115 kV ring bus and add new 115/13.8 kV transformer at Nemadji Switching Station for customer | WI | Other | Load Growth |  |  |  |  | 2021-11-01 | 115 | 13.8 | 2500000
MTEP20 | East | ITCT | 18240 | Install Capacitor at Boyne 120 kV | Low voltage is projected to occur at the Golf 120 kV, Houston 120 kV, and Macomb 120 kV buses for shutdown plus contingency scenarios involving a DTE transformer in surrounding area plus either the Macomb – Stephens 120 kV line or the Golf – Bismarck 120 kV line. The low voltage violations were identified in the 2020, 2023, and 2028 peak and off-peak load models. | MI | BRP | [5 empty] | 2023-12-31 | 120 | 0 | 2430000
MTEP20 | Central | IPL | 18145 | Hanna Substation | Replace three 345 kV breakers. | IN | Other | Age and Condition |  |  |  |  | 2021-12-31 | 345 | 0 | 2400000
MTEP20 | West | ITCM | 17741 | ITCM Customer Interconnects with short lead time 2023 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL | Other | Load Growth |  |  |  |  | 2023-12-31 | 345 | 69 | 2400000
MTEP20 | West | ATC | 19265 | J878 GIC Paris SS, Generator Interconnection Facilities and Network Upgrades | Interconnection Customer will install a 200 MW solar farm interconnecting at the Paris SS in Kenosha County, Wisconsin. | WI | GIP | [5 empty] | 2022-09-30 | 138 | 0 | 2353840
MTEP20 | East | ITCT | 18175 | Rebuild the Van Dyke 2 – Sloan 120 kV Line | Rebuild approximately 0.6 miles 795 ACSR utilizing 1431 ACSR on double circuit structures and upgrade terminal station equipment at Sloan. | MI | BRP | [5 empty] | 2025-06-01 | 120 | 0 | 2350000
MTEP20 | East | METC | 18245 | Kenowa 345kV Reactor 33F Replacement | Replace Kenowa 345kV Shunt Reactor #33F with a new reactor. | MI | Other | Age and Condition |  |  |  |  | 2023-12-31 | 345 | 0 | 2350000
MTEP20 | East | ITCT | 18168 | Reconductor of Bismarck - Red Run 230 kV | Reconductor approximately 2 miles of the Bismarck – Red Run 230 kV circuit utilizing 1431 ACSR and upgrade terminal station equipment at Bismarck and Red Run. | MI | BRP | [5 empty] | 2024-06-01 | 230 | 0 | 2344000
MTEP20 | West | ATC | 17526 | J886 GIC Kewaunee SS Interconnection Facilities and Network Upgrades | To modify the existing 138kV Kewaunee Substation to provide transmission interconnection of the J866 with a total summer capacity of 150MW. | WI | GIP | [5 empty] | 2020-08-01 | 138 | 0 | 2293039
MTEP20 | South | Entergy-AR | 19726 | Bob White 161kV: Cut In Switching Station (J1007) | This project will cut in the J1007 161kV substation on the Marion - Marked Tree 161kV substation. J1007 is a 180 MW solar generating facility with an executed generator interconnection agreement. | AR | GIP | [5 empty] | 2023-06-01 | 161 | 0 | 2276660
MTEP20 | East | ITCT | 16015 | Sunset - Quaker 120 kV Rebuild | The proposed solution is to rebuild 0.259 mile of the Sunset – Quaker 120kV circuit using 2156 ACSR conductor with single circuit steel structures and replace terminal equipment and station equipment at Quaker Pos HD and Sunset Pos HN. | MI | BRP | [5 empty] | 2025-12-31 | 120 | 0 | 2260000
MTEP20 | South | Entergy-AR | 18094 | Hot Springs 115kV SPOF | Install dual primary protection on the 115 kV bus schemes at Hot Springs. | AR | BRP | [5 empty] | 2022-12-31 | 115 | 0 | 2256239
MTEP20 | West | ATC | 18019 | Glenview SS, Transformer Retirement and Breaker & Relay Asset Renewal | -Retire and dispose of the T1 Power Transformer including the station power -Replace 5 69kV oil circuit breakers and 2 138kV oil circuit breakers -Replace 8 disconnect switches -Install line arresters on the E-57 and GLWG21 138kV line terminals and retire bus 1 and 2 arresters | WI | Other | Age and Condition |  |  |  |  | 2023-12-31 | 138 | 69 | 2200000
MTEP20 | East | METC | 18073 | Reconductor Argenta - Riverview 138kV | The proposed solution is to reconductor approximately 3 miles of the Argenta - Riverview 138kV circuit using 1431 ACSR conductor. Also upgrade relay at Argenta pos. 14MB to meet or exceed 385 MVA (1612 Amps). | MI | BRP | [5 empty] | 2024-06-01 | 138 | 0 | 2200000
MTEP20 | Central | AmerenMO | 17065 | Upgrade Tegeler 138 kV substation | Install a new 2000 A circuit breaker and associated disconnect switches in the TGLR-BLAN-6756 138 kV line terminal. Replace the existing 1600 A circuit breaker and associated 1200 A disconnect switches and 1590 kcmil AAC bus conductor at position H5 with equipment capable of carrying 2000 A during summer emergency conditions. Increase relay load limit. Replace the existing 1200 A disconnect switches and 1590 kcmil AAC bus conductor in position H9 to match the capability of the 2000 A circuit breaker. Install 2 circuit switchers on the high-side of the new and existing 138/34.5 kV transformers, having a minimum continuous current rating of 600 A. | MO | Other | Age and Condition |  |  |  |  | 2021-12-01 | 138 | 0 | 2100000
MTEP20 | West | MEC | 18151 | Granger Tap-100th St & 54th Ave 161 kV Reconductor | Reconductor Granger Tap-100th St & 54th Ave 161 kV line with T2-795 ACSR Drake. | IA | GIP | [5 empty] | 2021-12-31 | 161 | 0 | 2085000
MTEP20 | South | SMEPA | 18180 | Missionary 230kV Reactor Bank | Add new bay and breaker at Missionary 230 kV substation. Add new Reactor Bank (Single Stage 30 MVAR) at Missionary 230 kV substation. | MS | Other | Reliability |  |  |  |  | 2021-03-01 | 230 | 0 | 2055000
MTEP20 | Central | AmerenIL | 17827 | Upgrade Cottage Hills-Stallings 161 kV line (1622) | Replace ~4 miles of existing 3 #7 Copperweld shield wire from Str. 51-Wanda Sub | IL | Other | Age and Condition |  |  |  |  | 2020-12-01 | 138 | 0 | 2000000
MTEP20 | Central | AmerenIL | 18041 | Upgrade Ottawa 138 kV substation | Install new line breaker on the HENN-OGLE-1516 line at Ottawa Substation. | IL | Other | Reliability |  |  |  |  | 2022-12-01 | 138 | 0 | 2000000
MTEP20 | Central | AmerenIL | 18042 | Upgrade Wedron-Fox River 138 kV line (1652) | Install new line breaker on the OTTA-FOXR-1652 circuit at Wedron Fox River Substation. | IL | Other | Reliability |  |  |  |  | 2022-12-01 | 138 | 0 | 2000000
MTEP20 | Central | AmerenIL | 18080 | Upgrade Meredosia E 138 kV substation | Replace breakers MERE-138KV BT 1938, MERE-138KV BT 1958, MERE-138KV BKR 1957, MERE-138KV BKR 1947 and MERE-138KV BT 1948 at Meredosia East Substation. | IL | Other | Age and Condition |  |  |  |  | 2023-12-01 | 138 | 0 | 2000000
MTEP20 | Central | AmerenIL | 18625 | New MJM-Nutwood 69 kV line | New 69 kV loop feed to the MJM-Nutwood 69/12kV substation | IL | Other | Reliability |  |  |  |  | 2022-12-31 | 69 | 0 | 2000000
MTEP20 | Central | IPL | 18142 | Mooresville Substation | Add a total of two new 138 kV breakers and convert the substation to a ring bus. | IN | Other | Age and Condition |  |  |  |  | 2021-12-31 | 138 | 0 | 2000000
MTEP20 | South | AECC | 18805 | NUCOR Cap Bank | AECC to install a 60 MVAR capacitor bank at Hickman North substation in Mississippi County Electric. | AR | BRP |  | Mitigate low voltages for N-1 contingency; feeds Hickman North / NUCOR II steel plant | Large Industrial (NUCOR) |  |  | 2021-06-01 | 161 | 0 | 2000000 | NUCOR steel plant load
MTEP20 | South | Entergy-LA | 15568 | Oak Grove 138kV : Add Breaker | Install transmission breakers at the existing Oak Grove 138 kV substation, located on the Willow Glen to Gonzales 138 kV transmission circuit. | LA | Other | Reliability |  |  |  |  | 2022-12-01 | 138 | 0 | 2000000
MTEP20 | West | CMMPA | 18118 | Windom_Transmission_Upgrade | Windom Municipal Utilities (WMU) has two transmission lines that source the Power Plant Substation. The south transmission line is sourced from the ITC substation located south of the city. This line is approximately 1.5 miles. The east transmission line interconnects with an ITC 69 kV transmission line on the east side of the city. This line is approximately 1.36 miles. It appears both transmission lines were constructed circa 1971. WMU has indicated it would like to relocate the south transmission line along the 1st Avenue between the Power Plant substation and 6th Street. This section of line has two overhead distribution circuits under built on the transmission structures. WMU indicated that the distribution lines could be converted to underground. In addition, WMU has requested a cost estimate to construct a new 69 kV transmission to the north of the city for a possible future substation. This new segment would replace the existing east transmission line that interconnects with ITC east of the city. | MN | Other | Age and Condition |  |  |  |  | 2021-12-15 | 69 | 0 | 2000000
MTEP20 | East | CETO | 18886 | Jaguar 138 kV Lines | Construct two new 138 kV lines from CE's new Morrow South Substation to METC's new Jaguar station. | MI | Other | Load Growth |  |  |  |  | 2022-12-31 | 138 | 0 | 2000000
MTEP20 | East | ITCT | 17744 | ITCT Customer Interconnections - Year 2023 | Customer interconnection requests and retirements less than $1 million with in service date in year 2023. | MI | Other | Load Growth |  |  |  |  | 2023-12-31 | 120 | 0 | 2000000
MTEP20 | East | METC | 17745 | METC Customer Interconnections - Year 2023 | Customer interconnection requests and retirements less than $1 million with in service dates in the year 2023. | MI | Other | Load Growth |  |  |  |  | 2023-12-31 | 138 | 0 | 2000000
MTEP20 | Central | SIGE | 15961 | Rebuild Y31-1 NW - ORS 69 kV | Rebuild ~2.1 miles of 69 kV overhead transmission between the Northwest and Ohio River Station substations (line Y31-1). | IN | Other | Age and Condition |  |  |  |  | 2022-12-31 | 69 | 0 | 1930000
MTEP20 | Central | AmerenIL | 18096 | Upgrade Goose Creek 345 kV substation | Replace breakers GOSC-345KV BKR 4545, GOSC-345KV BKR 4575 and GOSC-345KV LT BKR 4555 at Goose Creek Substation. | IL | Other | Age and Condition |  |  |  |  | 2023-12-01 | 345 | 0 | 1800000
MTEP20 | South | Entergy-LA | 18785 | J639 Station Interconnection Project | This project is to support the interconnection of solar project J639 on 230 kV line 731 (Addis to Big Cajun). | LA | GIP | [5 empty] | 2022-10-20 | 230 | 0 | 1790777
MTEP20 | West | ATC | 19225 | J864 Lone Rock SS Generator Interconnection Facilities and Network Upgrades | Interconnection of a 49.98 MW solar farm at the Lone Rock SS. | WI | GIP | [5 empty] | 2022-09-01 | 69 | 0 | 1767400
MTEP20 | South | Entergy-AR | 18100 | Danville 161kV: Install Cap Bank | Install a 24 MVAR cap bank at Danville 161kV | AR | Other | Reliability |  |  |  |  | 2023-06-01 | 161 | 0 | 1755533
MTEP20 | Central | AmerenIL | 17826 | Upgrade Greenville McCord-South Centralia 138 kV line (1419) | Replace ~22 miles of existing 5/16" HS Steel Shield Wire with 1 3/8" E.H.S. Steel Shield Wire and 1 OPGW | IL | Other | Age and Condition |  |  |  |  | 2022-12-01 | 138 | 0 | 1700000
MTEP20 | Central | AmerenIL | 18314 | New McLean County Wind (J826) interconnection | Add breaker position to existing ring bus at Weedman 138 kV Substation for the J826 interconnection. | IL | GIP | [5 empty] | 2021-05-28 | 138 | 0 | 1700000
MTEP20 | Central | SIGE | 15950 | Hemenway 69/12 kV Dist. T1 Repl. | Replace 69/12 kV distribution transformer T1 at the Hemenway substation | IN | Other | Age and Condition |  |  |  |  | 2022-12-31 | 69 | 0 | 1700000
MTEP20 | Central | SIGE | 15958 | Rockport 69/12 kV T2 Repl. | Replace 69/12 kV distribution transformer T2 at the Rockport substation | IN | Other | Age and Condition |  |  |  |  | 2022-12-31 | 69 | 12 | 1700000
MTEP20 | Central | AmerenMO | 16504 | Reconfigure Viburnum 161/34 kV Substation | Install 2 161 kV line breakers and 1 161 kV circuit switcher on the transformer to split the CLK-CMCO-2 line and create 2 circuits into Viburnum Substation. | MO | Other | Reliability |  |  |  |  | 2023-12-01 | 161 | 34 | 1600000
MTEP20 | Central | AmerenMO | 17805 | Rebuild Campbell-Maline 138 kV lines 1/2 | Replace existing conductor with composite core conductor on branches 93 and 94. | MO | Other | Reliability |  |  |  |  | 2021-12-01 | 138 | 0 | 1600000
MTEP20 | Central | AmerenMO | 17909 | Upgrade Campbell-Euclid 161 kV line | Replace shield wires on the Campbell-Euclid-4 circuit. Replace structures and crossarms as needed. | MO | Other | Age and Condition |  |  |  |  | 2021-12-01 | 138 | 0 | 1600000
MTEP20 | West | MRES | 18906 | McLeod Cap Bank Addition | The August 2016 West DPP cycle identified a network upgrade at the McLeod 230 kV bus. The project involves adding a switchable 50 MVAR capacitor bank to mitigate low voltages. | MN | GIP | [5 empty] | 2021-09-01 | 230 | 0 | 1600000
MTEP20 | West | MP | 17870 | National Taconite Breaker Replacements | Replace existing breakers and associated equipment at National Taconite Substation | MN | Other | Age and Condition |  |  |  |  | 2021-12-31 | 115 | 0 | 1580000
MTEP20 | East | ITCT | 18525 | Brownstown 3 345 kV - Upgrade 345 kV Switches | Upgrade five (5) 345 kV switches (“ED”, “FD”, “FH”, “FK”, “FO”) at Brownstown 3 345 kV station. | MI | Other | Reliability |  |  |  |  | 2021-12-31 | 345 | 0 | 1560000
MTEP20 | West | GRE | 17986 | Lake Jennie Tap 69 kV Line Rebuild | Rebuild 2.77 miles of Lake Jennie Tap line. | MN | Other | Age and Condition |  |  |  |  | 2021-11-01 | 69 | 0 | 1550000
MTEP20 | West | MEC | 18183 | Midport 161 kV Capacitor | Add 161 kV, 50 MVAR capacitor at Midport. Includes addition of 161 kV circuit breakers on 161 kV line terminals. | IA | GIP | [5 empty] | 2021-12-31 | 161 | 0 | 1545000
MTEP20 | West | ITCM | 17724 | Sixth Street 115kV Substation Retirement | Once the remaining 34.5 kV lines at the Sixth St Substation are converted to 69 kV, the remaining substation equipment should be retired, including any control enclosures and fence, etc. The 34.5 kV lines will be connected to bypass the substation as part of the conversion work, but the 115 kV lines will need to be connected to bypass the substation as part of the substation retirement project. The communications currently routed through Sixth Street will also need to be moved/removed before the retirement can be completed. | IA | Other | Age and Condition |  |  |  |  | 2023-01-31 | 115 | 34 | 1506540
MTEP20 | East | ITCT | 17124 | Frisbie - Midtown 120kV Cable Relocation | Relocate the Frisbie-Midtown underground circuit out of the current location in the Milwaukee Ave bridge over I-75. Utilize 954 ACSR on overhead structures from each side of I-75. | MI | Other | Other Local Needs |  |  |  |  | 2021-06-01 | 120 | 0 | 1500000
MTEP20 | East | METC | 17997 | Donaldson Creek Interconnection Phase 2 | Build a new breaker row 13, breakers 13B7 and 13M9 with associated switches and terminate a new WPSC line to Rodgers. | MI | Other | Other Local Needs |  |  |  |  | 2022-06-01 | 138 | 0 | 1450000
MTEP20 | West | ATC | 19246 | J864 J870 J871 J947 MPFCA Common Use Upgrades | Each individual Customer is responsible for a proportionate percentage share of the Common Use Upgrades estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU - J864 Customer is seeking interconnection service for 49.98 MW - J870 Customer is seeking interconnection service for 200 MW - J871 Customer is seeking interconnection service for 100 MW - J947 Customer is seeking interconnection service for 200 MW | WI | GIP | [5 empty] | 2021-03-31 | 138 | 0 | 1406518
MTEP20 | Central | AmerenIL | 17604 | Upgrade Stallings-Roxford 345 kV line (4581) | Upgrade 345 kV switches V4A and V4b to 3000A. Remove the 2000A wave trap. Install OPGW. | IL | Other | Reliability |  |  |  |  | 2023-12-01 | 345 | 0 | 1400000
MTEP20 | West | GRE | 17988 | Lake Mary 115 kV Conversion | Convert the GRE/REA Lake Mary substation from 41.6 kV to 115 kV service. | MN | Other | Reliability |  |  |  |  | 2022-11-30 | 115 | 0 | 1400000
MTEP20 | West | XEL | 17989 | EREPC Wellington Interconnection | Install new 3 way switch and 4 mile 69Kv line to new EREPC Wellington substation | MN | Other | Load Growth |  |  |  |  | 2020-09-01 | 69 | 0 | 1320000
MTEP20 | Central | AmerenMO | 17344 | Upgrade Berkeley 138 kV Substation | Replace 138 kV bus tie 1-2 and 2-3 breakers. Upgrade position to 2000A. | MO | Other | Age and Condition |  |  |  |  | 2021-12-01 | 138 | 0 | 1300000
MTEP20 | Central | AmerenMO | 17625 | Upgrade McClay 138 kV Substation | Add breakers to each of the 138 kV lines and upgrade relays. | MO | Other | Reliability |  |  |  |  | 2022-12-01 | 138 | 0 | 1300000
MTEP20 | West | MP | 15593 | 25 Line Upgrade | Increase rating of Hibbing - Virginia 115 kV Line | MN | BRP | [5 empty] | 2022-03-31 | 115 | 0 | 1280000
MTEP20 | West | MP | 15592 | Hibbing 14 Line Upgrade | Increase rating of Hibbing - 14 Line Tap 115 kV Line | MN | BRP | [5 empty] | 2021-10-31 | 115 | 0 | 1230000
MTEP20 | West | ITCM | 18113 | J523 Generator Interconnection Network Upgrades | Add two 161kV breakers in series with the bus-tie breaker 6620 to create a breaker and 1/2 row. Relocate the line for the Adams 345/161kV transformer from the existing terminal to a new terminal position on a breaker and 1/2 row (install dead end, coordinate relocation of metering with Xcel, and replace necessary equipment to accommodate the relocation of the transformer terminal). All new equipment must be capable of 2000 amp operation. | MN | GIP | [5 empty] | 2021-09-15 | 161 | 161 | 1217897
MTEP20 | Central | AmerenIL | 17907 | New Prairie Wolf Solar Farm (J949) interconnection | Add terminal facilities including one 138 kV breaker at Kansas Substation. | IL | GIP | [5 empty] | 2021-10-01 | 138 | 0 | 1200000
MTEP20 | Central | AmerenIL | 18039 | Upgrade Havana 138 kV substation | Replace breakers HAV-138KV BKR 1406, HAV-138KV BT BKR 1302 and HAV-138KV BKR 1422 at Havana Substation. | IL | Other | Age and Condition |  |  |  |  | 2022-12-01 | 138 | 0 | 1200000
MTEP20 | Central | AmerenIL | 18316 | New Big River Solar (J853) interconnection | Add terminal facilities to the Norris City North 138 kV bus to interconnect J853. | IL | GIP | [5 empty] | 2021-05-28 | 138 | 0 | 1200000
MTEP20 | Central | PPI | 18120 | Upgrade Berlin-Amos 69 kV Line | Upgrade 3-mile portion of Berlin to Amos 69 kV line from 4/0 ACSR to 336.4 MCM ACSR associated with fiber and distribution installation | IL | Other | Age and Condition |  |  |  |  | 2021-12-31 | 69 | 69 | 1200000
MTEP20 | Central | PPI | 18159 | Upgrade East Lanesville 138/69 kV transformer | Upgrade existing 37.33 MVA transformer with 84 MVA unit. Existing transformer will be moved to Kuhlman | IL | Other | Reliability |  |  |  |  | 2022-12-31 | 138 | 69 | 1200000
MTEP20 | Central | SIGE | 15860 | Broadview 69/12 kV Dist. T2 Repl | Replace 69/12 kV distribution transformer T2 at the Broadview substation | IN | Other | Age and Condition |  |  |  |  | 2022-12-31 | 69000 | 0 | 1200000
MTEP20 | Central | SIGE | 15940 | East Industrial Trans. Repl. | Replace the 69/12 kV distribution transformer at the East Industrial substation. | IN | Other | Age and Condition |  |  |  |  | 2022-12-31 | 69 | 0 | 1200000
MTEP20 | Central | SIGE | 15948 | Fairlawn 69/12 kV Dist. T1 Repl. | Replace the 69/12 kV distribution transformer T1 at the Fairlawn substation. | IN | Other | Age and Condition |  |  |  |  | 2022-12-31 | 69 | 0 | 1200000
MTEP20 | Central | SIGE | 15949 | Fuquay 69/12 kV Dist. T1 Repl. | Replace 69/12 kV distribution transformer T1 at the Fuquay substation | IN | Other | Age and Condition |  |  |  |  | 2022-12-31 | 69 | 0 | 1200000
MTEP20 | Central | SIGE | 15960 | St. Phillips 69/12 kV T1 Repl. | Replace 69/12 kV distribution transformer T1 at the St. Phillips substation | IN | Other | Age and Condition |  |  |  |  | 2022-12-31 | 69 | 12 | 1200000
MTEP20 | West | MEC | 18127 | Sycamore: 345 kV Equipment Upgrades | At the Sycamore substation, replace two 345 kV circuit breakers, associated disconnect switches, and jumpers to increase the rating of the Grimes-Sycamore 345 kV south line. | IA | GIP | [5 empty] | 2021-06-30 | 345 | 0 | 1200000
MTEP20 | West | MEC | 18280 | Floyd 161-69 kV Transformer Terminal Upgrade | Replace terminal equipment adjacent to Floyd Substation 161-69 kV Transformer AB. | IA | Other | Reliability |  |  |  |  | 2020-11-01 | 161 | 69 | 1200000
MTEP20 | West | XEL | 17985 | Rosemount 2nd XFMR | Add second 115/34.5 kV transformer to Rosemount Substation | MN | Other | Reliability |  |  |  |  | 2020-12-15 | 115 | 34.5 | 1200000
MTEP20 | West | OTP | 10043 | Jamestown 345 Breaker Addition | Install an additional 345 kV breaker to meet TPL-001-4 Compliance Standard. | ND | BRP | [5 empty] | 2020-07-03 | 345 | 0 | 1178852
MTEP20 | Central | AmerenMO | 18139 | Upgrade Labadie 345 kV substation | Upgrade switches and CTs to 3000A. Labadie 345 kV bus-tie 2-3 Upgrade | MO | BRP | [5 empty] | 2022-12-01 | 345 | 0 | 1100000
MTEP20 | Central | SIGE | 15987 | Berry Plastics Dist. XFMR Repl. | Replace one of the distribution transformers serving Berry Plastics. (PSP project) | IN | Other | Age and Condition |  |  |  |  | 2024-12-31 | 69 | 0 | 1100000
MTEP20 | East | ITCT | 18205 | Upgrade Red Run 120 kV Station Equipment | Upgrade the station equipment at Redrun 120 kV station. | MI | BRP | [5 empty] | 2023-12-31 | 120 | 0 | 1100000
MTEP20 | East | ITCT | 19607 | Brownstown - Navarre #2 230 kV Sag Remediation | Remediate the sag on the Brownstown - Navarre #2 230 kV circuit up to the conductor limit and upgrade station equipment at Navarre 230 kV Station | MI | BRP | [5 empty] | 2024-06-01 | 230 | 0 | 1070000
MTEP20 | West | MEC | 18128 | Raun: Retire 13 kV Reactors | Retire the three 13.8 kV reactors at Raun substation and replace relaying and switching device on Raun 345 kV reactor | IA | Other | Reliability |  |  |  |  | 2021-06-01 | 345 | 0 | 1030000
MTEP20 | East | ITCT | 16024 | River Rouge 120 kV Capacitor | Install a three 18 MVAR capacitors at River Rouge 120 kV station. | MI | BRP | [5 empty] | 2023-12-31 | 120 | 0 | 1030000
MTEP20 | East | METC | 18384 | Sag Remediation Bullock - Saginaw River | Increase the sag limits on the Bullock to Gleaner J and Gleaner J to Hacket J sections of the Bullock - Saginaw River 138 kV circuit | MI | GIP | [5 empty] | 2020-12-31 | 138 | 0 | 1024800
MTEP20 | Central | SIGE | 18268 | Grandview Generation Interconnect | Installation of Interconnection Facilities and Network Upgrades for generation interconnection project J783 at the Grandview 69 kV substation. | IN | GIP | [5 empty] | 2021-04-01 | 69 | 0 | 1017496
MTEP20 | Central | AmerenIL | 18045 | Upgrade Murdock 138 kV substation | Install a 138 kV circuit switcher on the high-side of XFMR #1 at Murdock Substation. | IL | Other | Reliability |  |  |  |  | 2023-06-01 | 138 | 0 | 1000000
MTEP20 | Central | AmerenIL | 18705 | Bypass Coffeen 345 kV Switchyard | Bypass the Coffeen 345 kV switchyard by re-terminating the lines at the Coffeen North 345 kV substation. | IL | Other | Reliability |  |  |  |  | 2020-06-01 | 345 | 0 | 1000000
MTEP20 | Central | AmerenMO | 17865 | Upgrade Lakeshire 161 kV substation | Replace 40 kA breakers on positions H and U for cap banks 2A and 2B with 50 kA breakers. | MO | Other | Reliability |  |  |  |  | 2022-12-01 | 138 | 0 | 1000000
MTEP20 | West | GRE | 18025 | Cannon River Park 115 kV Substation | Construct a new 115 kV transmission line from Cannon River Park to the Cannon River Park tap in the Xcel 0832 line near the Xcel Faribault Energy Park. | MN | Other | Load Growth |  |  |  |  | 2021-03-05 | 115 | 0 | 1000000
MTEP20 | West | MP | 18064 | Hibbing Breaker Replacements | Replace existing 115 kV circuit breakers and associated equipment at Hibbing Substation | MN | Other | Age and Condition |  |  |  |  | 2022-10-31 | 115 | 0 | 1000000
MTEP20 | East | CETO | 17993 | Muskegon #2 Line Rebuild | Rebuild a portion of the Muskegon #2 138 kV Line, approximately 2.1 miles, utilizing 138 kV single circuit construction | MI | Other | Age and Condition |  |  |  |  | 2022-12-31 | 138 | 0 | 1000000
MTEP20 | East | WPSC | 18015 | Cadillac Substation Line Modifications | Line modifications including structure relocation and switch replacement in order to accommodate a new Cadillac distribution station. | MI | Other | Load Growth |  |  |  |  | 2021-12-31 | 69 | 0 | 1000000
MTEP20 | Central | BREC | 18012 | Hardinsburg Upgrade | Add a 161 kV breaker and upgrade protection equipment | KY | Other | Reliability |  |  |  |  | 2023-06-01 | 161 | 0 | 980000
MTEP20 | East | METC | 18133 | Station Eq. Upgrades Pere Marquette 138 kV 5M9 & 7W8 | Upgrade two breakers (at positions 5M9 and 7W8) and other terminal station equipment at the Pere Marquette 138 kV station. | MI | BRP | [5 empty] | 2022-12-31 | 138 | 0 | 970000
MTEP20 | East | ITCT | 18313 | Sag Remediation of Bauer - Pontiac 345 kV | Raise the sag limit on the 2-954 ACSR 54/7 conductor span of the Bauer - Pontiac 345 kV circuit to achieve a summer emergency rating of at least 1258 MVA. | MI | GIP | [5 empty] | 2020-12-31 | 345 | 0 | 961200
MTEP20 | West | OTP | 19685 | OTP Hoot Lake 115/41.6 kV Transformer Replacement | Replace Hoot Lake 115/41.6 kV Transformer with 115/41.6/34.5 kV Transformer with higher capacity and LTC. | MN | Other | Age and Condition |  |  |  |  | 2021-12-31 | 115 | 41.6 | 950000
MTEP20 | West | ITCM | 17966 | Metform Substation 69kV Conversion | ITC will be converting the Metform Substation to 69kV. All network path 69kV equipment will be capable of 1200A or greater. All network path switches will need to be replaced to be capable of 1200A or greater. ITC will retire the bypass bus and switches. | IL | Other | Age and Condition |  |  |  |  | 2021-12-31 | 69 | 69 | 925200
MTEP20 | West | ATC | 19269 | J864 J870 J871 MPFCA Common Use Upgrades | Each individual Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. -J864 Customer is seeking interconnection service for 49.98 MW -J870 Customer is seeking interconnection service for 200 MW -J871 Customer is seeking interconnection service for 100 MW | WI | GIP | [5 empty] | 2021-03-31 | 138 | 0 | 915243
MTEP20 | South | SMEPA | 18224 | Batesville 161 kV Bus Reconfigure | Reconfigure the Batesville 161kV substation so that the Batesville - Batesville TVA ties lines do not share a common breaker. | MS | BRP | [5 empty] | 2022-06-01 | 161 | 0 | 910000
MTEP20 | Central | AmerenIL | 17864 | Upgrade Cahokia 345/138 kV substation | Replace OCB H27 on the C-GRAT-3 position and OCB H35 on the C-RUSL-2 positon with symmetrically rated SF6 55 kA circuit breakers. | IL | Other | Reliability |  |  |  |  | 2022-12-01 | 138 | 0 | 900000
MTEP20 | Central | AmerenIL | 18322 | New City of Roses Wind (J848) interconnection | Add terminal facilities at the Pana 138 kV Substation to make the inteconnection for J848. | IL | GIP | [5 empty] | 2021-05-28 | 138 | 0 | 900000
MTEP20 | Central | AmerenIL | 18706 | Bypass Duck Creek 345 kV Switchyard | Bypass the Duck Creek 345 kV switchyard. | IL | Other | Reliability |  |  |  |  | 2020-06-01 | 345 | 0 | 900000
MTEP20 | Central | IPL | 17884 | Replace Southeast #4 Breaker | Replacement of one (1) 138 kV breaker at Southeast, #4 | IN | BRP | [5 empty] | 2025-12-31 | 138 | 0 | 900000
MTEP20 | Central | IPL | 17885 | Replace Southeast #6 Breaker | Replacement of one (1) 138 kV breaker at Southeast, #6 | IN | BRP | [5 empty] | 2025-12-31 | 138 | 0 | 900000
MTEP20 | Central | IPL | 17886 | Replace Southeast #8 Breaker | Replacement of one (1) 138 kV breaker at Southeast, #8 | IN | BRP | [5 empty] | 2025-12-31 | 138 | 0 | 900000
MTEP20 | Central | IPL | 17887 | Replace Stout South #1A Breaker | Replacement of one (1) 138 kV breaker at Stout South #1A | IN | BRP | [5 empty] | 2023-12-31 | 138 | 0 | 900000
MTEP20 | Central | IPL | 17888 | Replace Southport #2 Breaker | Replacement of one (1) 138 kV breaker at Southport, #2 | IN | BRP | [5 empty] | 2023-12-31 | 138 | 0 | 900000
MTEP20 | East | WPSC | 14005 | Hammond Bay Interconnection Line | Construct approximately 2 miles of new transmission line to connect the Hammond Bay Distribution Station to METC’s 138 kV transmission line. | MI | Other | Load Growth |  |  |  |  | 2022-12-31 | 138 | 0 | 900000
MTEP20 | West | XEL | 18444 | J526 Panther - HUC-McLeod upgrade | Replace structures on HUC - McLeod 230kV line to increase capacity to accommodate J526 wind generation. | MN | GIP | [5 empty] | 2020-03-31 | 230 | 0 | 880000
MTEP20 | West | ATC | 18566 | J807 GIC Falcon SS Addition - Generator Interconnection Facilities and Network Upgrades | A 41.4 MW wind farm in Lafeyette County, Wisconsin. Customer has requested a Point of Interconnection (POI) at a new terminal at the existing 138kV Falcon Substation. | WI | GIP | [5 empty] | 2021-08-27 | 138 | 0 | 870186
MTEP20 | East | METC | 18043 | Sag Remediation Scott Lake - Argenta 138kV | The proposed solution is to remediate sag limit on the Scott Lake - Trowbridge 138kV section to increase its summer emergency rating to a minimum of 219 MVA (917 Amps) and also remediate sag limit on the Trowbridge - Argenta 138kV section to increase its summer emergency rating to a minimum of 235 MVA (985 Amps). | MI | BRP | [5 empty] | 2023-12-31 | 138 | 0 | 830000
MTEP20 | East | METC | 18004 | Sag Remediation Meyer - Briggs & Stratton Jct. 138kV | The proposed solution is to remediate the sag limit on the 6.02 mile-long length of 795 ACSR conductor of the Tanner – Briggs & Stratton Jct. 138kV section to increase its summer emergency rating to a minimum of 262 MVA/1096 Amps. Also completely remediate the sag limit on the 8.25 mile-long length of 795 ACSR conductor of the Meyer - Tanner 138kV line to conductor limit. | MI | BRP | [5 empty] | 2023-12-31 | 138 | 0 | 807000
MTEP20 | Central | AmerenIL | 18037 | Upgrade Decatur N 27th Street 138 kV substation | Replace breakers N27D-138KV BKR 1522 and N27D-138KV BKR 1602 at Decatur North 27th street. | IL | Other | Age and Condition |  |  |  |  | 2022-12-01 | 138 | 0 | 800000
MTEP20 | Central | AmerenIL | 18081 | Upgrade Newton 138 kV substation | Replace 138 kV breakers NWTY-138KV LT 1869 and NWTY-138KV LT 1868 at the Newton switchyard. | IL | Other | Age and Condition |  |  |  |  | 2023-12-01 | 138 | 0 | 800000
MTEP20 | Central | AmerenIL | 18093 | Upgrade Fargo 138 kV substation | Replace breakers FARG-138KV BKR & LINE 1394 and FARG-138KV BKR 1371 at Fargo Substation. | IL | Other | Age and Condition |  |  |  |  | 2024-12-01 | 138 | 0 | 800000
MTEP20 | Central | AmerenIL | 18095 | Upgrade Gibson City S 138 kV substation | Replace breakers GBCS-138KV LINE 1524 and GBCS-138KV LINE 1522 at Gibson City South Substation. | IL | Other | Age and Condition |  |  |  |  | 2024-12-01 | 138 | 0 | 800000
MTEP20 | Central | AmerenIL | 18105 | Upgrade Makanda N 138 kV substation | Replace breakers MAKN-138KV LINE 1674 and MAKN-138KV LINE 1672 at Makanda North Substation. | IL | Other | Age and Condition |  |  |  |  | 2024-06-01 | 138 | 0 | 800000
MTEP20 | Central | AmerenIL | 18106 | Upgrade Marblehead N 138 kV substation | Replace breakers MRBN-138KV LINE 1852 and MRBN-161/138KV XFMR 1 at Marblehead north substation. | IL | Other | Age and Condition |  |  |  |  | 2024-06-01 | 161 | 138 | 800000
MTEP20 | Central | AmerenIL | 18108 | Upgrade Watseka 138 kV substation | Replace breakers WATK-138KV LINE 1372 and WATK-138KV LINE 1374 at Watseka Substation. | IL | Other | Age and Condition |  |  |  |  | 2024-12-01 | 138 | 0 | 800000
MTEP20 | Central | AmerenIL | 18279 | Upgrade South Ottawa 138 kV substation | Install 138 kV bus-tie breaker at the switch 1516 position at South Ottawa | IL | Other | Reliability |  |  |  |  | 2022-12-01 | 138 | 0 | 800000
MTEP20 | West | MEC | 18050 | Sub 77: Add 161 kV Circuit Breaker | Add new 161 kV circuit breaker at Sub 77 on the 161 kV line terminal to Sub 91. | IA | Other | Reliability |  |  |  |  | 2021-12-01 | 161 | 0 | 800000
MTEP20 | East | ITCT | 19526 | Stephens 120 kV Install Breaker GP | Install the GP breaker between Bus 105 and 106 at the Stephens 120 kV station including the associated GQ disconnect, and replacement of GO disconnect | MI | Other | Reliability |  |  |  |  | 2022-12-31 | 120 | 0 | 786389
MTEP20 | West | MEC | 18125 | Grimes-Beaver Creek 345 kV Uprate | Replace structures to uprate the Grimes-Beaver Creek 345 kV line. | IA | GIP | [5 empty] | 2020-12-31 | 345 | 0 | 753000
MTEP20 | Central | AmerenMO | 17824 | Upgrade Spencer Creek 345 kV substation | Replace switches on 345kv pos V3, V5, V6, V7 and reactor position. | MO | Other | Age and Condition |  |  |  |  | 2021-12-01 | 345 | 0 | 700000
MTEP20 | West | MP | 17871 | Laskin Breaker Replacements | Replace breakers and associated equipment at Laskin Substation | MN | Other | Age and Condition |  |  |  |  | 2023-12-31 | 115 | 0 | 700000
MTEP20 | West | MP | 18065 | Verndale Substation Modernization | Replace existing 115 kV circuit breakers at Verndale Substation | MN | Other | Age and Condition |  |  |  |  | 2024-12-31 | 115 | 0 | 700000
MTEP20 | West | XEL | 17984 | New Turtle Lake Sub | A new substation will be built to replace existing distribution Turtle Lake sub allow future load. Existing Turtle Lake sub will be retired once distribution conversion is complete. | WI | Other | Reliability |  |  |  |  | 2021-06-15 | 69 | 23.9 | 700000
MTEP20 | South | SMEPA | 18182 | Cole Road 69 kV Capacitor Bank | Install new 69kV capacitor bank at Cole Road substation. | MS | Other | Reliability |  |  |  |  | 2021-03-01 | 69 | 0 | 660000
MTEP20 | East | ITCT | 18745 | Reconductor Bunce Creek- Scott (B3N) 220kV | The proposed solution is to reconductor approximately 0.44 mile of the Bunce Creek- Scott (B3N) 220kV circuit using 795 ACSS conductor. | MI | BRP | [5 empty] | 2024-06-01 | 220 | 0 | 660000
MTEP20 | South | SMEPA | 17524 | Batesville 161kV Ties Reconductor | Cooperative Energy’s Network Upgrades shall consist of reconductoring both Batesville to Batesville TVA 161kV tie lines with Aluminum Conductor Composite Reinforced (ACCR) conductor. | MS | GIP | [5 empty] | 2021-06-01 | 161 | 0 | 650000
MTEP20 | Central | SIGE | 15952 | Culley 138 kV OCB 2200 2277 Repl. | Replace two 138 kV oil circuit breakers (OCBs) with gas circuit breakers (GCBs). Breaker numbers 2200 and 2277 | IN | Other | Age and Condition |  |  |  |  | 2022-12-31 | 138 | 0 | 615000
MTEP20 | Central | SIGE | 15953 | Replace Heidelbach OCB - 2177 2277 | Replace two 138 kV oil circuit breakers (OCBs) with gas circuit breakers (GCBs) at the Heidelbach station - breaker numbers 2177 & 2277. | IN | Other | Age and Condition |  |  |  |  | 2022-12-31 | 138 | 0 | 615000
MTEP20 | Central | AmerenIL | 17866 | Upgrade Neoga 345/138 kV substation | Replace OCB 1402 on the HUTY-NEGS-1 position with a symmetrically rated 40 kA SF6 breaker. | IL | Other | Reliability |  |  |  |  | 2022-12-01 | 138 | 0 | 600000
MTEP20 | Central | AmerenMO | 17346 | Upgrade Rivermines 138 kV substation | Replace 138kV breakers on bus tie 1-2 and bus tie 2-3 | MO | Other | Age and Condition |  |  |  |  | 2022-12-01 | 138 | 0 | 600000
MTEP20 | Central | AmerenMO | 17867 | Upgrade Gray Summit 345/161 kV substation | Replace the Bus-Tie 1-2 breaker at Gray Summit with a symmetrically rated 40 kA circuit breaker. | MO | Other | Reliability |  |  |  |  | 2022-12-01 | 138 | 0 | 600000
MTEP20 | West | ATC | 19267 | J807 J864 J870 J871 J947 MPFCA Common Use Upgrades | Each individual Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. -J807 Customer is seeking interconnection service for 41.4 MW -J864 Customer is seeking interconnection service for 49.98 MW -J870 Customer is seeking interconnection service for 200 MW -J871 Customer is seeking interconnection service for 100 MW -J947 Customer is seeking interconnection service for 200 MW | WI | GIP | [5 empty] | 2021-03-31 | 138 | 0 | 537753
MTEP20 | East | CETO | 17991 | CE Pole & Line Equipment Replacement Program - 2022 | Replace damaged or defective poles, towers, cross arms, insulators, guying, and switches, as needed, to maintain the lines' condition | MI | Other | Age and Condition |  |  |  |  | 2022-12-31 | 138 | 0 | 530000
MTEP20 | East | ITCT | 18201 | Sag Remediation of Hunters Creek – Stratford 120 kV | Remediate the sag on the Hunters Creek – Stratford 120 kV line to at least 175 MVA for summer emergency rating. | MI | BRP | [5 empty] | 2023-12-31 | 120 | 0 | 510000
MTEP20 | East | CETO | 17994 | Four Mile-Northridge 138 kV Lines | Construct two new 138 kV lines from Four Mile Substation to the new Northridge Substation | MI | Other | Other Local Needs |  |  |  |  | 2022-12-31 | 138 | 0 | 500000
MTEP20 | East | CETO | 18272 | Dort-Mott Lake 138 kV Lines | Construct two new 138 kV lines from Dort Substation to the new Mott Lake Substation | MI | Other | Other Local Needs |  |  |  |  | 2024-06-01 | 138 | 0 | 500000
MTEP20 | Central | AmerenIL | 18035 | Upgrade Eastern 138 kV substation | Replace TAZW-138KV BKR 1321-73 at Eastern Substation | IL | Other | Age and Condition |  |  |  |  | 2022-12-01 | 138 | 0 | 500000
MTEP20 | Central | AmerenIL | 18036 | Upgrade Pioneer 138 kV substation | Replace breaker PION-138KV LINE 1326 at Pioneer Substation. | IL | Other | Age and Condition |  |  |  |  | 2022-12-01 | 138 | 0 | 500000
MTEP20 | Central | AmerenIL | 18075 | Upgrade North Decatur 138 kV substation | Replace 138 kV breaker NDEC-138KV BKR 1602 at North Decatur Substation. | IL | Other | Age and Condition |  |  |  |  | 2023-12-01 | 138 | 0 | 500000
MTEP20 | Central | AmerenIL | 18076 | Upgrade Steeleville 138 kV substation | Replace 138 kV breaker STVL-138KV BKR 1636 at Steeleville Substation. | IL | Other | Age and Condition |  |  |  |  | 2023-12-01 | 138 | 0 | 500000
MTEP20 | Central | AmerenIL | 18077 | Upgrade Vermilion 138 kV substataion | Replace 138 kV breaker VERM-138KV BKR 1306 at Vermilion Substation. | IL | Other | Age and Condition |  |  |  |  | 2023-12-01 | 138 | 0 | 500000
MTEP20 | Central | AmerenIL | 18078 | Upgrade Carbondale NW 138 kV substation | Replace 138 kV breaker CDNW-138KV LINE 1744 at Carbondale NW Substation. | IL | Other | Age and Condition |  |  |  |  | 2023-12-01 | 138 | 0 | 500000
MTEP20 | Central | AmerenIL | 18079 | Upgrade Mason City W 138 kV substation | Replace 138 kV breaker MSCW-138KV LINE 1684 at Mason City West substation. | IL | Other | Age and Condition |  |  |  |  | 2023-12-01 | 138 | 0 | 500000
MTEP20 | Central | AmerenIL | 18091 | Upgrade Clinton 345 kV substation | Replace breaker CLNT-345KV BKR 4506 at Clinton switchyard. | IL | Other | Age and Condition |  |  |  |  | 2023-12-02 | 345 | 0 | 500000
MTEP20 | Central | AmerenIL | 18092 | Replace East Galesburg 138/69 kV transformer | Replace breaker EGAL-138/69KV AUTO XFMR 2 at East Galesburg Substation. | IL | Other | Age and Condition |  |  |  |  | 2024-12-01 | 138 | 0 | 500000
MTEP20 | Central | AmerenIL | 18098 | Upgrade Grand Tower 138 kV substation | Replace breaker GDTY-138KV LT 1449 at Grand Tower Switchyard. | IL | Other | Age and Condition |  |  |  |  | 2024-12-01 | 138 | 0 | 500000
MTEP20 | Central | AmerenIL | 18102 | Upgrade Hines 138 kV substation | Replace breaker HINE-138KV BKR & LINE 1357 at Hines Substation. | IL | Other | Age and Condition |  |  |  |  | 2023-12-01 | 138 | 0 | 500000
MTEP20 | Central | AmerenIL | 18104 | Upgrade Latham 345 kV substation | Replace breaker LATM-345KV POS V19 at Latham Substation. | IL | Other | Age and Condition |  |  |  |  | 2023-12-01 | 345 | 0 | 500000
MTEP20 | Central | AmerenIL | 18107 | Upgrade Tilton Energy Center 138 kV substation | Replace breaker TEC-138KV LINE TIE BKR 1320 at Tilton Energy Center. | IL | Other | Age and Condition |  |  |  |  | 2023-12-01 | 138 | 0 | 500000
MTEP20 | Central | AmerenIL | 18310 | New Dressor Plains Solar (J811) interconnection | Add terminal facilities to Ramsey East Substation. | IL | GIP | [5 empty] | 2021-05-28 | 138 | 0 | 500000
MTEP20 | Central | AmerenMO | 12428 | Replace Stoddard 161 kV breakers | Replace 1-161 kV breaker at Stoddard | MO | Other | Reliability |  |  |  |  | 2021-12-01 | 161 | 0 | 500000
MTEP20 | Central | DEI | 18306 | New H.E. Batesville 138/12 kV new substation | H.E. Batesville 138/12 kV substation: new sub to be located in the 13833 ckt between Batesville 138 kV and Laurel 138 kV | IN | Other | Load Growth |  |  |  |  | 2021-12-31 | 138 | 12 | 500000
MTEP20 | East | METC | 18187 | Sag Remediation Pere Marquette – Stronach 138 kV | Completely remediate the sag on the Pere Marquette – Stronach 138 kV line and replace terminal equipment at the Stronach end of the line. | MI | BRP | [5 empty] | 2023-12-31 | 138 | 0 | 465000
MTEP20 | West | ATC | 19226 | J807 J819 J864 J870 J871 J947 MPFCA Common Use Upgrades | Each individual Customer is responsible for a proportionate percentage share of the Common Use Upgrades estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. -J807 Customer is seeking interconnection service for 41.4 MW -J819 Customer is seeking interconnection service for 99.9 MW -J864 Customer is seeking interconnection service for 49.98 MW -J870 Customer is seeking interconnection service for 200 MW -J871 Customer is seeking interconnection service for 100 MW -J947 Customer is seeking interconnection service for 200 MW | WI | GIP | [5 empty] | 2021-03-31 | 69 | 0 | 440000
MTEP20 | East | ITCT | 18200 | Sag Remediation of Hemphill – Hunters Creek 120 kV | Remediate the sag on the Hemphill – Hunters Creek 120 kV line up to the conductor’s limit. | MI | BRP | [5 empty] | 2023-12-31 | 120 | 0 | 430000
MTEP20 | East | CETO | 17990 | CE Substation Equipment Replacement Program - 2022 | Replace damaged or defective substation equipment with new equipment | MI | Other | Age and Condition |  |  |  |  | 2022-12-31 | 138 | 0 | 410000
MTEP20 | Central | PPI | 18115 | Relocate Kampsville Capacitor Bank to Pearl | Move 2.4 MVAR capacitor bank from Kampsville to Pearl Substation | IL | Other | Reliability |  |  |  |  | 2020-12-31 | 69 | 69 | 400000
MTEP20 | Central | PPI | 18167 | New Smithfield 69 kV capacitor bank (4.8 Mvar) | Addition of 4.8 Mvar capacitor bank in Spoon River Electric Cooperative | IL | Other | Reliability |  |  |  |  | 2024-12-31 | 69 | 69 | 400000
MTEP20 | Central | PPI | 18169 | New Macomb 69 kV capacitor bank (4.8 Mvar) | Addition of 4.8 Mvar capacitor bank in McDonough Power Cooperative | IL | Other | Reliability |  |  |  |  | 2026-12-31 | 69 | 69 | 400000
MTEP20 | West | ATC | 19245 | J807 J819 J850 MPFCA Common Use Upgrades | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. - J807 is seeking interconnection service for 41.4 MW - J819 is seeking interconnection service for 99.9 MW - J850 is seeking interconnection service for 250 MW | WI | GIP | [5 empty] | 2021-03-31 | 138 | 0 | 372880
MTEP20 | West | MDU | 19485 | Big Stone-Browns Valley 230 Line Structure Replacements | GI network upgrade to replace structures on Big Stone-Browns Valley 230 kV line. | SD | GIP | [5 empty] | 2020-06-22 | 230 | 0 | 350000
MTEP20 | West | MEC | 18188 | Diamond Trail-Hills 345 kV Uprate | Replace structures to uprate the Diamond Trail (J530 POI) - Hills 345 kV line. | IA | GIP | [5 empty] | 2020-06-30 | 345 | 0 | 350000
MTEP20 | West | XEL | 18033 | Hydro Lane Expansion | Expand Hydro Lane substation to support increased customer load | MN | Other | Load Growth |  |  |  |  | 2020-05-15 | 69 | 12.5 | 350000
MTEP20 | West | XEL | 18038 | Kinnickinick Substation Rebuild | Build new Kinnickinick Distribution substation near existing Kinnickinick substation. | WI | Other | Age and Condition |  |  |  |  | 2020-12-15 | 69 | 23.9 | 350000
MTEP20 | Central | CWLP | 18140 | Reconductor Chatham Main-Chatham Independence 138 kV line | Reconductor Chatham Main - Chatham Independence 138 kV line with 795 ACSS. | IL | BRP | [5 empty] | 2021-03-01 | 138 | 0 | 350000
MTEP20 | West | ITCM | 17738 | Thompson MacTavish 69kV Substation Interconnection | ITC will install an ~0.02 mile tap line to IPL’s new Thompson MacTavish 69/24.9kV Distribution Substation. This substation will be Open Air Single Bus with a 12/20MVA 69/24.9kV transformer and high side breaker. The substation will be located on one of the two land options available to IPL. The Thompson and Buffalo Center substations will be retired on future EI sketches once IPL moves the loads from those substations to Thompson MacTavish. Coordinate with IPL and DPC for outages. | IA | Other | Load Growth |  |  |  | 20 MVA | 2025-12-31 | 69 | 69 | 346800
MTEP20 | East | ITCT | 19565 | Trenton Channel 120 kV - Upgrade HH Station Equipment | Upgrade station equipment at Trenton Channel 120 kV position HH. | MI | BRP | [5 empty] | 2024-06-01 | 120 | 0 | 335000
MTEP20 | East | CETO | 17992 | Rebuild Hodenpyl Line | Rebuild the Hodenpyl 138 kV Line, approximately 0.6 miles, utilizing 138 kV single circuit construction | MI | Other | Age and Condition |  |  |  |  | 2021-12-31 | 138 | 0 | 330000
MTEP20 | West | MEC | 18174 | Bondurant-Montezuma 345 kV Uprate | Replace structures to uprate the Bondurant-Montezuma 345 kV line. | IA | GIP | [5 empty] | 2020-06-30 | 345 | 0 | 320000
MTEP20 | Central | BREC | 18071 | Reid and Reid EHV Capacitor Re-Size | Re-size two existing capacitors by replacing the cans with larger cans. | KY | Other | Reliability |  |  |  |  | 2019-10-01 | 161 | 0 | 300000
MTEP20 | Central | PPI | 18122 | Upgrade St. David 69 kV Substation | Replace St. David OCB with SF6 breaker and new relays | IL | Other | Age and Condition |  |  |  |  | 2020-12-31 | 69 | 69 | 280000
MTEP20 | South | Entergy-AR | 19725 | Plum Point Network Upgrades (J1146) | Network Upgrades associated with GIA J1146 for 10 MW's of incremental NRIS at Plum Point Generation Facility. This includes reviewing and updating relay settings at San Souci 500kV Switch Station, Driver 500kV substation, and Dell 500kV substation. | AR | GIP | [5 empty] | 2020-10-10 | 500 | 0 | 275000
MTEP20 | West | ITCM | 16865 | J504 Generator Inteconnection | The DAEC 161 kV substation will be expanded to accommodate the J504 terminal, including the addition of breaker position 5953. New equipment should be capable of 2000A. | IA | GIP | [5 empty] | 2020-10-15 | 161 | 161 | 273780
MTEP20 | East | WPSC | 14004 | Hagensville Interconnection Line | Construct approximately 0.25 miles of new 138kV transmission line to connect the Grand Lake Distribution Station to METC’s 138 kV Port Calcite to Rockport transmission line. | MI | Other | Other Local Needs |  |  |  |  | 2022-12-31 | 138 | 0 | 260000
MTEP20 | West | MP | 18109 | 15th Ave West Transformer Addition | Add 115/34.5 kV transformer to existing 15th Ave West Substation. This project includes the transmission equipment necessary to accommodate the new transformer. | MN | Other | Reliability |  |  |  |  | 2022-12-31 | 115 | 34.5 | 250000
MTEP20 | Central | CWLP | 18134 | New Palomino 69 kV capacitor banks | New capacitor banks (x2 @ 20 Mvar) to the Palomino substation. In adding two capacitor banks to the Palomino substation, we will also be retiring the existing cap bank at Palomino. | IL | BRP | [5 empty] | 2021-03-01 | 69 | 0 | 250000
MTEP20 | Central | CWLP | 18172 | New Taintor 69 kV capacitor banks (x2 20 Mvar) | Add two (2) 20 MVAR capacitor banks at Taintor Substation | IL | Other | Reliability |  |  |  |  | 2021-03-01 | 69 | 0 | 250000
MTEP20 | Central | DEI | 18335 | New Tate and Lyle Generation | Tate and Lyle (old Staley) Generation - existing sub on the 13808 ckt; 2 units -32.8MW each - non-MISO queue | IN | Other | Reliability |  |  |  |  | 2021-04-01 | 138 | 12 | 250000
MTEP20 | West | MP | 18110 | Little Falls Bus Reconfiguration | Reconfigure Little Falls 115 kV bus to eliminate line-connected transformer configuration | MN | Other | Reliability |  |  |  |  | 2025-12-31 | 115 | 34 | 250000
MTEP20 | West | ITCM | 16866 | J498/J499/J500 Generator Interconnection | One span on the Poweshiek - Reasnor kV line will be raised to mitigate sag limits and increase the summer rating to 366 MVA (1313 A). | IA | GIP | [5 empty] | 2019-11-07 | 161 | 161 | 240000
MTEP20 | West | ATC | 18849 | J870 Highland SS Interconnection Facilities | A 300 MW solar farm in Grant and Iowa County, Wisconsin. Customer has requested a Point of Interconnection (POI) at Highland Substation that taps the existing X-17 line between Eden and Wyoming Valley Substations. | WI | GIP | [5 empty] | 2020-08-01 | 138 | 0 | 230118
MTEP20 | East | ITCT | 18198 | Sag Remediation of Airport – Tulsa 120 kV | Remediate the sag on the Airport – Tulsa 120 kV line section up to the conductor’s limit. | MI | BRP | [5 empty] | 2023-12-31 | 120 | 0 | 230000
MTEP20 | West | MEC | 18126 | Franklin-Wall Lake 161 kV Uprate | Replace structures to uprate the Franklin-Wall Lake 161 kV line. | IA | GIP | [5 empty] | 2020-06-30 | 161 | 0 | 220000
MTEP20 | West | OTP | 18504 | OTP Hankinson to Wahpeton Network Upgrades-G736/J442 | This project consists of upgrades to Otter Tail Power Company’s substations and transmission lines to accommodate the interconnection of a wind generators, G736/J442, to the Big Stone South substation. Three Facility upgrades are needed: • Hankinson Substation • Wahpeton substation • Wahpeton to Hankinson 230 kV line | ND | GIP | [5 empty] | 2020-03-10 | 230 | 0 | 219567
MTEP20 | West | ITCM | 17739 | Calmar Prairie Farmer 69kV Substation Interconnection | ITC will install an ~0.02 mile tap line to IPL’s new Calmar Prairie Farmer 69/24.9kV Distribution Substation. The transformer will have a highside breaker installed by IPL. This substation will be located near the existing Calmar substation. IPL has provided four proposed locations. The Calmar and Ossian substations will be retired on future EI sketches once IPL moves the loads from those substations to Calmar Prairie Farmer. | IA | Other | Load Growth |  |  |  |  | 2021-12-31 | 69 | 69 | 205200
MTEP20 | West | OTP | 18364 | OTP Oslo 115 kV Switch Replacement | Replace 600 Amp Switch at OTP Oslo with 1200 Amp Switch. | MN | Other | Reliability |  |  |  |  | 2022-11-30 | 115 | 0 | 200000
MTEP20 | West | ATC | 19247 | J807 J819 J850 J947 MPFCA Common Use Upgrades | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. - J807 is seeking interconnection service for 41.4 MW - J819 is seeking interconnection service for 99.9 MW - J850 is seeking interconnection service for 250 MW - J947 is seeking interconnection service for 200 MW | WI | GIP | [5 empty] | 2021-03-01 | 138 | 0 | 199855
MTEP20 | West | ATC | 19248 | J807 J819 J870 J947 MPFCA Common Use Upgrades | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. - J807 is seeking interconnection service for 41.4 MW - J819 is seeking interconnection service for 99.9 MW - J870 is seeking interconnection service for 200 MW - J947 is seeking interconnection service for 200 MW | WI | GIP | [5 empty] | 2021-03-01 | 138 | 0 | 181784
MTEP20 | East | WPSC | 18021 | Eastport 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate facility equipment replacement. | MI | Other | Age and Condition |  |  |  |  | 2021-12-31 | 69 | 0 | 170000
MTEP20 | East | WPSC | 18022 | Westwood 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate facility equipment replacement. | MI | Other | Age and Condition |  |  |  |  | 2022-12-31 | 69 | 0 | 170000
MTEP20 | East | WPSC | 18023 | Eaton Rapids 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate facility equipment replacement. | MI | Other | Age and Condition |  |  |  |  | 2022-12-31 | 69 | 0 | 170000
MTEP20 | East | WPSC | 18024 | Atlanta 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate station equipment replacement. | MI | Other | Age and Condition |  |  |  |  | 2022-12-31 | 69 | 0 | 170000
MTEP20 | East | WPSC | 18026 | Hawks 69kV BUS replacement | Rebuild the existing 69kV bus to accommodate equipment replacement at station. | MI | Other | Age and Condition |  |  |  |  | 2022-12-31 | 69 | 0 | 170000
MTEP20 | East | WPSC | 18027 | Hammond Bay 138kV BUS Replacement | 138kV BUS replacement in order to accommodate voltage increase. | MI | Other | Age and Condition |  |  |  |  | 2021-12-31 | 138 | 0 | 170000
MTEP20 | East | WPSC | 18028 | Hagensville 138kV BUS replacement | Install BUS to 138kV standard to accommodate voltage conversion. | MI | Other | Age and Condition |  |  |  |  | 2021-12-31 | 138 | 0 | 170000
MTEP20 | West | ITCM | 17735 | Clinton South 69kV Substation Retirement | Retire all ITC owned equipment in the Clinton South 69/distribution sub and reroute the 69kV line to bypass the Clinton South sub. | IA | Other | Load Growth |  |  |  |  | 2024-12-31 | 69 | 69 | 161873
MTEP20 | West | XEL | 19406 | Chisago Capacitor Retirement | Chisago 34.5kV capacitors on the tertiary of TR9 and TR10 have failed catastrophically. There is currently no operational or planning need for the capacitors at this time and they will be retired. | MN | Other | Age and Condition |  |  |  |  | 2020-12-01 | 34.5 | 0 | 156000
MTEP20 | Central | BREC | 18765 | Relocate Reid EHV 345/161 kV Transformer | Reallocate existing transformers - move one existing Reid EHV 161/345 kV transformer to Otter Creek (steel mill project). | KY | Other | Reliability |  |  |  |  | 2021-03-01 | 345 | 161 | 150000
MTEP20 | Central | CWLP | 18171 | Reconductor Chatham Independence-Spaulding 138 kV line | Reconductor Chatham Ind.-Spaulding 138 kV line with 795 ACSS. | IL | BRP | [5 empty] | 2021-03-01 | 138 | 0 | 150000
MTEP20 | South | AECC | 16884 | Helena Industrial Breaker Removal | Remove inline breaker at the AECC Helena Industrial Switching Station | AR | Other | Other Local Needs |  |  |  |  | 2021-06-01 | 115 | 0 | 150000
MTEP20 | East | METC | 18825 | Island Rd - Replace White Bus and Position 177 Conductor | Replace the 4/0 CU and 1/0 CU bus conductor at Island Rd White bus and Position 177 to achieve a rating of at least 141 MVA (590 amps). | MI | GIP | [5 empty] | 2022-05-01 | 138 | 0 | 134000
MTEP20 | West | MEC | 19646 | Franklin to Wall Lake 161 kV Line Structure Replacement | Line structure replacements to increase line ratings. | IA | BRP | [5 empty] | 2021-12-31 | 161 | 0 | 125000
MTEP20 | West | MEC | 18121 | Deere Northeast-Washburn 161 kV Uprate | Replace limiting substation terminal equipment at Deere Northeast and Washburn to increase the rating of the Deere Northeast-Washburn 161 kV line. | IA | GIP | [5 empty] | 2020-10-31 | 161 | 0 | 100000
MTEP20 | South | Entergy-LA | 18136 | Scott to Lafayette 69 kV: Upgrade Station Equipment | Upgrade all station equipment to achieve a through path rating of 588 Amps. | LA | Other | Reliability |  |  |  |  | 2021-06-01 | 69 | 0 | 50000
MTEP20 | West | MEC | 18119 | Lundquist-Deere Northeast 161 kV Uprate | Replace terminal equipment at Deere Northeast substation to increase 161 kV line rating. | IA | GIP | [5 empty] | 2020-10-31 | 161 | 0 | 50000
MTEP20 | South | Entergy-MS | 18226 | Refuge 115 kV Equipment Upgrade | Upgrade switches at the Cooperative Energy owned Refuge 115kV GOAB with higher amp rated switches. | MS | BRP | [5 empty] | 2021-03-01 | 115 | 0 | 25000
MTEP20 | Central | CWLP | 18141 | Upgrade Interstate 138 kV substation | Replace the wavetrap on the Interstate - Lanesville 138 kV line (at Interstate Sub) with a 2000A wave trap. This will increase the rating of the line. | IL | BRP | [5 empty] | 2021-03-01 | 138 | 0 | 20000
MTEP20 | West | MRES | 18645 | Hutchinson Jumper Replacement | Overloads on the Hutchinson 230/115 kV transformer were observed in the MTEP19 results. The transformer is limited by a couple sets of jumpers. To increase the transformer capacity the jumpers will be replaced. | MN | BRP | [5 empty] | 2021-06-01 | 115 | 0 | 20000
MTEP20 | East | ITCT | 17995 | J752 Network Upgrades | Install Relay and communication cutoff switch at Ringle 345 kV station for the J752 expansion of J161. | MI | GIP | [5 empty] | 2019-10-31 | 345 | 0 | 17904.43
MTEP20 | West | ITCM | 17733 | J504 Generator Inteconnection-TOIF | The GIA between ITCM, Duane Arnold Solar, LLC (NextEra Energy) and MISO has been executed to facilitate the interconnection of project J504, a 60 MVA solar generating facility rated 51 MW gross and 50MW net with a Point of Interconnection at the DAEC 161 kV substation. The Interconnection Customer is responsible for costs associated with the TOIF. | IA | GIP | [5 empty] | 2020-10-15 | 161 | 161
MTEP20 | West | ITCM | 18111 | J523 Generator Interconnection-TOIF | Install new terminal for J523 gen-tie line. This work includes installing switch, dead-end, CCVT's, switches, and relay panels (see GIA for further details). | MN | GIP | [5 empty] | 2021-09-15 | 161 | 161
MTEP20 | South | AXLA | 19408 | Sterkx – Willow Glen 138 kV Reconductor | Line re-conductor driven by aging infrastructure. | LA | Other | Age and Condition |  |  |  |  | 2021-06-01 | 138 | 0
MTEP20 | South | Entergy-MS | 19785 | Twinkletown 230 kV: Expand Substation (J962) | Interconnect new J962 100 MW generator to the existing Twinkletown 230 kV substation. | MS | GIP | [5 empty] | 2022-06-30 | 230 | 0
MTEP20 | Central | AmerenIL | 16144 | Replace Newton 345/138 kV transformer | Replace the existing Newton 345-138 kV unit #1 with a new 700 MVA unit | IL | BRP | [5 empty] | 2023-06-01 | 345 | 138
MTEP20 | Central | AmerenIL | 16709 | Upgrade Ashley-Venice 138 kV line at Venice substation | Replace 2 1200A switches and 1000 Kcmil CU bus conductor with equipment having 2000A capability. Upgrade the position to 2000A. | IL | Other | Reliability |  |  |  |  | 2021-12-01 | 138 | 0
MTEP20 | Central | AmerenMO | 15487 | New Vessel 138 kV Ring Bus | Install 4 position ring bus | MO | Other | Reliability |  |  |  |  | 2022-06-01 | 138 | 0
MTEP20 | Central | AmerenMO | 17224 | New Pershall 138/12 kV distribution Substation | Install main-tie-main straight bus substation connecting to Berkeley-Sioux-1 and Berkeley-Sioux-2 lines. | MO | Other | Load Growth |  |  |  |  | 2022-06-01 | 138 | 12
MTEP20 | Central | AmerenMO | 17665 | New Barrett Station 138/12 kV Transformer No. 2 | Install 3 breakers in a main-tie-main configuration with an open bus tie to facilitate the installation of a 2nd transformer. Install circuit switchers on the existing and new transformers. | MO | Other | Load Growth |  |  |  |  | 2021-12-31 | 138 | 12
MTEP20 | Central | AmerenMO | 17685 | New Creve Coeur 138/12 kV substation | Tap the Mason-Meramec-1 & 2 lines to provide a main-tie-main configuration for new 138-12 kV substation. | MO | Other | Load Growth |  |  |  |  | 2027-12-01 | 138 | 12
MTEP20 | Central | AmerenMO | 17686 | New Dougherty Ferry 138/12 kV substation | Tap the Mason-Meramec-1 & 2 lines to provided a main-tie-main configuration for the installation of a new 138-12 kV substation. | MO | Other | Load Growth |  |  |  |  | 2023-12-01 | 138 | 12
MTEP20 | Central | AmerenMO | 17945 | New Highway M 138/12 kV substation | Install 2 unit 138-12.47 kV substation on a site adjacent to the Dardenne Substation. | MO | Other | Load Growth |  |  |  |  | 2024-12-01 | 138 | 12.47
MTEP20 | Central | AmerenMO | 17947 | New Fountain Lakes 138/12 kV transformer No. 2 | Add 2nd 138-12 kV unit at Fountain Lakes Substation. | MO | Other | Load Growth |  |  |  |  | 2023-12-01 | 138 | 12.47

## MTEP21
MTEP Year | Planning Region | Utility/TO | Project ID | Project Name | Project Description | State | Project Type | Other Type | System Need / Rationale | Project Driver | Data Center Flag | Load (MW) | Expected ISD | Max kV | Min kV | Estimated Cost ($) | Report Notes
MTEP21 | South | Arkansas Electric Coopertive Corporation | 20161 | Tap EAL Monticello East - Reed: Construct Selma South 115/69 kV substation | Tap Entergy's Monticello to Reed 115 kV transmission and construct the Selma South 115/69 kV, 60/80/100 MVA transmission substation. | AR | Other | Reliability | This delivery point is needed to improve reliability to the C&L Electric Cooperative 69 kV transmission system currently served by the Glendale delivery point. |  |  |  | 2024-01-01 | 115 | 0 | 7500000
MTEP21 | South | Arkansas Electric Coopertive Corporation | 20265 | Glendale Capacitor Bank | Install 9.6 MVAR capacitor bank at Glendale. | AR | Other | Reliability | This project is needed in conjunction with the Selma South transmission substation. For the loss of the Glendale delivery point, Selma South needs additional voltage support from a capacitor bank to serve the C&L 69 kV transmission system. |  |  |  | 2024-01-01 | 69 | 0 | 1000000
MTEP21 | West | American Transmission Co. LLC | 10590 | Academy - Columbus, 69kV (Y-21), rebuild & OPGW | The Academy - Columbus (Y-21) 69kV circuit is 3 miles long and uses 336 kcmil ACSR supported on lattice steel structures - Field inspection reports indicate the 1910 vintage structures require replacement to continue reliable operation - New conductor will be installed and will be similar or slightly larger than the existing circuit capability - Optical Ground Wire (OPGW) will be installed to provide protection and SCADA communications along this ROW Substation Work Scope: - Academy Substation - Replace line side jumper to meet planning long term rating needs and terminate fiber. - Columbus (ALTE) - Remove control house, oil circuit breakers, and switches; - Install motor operated disconnects, gas circuit breaker, control house, and RTU for SCADA control - Improve drive access to site with purchase and demolition of existing residence - Terminate fiber with line project. | WI | Other | Age and Condition | Asset Renewal - Line Rebuild |  |  |  | 2024-12-31 | 69 | 0 | 8800000
MTEP21 | West | American Transmission Co. LLC | 14964 | Small Capital Project and Asset Renewal Program 2022 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, re-insulations and uprates and Pole hardware replacements - Estimated Cost - $4,000,000 Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. - Estimated Cost - $40,000,000 Substation Battery Replacement Program - Estimated Cost - $3,000,000 Substation Physical Security Asset Renewal - Estimated Cost - $3,000,000 Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2022. | WI,MI | Other | Age and Condition | Asset Renewal or Reliability |  |  |  | 2025-06-30 | 345 | 69 | 52320773
MTEP21 | West | American Transmission Co. LLC | 14965 | Communication Reliability Program 2022 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2022. | WI,MI | Other | Other Local Needs | Communications |  |  |  | 2025-06-30 | 345 | 69 | 19252066
MTEP21 | West | American Transmission Co. LLC | 14966 | Line Clearance Mitigation Program 2022 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2022. | WI,MI | Other | Reliability | Line Clearance |  |  |  | 2025-06-30 | 345 | 69 | 2832841
MTEP21 | West | American Transmission Co. LLC | 14967 | Physical Security Program 2022 | Physical Security projects typically have shorter project life cycles. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2022. | WI,MI | Other | Other Local Needs | Physical Security |  |  |  | 2025-06-30 | 345 | 69 | 11797871
MTEP21 | West | American Transmission Co. LLC | 14968 | Load Interconnection Program 2022 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2022. | WI,MI | Other | Load Growth | Load Interconnection |  |  |  | 2025-06-30 | 138 | 69 | 27586994
MTEP21 | West | American Transmission Co. LLC | 16489 | Empire SS, Control House, Relays, and Circuit Breaker Asset Renewal | Asset renewal at the Empire SS would include: - Install new control building - Retirement and replacement of circuit breakers, protective relays, and disconnect switches | MI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2024-12-31 | 138 | 138 | 9900000
MTEP21 | West | American Transmission Co. LLC | 16490 | Granville SS, Control House and Relay Replacement and Asset Renewal | 345kV Project Scope • Replace 4 1970-vintage Westinghouse 3450-GW-25000 oil breakers • Replace 7 disconnect switches 138kV Project Scope • Replace 7 1969-vintage Westinghouse 1380-GM-15000 oil breakers • Replace 2 underground HPFF lines with overhead and retire pump house at Granville and East Granville Terminal General Project Scope • Reconfigure 345kV bus to 6-position ring (5 positions plus one future position) • Vacate existing control house, transfer ownership to We Energies, obtain new high-security control house • Replace all relays and SCADA with current standard • Address planning-identified need for redundant bus differential protection • Expand yard to accommodate ring bus | WI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2024-12-01 | 345 | 138 | 28950000
MTEP21 | West | American Transmission Co. LLC | 18048 | Lincoln - 43rd Street Terminal 138 kV (5053), Replace with double circuit duct bank and XLPE cable | • Rebuild existing 5053 HPFF line with new XLPE in double circuit duct bank in existing road ROW. o Install ~2.2 miles of XLPE in double circuit duct bank package and new manholes. | WI | Other | Age and Condition | Asset Renewal - Line Rebuild |  |  |  | 2024-12-31 | 138 | 0 | 35800000
MTEP21 | West | American Transmission Co. LLC | 19105 | Nelson Dewey SS - Control House, Relay Asset Renewal | • Replace control house and contents, including but not limited to: - Relays and panels, relocating and reusing five reply panels in the new house - Two batteries and charger - Project team will evaluate location and elevation and relay panel design to mitigate flood risk • Replace control cabling between new control house and all station equipment | WI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2022-06-01 | 138 | 69 | 6170000
MTEP21 | West | American Transmission Co. LLC | 19587 | Petenwell – Council Creek, (X-40) 138kV, Partial Structure and OPGW Replacement | - Replace 30 miles of shield wire with 48 Strand OPGW Fiber cable between Petenwell and Council Creek substations - Replace ~67 wood monopoles structures | WI | Other | Other Local Needs | Communications |  |  |  | 2024-12-31 | 138 | 0 | 9000000
MTEP21 | West | American Transmission Co. LLC | 19705 | Crivitz SS, Transformers and Relays Asset Renewal | • Replace T1, 138/69 kV power transformer with the on-site 138/69 kV system spare • Replace T3, 138/69 kV power transformer with the 138/69kV power transformer from Pioneer SS that will be taken out of service in 2023 due to elimination of the 69 kV system at that substation • Replace 69 kV Mark V circuit switcher with an existing on site circuit breaker and new disconnect switch • Replace a single line relay in an existing panel | WI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2024-12-31 | 138 | 0 | 4599154
MTEP21 | West | American Transmission Co. LLC | 19706 | North Appleton SS, Transformer and Reactor Asset Renewal | • Replace T7 138/345 kV power transformer (three single phase units) with the on-site system spare (standard three phase). • Retire two three-phase reactors, bus, structures and insulators and install a new standard 24.9 kV design connected to the tertiary of the newly installed 138/345 kV power transformer • Retire original design 34.5 kV vacuum breaker and associated disconnect switches • Install new station service on 24.9 kV bus salvaging three newer vintage reactors for use in a future project • Replace seven 138 kV disconnect switches | WI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2024-12-01 | 345 | 0 | 7938249
MTEP21 | West | American Transmission Co. LLC | 19729 | J732 Superior SS Network Upgrades and Interconnection Facilities | Interconnection of about 560 MW the facility composed of one (1) steam turbine unit and one (1) natural gas unit in a 1x1 combined cycle facility interconnecting at the new Superior Substation. | WI | GIP |  | Inteconnection |  |  |  | 2023-11-30 | 345 | 230 | 21245605
MTEP21 | West | American Transmission Co. LLC | 19806 | Bonnie Road SS, DIC, New Substation | • Extend approximately 0.38 miles of 69 kV double circuit transmission line on new right-of-way. • Construct new 69 kV substation with a bus-tie switch and provisions for a future bus-tie breaker. • Install 69 kV line breakers as sectionalizing devices. | WI | Other | Load Growth | Load Interconnection |  |  |  | 2023-06-01 | 69 | 0 | 3504413
MTEP21 | West | American Transmission Co. LLC | 19959 | Sussex to Bark River (46143/2661), 138kV, OPGW Installation | Install 8 miles of fiber optic cable between the Sussex to Bark River substations and terminate it within the control houses. | WI | Other | Other Local Needs | Communications |  |  |  | 2023-12-31 | 138 | 0 | 3766000
MTEP21 | West | American Transmission Co. LLC | 19961 | Wells St. DIC – New West Marinette-Wells St. 69 kV line | -Construct a new 69kV transmission line from West Marinette SS to Wells St. SS -Rebuild the existing 1.6 mile portion of the West Marinette-Roosevelt Rd. 69 kV as double-circuit -Add a 2nd 69 kV circuit on the existing overhead 1.9 mile section of Roosevelt Rd.-Wells St. -Add a 2nd underground cable in the spare conduit ducts from Riser Structure #27 to Wells St. -At the West Marinette SS add a new 69kV bus position and circuit breaker | WI | Other | Load Growth | Load Interconnection |  |  |  | 2024-05-31 | 69 | 0 | 16100000
MTEP21 | West | American Transmission Co. LLC | 19965 | Marquette County Reactive Power Project | Relocate one 138 kV line position (line 16343) to a different bus position at National substation. • Install one +/- 50 MVA, 138 kV STATCOM (Static Synchronous Compensator) at National substation. o Include one spare 138 kV transformer o Add a new 138 kV circuit breaker and protection package at National | MI | Other | Reliability | Reliability The central U.P. experiences voltage limitations on a regular basis due to the retirement of the Presque Isle Power Plant generation and the consistent off-line operation of the RICE units at Mihm and Kuester each night. • High intact system voltages • Single-contingency low voltage limitations • Limited reactive power control in this area |  |  |  | 2023-12-01 | 138 | 0 | 24200000
MTEP21 | West | American Transmission Co. LLC | 20625 | J986 7 Mile Creek SS, Generator Interconnection Facilities and Network Upgrades | J986 is a proposed 149.76 MW solar farm power plant in Wood County, Wisconsin. | WI | GIP |  | Interconnection |  |  |  | 2022-06-01 | 138 | 69 | 17564028
MTEP21 | West | American Transmission Co. LLC | 20785 | Highway V -Preble 138 kV (X-154), reconductor | The Highway V-Preble 138 kV line reconductor project consists of the following: -Reconductor 138kV line from Highway V to Preble -Replace five 138 kV jumpers at Highway V -Replace one 138 kV jumper at Preble | WI | BRP |  | Reliability |  |  |  | 2023-05-15 | 138 | 0 | 1777603
MTEP21 | West | American Transmission Co. LLC | 20925 | Lancaster Transformer Replacement & Substation Rebuild | ATC will retire the Lancaster 138/69 kV transformer, 69 kV bus, and associated equipment and expand the 138 kV bus (box structure) and add bus-tie switches and space provisions for a future bus-tie breaker. In addition: - install 2 circuit breakers on line X-1 - replace the control house and relay equipment | WI | Other | Load Growth | Load Interconnection |  |  |  | 2023-12-31 | 138 | 69 | 3700000
MTEP21 | Central | Ameren Services Company | 9843 | New Normal East 138/34.5 kV transformer | Install 112 MVA Transformer | IL | Other | Load Growth | Local load serving need |  |  | 112 MVA | 2017-05-26 | 138 | 34.5 | 1500000
MTEP21 | Central | Ameren Services Company | 16989 | New Mattoon W 138 kV substation | Install new 6 position ultimate ring bus at Mattoon West Substation. | IL | Other | Reliability | Increased reliability and operating flexibility. |  |  |  | 2023-12-01 | 138 | 0 | 8500000
MTEP21 | Central | Ameren Services Company | 16990 | New Kline 138 kV substation | Install new 6 position ultimate ring bus at Kline Substation (formerly known as Wanda). | IL | Other | Reliability | This project will increase reliability and flexibility of the transmission system and to the customers supplied from the existing substation. A fault on the bus or transformer would outage the entire substation. The new substation will also accommodate future transmission expansion. |  |  |  | 2022-06-01 | 138 | 0 | 7200000
MTEP21 | Central | Ameren Services Company | 17864 | Upgrade Cahokia 345/138 kV substation | Replace OCB H27 on the C-GRAT-3 position and OCB H35 on the C-RUSL-2 positon with symmetrically rated SF6 55 kA circuit breakers. | IL | Other | Reliability | General system expansion has increased the fault duty on these breakers, necessitating their replacement. |  |  |  | 2022-12-01 | 138 | 0 | 4200000
MTEP21 | Central | Ameren Services Company | 17979 | Rebuild North Staunton 138 kV substation | Rebuild the North Staunton 138 kV substation to a ring bus configuration. New name is Rezzy. | IL | Other | Reliability | This project will increase reliability and flexibility of the transmission system and to the customers supplied from the existing substation. A fault on the bus, transformers, or a breaker failure event would outage the entire substation. The new substation will also accommodate future transmission expansion. |  |  |  | 2022-12-01 | 138 | 0 | 16200000
MTEP21 | Central | Ameren Services Company | 18074 | Replace Jacksonville Industrial Park 138 kV Breakers | Jacksonville Industrial Park Breaker Replacement: Replace 138 kV breaker JCKI-138KV BT 1-2 BKR 1302 at Jacksonville Industrial Park Substation. | IL | Other | Reliability | Increased reliability |  |  |  | 2022-06-01 | 138 | 0 | 1300000
MTEP21 | Central | Ameren Services Company | 18889 | Rebuild Hickok-North LaSalle 138 kV line (1659) | Rebuild the Hickok-North LaSalle 138 kV line for 2000 amps. | IL | BRP |  | Address an overload on the Hickok North LaSalle 138 kV line upon completion of the Statcom |  |  |  | 2023-12-01 | 138 | 0
MTEP21 | Central | Ameren Services Company | 19025 | New J815 Hickory Point Wind Generator Interconnection (Yvonne 138 kV switching Station) | Install new Yvonne 138 kV switching Station (J815 Hickory Point Wind Generator Interconnection) on the Austin-Taylorville S.-1545 line. | IL | GIP |  | Generator Interconnection |  |  |  | 2022-11-01 | 138 | 0 | 5700000
MTEP21 | Central | Ameren Services Company | 19026 | New J912 Christian County Solar Generator Interconnection (Pana 138 kV switching station) | New J912 Christian County Solar Generator Interconnection at Pana 138 kV switching station | IL | GIP |  | Generator Interconnection |  |  |  | 2023-10-01 | 138 | 0 | 900000
MTEP21 | Central | Ameren Services Company | 19085 | New Shelbyville S. 138 kV Ring Bus for PPI ISHI Load Addition | Rebuild the Shelbyville S. 138 kV bus to a 6 position ultimate ring bus. This will allow a new interconnection with PPI to serve their ISHI load. | IL | Other | Load Growth | Customer load addition |  |  |  | 2022-06-01 | 138 | 0 | 10000000
MTEP21 | Central | Ameren Services Company | 19345 | New Valmeyer 138 kV Substation | Construct Valmeyer 138 kV Substation Ring Bus and add a second 138/34.5 kV Transformer | IL | Other | Reliability | Increased reliability. Distribution driven project. |  |  |  | 2024-06-01 | 138 | 34.5 | 5900000
MTEP21 | Central | Ameren Services Company | 19826 | Upgrade Dupo Ferry 138 kV Substation | Replace overstressed breakers | IL | Other | Reliability | Replace overstressed breakers |  |  |  | 2025-12-01 | 138 | 0
MTEP21 | Central | Ameren Services Company | 19956 | Rebuild Tanner-Jasper 138 kV line | Rebuild 23 miles to 2000 A. To coincide with Tanner 345/138 kV | IL | BRP |  | Baseline reliability |  |  |  | 2022-12-01 | 138 | 0 | 7900000
MTEP21 | Central | Ameren Services Company | 19988 | New Roxford 345/138 kV Transformer Addition | Add second 345/138 kV transformer | IL | Other | Reliability | Increased reliability and system strength for customers. |  |  |  | 2023-12-01 | 345 | 138 | 10200000
MTEP21 | Central | Wabash Valley Power Association, Inc. | 20079 | Rebuild Butler 69/12kV Substation | Rebuild Butler sub with new 5/6.25MVA 3ph transformer, relocate regulators, replace all switches | IL | Other | Reliability | Reliability |  |  |  | 2021-12-31 | 69 | 12 | 1800000
MTEP21 | Central | Ameren Services Company | 20184 | New REOS 138 kV substation | Ring bus North of RS Wallace that ties together RS Wallace - Spring Bay and CAT2 - Hines 138 kV lines. | IL | BRP |  | Baseline reliability |  |  |  | 2024-12-01 | 138 | 0 | 8700000
MTEP21 | Central | Ameren Services Company | 20187 | Upgrade Chesterville 138 kV Substation | Add 2 line breakers | IL | Other | Reliability | Increased reliability. |  |  |  | 2025-12-01 | 138 | 69 | 1700000
MTEP21 | Central | Ameren Services Company | 20188 | New Upgrade Gibson City S 138 kV Substation | Add 5 position ring bus. | IL | Other | Reliability | Increased reliability |  |  |  | 2025-12-01 | 138 | 69 | 7000000
MTEP21 | Central | Ameren Services Company | 20191 | Upgrade Marion N 138 kV Substation | Add line breakers, disconnect switches and circuit switcher | IL | Other | Reliability | Increased reliability |  |  |  | 2024-12-01 | 138 | 69 | 8000000
MTEP21 | Central | Ameren Services Company | 20285 | Reconfigure Herrin East 138 kV substation | Install initial 4-position ring bus at the existing Herrin East substation location | IL | Other | Reliability | Increased reliability on the area distribution system and increased operating flexibility on the transmission system. |  |  |  | 2022-12-01 | 138 | 0 | 7500000
MTEP21 | Central | Ameren Services Company | 20365 | New Normal East 138/69 kV transformer | Install new 112 MVA, 138/69 kV Transformer | IL | Other | Load Growth | Local load serving need |  |  | 112 MVA | 2022-06-01 | 138 | 69 | 2000000
MTEP21 | Central | Ameren Services Company | 20425 | Upgrade Holland-Kickapoo 138 kV | Remove CT limit as part of Kickapoo substation rebuild | IL | Other | Reliability | Increased reliability and operational flexibility |  |  |  | 2022-12-01 | 138 | 0 | 500000
MTEP21 | Central | Ameren Services Company | 20465 | New Commodore 230 kV Interim Configuration | Interim configuration. 345/230 kV transformer at Commodore to serve the 230 kV St.John and West Frankfort area until the 230 kV to 345 kV line from Commodore to Jordan, and 138 kV line from Pinkneyville to St. John is finished. | IL | Other | Reliability | Increased reliability. |  |  |  | 2021-10-05 | 345 | 230
MTEP21 | Central | Ameren Services Company | 21045 | Relocate ADM North-Mt. Zion 138 kV line (1616) | Relocate 0.6 miles of existing 138 kV ADM North-Mt. Zion Route 121-1616 to single circuit, single shaft steel poles. The entire section has distribution underbuild. | IL | Other | Other Local Needs | The project was requested by the City of Decatur due to a Public Works project that is reconfiguring an intersection along Brush College Road. |  |  |  | 2021-12-01 | 138 | 0 | 3500000
MTEP21 | Central | Ameren Services Company | 21325 | Rebuild Rossville-Vermilion 138 kV line (1305) | Rebuild the Rossville-Vermilion-1305 138 kV circuit with 2000 A summer emergency capability conductor. Also, install OPGW. | IL | Other | Age and Condition | Age and condition; OPGW |  |  |  | 2022-06-01 | 138 | 0 | 12800000
MTEP21 | Central | Ameren Services Company | 21585 | Rebuild Decatur East Main St-Route 51 Decatur 138 kV line (1416) | Rebuild the Decatur East Main St-Decatur Route 51 138 kV line. Scope of work includes: Replacement of existing OPGW with new OPGW, all to be installed in upper static position. Replacement remaining (31) wood pole structures; (28) will be replaced with single wood pole structures and 3 will be replaced with steel monopole structures. Reconductor with 2000A conductor. | IL | Other | Reliability | This project replaces the jointly-owned Ameren and Windstream 24-fiber OPGW with a new 72-fiber OPGW wholly owned by Ameren. Ameren's joint ownership agreement with Windstream expires at the end of 2022, and the terms of that agreement state that neither party can use the fiber optic cables included in that 24-fiber OPGW. Therefore, Ameren needs to replace that cable to maintain communications continuity in this area. Engineering identified that the existing structures on this line cannot handle the increased loading caused by the new OPGW. Engineering proposes replacing all the structures on this line with larger poles to handle this increased loading. Finally, Engineering proposes to replace the existing conductor with new conductors capable of carrying 2000 amps and Summer Emergency conditions. This provides greater operational flexibility but increasing the capacity of the line, reduces galloping related wear on the structures at the river crossing and removes aging infrastructure from the transmission system. |  |  |  | 2022-12-01 | 138 | 0 | 4200000
MTEP21 | Central | Ameren Services Company | 20193 | Replace Breakers Program - MTEP21 | Breaker Upgrades Requested by Maintenance. Ameren Transmission has an initiative to replace about 35 Hitachi breakers (HVB) on the system. There were eight (8) inadvertent transmission interruptions in the period of 2014-2021 due to HVB breakers, which is a high percentage for such a small population. In addition, modern breakers have spring trip (stored energy) and air close (compressor) mechanisms while HVB breakers have air trip and spring close mechanisms. Having an air trip mechanism makes HVB breakers dependent on a hydraulic system to trip, which is prone to problems. Also having a stored energy for close operation means that workers have to be alert to controlling this energy when working on HVB breakers to avoid any accident. | IL,MO | Other | Age and Condition | Age and condition. Increased reliability. |  |  |  | 2022-12-01 | 345 | 138 | 13500000
MTEP21 | Central | Ameren Services Company | 20194 | Replace Relays Program - MTEP21 | Electromechanical Relay Upgrades Requested by System Protection | IL,MO | Other | Age and Condition | Age and condition |  |  |  | 2022-12-01 | 345 | 138 | 10350000
MTEP21 | Central | Ameren Services Company | 20195 | Replace Pole and Insulator Program - MTEP21 | Pole and Insulator replacements requested by Maintenance. 432 structures in Missouri. 320 structures in Illinois. | IL,MO | Other | Age and Condition | Age and Condition |  |  |  | 2022-12-01 | 345 | 138 | 97500000
MTEP21 | Central | Ameren Services Company | 9830 | Reconductor Meramec-Joachim 138 kV line 2 | Meramec-Joachim-2 138 kV Line - Increase ground clearance to permit operation at 120 degrees C. Test the condition of the conductor, replace the deadends, shunt the splices and replace the hardware. | MO | BRP |  | Other-Increased reliability. Completion of NERC remediation. |  |  |  | 2021-12-31 | 138 | 138 | 300000
MTEP21 | Central | Ameren Services Company | 17344 | Upgrade Berkeley 138 kV Substation | Replace 138 kV bus tie 1-2 and 2-3 breakers. Upgrade position to 2000A. | MO | Other | Age and Condition | Age and condition of existing breakers. |  |  |  | 2021-12-01 | 138 | 0 | 1300000
MTEP21 | Central | Ameren Services Company | 19827 | Upgrade Sioux 138 kV Substation-MTEP21 | Replace overstressed breaker 3H | MO | Other | Age and Condition | Replace overstressed breaker |  |  |  | 2025-12-01 | 345 | 138 | 700000
MTEP21 | Central | Ameren Services Company | 19852 | New Sikeston 161 kV Substation | Construct new Comstock (Sikeston) 161kV breaker-and-a-half substation to interconnect Ameren's Miner-Sikeston line and Sikeston Board of Municipal Utilities' New-Madrid-Sikeston 161kV line. Construct new 161kV Reelfoot ring bus near New Madrid and extend SBMU's 161kV in/out of the ring bus. The City of New Madrid will install a 161/69kV xfmr to serve new industrial customer. | MO | Other | Load Growth | Business development |  |  |  | 2022-12-01 | 161 | 161 | 15200000
MTEP21 | Central | Ameren Services Company | 19968 | New Zachary-Maywood 345 kV Ring Bus for (J1025) | Zachary-Maywood 345 kV New Ring Bus for J1025 Generator Interconnection (Station name is Fabius) | MO | GIP |  | Generator Interconnection |  |  |  | 2022-06-01 | 345 | 0 | 9800000
MTEP21 | Central | Ameren Services Company | 19969 | New Belleau 138 kV Capacitor Bank | Install 120 Mvar capacitor bank at Belleau 138 kV | MO | BRP |  | Baseline Reliability |  |  |  | 2025-06-02 | 345 | 138 | 3500000
MTEP21 | Central | Wabash Valley Power Association, Inc. | 20065 | Replace New Bourbon 69 kV Breakers | Replace 69 kV brkrs B24, B25, B26, B39, & B40 at New Bourbon Sub. Also purchase a spare brkr. Install GPS clocks and wire to the microprocessor relays. | MO | Other | Age and Condition | Breaker reliability due to age and condition. GPS clocks necessary to match timeframe of operations. |  |  |  | 2020-09-03 | 69 | 0 | 1200000
MTEP21 | Central | Wabash Valley Power Association, Inc. | 20069 | New Salem Bulk DFR Installation | Install a new SEL data concentrator, Install GPS clocks and wire the GPS clocks to the microprocessor relays, Remove the relay 67 directional overcurrent tripping. | MO | Other | Reliability | Install a new SEL data concentrator, Install GPS clocks and wire the GPS clocks to the microprocessor relays, Remove the relay 67 directional overcurrent tripping elements that trip the transformer 69 kV breakers |  |  |  | 2020-12-31 | 69 | 12 | 100000
MTEP21 | Central | Wabash Valley Power Association, Inc. | 20070 | Upgrade Trail of Tears 69 kV Breakers | Replace the four oil filled 69 kV breakers at Trail of Tears to fix identified constraints for CT availability for the new bus differentials | MO | Other | Reliability | Equipment needed to add new bus differential relays. |  |  |  | 2021-12-31 | 69 | 69 | 2800000
MTEP21 | Central | Wabash Valley Power Association, Inc. | 20072 | Rebuild Seminary to Park 69 kV Line | Upgrade 3.06 mi. 3/0ACSR to 477ACSR of 69kV Line T17 from Seminary B43 to Park tap switch 117. Add 48 fiber OPGW to entire 3.06 mile line. | MO | Other | Reliability | Reliability. Load transfers cause loading issues. |  |  |  | 2021-06-01 | 69 | 69 | 2000000
MTEP21 | Central | Ameren Services Company | 20156 | New Galena 161 kV Capacitor Bank | Install 28.8 MVAR capacitor bank at Galena 161 kV | MO | BRP |  | Baseline reliability |  |  |  | 2022-12-01 | 161 | 0 | 900000
MTEP21 | Central | Ameren Services Company | 21125 | New Burns 345 kV Substation (J1145 Solar) | Construct 3 position ring bus on Montgomery-McCredie 345 kV line for 250 MW Show Me State Solar project J1145 | MO | GIP |  | Interconnection facilities for J1145 according to engineering agreement. |  |  |  | 2022-10-01 | 345 | 0 | 10100000
MTEP21 | Central | Big Rivers Electric Corporation | 3439 | New Ensor 161/69 kV Substation | Construct new 161/69 kV substation with 56 MVA transfomer. Include a 30 MVAR 69 kV capacitor | KY | BRP |  | Base case voltage issues and overloads during loss of one Daviess County 161/69 kV transformer. Capacitor needed to mitigate low voltages during loss of Reid to Daviess County 161 kV circuit. |  |  |  | 2024-12-31 | 161 | 69 | 5800000
MTEP21 | Central | Big Rivers Electric Corporation | 18605 | New Hardinsburg 161kV Substation (J753) for solar Interconnection | Hardinsburg 161kV Substation (J753) for 100 MW solar Interconnection | KY | GIP |  | Hardinsburg 161kV Substation expansion (J753) for solar Interconnection |  |  |  | 2021-04-01 | 161 | 0 | 200000
MTEP21 | Central | Big Rivers Electric Corporation | 18606 | New Meade 161kV Substation (J762) for solar Interconnection | Meade County 161kV Substation modification for (J762) solar Interconnection | KY | GIP |  | Meade County 161kV Substation modification for 200 MW (J762) solar Interconnection |  |  |  | 2021-04-01 | 161 | 0 | 500000
MTEP21 | Central | Big Rivers Electric Corporation | 19006 | New Hartford 69 kV Tie line | 69 kV normally open tie from KU Hartford to a BREC tap near Beda. | KY | Other | Reliability | Provide emergency service to KU on an as-available basis. |  |  |  | 2020-11-03 | 69 | 0
MTEP21 | Central | Big Rivers Electric Corporation | 21165 | New Maxon Load Addition | For the near term, the industrial customer is requiring 30 MW capacity. This load will be served on an interruptible basis through the expansion of an existing site on BREC's 69 kV system. The cost estimate for this phase is $1,200,000. For the long term, the industrial customer is expandable to require 60 MW capacity. This will require the addition of a 3.5 mile radial 161 kV circuit from BREC's McCracken substation to be overbuilt on an existing 69 kV circuit. The 69 kV circuit will be reconductored to allow for an alternate feed. The cost estimate for this phase is $10,200,000. | KY | Other | Load Growth | Phase I: Expand 69 kV substation for 30 MW industrial load; Phase II: increase to 60 MW | Large Industrial |  | 30-60 |  | 161 | 0 | 11400000 | Maxon Load Addition: 30MW industrial (expandable to 60MW) in BREC KY. $11.4M
MTEP21 | Central | Big Rivers Electric Corporation | 21387 | Hancock County Capacitor Bank Addition | Add a 35 MVar capacitor bank on the 69 kV bus at the existing Hancock County substation. | KY | BRP |  | Low voltage mitigation at Daviess County 161 kV bus for loss of Reid-Daviess 161 kV line. |  |  |  |  | 69 | 0 | 500000
MTEP21 | South | Cleco Power LLC | 13874 | Flagon Substation | Build a new 230 kV substation Tapped into the Donahue to Sherwood 230 kV line. Use the distribution in the area to move 16 MW from Beaver Creek substation. | LA | BRP |  | P7 contingencies on Donahue to Beaver Creek line 1 & 2 create low voltage at Beaver Creek substation in Summer Peak models. Building Flagon substation will allow more distribution flexibility in the area and reduce the load at Beaver Creek by at least 16 MW which will eliminate the low voltage condition associated with the P7 contingency. |  |  |  | 2022-07-01 | 230 | 0 | 8130000
MTEP21 | South | Cleco Power LLC | 21169 | Bayou Sale Cap Bank Move | Move the existing Bayou Sale 19.2 MVAR cap bank to Pelican 138 kV substation. | LA | BRP |  | P6 contingencies show low voltage issues and potential overloads. This project will help with the voltage issues and can be build before the longer term fix which is scheduled to be in-service by 2025. |  |  |  | 2023-06-01 | 138 | 0 | 700000
MTEP21 | South | Cleco Power LLC | 21207 | Slidell Airport Line Move | Slidell airport expansion requires moving our North Slidell to Tailsheek 230 kV line and North Slidell to Cane Bayou 230 kV line. | LA | Other | Other Local Needs | Required for Airport Expansion at Slidell |  |  |  | 2023-12-01 | 230 | 0 | 9800000
MTEP21 | West | Central Minnesota Municipal Power Agency | 20166 | Delano_Municipal_Utilities_Substation_A_Transformer_Upgrade | Facility Type: Transformer Project Description: Replace the Sub A 10 MVA 69/12.47kV transformer with a new 12/16/20 MVA 69/12.47kV transformer. System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. Delano currently has two 10 MVA 69/12.47kV transformers. The Sub A transformer is 27 years old built in 1993, rewound once, and reaching the end of its life. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers by 2022, extra capacity is needed. Proposed Solution: Delano is planning to replace the Sub A transformer with a new 12/16/20 MVA 69/12.47kV transformer. This new transformer will meet the load growth forecasted for the city and provide reliability for its customers. Reconfiguration within the substation may also allow for more customers to be served in the event one of the two 69kV transformers is out of service. | MN | Other | Load Growth | System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. Delano currently has two 10 MVA 69/12.47kV transformers. The Sub A transformer is 27 years old built in 1993, rewound once, and reaching the end of its life. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers by 2022, extra capacity is needed. |  |  | 8 | 2021-04-05 | 69 | 0 | 1750000
MTEP21 | West | Central Minnesota Municipal Power Agency | 20168 | Delano_Municipal_Utilities_Substation_B_Transformer_Upgrade | Facility type: Transmission System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. Delano currently has two 10 MVA 69/12.47kV transformer. The Sub B transformer was original in 1970 and rewound in 1999. There has been another project submitted into MTEP 21 for the substation A transformer upgrade. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers in 2022 extra capacity is needed. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers by 2022, extra capacity is needed. Proposed Solution: Delano is planning to replace substation B transformer with new 12/16/20 MVA 69/12.47kV transformer. This new transformer will meet the load growth forecasted for the city and provide reliability for its customers. Reconfiguration within the substation may also allow for more customers to be served in the event one of the two 69kV transformers is out of service. This solution also includes a new fire wall between the new transformers and additional distribution feeders for load transfer. | MN | Other | Load Growth | System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. Delano currently has two 10 MVA 69/12.47kV transformer. The Sub B transformer was original in 1970 and rewound in 1999. There has been another project submitted into MTEP 21 for the substation A transformer upgrade. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers in 2022 extra capacity is needed. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers by 2022, extra capacity is needed. |  |  | 8 | 2022-04-04 | 69 | 0 | 2500000
MTEP21 | West | Central Minnesota Municipal Power Agency | 20169 | Delano_Municipal_Utilities_New_69_kV_Industrial_Park_Substation | Facility Type: Substation Project Description: Build a new 69kV substation to serve expected residential and future industrial park load growth. System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. The downtown substation does not have room for expansion. A new substation next to the GRE Crow River 115/69kV substation will need the future load growth needs of Delano. Proposed Solution: Delano is planning to build a new 69kV substation to serve expected residential and future industrial park load growth on the NW side of the city. Please also refer to the attachment of a DGR study for the new substation request under "Attachments". | MN | Other | Load Growth | System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. The downtown substation does not have room for expansion. A new substation next to the GRE Crow River 115/69kV substation will need the future load growth needs of Delano. |  |  | 8 | 2022-04-04 | 69 | 0 | 4100000
MTEP21 | Central | City of Columbia, MO | 19805 | New UMC 69 kV Substation | Build a new UMC substation and add a new 69/13.8 kV transformer, build a 69 kV ring bus switch station, and connect two 69 kV lines to UMC ring bus. Ring bus will have four 69 kV breakers protecting two incoming 69 kV transmission lines, and will be connected to two parallel output 69 kV lines feeding two 69/13.8 kV transformers through their own 69 kV breakers. | MO | Other | Reliability | Improve reliability for University of Missouri-Columbia (UMC) due to expected load growth. |  |  |  | 2025-09-01 | 69000 | 13800 | 26000000 | CWLD Local Reliability; university load growth
MTEP21 | Central | Duke Energy Corporation | 20174 | New Sullivan 69 kV capacitor | Sullivan 69 kV - 19.8 Mvar capacitor | IN | Other | Reliability | Reduced voltage support at Edwardsport Bk10 being replaced on emergent project |  |  |  | 2023-06-01 | 69 | 0 | 500000
MTEP21 | Central | Duke Energy Corporation | 20181 | Replace Five Points 138 kV Circuit Breakers | Replace (5) 138kV oil circuit breakers with SF6 gas circuit breakers - 13803, 13804, 13809, 13813, and 138kV Bus tie breaker; 13803,04,13 were identified in 2020 as overdutied in the DEI short ckt analysis by P&C Eng'g | IN | Other | Age and Condition | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2022-12-31 | 138 | 0 | 4987000
MTEP21 | Central | Duke Energy Corporation | 20190 | Rebuild Monroe City Jct - Petersburg Jct 69 kV line | 6960 Pt 3 Rbld Monroe City Jct_Petersburg Jct w/ 477acsr - 6.25 miles. Reconductor 2.4 miles of circuit 13825 (structures #844-1162 to #844-1190/#844-3100) and 1.2 miles of circuit 13838 where they are double-circuited with 6960. Replace Monroe City Jct #1 and #2 switches and rename to 69-1 and 69-2. Rebuild the line at the Petersburg Jct (poles #821-1322 through 821-1327). | IN | Other | Age and Condition | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2022-12-31 | 138 | 69 | 10010000
MTEP21 | Central | Duke Energy Corporation | 20196 | New Rosston 69/12 kV substation | new sub to be fed from the 69182 ckt and will replace existing Whitestown 69/12kV sub in the 6983 ckt. | IN | Other | Load Growth | Distribution load growth |  |  |  | 2022-06-01 | 69 | 12 | 1337000
MTEP21 | Central | Duke Energy Corporation | 20197 | Reconfigure Wabash 138 kV substation | Upgrade misc 69 kV station equipment and convert Wabash 138 kV straight bus to ring bus | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2022-12-31 | 138 | 69 | 12570000
MTEP21 | Central | Duke Energy Corporation | 20198 | Reconfigure Hortonville 345 kV substation | Replace line relays: 34504, 34527, 6917, 69142, 69155. Install equipment to convert 345 kV bus to ring bus config. | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2022-12-31 | 345 | 69 | 1871000
MTEP21 | Central | Duke Energy Corporation | 20199 | Reconfigure Tipton West 230 kV substation | reconfigure Tipton West 230 kV bus to ring configuration | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2022-12-31 | 230 | 0 | 1864000
MTEP21 | Central | Duke Energy Corporation | 20200 | Replace Noblesville Generating Station 138/69 kV equipment | replace 138/69/2.4kV Bk9; misc upgrades to 138kV relays and wave traps, etc. | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2022-12-31 | 138 | 69 | 4328000
MTEP21 | Central | Duke Energy Corporation | 20205 | Reconfigure Greenwood Clark Township 69 kV substation | expand ring bus and add 69165 line terminal at Clark Twnshp; build short line to HE Willard Green | IN | Other | Reliability | This project will effectively increase capacity on the 69165 line by 5-10MVA to help serve increasing load in the Greenwood area and will also provide a reserve source to HE Willard Green. |  |  |  | 2021-12-08 | 69 | 0 | 4056000
MTEP21 | Central | Duke Energy Corporation | 20206 | Rebuild Huntington 138 kV to Meridian Rd Jct 69 kV | 6923 Part 2 rebuild with 954acsr; replace switches at Erie Stone jct | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2022-12-31 | 69 | 0 | 4006000
MTEP21 | Central | Duke Energy Corporation | 20207 | Rebuild Loogootee Jct to Loogootee 69kV line | Rebuild transmission line 69194 from Loogootee Jct (pole #816-2001 through #816-2152). Approx 10.2 miles. Approx 152 poles. Replace Loogootee Jct #1, #2, and #3 switches. Replace H.E. Bramble #1 and #2 switches. | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2022-12-31 | 69 | 0 | 13761000
MTEP21 | Central | Duke Energy Corporation | 20208 | Rebuild Morgantown to Bean Blossom 69 kV line | Rebuild transmission line 6949 from Morgantown substation (pole #825-3122) to Bean Blossom substation (pole #825-3270) using light duty steel poles, 477 ACSR | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2022-12-31 | 69 | 0 | 13353000
MTEP21 | Central | Duke Energy Corporation | 20225 | Rebuild McKay Rd Jct. to H.E. Lewis Creek Jct. 69 kV line | Rebuild transmission line 6975 from McKay Rd Junction (pole #807-3096) to H.E. Lewis Creek Junction (pole #807-3168) using light duty steel poles, 477 ACSR conductor and OPGW. - 5.9 miles ; Replace two switches at McKay Rd Junction 2000A | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2022-12-31 | 69 | 0 | 7244000
MTEP21 | Central | Duke Energy Corporation | 20226 | Reconfigure Deedsville 345 kV substation | Reconfigure 345kV to ring bus. Replace various 345kV and 69kV transmission equipment including relays and OCBs | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2022-12-31 | 345 | 69 | 7710000
MTEP21 | Central | Duke Energy Corporation | 20227 | Reconfigure Middlefork 69 kV substation | Replace misc. 69kV OCBs and relays; replace 6910-01 line switch with 2000A; establish 69kV ring bus | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2022-12-31 | 69 | 0 | 8713000
MTEP21 | Central | Duke Energy Corporation | 20228 | Reconfigure Prescott 345 kV substation | Replace misc. 69kV OCBs and relays; establish 345kV ring bus | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2022-12-31 | 345 | 69 | 7543000
MTEP21 | Central | Duke Energy Corporation | 20230 | Rebuild Purdue NW Tap to Purdue to Cincinnati St. 138 kV line | Rebuild the 13820 line from the Purdue Northwest Tap to West Lafayette Purdue University to Cincinnati St. substation using 954 ACSR at 120 C | IN | Other | Reliability | (Replaces previous project 17485) With the new West Lafayette Airport sub getting placed in-service on the 13820 line between the Purdue Northwest Tap and West Lafayette Purdue subs, when there is a breaker failure that takes out bus 2 at Westwood, the line segments from the Purdue Northwest Tap to West Lafayette Airport to Purdue to Cincinnati St. are loaded to 99.7% or higher per the MTEP21 - 2023 sum peak _AA model. |  |  |  | 2023-12-31 | 138 | 0 | 9580000
MTEP21 | Central | Duke Energy Corporation | 20245 | J805 Gwynneville Solar | J805 Gwynneville Solar | IN | GIP |  | GIA |  |  |  | 2021-12-31 | 345 | 0.6 | 7657657
MTEP21 | Central | Duke Energy Corporation | 20246 | J829 Fairbanks Solar | J829 Fairbanks Solar | IN | GIP |  | GIA |  |  |  | 2022-08-19 | 345 | 0.63 | 15447998
MTEP21 | Central | Duke Energy Corporation | 20247 | Rebuild Lafayette S. to Shadeland 138 kV line | Rebuild 138100 ckt with 954ACSR@120C - 3.2 miles | IN | BRP |  | Line overload identified in MTEP20 analysis - (2) Cat. P7; Multiple P6 |  |  |  | 2023-06-01 | 138 | 0 | 7500000
MTEP21 | Central | Duke Energy Corporation | 20248 | Dresser 345kV Redundant Ckt Brkr Addition | Dresser 345kV Redundant Ckt Brkr Addition between Bk1 and Bk2 with fully redundant protection scheme per future P5 definition | IN | BRP |  | MTEP20 contingency flow jumped up 64MVA (over 2019 results) which has violated the 15 minute 675MVA rating of Bk3; Violations are caused by the coincidental loss of Dresser 345/138kV Bks 1 and 2 due to misoperation / failure of their 345kV common ring bus breaker. Operating mitigation: open Dresser ckt breakers 13861 (towards Staunton - 249721,249685,1) and 13868 (towards Terre Haute S. 1st St. - 249721,249857,1) to alleviate OL until either Bk1 or Bk2 can be placed back in service. Project will insert a redundant breaker to eliminate the contingency. |  |  |  | 2023-06-01 | 345 | 0 | 8000000
MTEP21 | Central | Duke Energy Corporation | 20250 | DEI Bolivar to NIPS Templeton 69kV line | WVPA to construct new N.O. reserve 69kV line to existing NIPS Templeton sub from DEI Bolivar | IN | Other | Reliability | WVPA planned project to supply an alternate feed to their existing NIPS Templeton sub to increase reliability |  |  |  | 2022-04-01 | 69 | 0 | 7000000
MTEP21 | Central | Duke Energy Corporation | 20645 | New Greenfield Hastings Park 138 kV ring bus | Greenfield Hastings Park - establish a 3-breaker, 138kV, ring bus | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2021-10-01 | 138 | 0 | 4237000
MTEP21 | West | Dairyland Power Cooperative | 19953 | Frenchville Tap N223 Rebuild | Rebuild 11.1 miles of the N-223 line from the N-122 tap to the XEL Ettrick substation with 4/0 conductor. | WI | Other | Age and Condition | Age and Condition |  |  |  | 2023-04-14 | 69 | 0 | 3848576.89
MTEP21 | West | Dairyland Power Cooperative | 20136 | Pine Lake to Dunn Ethanol N4 Rebuild | This project is a mix of a rebuild of DPC’s existing 69 kV line in the area and construction on new right-of-way. The recommended plan in this area is to construct new transmission line with 477 ACSR conductor, a mix of replacement of existing line and new right-way from XEL’s Pine Lake transmission substation to the east towards the Dunn Ethanol distribution substation. The recommended plan will address the age and condition issues, constructing the line with new poles and 477 ACSR conductor. The plan will also address the longer tap lines to distribution substations with individual taps to all five distribution substations served from this line. Finally, building to the Dunn Ethanol distribution substation will provide backup service. | WI | Other | Age and Condition | DPC’s transmission line in this area was constructed in 1947 and has age and condition issues. |  |  |  | 2024-02-09 | 69 | 0 | 13051779.51
MTEP21 | South | Entergy Arkansas | 19907 | Moreland 161kV: Rebuild Substation | Wreck out the existing 20 MVA substation Transformer and associated bus and breakers and install a new substation consisting of 2-new 40 MVA substation transformers on the existing property to include two 161-13.8 KV, 40 MVA LTC transformers. Build 13.8kV low-side operating bus and transfer buses as per Entergy Substation Specifications including a 2000A bus tie breaker and bay connecting the two transformer busses. Install two 2000A main breaker bays and eight feeder breaker bays. | AR | Other | Load Growth | There is approximately 20 MVA of load at risk for the loss of the single transformer at Moreland substation. Currently there is load shifted from Moreland to Russellville to eliminate a real time overload on the existing transformer. |  |  | 20 MVA | 2022-12-30 | 161 | 0 | 13400000
MTEP21 | South | Entergy Arkansas | 19908 | Cave City 161kV: Add 2nd Transformer | Add a 40 MVA 161/34.5kV LTC transformer in the existing substation. Install three 1200 Amp feeder breakers and a 1200 Amp bus tie breaker. | AR | Other | Load Growth | The existing 14 MVA transformer and regulator is projected to be loaded to 109% in the winter of 2023. |  |  | 40 MVA | 2023-06-01 | 161 | 34.5 | 8054670
MTEP21 | South | Entergy Arkansas | 19909 | 2021 EAL Asset Renewal Program | This project includes the EAL asset renewal projects that will be performed in 2021. | AR | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc. |  |  |  | 2021-12-30 | 500 | 115 | 27200000
MTEP21 | South | Entergy Arkansas | 19910 | 2022 EAL Asset Renewal Program | This project is for the EAL Asset Renewal Program that will be executed in 2022. | AR | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc. |  |  |  | 2022-12-30 | 500 | 115 | 19300000
MTEP21 | South | Entergy Arkansas | 21447 | Happy 115kV: New Switching Station (J1373) | Happy 115kV (J1373) is a new ring bus switching station tapped on the Searcy Price - Griffithville line section. Entergy Arkansas will install line taps into and out of the Happy 115kV switching station as well as line protection and breaker control relay upgrades, new RTU installation, and wave trap removal at the remote end Brinkley East and Searcy Price 115kV substations. Approximately 4.7 miles of underground fiber will be installed between Happy and Griffithville 115kV substation. | AR | GIP |  | This project is needed to provide a point of interconnection for the solar project J1373. |  |  |  | 2023-03-15 | 115 | 0 | 3717000
MTEP21 | South | Entergy | 15605 | Frisco-Tezcuco 230kV: Upgrade Circuit 1 and 2 | Increase the rating of the Tezcuco to Frisco 230 circuit #1 and #2 to a minimum of 1925A (765 MVA). | LA | BRP |  | MISO identified thermal overloads on the Tezcuco to Frisco circuit #1 and #2 during generator interconnection and deliverability analysis. • Tezcuco to Frisco 230kV circuit #1 following the loss of Tezcuco to Frisco 230kV circuit #2 • Tezcuco to Frisco 230kV circuit #2 following the loss of Tezcuco to Frisco 230kV circuit #1 |  |  |  | 2021-12-01 | 230 | 0 | 2200000
MTEP21 | South | Entergy | 18228 | Golden Meadow to Clovelly 115 kV: Rebuild line | Rebuild the ~7 mile Golden Meadow to Clovelly 115 kV line to 230 kV specifications. | LA | Other | Reliability | Enhanced Reliability. The P1.3 loss of the Barataria 230/115 kV autotransformer creates loadings on Clovelly to Golden Meadow over 90%. Increase reliability to the area. Hurricane damage to the other source into the region has elevated the need for this project. |  |  |  | 2022-02-28 | 115 | 0 | 86300000
MTEP21 | South | Entergy | 19957 | Lake Arthur 69 kV Switch Upgrade | Replace switch 732 at Lake Arthur with a motorized load break switch that has whips and bottles. Move the Normally Open point from switch 8873 to switch 732 so that Lake Arthur 69 kV station is fed out of Lawtag 69 kV station. | LA | Other | Reliability | This project is needed to mitigate N-0 voltage violation at Lake Arthur 69 kV bus and to maintain compliance with Entergy’s Transmission Planning Criteria. |  |  |  | 2022-06-01 | 69 | 0 | 706000
MTEP21 | South | Entergy | 19987 | Nelson 230/138 kV Relay Improvement SPOF | Dual Battery installations or monitoring sufficient to FERC 754 guidelines at Nelson 230 kV and 138 kV stations. Install and verify high speed dual primary protection on the GSU for all power plants interconnected at Nelson 230 kV and 138 kV substations | LA | BRP |  | NERC TPL-001-4 violations observed for a P5 contingency at Nelson including thermal overloads on the Carlyss 230-138 kV Autotransformer and the Sphere to Mossville 69 kV line. |  |  |  | 2023-12-01 | 230 | 138 | 17900000
MTEP21 | South | Entergy | 20039 | 2021 ELL Asset Renewal Program | This project is for the ELL Asset Renewal Program that will be executed in 2021. | LA | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | 2021-12-31 | 500 | 69 | 96480929
MTEP21 | South | Entergy | 20040 | 2022 ELL Asset Renewal Program | This project is for the ELL Asset Renewal Program that will be executed in 2022 | LA | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | 2022-12-31 | 500 | 69 | 42100000
MTEP21 | South | Entergy | 20045 | Northline 230 kV: New Substation | Northline 230 kV distribution substation will cut in between the existing Addis and Cohen 230 kV stations. | LA | Other | Load Growth | Distribution System Load Growth. | Large Industrial |  | 50 | 2024-06-01 | 230 | 0 | 42800000 | Northline 230kV: 50MW new load. $42.8M
MTEP21 | South | Entergy | 20122 | 2021 ENOL Asset Renewal Program | This project is for the ENOL Asset Renewal Program that will be executed in 2021 | LA | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | 2021-12-31 | 230 | 69 | 5900000
MTEP21 | South | Entergy | 20124 | 2022 ENOL Asset Renewal Program | This project is for the ENOL Asset Renewal Program that will be executed in 2022 | LA | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | 2022-12-31 | 230 | 69 | 4500000
MTEP21 | South | Entergy | 20306 | Adams Creek Relay upgrades (J830,J868,J908) | Relay upgrades at Adams Creek/Bogalusa 500 kV. | LA | GIP |  | Identified by MISO for NRIS/ERIS for the interconnection customers J830, J868, and J908. |  |  |  | 2021-12-15 | 500 | 0 | 417756
MTEP21 | South | Entergy | 20307 | Par 115 kV Station(J1184) | Construct a 115 kV substation named Par between the existing Franklinton and Holton 115 kV substations. | LA | GIP |  | This station is being constructed to accommodate the interconnection of a solar facility (J1184). |  |  |  | 2021-03-02 | 115 | 0 | 4050923
MTEP21 | South | Entergy | 20585 | J1142 Generator Interconnection at Vacherie 230 kV | Facilities required for the interconnection of J1142 at the existing Vacherie 230 kV substation. | LA | GIP |  | This construction at the existing Vacherie 230 kV substation is to accommodate the interconnection of a solar facility (J1142) |  |  |  | 2021-03-29 | 230 | 0 | 4300000
MTEP21 | South | Entergy | 20628 | J1158 Generator Interconnection at Vacherie 230 kV | Facilities required for the interconnection of J1158 at the existing Vacherie 230 kV substation. | LA | GIP |  | This construction at the existing Vacherie 230 kV substation is to accommodate the interconnection of a solar facility (J1158) |  |  |  | 2022-12-01 | 230 | 0 | 40000
MTEP21 | South | Entergy | 21085 | Sugar House 230 kV: New Station | Entergy is proposing to construct a new 230 kV substation (Sugar House 230 kV Substation) which will serve an industrial customer’s 50 MW of new load in Port Allen, LA. The new lines into the Sugar House substation will be cut in and out (~.7 miles total) of the existing Formosa to Placid 230 kV line. The Sugar House 230 kV station will be constructed as a 3 breaker ring bus. Relocation of a portion of the existing 138 kV line that shares right of way with the 230 kV line will also be part of this project. | LA | Other | Load Growth | Entergy has received a request from a customer interested in adding new load to a new station on the transmission system. | Large Industrial |  | 50 | 2022-12-31 | 230 | 0 | 20100000 | Sugar House 230kV: 50MW industrial customer. $20.1M
MTEP21 | South | Entergy | 21525 | Sullivan 230 kV: New Station, Southport to Sullivan 230 kV Line upgrade | Construct new 230 kV station to be cut into the Southport to Joliet 230 kV line. Upgrade the Southport to Sullivan 230 kV line. | LA | BRP |  | The Sullivan station will be dedicated to serve New Orleans Sewerage and Water Board load. The Southport to Sullivan 230 kV upgrade is driven by NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. In 2023 summer the P2.3 Internal Breaker Fault of a Ninemile breaker will cause overloads on the Southport to Sullivan 230kV line. | Large Industrial |  |  | 2023-06-01 | 230 | 0 | 27100000 | BRP; New Orleans Sewerage & Water Board customer
MTEP21 | South | Entergy Mississippi | 20058 | Baxter Wilson - Perryville 500 kV terminal equipment upgrade | Upgrade the following terminal equipment at Baxter Wilson SES SWYD (Perryville Line Bay) to a minimum through-path rating of 1940 MVA: J2217, J2219, Line Trap, SEL321. | MS | Other | Reliability | Enhanced Reliability. P1.1 Loss of Grand Gulf generator causes thermal loading of 98% in 2021 Winter. P3 loss of Grand Gulf coupled with loss of the McAdams to Lakeover 500 kV line requires over 2500 MW of generation redispatch to mitigate in 2025 Winter. |  |  |  | 2022-12-15 | 500 | 0 | 1110925
MTEP21 | South | Entergy Mississippi | 13995 | Mannsdale 230kV Substation | Build new Mannsdale 230kV substation in operating and transfer configuration. Include appropriate high-side fault protection. Install two (2) – 40 MVA, 230 kV-13.8kV, LTC, transformers including high-side circuit switchers to operate at 12.47kV. Install two (2) – 2,000 amp, 13.8kV, main breakers. Install eight (8) 1200 amp, 12.47 kV, breaker bays and equip with six (6) breakers; three (3) breakers to be served by T-1, and three (3) to be served by T-2. Install control house and all necessary relaying equipment. | MS | Other | Load Growth | The service area of the planned Mannsdale substation is a portion of west Madison county experiencing growth rates of 3% or more with several known block load subdivisions planned in the near future and multiple tracks for potential build out. It is currently being served by circuits from Flora, Bozeman, and Lake Castle substations at 3 to 7 line miles away. There is some transfer capability between circuits for contingency conditions but it is limited by voltage decay due to heavy loading and distance. Beginning in 2020 feeder configurations will have to be switched to non-optimal reliability configurations due to load growth in the area. |  |  | 40 MVA | 2025-06-01 | 230 | 0 | 32200000
MTEP21 | South | South Mississippi Electric Power Association | 15848 | Jayess Loop Project | Rebuild L523 (Norfield SS to Little Creek) with sufficient ACSR conductor. Tap L549 (Jayess SS to Jayess) with a 115kV GOAB, tap L523 with a 115kV GOAB and build a new 115kV transmission line from Jayess GOAB to Little Creek GOAB. Build a new 115kV breaker switching station at Jayess and build a new 115kV breaker switching station at Norfield. | MS | Other | Reliability | Current radial transmission service violates MW-Mile planning criteria. |  |  |  | 2024-05-01 | 115 | 0 | 14660000
MTEP21 | South | South Mississippi Electric Power Association | 15850 | Olive Oil Loop Project | Rebuild L546 (Pisgah GOAB to Magee Road SS) with sufficient ACSR conductor. Rebuild L547 (Arlington GOAB to Arlington) with sufficient ACSR conductor. Tap L547 with a 115kV GOAB, tap L576 (Magee Road SS to Olive Oil) with a 115kV GOAB and build a new 115kV transmission line from Arlington GOAB to Olive Oil GOAB. Build a new 115kV breaker switching station at Arlington. | MS | Other | Reliability | Current radial transmission service violates MW-Mile planning criteria. |  |  |  | 2024-12-01 | 115 | 0 | 12106000
MTEP21 | South | Entergy Mississippi | 20055 | McAdams 230 kV: Relay Improvement SPOF | Project addresses Relay Single Point of Failure at McAdams 230 kV substation by adding or replacing bus differential protection on the 230kV buses, adding or replacing bus potential transfer panel, replacing two (2) OCBs, breaker control panel and CCVTs. | MS | BRP |  | The P5 loss of the McAdams 230kV bus due to a failed bus differential relay causes thermal overloads on the S. Grenada to Elliot 115kV line. There is also the potential for ~2000 MW of generation trip to occur for a 3PH fault on the McAdams 230 kV bus with non-redundant relay failure (TPL-001-4 category 2 stability extreme event). This project improves relay protection deficiencies at the McAdams 230 kV substation. |  |  |  | 2023-06-01 | 230 | 0 | 4600000
MTEP21 | South | Entergy Mississippi | 20057 | Franklin 115 kV: Relay Improvement SPOF | Install dual primary protection with independent CT and PT winding inputs on the Franklin 115 kV bus. Dual battery installations or monitoring sufficient to meet FERC 754 guidelines. | MS | BRP |  | NERC TPL-001-4 violations observed for a P5 contingency at Franklin 115 kV substation. Failure of the 115kV bus differential relay to clear a fault causes the loss of the Franklin 115kV and 500kV busses. This results in widespread thermal and voltage issues in Southwest Mississippi. |  |  |  | 2023-06-01 | 115 | 0 | 1700000
MTEP21 | South | Entergy Mississippi | 20060 | 2021 EML Asset Renewal Program | This project includes the EML asset renewal projects that will be performed in 2021. | MS | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc. |  |  |  | 2021-12-31 | 500 | 115 | 29069307
MTEP21 | South | Entergy Mississippi | 20061 | 2022 EML Asset Renewal Program | This project includes the EML asset renewal projects that will be performed in 2022. | MS | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc. |  |  |  | 2022-12-31 | 500 | 115 | 30477959
MTEP21 | South | Entergy Mississippi | 20308 | Franklin Relays Upgrade (J830 J868 J908) | Relay upgrade at Franklin 500 kV. | MS | GIP |  | Identified by MISO for NRIS/ERIS for the interconnection customers J830 J868 J908. |  |  |  | 2021-12-15 | 500 | 0 | 900000
MTEP21 | South | East Texas Electric Cooperative Inc. | 19853 | Fork Creek 138kV Station Upgrade | Upgrade of existing substation with addition of 138kV line breakers for through-bus operation. | TX | Other | Reliability | Increase transmission system reliability, improve response to outage conditions, reduce time for switching operations. |  |  |  | 2022-12-31 | 138 | 0 | 900000
MTEP21 | South | East Texas Electric Cooperative Inc. | 19954 | Newton 138 kV Station | Convert existing radial substation to looped substation and install 138/69 kV transformer. | TX | Other | Reliability | Increase transmission system reliability, improve customer reliability, improve response time to outages, reduce time required for switching operations. |  |  |  | 2023-04-01 | 138 | 69 | 5300000
MTEP21 | South | Entergy | 20042 | 2021 ETI Asset Renewal Program | This project is for the ETI Asset Renewal Program that will be executed in 2021. | TX | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | 2021-12-31 | 500 | 69 | 22100000
MTEP21 | South | Entergy | 20043 | 2022 ETI Asset Renewal Program | This project is for the ETI Asset Renewal Program that will be executed in 2022 | TX | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | 2022-12-31 | 500 | 69 | 32500000
MTEP21 | South | Entergy | 20067 | Southline 138 kV: New Substation | Southline 138 kV substation is a distribution station that will be cut into the Cleveland to Jayhawker 138 kV line. | TX | Other | Load Growth | Distribution system load growth |  |  |  | 2023-12-01 | 138 | 0 | 34800000
MTEP21 | South | Entergy | 20073 | Ponderosa 230 kV: Install Power Transformer | Install power transformer at the Ponderosa 230 kV substation. There are no power transformers currently installed at Ponderosa. | TX | Other | Load Growth | Distribution system load growth |  |  |  | 2024-06-01 | 230 | 0 | 23500000
MTEP21 | South | Entergy | 20405 | J1030 Station Interconnection Project | This project is to construct the interconnection station for the solar project J1030 on the Poco to Menard 138 kV line. | TX | GIP |  | This project is to support the interconnection of solar project J1030 on the Poco to Menard 138 kV line. |  |  |  | 2023-01-01 | 138 | 0 | 7150200
MTEP21 | Central | Gridliance | 19746 | Rebuild Joppa-Shawnee 161 kV line Ckt 2 | Rebuild the GridLiance Heartland portion of the Joppa - Shawnee 161 kV ckt 2 line | IL,KY | Other | Age and Condition | After purchasing the transmission facilities in March 2020, GridLiance Heartland as part of our integration of facilities into our Operatons plan performed a LiDAR survey and identified clearance issues with the line and found a significant number of the structures require replacement on this circuit. Typically these issues would be indentified in a maintenance plan and submitted for future MTEP cycles but GridLiance has identified the issues on this line as critical. GridLiance has been working with MISO RC and SERC to resolve the clearance issues. The 2010 NERC Alert was not previously addressed by former TOs of these facilities and has just been identified by GridLiance as an issue. GridLiance determined its mitigation is to rebuild the line in consideration of the clearance issues and the overall poor condition of a majority of the structures with an age of the facilities (>60 years). GridLiance must start immediately to address the reliability issues. |  |  |  | 2022-03-01 | 161 | 0 | 11000000
MTEP21 | Central | Gridliance | 20001 | Rebuild Joppa-Shawnee 161 kV Ckt 3 | Rebuild the GridLiance Heartland portion of Joppa-Shawnee 161 kV Ckt 3 | IL,KY | Other | Age and Condition | Age and condition of line |  |  |  | 2023-06-01 | 161 | 0 | 11700000
MTEP21 | Central | Gridliance | 20004 | Rebuild Joppa-Shawnee 161 kV Ckt 4 | Rebuild the GridLiance Heartland portion of Joppa-Shawnee 161 kV Ckt 4 | IL,KY | Other | Age and Condition | Age and condition of line |  |  |  | 2023-06-01 | 161 | 0 | 11700000
MTEP21 | Central | Gridliance | 20005 | Rebuild Joppa-Shawnee 161 kV Ckt 1 | Rebuild GridLiance Heartland portion of Joppa-Shawnee 161 kV Ckt 1. | KY,IL | Other | Age and Condition | Age and condition of line |  |  |  | 2023-06-01 | 161 | 0 | 14700000
MTEP21 | West | Great River Energy | 18865 | Square Butte - Stanton 230 kV Upgrade (J302/J503) | Upgrade Square Butte - Stanton 230 kV line for generation interconnections J302 & J503. | ND | GIP |  | Generation interconnections J302 & J503. |  |  |  | 2021-07-10 | 230 | 0 | 6379446
MTEP21 | West | Great River Energy | 20139 | Winthrop McLeod - Winthrop Xcel (MC-WW) 69 kV Rebuild | Rebuild MC-WW (9 miles) to upgradable 69kV with T2 capable of 1500-1600 amps. Remove SS2950 Winthrop tap switch. | MN | Other | Reliability | The existing MC-WW line is lossy and introduces a significant voltage drop causing a weaken/marginal voltage at McLeod’s Highland substation during contingencies. System analysis show that the existing transmission system doesn’t have capacity to serve additional load that may come to connect to the 69 kV system. Rebuilding this transmission line with a less lossy line strengths voltage profile and make additional capacity available in the 69 kV system. |  |  |  | 2024-05-01 | 69 | 0 | 6616829
MTEP21 | West | Great River Energy | 20141 | Decoria - Decoria Tap - Stoney Creek (BE-MD) 69 kV Rebuild | Rebuild BE-MD segments 1 and 2 (4.02 miles) and SS2826 to 69kV with T2 1200 amp capable conductor. | MN | Other | Reliability | Poor reliability. |  |  |  | 2023-10-27 | 69 | 0 | 3015848.74
MTEP21 | West | Great River Energy | 20151 | Milaca Breaker Addition 69 kV | Move ECE’s Milaca delivery points from the auxiliary bus onto the main bus and with circuit breaker protection. | MN | Other | Reliability | The Milaca – Ogilvie 69 kV line is 12.7 miles, 170°F, 36.2/55.6 MVA line that is limited by jumpers (30.1/45.7 MVA). During summer peak loading, the “PG” (Milaca – Ogilvie 69 kV) line will overload when Milaca 5NB1 trips. This is based off existing summer peak loads and does not depend on load growth to achieve the need. |  |  |  | 2021-12-31 | 69 | 0 | 419407.71
MTEP21 | West | Great River Energy | 20143 | Wing River 230 kV Ring Bus | Convert the 230 kV portion of the Wing River substation into a ring bus. | MN | Other | Reliability | Avoid excessive tripping of BES elements for both normal and abnormal fault clearing scenarios. |  |  |  | 2022-08-26 | 230 | 0 | 3722667.74
MTEP21 | West | Great River Energy | 17996 | Willmar 230/115 kV Transformer | Add a 230/115 kV LTC transformer at Willmar substation. | MN | Other | Reliability | Low voltage during loss of Morris - Morris OTP 115 kV line. Better load sharing between Priam 115/69 kV transformer and Willmar 230/69 kV transformer. |  |  |  | 2022-05-01 | 230 | 115 | 12285046.31
MTEP21 | West | Great River Energy | 20148 | Appleton - Benson (AG-AB) 115 kV Line | Construct about 27 miles of 115 kV transmission line from Appleton to GRE’s AG-BK line and about 1.75-mile 115 kV transmission line from AG-BK line to Benson Muni substation with associated tap switch, distribution sub, and retirement projects. | MN | Other | Reliability | This project is needed for the following reasons: 1. Accommodate future load growth in the Benson and other areas along the 115-kV transmission system 2. Improve load serving capability of the 41.6 kV and 115 kV transmission system 3. Address future NERC standard reliability violations, such as contingency low voltage concerns in the 115-kV system 4. Address existing N-2 contingency voltage collapse cases it the 115-kV system |  |  |  | 2026-07-31 | 115 | 0 | 34773673 | GRE West Region; classified Local Reliability but serves load growth
MTEP21 | West | Missouri River Energy Services (MRET) | 20608 | Worthington Substation | This project is for the construction of a 69/12.47 kV substation, preliminary referred to as the New Worthington Sub, on the east side of Worthington, MN. In addition, MRES and GRE are recommending a two-stage capacitor bank (2 x 7.0 MVAR) to address transmission needs and improve operations. | MN | Other | Reliability | Based on the planned customer expansions, the Worthington load is expected to exceed capacity capabilities of the WPU transmission-to-distribution system (along with inadequacies in the distribution system to backup this load effectively). So, additional load service is necessary. GRE and MRES have concluded that the addition of the New Worthington Sub is necessary. With the transmission system exceeding its voltage support capabilities, some investment in the transmission system is necessary. For that, we have concluded that capacitor banks should be included in that substation addition. |  |  |  | 2022-11-01 | 69 | 0 | 4800000
MTEP21 | Central | Indianapolis Power & Light Company | 20134 | New Stout 345 kV Breaker | Add one 345 kV breaker to form a ring bus at the Stout S substation. | IN | Other | Reliability | Adding the 345 kV breaker to form a ring bus allows for the Stout to Thompson and Stout to Hanna 345 kV lines to remain in service for the Stout 345-138 kV auto-transformer contingency. This allows for the removal of the operating procedures needed for P6 contingency thermal overloads that are the result of the loss of the Stout 345-138 kV auto-transformer combined with other elements. |  |  |  | 2022-12-31 | 345 | 0 | 3150400
MTEP21 | Central | Indianapolis Power & Light Company | 20137 | New Guion 345/138 kV transformer No. 3 | One (1) new third 500 MVA auto transformer is scheduled to be installed at Guion substation. This project is needed to increase import capability and plan for the possible unavailability of long lead time equipment. The project includes three (3) new 345 kV breakers, two (2) replacement 345kV breakers, two (2) 138 kV breakers, and terminal equipment including disconnect switches, relays, etc. | IN | Other | Reliability | Removes the need for numerous operating guides for P6 contingencies. |  |  |  | 2023-12-31 | 345 | 138 | 13376000
MTEP21 | West | ITC Midwest | 17968 | Thisius 161/69kV Substation | ITCM will construct a 161:69kV substation at the crossing of the Huntley – Freeborn 161kV and Huntley – Walters 69kV circuits. | MN | Other | Reliability | Low voltage on the 69kV system in the area and to increase operational flexibility in the Albert Lea area |  |  |  | 2023-05-31 | 161 | 69 | 7888877
MTEP21 | West | ITC Midwest | 19925 | Albia-Melrose 69kV Rebuild | The majority of the Albia to Melrose 69kV line is near end of life and in poor condition. The line between the Albia and Melrose substations (~17.25 miles) will be rebuilt to current 69kV standards. All new equipment should be rated at 600A or higher minimum summer normal rating. | IA | Other | Age and Condition | The majority of the Albia to Melrose 69kV line is near end of life and in poor condition. |  |  |  | 2024-12-31 | 69 | 69 | 16293244
MTEP21 | West | ITC Midwest | 19926 | Osceola North-Woodburn Jct 69kV Rebuild | The majority of the Osceola North to Woodburn 69kV line is near end of life and in poor condition. The line between the Osceola North, Osceola Rec, and Woodburn Jct. substations (~9.57 miles) will be rebuilt to current 69kV standards. All new equipment should be rated at 600A or higher minimum summer normal rating. | IA | Other | Age and Condition | The majority of the Osceola North to Woodburn 69kV line is near end of life and in poor condition. |  |  |  | 2024-12-31 | 69 | 69 | 8964000
MTEP21 | West | ITC Midwest | 19928 | Marion-Old Settlers 115kV Ckt#2 | To better serve the Northeast Cedar Rapids load pocket, ITC will energize the second circuit on the Marion – Old Settlers 115kV structures and terminate it into Marion & Old Settlers substations. | IA | Other | Reliability | To better serve the Northeast Cedar Rapids load pocket, ITC will energize the second circuit on the Marion – Old Settlers 115kV structures and terminate it into Marion & Old Settlers substations. |  |  |  | 2025-12-31 | 115 | 115 | 4232578
MTEP21 | West | ITC Midwest | 19931 | Dickinson County-Triboji 161kV Sag Remediation | Remove all existing sag limits on Dickinson County – Triboji 161 kV line to raise 636 ACSR to full summer conductor rating at 212 F (953/953/953 amps SN/SE/SSE 266/266/266 MVA SN/SE/SSE). | IA | Other | Reliability | Remove all existing sag limits on Dickinson County – Triboji 161 kV line to raise 636 ACSR to full summer conductor rating at 212 F (953/953/953 amps SN/SE/SSE 266/266/266 MVA SN/SE/SSE). |  |  |  | 2022-12-31 | 161 | 161 | 369600
MTEP21 | West | ITC Midwest | 19993 | Triboji 69kV Cap Bank | ITC will install a 11.25MVAR Effective cap bank, zero crossing/sync breaker and 0.5 mH pre-insertion reactor on the Triboji J2 bus. All new substation equipment should have a minimum rating of 1200A. | IA | Other | Reliability | Low voltage on the 69kV system in the Triboji area under contingency. |  |  |  | 2023-12-31 | 69 | 69 | 813960
MTEP21 | West | ITC Midwest | 19995 | West Union 69kV Cap Bank | ITC will install a 11.25MVAR Effective cap bank, zero crossing/sync breaker and 0.5 mH pre-insertion reactor on the West Union J2 bus. All substation equipment should have a minimum rating of 1200A. | IA | Other | Reliability | Low contingency voltage in the West Union area. |  |  |  | 2023-12-31 | 69 | 69 | 812280
MTEP21 | West | ITC Midwest | 19996 | Monona 69kV Sub Rebuild & Cap Bank Addition | ITC rebuild the Monona 69kV substation and install a 11.25MVAR effective cap bank, zero crossing/sync breaker and 0.5 mH pre-insertion reactor at a new Monona Substation adjacent to the existing site. All substation equipment should have a minimum rating of 1200A. This will allow for two 69kV buses and the cap bank installation at the new Monona site improving operational flexibility and addressing voltage concerns in the area. | IA | Other | Reliability | Low voltage on the 69kV system in the area under contingency. |  |  |  | 2022-12-31 | 69 | 69 | 1152000
MTEP21 | West | ITC Midwest | 20025 | Bethel-Tripoli 69kV Rebuild | The majority of the Bethel-Tripoli 69kV line is near end of life and in poor condition. The line between the Bethel substation and Fredericksburg Tap (~8 miles) will be rebuilt to current 69kV standards. All new equipment should be rated 600A or higher minimum summer normal rating. | IA | Other | Age and Condition | The majority of the Bethel-Tripoli 69kV line is near end of life and in poor condition. |  |  |  | 2024-12-31 | 69 | 69 | 7740000
MTEP21 | West | ITC Midwest | 20026 | Osage Jct-Rice 69kV Rebuild | The majority of the Osage JCT-Rice 69kV line is near end of life and in poor condition. The line between Osage JCT and Douglas Tap (~13.9 miles) and Riceville to Rice (~9.8 miles) will be rebuilt to current 69kV standards. All new line equipment should be rated 600A or higher. | IA | Other | Age and Condition | The majority of the Osage JCT-Rice 69kV line is near end of life and in poor condition. |  |  |  | 2024-12-31 | 69 | 69 | 22980000
MTEP21 | West | ITC Midwest | 20027 | Meservey 69kV Tap Retirement | Retire ~6.9 miles of 69kV line to the IPL owned Meservey substation. Also remove line switches 4122 and 4123. All poles with underbuild should be topped per underbuild owner specification. All necessary outages should be coordinated with IPL. | IA | Other | Other Local Needs | The Meservey 69kV tap will no longer be needed. Customer Requested. |  |  |  | 2022-12-31 | 69 | 69 | 420000
MTEP21 | West | ITC Midwest | 20028 | Emery-6th Ave 69kV Rebuild | Beginning at where the double circuit ends (~0.35 miles outside Emery) - IPL’s 6th Ave substation will be rebuilt (~5.54 miles of line) to current 69kV standards. All new line should be rated 1200A or higher. | IA | Other | Age and Condition | The majority of the Emery 6th Ave 69kV line is near end of life and in poor condition. |  |  |  | 2024-12-31 | 69 | 69 | 7200000
MTEP21 | West | ITC Midwest | 20029 | Southern Iowa New 161kV line and Breaker Stations | ITC will be building about 29 miles of 161kV line from CIPCO’s Winterset Jct. to Osceola’s new substation. This new line will be constructed using T2 636 ACSR and all new 161kV terminal equipment should be rated at 2000A or higher minimum summer normal rating. In addition, a new 161/69kV, 150 MVA transformer will be needed at the Osceola substation. ITC and CIPCO will install new breaker(s) at their respective substations. ITC will be building a new breaker station northeast of the Albia substation. This station will connect the 69kV line from Albia to Court and the 69kV line from Bridgeport to Centerville. Since the two lines have an intersection point (about 1.5 miles NE of the Albia sub), minimal line construction will be needed. ITC will be building a new breaker station at the “Lenox Tap” position. This station will replace the 3-way switch currently in use and connect our Lenox line and substation (IPL owned) to the new 69kV transmission system being built by CIPCO from the northwest (Corning/Brooks). All new 69kV equipment will need to be rated for 1200A minimum summer normal rating. ITC will be installing a 2-way switch outside IPL’s Lenox substation, building a new 69kV line (about 2.6 miles), and connecting it into CIPCO’s substation “Lenox Muni”. ITC will need to coordinate with CIPCO, NEMO, and IPL for necessary outages and construction | IA | Other | Reliability | Low voltage concerns in southern Iowa. |  |  |  | 2026-05-01 | 161 | 69 | 71210187
MTEP21 | West | ITC Midwest | 20035 | MPFCA - Hickory Creek and Killdeer 345 kV Cap Bank TO-Funded Network Upgrades | ITC Midwest entered into a Multi-Party Facilities Construction Agreement (“MPFCA”) with MISO and the Interconnection Customers for MISO Projects J302, J476, J503, J512, J555, J569, J583, J587, J590, J611 and J614 for the construction of Network Upgrades at Killdeer 345 kV and Hickory Creek 345 kV. The MPFCA provides for ITC Midwest to fund the cost of 2 x 84 MVAR (rated) capacitor banks at Killdeer 345 kV substation and 2 x 84 MVAR capacitor banks at Hickory Creek 345 kV substation. | IA | GIP |  | ITC Midwest entered into a Multi-Party Facilities Construction Agreement (“MPFCA”) with MISO and the Interconnection Customers for MISO Projects J302, J476, J503, J512, J555, J569, J583, J587, J590, J611 and J614 for the construction of Network Upgrades at Killdeer 345 kV and Hickory Creek 345 kV. |  |  |  | 2022-07-01 | 345 | 345 | 16097861
MTEP21 | West | ITC Midwest | 20037 | Carbide-Viele 161kV Rebuild | ITC Midwest has entered into an agreement with Northeast Missouri Electric Cooperative to rebuild approximately 12.3 miles of the ITC Carbide – Viele 161 kV line to double circuit to allow Northeast to connect a new 161 kV line from their Franklin Substation in Lee County, Iowa to their Winchester Substation in Clarke County, Missouri. Per the terms of the agreement, Northeast will be responsible for design and construction for this project. ITC will contribute a fixed amount of $6,120,00 for the project as a credit for planned maintenance ITC needs to perform on this line. The ITC portion of the rebuild will be constructed with T2-795 ACSR conductor and OPGW. ITC will own the double circuit poles, conductor, insulators, and 1 OPGW static wire. | IA | Other | Load Growth | Customer requested interconnection. |  |  |  | 2024-12-31 | 161 | 161 | 6200000
MTEP21 | West | ITC Midwest | 20180 | ITCM Customer Interconnects with short lead time 2024 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL | Other | Load Growth | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. |  |  |  | 2024-12-31 | 345 | 69 | 2400000
MTEP21 | West | ITC Midwest | 21429 | Tiffin Crossroads Substation Interconnection | IPL will be building a new 69/25x12.5 kV substation named “Tiffin Crossroads” adjacent to the existing MidAmerican Tiffin Sub K substation. This new substation will replace the existing IPL Tiffin distribution substation and accommodate future area load growth. IPL will be installing one 12/20 MVA transformer initially but is planning the substation to accommodate a 2nd 12/20 MVA transformer in the future. For the ITC owned portion of Tiffin Crossroads, ITC will build a new 69 kV substation with two single boxes, two line breakers, and a bus tie breaker. As part of this, the existing Sub K Tiffin double circuit line tap will be reconfigured to two single circuits, to avoid having a double circuit line tap going into the distribution substation and avoid issues with planned outages on the double circuit requiring the distribution substation to be taken out of service. | IA | Other | Load Growth | Customer requested interconnection |  |  | 20 MVA | 2022-12-31 | 69 | 69 | 5132408
MTEP21 | West | ITC Midwest | 21625 | Keokuk Geode 69kV Substation Interconnection | IPL will be building a new 69/25x12.5 kV Substation named Keokuk Geode. The new Keokuk Geode Substation will replace the Messenger Substation and Commercial Substation. IPL will be installing one 69/24.9x12.5 kV 20/33MVA transformer initially but is planning the substation to accommodate a second 69/24.9x12.5 kV transformer when all the load is transferred from the Messenger Substation and Commercial Substation. | IA | Other | Load Growth | Interstate Power and Light Company (IPL) has requested to connect a new substation in Keokuk, IA. |  |  | 33 MVA | 2022-10-30 | 69 | 69 | 4764418
MTEP21 | West | MidAmerican Energy Company | 20685 | J535 Gard Ave. | J535 Network Upgrades and Interconnection Facilities | IA | GIP |  | New three-breaker, 345 kV ring bus substation off the Ida County-Lehigh 345 kV line with two line taps |  |  |  | 2020-04-01 | 345 | 0 | 12700000
MTEP21 | East | ITC Transmission | 18237 | 2023 ITCT Asset Replacement Program | Replace aging and outdated equipment at a pace that will insure each type of equipment is replaced near its projected end of life. | MI | Other | Age and Condition | This Asset Replacement Program will replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use of state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. The Asset Replacement program includes a variety of replacement programs for several types of equipment including but not limited to: • Circuit Breakers/switchers • Protective equipment (relays/control) • DC battery and charging systems • Surge Arresters • Instrument Transformers • Disconnect Switches • Wood poles • Miscellaneous line equipment (insulators, cross-arms, etc.) |  |  |  | 2023-12-31 | 345 | 120 | 34200000
MTEP21 | East | ITC Transmission | 19185 | Red Run & Bismarck Line Breakers | The proposed solution is to install two 230 kV Line breakers, one at Red Run position “HW” and one at Bismarck position “HC" on the Red Run – Bismarck line. | MI | Other | Reliability | The Red Run - Bismarck line has a line terminated transformer at Red Run and Bismarck, meaning that primary protection for Red Run T201 protection is dependent on remote clearing at Bismarck through transfer tripping. Similarly, Bismarck T303 protection is dependent on remote clearing of Red Run through transfer tripping. By installing a 230kV line breaker Red Run “HW” and Bismarck “HC” positions, we can provide local tripping for transformer faults. • Relaying - Adds local tripping for the Red Run 230/120 kV Transformer 201 and Bismarck Transformer 303 resulting in: ¿ 25% faster fault clearing. ¿ Increased reliability of transformer protection as primary fault clearing does not rely on power line carrier scheme to trip the remote end breaker. - This improved reliability and reduced fault clearing times can help avoid catastrophic damage for very expensive equipment that have long lead time replacement. • Operations ¿ The installation of the breaker at Red Run would also serve a proper means of dropping line charging current. Without a line breaker at Bismarck the 345kV breakers need to be opened to operate the line. This reduces system reliability by unnecessarily opening the ring bus. • Equipment ¿ There are currently 3 disconnect switches at Red Run that need replacement. Installation of the breaker will eliminate the need to replace 2 of them. ¿ Adding a line breaker at both terminals will make the transformer part of the system. This naturally eliminates any delayed current zero (DCZ) issues. This has the potential of causing the existing breakers to fail when opening a line with an energized transformer. |  |  |  | 2023-12-31 | 230 | 0 | 2700000
MTEP21 | East | ITC Transmission | 19266 | J799 Interconnection | Construct the J799 Interconnection 120kV station as a three breaker ring bus station. The Milan - Pioneer 120kV line will be extended to loop in the J799 Interconnection station for transmission service. Changes will require relaying upgrades at Milan 120kV | MI | GIP |  | J799 is a 189MW solar generator in the 2017-AUG DPP Cycle. The station is needed to connect J799 to the requested Milan - Pioneer 120kV POI. |  |  |  | 2022-03-31 | 120 | 0 | 7520000
MTEP21 | East | ITC Transmission | 19405 | J833 Interconnection | Construct J833 Interconnection station as a breaker and half station with three 40kA breakers in a ring bus configuration. Extend the Milan - Pioneer 120kV line 0.1 miles to loop in J833. | MI | GIP |  | J833 is a 50MW solar plant in the Aug-2017-DPP study cycle. The station is needed to connect the generator. The changes will require updates at Pioneer 120kV to accommodate the new interconnection. |  |  |  | 2022-04-29 | 120 | 0 | 10290000
MTEP21 | East | ITC Transmission | 19508 | Bauer - Pontiac 345kV Sag Remediation & Station Equipment Upgrade (J701, J794, J796, J832) | Sag remediation requires replacing sixteen (16) 345kV double circuit structures. The terminal equipment upgrade requires replacing four disconnect switches at Pontiac 345kV. | MI | GIP |  | Mitigate thermal violations caused by the J701, J794, J796, and J832 interconnection customers in the August 2017 MISO DPP Phase 3 study. To mitigate the thermal violations ITCT will perform sag remediation on the Bauer - Pontiac 345kV lines as well as replace terminal equipment at Pontiac 345kV. |  |  |  | 2021-12-31 | 345 | 0 | 8209000
MTEP21 | East | ITC Transmission | 19509 | Thetford - Jewell Sag Remediation and Reconductor (J701, J794, J796,J832) | Reconductor approximately 0.1 miles of the Thetford – Jewell 345kV circuit with a conductor rated at least that of 2-945 ACSR. Remediate the sag on the Thetford - Jewell 345kV circuit to achieve a minimum rating of minimum summer emergency circuit rating of 1556 MVA. | MI | GIP |  | Thetford - Jewell is projected to overload due to increase in generation in the area. DPP cycle August 2017 determined generators J701, J794, J796, and J832 contribute to the projected overload. |  |  |  | 2021-12-31 | 345 | 0 | 5662000
MTEP21 | East | ITC Transmission | 19585 | Placid - Pontiac 345kV Sag Remediation (J701,J793,J794,J796,J832) | The scope of this network upgrade involves sag remediation on the Placid - Pontiac 345kV circuit. The sag remediation requires replacing nine 345kV double circuit structures. | MI | GIP |  | The scope of this network upgrade is to mitigate thermal violations caused by the J701, J793, J794, J796, J832, and J839 interconnection customers in the August 2017 MISO DPP Phase 3 study. To mitigate the thermal violations ITCT will raise the sag limit on the Placid - Pontiac 345kV line |  |  |  | 2021-12-31 | 345 | 0 | 2956000
MTEP21 | East | ITC Transmission | 19586 | Pontiac - Wixom 345kV Sag Remediation & Station Equipment Upgrade (J701,J793,J794,J796,J832) | The scope of this network upgrade involves sag remediation on the Pontiac - Wixom 345kV circuit as well as upgrading terminal equipment at Pontiac 345kV & Wixom 345kV. | MI | GIP |  | The scope of this network upgrade is to mitigate thermal violations caused by the J701, J793, J794, J796, J832, and J839 interconnection customers in the August 2017 MISO DPP Phase 3 study. To mitigate the thermal violations ITCT will raise the sag Pontiac - Wixom 345kV line |  |  |  | 2021-12-31 | 345 | 0 | 2482000
MTEP21 | East | ITC Transmission | 19992 | ITCT Pole Top Switch Additions/Replacement Program 2022 | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. | MI | Other | Reliability | Without pole top switches in place, planned or unplanned outages to a transmission line will cause long outages to customers. |  |  |  | 2022-12-31 | 120 | 0 | 1000000
MTEP21 | East | ITC Transmission | 20036 | Sebewaing 345kV_Installation | Construct New Sebewaing station as a 345kV - 120kV station with three 345kV 40kA breakers and one 120kV 40kA breaker. Install a 345/120kV transformer. Install 4.5 miles of 954 ACSR in new right of way to connect Sebewaing to New ITC Station 120kV at position HQ. Extend the Bauer - Grassmere 345kV line by adding 0.2 miles of 954 ACSR to loop in New ITC Station 345kV for transmission service. | MI | Other | Load Growth | The city of Sebewaing in anticipating a load increase and is seeking to move up to 10MW to the new interconnection. |  |  | 10 | 2024-06-01 | 345 | 120 | 32544000
MTEP21 | East | ITC Transmission | 20044 | ITCT Customer Interconnections - Year 2024 | Customer interconnection requests and retirements less than $1 million with in service date in year 2024. | MI | Other | Load Growth | Customer Requests are often in need of interconnection on an expedited basis. This blanket allows interconnection requests of smaller nature to be quickly studied and connected by ITC. |  |  |  | 2024-12-31 | 120 | 0 | 2000000
MTEP21 | East | ITC Transmission | 20107 | Atlanta-Karn-Thetford Split & Station Reconfiguration (ITCT) | Install a 120 kV, 3000 Amp, 40 kA section breaker and expand 138 kV into a ring bus configuration Add two 138 kV breakers to configure the 138 kV into a ring bus. Add 0.75 miles of 1431 ACSR to complete the Atlanta – Thetford circuit. New equipment should be rated for 3000 Amps or higher. | MI | Other | Reliability | Atlanta station is presently configured such that routine NERC required periodic maintenance on some protection systems require the entire station be deenergized for the work to be performed safely. In order to maintain transmission service to the single distribution transformer, a temporary line needs to be constructed to bypass the deenergized Atlanta station. This project will reconfigure the station similar to other ITC stations such that periodic maintenance and other normal work activities can be performed without extensive temporary construction. Adding the section breaker also allows installation of SSVTs to the 120kV buses for station service, allowing for ITC to relocate the backup generator system presently installed. The Atlanta, Karn, and Thetford 138kV line facilities are relayed together; meaning a fault on any one element trips all three and interrupts network transmission flows on the remaining connected elements. The three lines are connect together very near Atlanta station so by bringing the lines the short distance in and out of Atlanta station, we can relay the Karn and Thetford lines individually, which improves system protection as follows: • Less sensitive protection settings on 2-terminal lines, resulting in: ¿ Eliminate risk of overtripping caused by ground miscoordination. ¿ Faster backup clearing times without risk of miscoordination. ¿ Eliminate risk of miscoordination caused by terminals open or with limited infeed. ¿ No concerns with sequential clearing. • The line relaying is newer and will be re-utilized for this 2-terminal line applications with modifications to reduce their complexity to match ITC’s standards: ¿ Increased reliability by reducing risk for human error during operations and maintenance of the schemes. • These 2-terminal lines can utilize double-ended fault locating methods, resulting in the following benefits: ¿ Increased likelihood of locating faults. ¿ Reduce patrol and tower climbing to locate faults. |  |  |  | 2024-12-31 | 138 | 120 | 5400000
MTEP21 | East | ITC Transmission | 20132 | Pontiac 303 Transformer Replacement | Replace the Pontiac #303 345/120 kV transformer with at least 750 MVA summer emergency rated transformer. | MI | Other | Age and Condition | The Pontiac #303 345/120kV transformer is reaching end of life. This transformer is a 1968 General Electric unit that is leaking oil. Electrical testing in 2006 also discovered deteriorated bushings. |  |  |  | 2025-12-31 | 345 | 120 | 4800000
MTEP21 | East | ITC Transmission | 20133 | Hines 201 Transformer Replacement | Replace the Hines #201 230/120kV transformer. The anticipated replacement is the ITCT-standard 230/120kV 560MVA transformer. | MI | Other | Age and Condition | The Hines #201 230/120kV transformer is reaching end of life. This transformer is a 1974 General Electric unit that is leaking oil. |  |  |  | 2025-12-31 | 230 | 120 | 4800000
MTEP21 | East | ITC Transmission | 20138 | Milan 303 Transformer Replacement | Replace the Milan #303 345/120 kV transformer with at least 750 MVA (3608 Amps) summer emergency rated transformer. | MI | Other | Age and Condition | The Milan #303 345/120kV transformer is reaching end of life. This transformer is a 1972 Cogenel unit that was refurbished in 1990. It is leaking oil and was internally producing gasses for a period of time in 2017. |  |  |  | 2023-12-31 | 345 | 120 | 4800000
MTEP21 | East | ITC Transmission | 20140 | Pontiac 301 Transformer Replacement | Replace the Pontiac #301 345/120kV transformer. The anticipated replacement is the ITCT-standard 345/120kV 560MVA transformer. | MI | Other | Age and Condition | The Pontiac #301 345/120kV transformer is reaching end of life. This transformer is a 1968 General Electric unit that is leaking oil. |  |  |  | 2023-12-31 | 345 | 120 | 4800000
MTEP21 | East | ITC Transmission | 20167 | Cato – Corktown 120 kV | Build approximately 0.85 miles of 120kV 1600mm² underground cable from Cato to Corktown and expand the Cato and Corktown stations to accommodate a third line termination. | MI | Other | Reliability | Multiple 120 kV underground lines in the Cato and Corktown area with adjacent hazard concerns, involving the need to shutdown lines that are adjacent to other circuits requiring maintenance. This causes the need to deenergize multiple lines in the area leaving one feed at the Cato and Corktown 120 kV stations. |  |  |  | 2024-12-31 | 120 | 0 | 40000000
MTEP21 | East | ITC Transmission | 20325 | Custer-Monroe Line Relocation | Relocate approximately 1.8 miles of 120kV circuit at the request of the city of Monroe. | MI | Other | Other Local Needs | The relocation is required as part of Monroe's upgrades to the River Raisin National Battlefield. |  |  |  | 2022-12-31 | 120 | 0 | 8800000
MTEP21 | East | ITC Transmission | 20845 | Apache-Seneca 120kV Relocation | Relocate 9 structures of the Apache-Seneca 120kV circuit along Rochester Road in the city of Troy | MI | Other | Other Local Needs | The city of Troy has directed ITCT to relocate approximately 9 120kV structures along Rochester Road by 12/31/2023. The city has a planned road construction project in which the current structure interfere. |  |  |  | 2023-12-31 | 120 | 0 | 2040000
MTEP21 | East | ITC Transmission | 21026 | Montcalm Equipment Removal and Bypass | Permanently bypass the Montcalm station and remove all ITCT assets. | MI | Other | Other Local Needs | DTE no longer has any load at the site, and the generation was retired in 2016. |  |  |  | 2022-12-31 | 120 | 0 | 1640000
MTEP21 | East | ITC Transmission | 21047 | Waterman 120kV Reactor HX Replacement | Replace Waterman 120kV series reactor HX with a new series reactor | MI | Other | Age and Condition | This reactor has reached it's end of life |  |  |  | 2023-12-31 | 120 | 0 | 900000
MTEP21 | East | ITC Transmission | 21105 | Apollo Interconnection | Construct a new in-and-out station consisting of a single tie breaker and three straight buses with room for future tie breaker. Install one 120 kV tie breaker, two 120 kV line breakers, buswork, and associated disconnects. Connect two customer owned transformers to the new station. | MI | Other | Load Growth | DTE has requested a new 120 kV interconnection on the ITCT Hunters Creek-Lapeer 120kV circuit. The interconnection request is to feed two DTE transformers, and a future third transformer. |  |  |  | 2023-05-28 | 120 | 0 | 17147252
MTEP21 | East | ITC Transmission | 21170 | Lenox-Stephens- Henry Ford MH - Shrine | Henry Ford Macomb Hospital is a DTE interconnection request. ITCT will construct Shrine as a straight bus station with two line breakers and a section breaker. ITCT will extend the Lenox-Stephens 120kV line by adding about 1 mile of 954 DCT to loop in the new station. Fiber will be run from Bismarck 120kV station requiring fiber patches at Bismarck, Jewell, and Sigma 120kV station. Interconnection will require relaying upgrades at Lenox and Stephens. | MI | Other | Load Growth | DTE interconnection for Henry Ford Macomb Hospital. Hospital is expanding, projecting an increase of 2.7 MW of load. Station will serve new load, in addition 3.7 MW of load will be transferred to Shrine from existing DTE distribution stations. |  |  | 7 | 2023-06-01 | 345 | 0 | 14563912
MTEP21 | East | ITC Transmission | 21206 | Coventry to Hager 120 kV Projects | Rebuild approximately 1 mile from Duvall tap to Hager utilizing 954 ACSR conductor on standard double circuit steel pole 120 kV structures. Disconnect the 954 ACSR conductor running north from the Baltic Tap and connect it to the 1431 ACSR conductor on the north side of the structures heading toward Coventry 120 kV. Remediate sag from Coventry to the Nitro cut-in to a target rating of 269 MVA SE. Install 3000 A 40 kA 120kV section breaker at Duvall 120 kV and all associated standard 3000 A 40 kA line breakers at Coventry and Hager 120 kV stations | MI | BRP |  | The Sunset – Hager 120kV line is projected to overload for P6 contingencies. |  |  |  | 2023-12-31 | 120 | 0 | 10955000
MTEP21 | East | ITC Transmission | 21626 | Superior DC Control Relocation | Install a new control building that will be large enough to eventually relocate all the ITCT relaying and controls into it. The new control building will include a dedicated ITCT AC and DC systems large enough to power all ITCTs assets at the substation. All ITCT assets will be cut over to the new dedicated AC/DC system as part of this project. | MI | Other | Reliability | The existing Superior control building has maintenance, safety, and human performance concerns due to DC reliability issues and the buildings space constraints. The existing DC system feeding the relaying at the station is owned by a third party and has multiple grounds on it. These grounds have caused multiple relay failures during fault events in the vicinity of the station. The older relaying and controls require high operations and maintenance expenses due to their age. The protection panels being dispersed on multiple houses of the creates human performance issues. Additionally, lack of available panel space creates difficulty replacing relaying without extended shutdowns or adding a new dedicated DC system within an existing control house. |  |  |  | 2022-12-31 | 120 | 0 | 2000000
MTEP21 | West | Montana-Dakota Utilities Company | 19205 | Tioga Loop | Build a 60 kV loop line around Tioga, ND | ND | Other | Load Growth | Load growth |  |  |  | 2021-12-31 | 60 | 0 | 1480722
MTEP21 | West | Montana-Dakota Utilities Company | 19605 | Beulah 115/46 kV substation | Replacement of the existing Beulah 115/46 kV substation. | ND | Other | Age and Condition | Age & condition of existing Beulah 115 and 46 kV bus and equipment. Improve reliability and operations by replacing old main and transfer bus with a ring bus and replacing old breakers and relays. |  |  |  | 2022-06-30 | 115 | 46 | 6000000
MTEP21 | West | MidAmerican Energy Company | 2938 | Uprate Sub 39 - Cordova 345 kV Line | Change out a limited number of existing 345 kV line structures to increase rating. | IL | BRP |  | Address Category P6 post-contingent overloads identified in MTEP20 study. |  |  |  | 2022-06-01 | 345 | 0 | 500000
MTEP21 | West | MidAmerican Energy Company | 4247 | Sub 18 - Sub 85 161 KV reconductor | Reconductor the 161 kV line from Sub 85 to Sub 18 and uprate substation terminal equipment | IA,IL | Other | Other Local Needs | Address congestion observed in MISO real-time operations |  |  |  | 2022-12-31 | 161 | 0 | 1600000
MTEP21 | West | MidAmerican Energy Company | 18885 | Clarinda to Braddyville 161 kV Line Rebuild | The project will consist of rebuilding the Clarinda-Braddyville 161 kV line and adding OPGW to improve relaying communication and reduce the potential for misoperations. The line is approximately 12.3 miles. | IA | Other | Age and Condition | The Clarinda to Iowa/Missouri state border 161 kV line is one of the oldest 161 kV lines in MidAmerican Energy territory. The wood H-frame line is presently a tie-line with KCPL. KCPL owns the line from Iowa/Missouri state border to Maryville substation in Missouri. The line will be rebuild and OPGW will be added due to its age and condition compared to the rest of the fleet. |  |  |  | 2020-10-01 | 161 | 0 | 6750000
MTEP21 | West | MidAmerican Energy Company | 18890 | Clarksville-Donald Feldman 69 kV Line | Construct a new 69 kV line between MidAmerican's Clarksville East Substation and Corn Belt Power Cooperative's Donald Feldman Switching Station. | IA | Other | Reliability | Convert MidAmerican’s Clarksville East-Shell Rock 34.5 kV line to 69 kV. Also, Corn Belt is constructing a new switching station northwest of Shell Rock, Donald Feldman Switching Station; Corn Belt is experiencing rapid load growth in the area. With the additional load, Corn Belt’s 69 kV system needs voltage support during contingencies. Corn Belt has obtained approval from SPP for a 69 kV interconnection between the new Donald Feldman Switching Station and MidAmerican’s Clarksville East Substation. MidAmerican’s Clarksville East-Shell Rock 34.5 kV line is in the vicinity of the new switching station. MidAmerican is pursuing options for a MidAmerican 69 kV line between Clarksville East Substation and the new Donald Feldman Switching Station. |  |  |  | 2020-12-31 | 69 | 0 | 5389340
MTEP21 | West | MidAmerican Energy Company | 18891 | Plymouth Substation 161 kV Switches and Jumpers Replacement | Replace seven 161 kV switches and remove one 161 kV switch at Plymouth Substation. Also, replace the jumpers associated with the switches. | IA | Other | Age and Condition | Plymouth 161 kV Switches 9460A, 9440B, 9440L, 9610B, 9610L, 9470B, and 9470L are being replaced due to condition. Also, Switch 9460C is being removed and replaced with bus. When the switches are replaced, the jumpers will also be replaced. |  |  |  | 2020-11-01 | 161 | 0 | 350000
MTEP21 | West | MidAmerican Energy Company | 19745 | 100th & 54th Avenue: Replace 161 kV Breaker 803 | Replace the 161 kV breaker 803 at 100th & 54th Avenue Substation with a breaker that has interrupting rating of 40 kA. | IA | Other | Reliability | A circuit breaker with a higher fault current interrupting capability will be needed when the second Booneville 345-161 kV transformer is added. |  |  |  | 2022-06-01 | 161 | 0 | 250000
MTEP21 | West | MidAmerican Energy Company | 19994 | Marcus East to Hospers 69 kV Line and Rebuild Marcus East Substation | Construct a new 69 kV line from Hospers-Marcus East, construct new 69 kV line terminal at Hospers Substation, rebuild Marcus East Substation to install 69 kV breakers and a 69 kV capacitor bank | IA | Other | Load Growth | Serves new customer load, resolves low voltage that could occur following contingencies by providing a second source into Marcus East Substation |  |  |  | 2022-12-01 | 69 | 0 | 25400000
MTEP21 | West | MidAmerican Energy Company | 19997 | Circuit Breaker Additions and Replacements 2022-2024 | Blanket project to add new 345 kV and 161 kV circuit breakers and replace existing 345 kV, 161 kV and 69 kV circuit breakers to increase reliability and operating flexibility. | IL | Other | Reliability | Three-year "blanket project" to add new 345 kV and 161 kV circuit breakers and replace existing 345 kV, 161 kV and 69 kV circuit breakers at several existing substations to increase system reliability and operating flexibility. The circuit breaker additions will eliminate existing operating issues such as three-terminal lines. Circuit breakers with operational or failure risk issues such as gassing will be replaced. Specific project locations and scope of work to be determined on an ongoing basis as determined by need. |  |  |  | 2021-12-31 | 345 | 0 | 17725000
MTEP21 | West | MidAmerican Energy Company | 19998 | NW 2nd Street Substation | Construct a new 69 kV substation and associated 69 kV line work. | IA | Other | Load Growth | Serve new customer load and provide for substation expansion |  |  |  | 2022-12-01 | 69 | 0 | 10000000
MTEP21 | West | MidAmerican Energy Company | 19999 | Booneville: Second 345-161 kV Xfmr | Add a second 345-161 kV xfmr. Expand 345 kV and 161 kV buses. | IA | BRP |  | Load growth in West Des Moines area increasing demand on Booneville 345-161 kV autotransformer after P6 N-1-1 contingencies | Area Load Growth (BRP) |  |  | 2023-06-01 | 345 | 161 | 16700000 | BRP driven by West Des Moines load growth; NERC P6/P23
MTEP21 | West | MidAmerican Energy Company | 20000 | Bondurant Substation: Add 345-161 Xfmr | Add a 345-161 kV xfmr. | IA | BRP |  | Mitigate thermal overloads for Category P6 N-1-1 contingencies observed in MTEP20 summer peak models | Area Load Growth (BRP) |  |  | 2024-12-01 | 345 | 161 | 11900000 | BRP driven by Altoona load growth; NERC P6
MTEP21 | West | MidAmerican Energy Company | 20002 | Waukee: Add 69 kV Capacitor Bank | Install 69 kV capacitor bank and 69 kV breakers | IA | Other | Reliability | Increase reliability and allow for additional customer load. |  |  |  | 2023-12-01 | 69 | 0 | 1600000
MTEP21 | West | MidAmerican Energy Company | 20003 | Highway 6 161/13.2 kV Substation | Construct a new 161 kV substation and associated 161 kV line work. New substation will have 161 kV connections to Grimes & South Waukee substations from line taps on future 161 kV lines | IA | Other | Load Growth | Serve new customer load |  |  |  | 2024-12-01 | 161 | 13.2 | 6000000
MTEP21 | West | MidAmerican Energy Company | 20006 | DPS 161 kV Strain Bus Uprate | Uprate strain bus at the Metro East 161 kV line terminal at DPS Substation | IA | BRP |  | Mitigates thermal overload in near term summer peak model following P6 N-1-1 contingency event. | Area Load Growth (BRP) |  |  | 2022-06-01 | 161 | 0 | 300000 | BRP driven by Altoona load growth; NERC P6
MTEP21 | West | MidAmerican Energy Company | 20007 | Clarion: Add 69 kV Breakers | Presently, Clarion Substation is tapped off the Hampton West--Eagle Grove 69 kV line. Reconfigure the 69 kV lines into Clarion Substation from a single tapped arrangement to an in and out breakered configuration, similar to Goldfield Substation. Build new 69 kV bus on MEC owned property adjacent to existing substation footprint. Install 69 kV circuit switcher between 69 kV bus and existing 69-13 kV transformer. Construct new 69 kV bus to accommodate a future 69 kV bus tie breaker, a future 69 kV circuit switcher, and a future second 69-13 kV transformer. | IA | Other | Reliability | Condition, increase reliability, and serve future load |  |  |  | 2022-03-01 | 69 | 0 | 375000
MTEP21 | West | MidAmerican Energy Company | 20008 | Hampton West –Latimer 69 kV Line Uprate | Replacing line structures to obtain maximum conductor rating | IA | Other | Load Growth | Increases line rating to accommodate new customer load |  |  |  | 2021-06-01 | 69 | 0 | 925000
MTEP21 | West | MidAmerican Energy Company | 20010 | Substation 73: 69 kV Line Taps | 69 kV line tap work to support converting Sub 73 from a tapped substation to an in-and-out substation with 69 kV line circuit breakers. | IA | Other | Reliability | Reliability improvement |  |  |  | 2021-12-31 | 69 | 0 | 500000
MTEP21 | West | MidAmerican Energy Company | 20011 | Sub 84: 69 kV Line Taps and Line Upgrades | 69 kV line tap work to support converting Sub 84 from a tapped substation to an in-and-out substation with 69 kV line circuit breakers. Install OPGW from Valley Drive to Sub 84 to Sub 55 for communications and replace structures and conductor on sections of line subject to galloping. | IA | Other | Reliability | Reliability improvement |  |  |  | 2023-06-01 | 69 | 0 | 5400000
MTEP21 | West | MidAmerican Energy Company | 20012 | Sub 17: Add 161-13.2 kV Transformer | Add 161 kV line circuit breaker at Sub 17 on the Sub 28 line terminal to support the addition of a new 161-13.2 kV transformer. | IA | Other | Load Growth | Serve expanding customer load |  |  |  | 2023-06-01 | 161 | 0 | 1000000
MTEP21 | West | MidAmerican Energy Company | 20013 | Sub 113: 161-69 kV Substation | Add a new 161-69 kV substation bisecting the Oak Grove-Mercer 161 kV line and Sub 108-Sub 111 69 kV line. | IL | Other | Reliability | Provide a third source to MidAmerican's Sherrard area 69 kV distribution system |  |  |  | 2022-12-31 | 161 | 69 | 5000000
MTEP21 | West | MidAmerican Energy Company | 20038 | Sub 56 - Sub 85 161 kV Line Uprate | Replace substation terminal equipment at Sub 56 to uprate the Sub 56-Sub 85 161 kV line | IA | Other | Other Local Needs | Address congestion observed in MISO real-time operations |  |  |  | 2022-12-31 | 161 | 0 | 900000
MTEP21 | West | MidAmerican Energy Company | 20121 | Hills 345 kV: Add Two 150 MVAR Capacitors | Expand the Hills 345 kV substation yard from a ring bus to a breaker-and-a-half configuration. Add two 150 MVAR, 345 kV capacitor banks. | IA | GIP |  | MISO DPP 2016 August West Network Upgrade. |  |  |  | 2022-12-31 | 345 | 0 | 12000000
MTEP21 | West | MidAmerican Energy Company | 20123 | Grimes 345 kV Breaker Addition | Add a new 345 kV breaker to the Grimes 345 kV ring bus to eliminate a NERC TPL-001 Category P2 breaker failure contingency | IA | GIP |  | MISO DPP 2016 August West Network Upgrade |  |  |  | 2021-12-31 | 345 | 0 | 1300000
MTEP21 | West | MidAmerican Energy Company | 20125 | Deep River to Parnell 161 kV Uprate | Replace structures to uprate the rating of the J438 POI Deep River-Parnell 161 kV line | IA | GIP |  | MISO DPP 2016 August West Network Upgrade |  |  |  | 2020-12-31 | 161 | 0 | 225000
MTEP21 | West | MidAmerican Energy Company | 20126 | Braddyville-MO State Line 161 kV Uprate | Reconductor the 161 kV line between the J611 POI Braddyville substation and the Iowa-Missouri border. | IA | GIP |  | MISO DPP 2016 August West Network Upgrade |  |  |  | 2020-10-01 | 161 | 0 | 500000
MTEP21 | West | MidAmerican Energy Company | 20127 | Macksburg-Winterset 161 kV Uprate | Replace structures to uprate the rating of the Macksburg-Winterset 161 kV line | IA | GIP |  | MISO DPP 2016 August West Network Upgrade |  |  |  | 2020-08-05 | 161 | 0 | 120000
MTEP21 | West | MidAmerican Energy Company | 20128 | Montezuma-Diamond Trail 345 kV Uprate | Replace structures to uprate the rating of the Montezuma-J530 POI Diamond Trail 345 kV line | IA | GIP |  | MISO DPP 2016 August West Network Upgrade |  |  |  | 2020-06-01 | 345 | 0 | 250000
MTEP21 | West | MidAmerican Energy Company | 20129 | Diamond Trail-Hills 345 kV Uprate (MISO DPP 2016 Aug.) | Reconductor the J530 POI Diamond Trail-Hills 345 kV Line and uprate Hills substation terminal equipment. | IA | GIP |  | MISO DPP 2016 August West Network Upgrade |  |  |  | 2021-12-31 | 345 | 0 | 27800000
MTEP21 | West | MidAmerican Energy Company | 20130 | Bondurant-Montezuma 345 kV Uprate (MISO DPP 2016 Aug.) | Replace structures to uprate the rating of the Bondurant-Montezuma 345 kV Line | IA | GIP |  | MISO DPP 2016 August West Network Upgrade |  |  |  | 2021-12-31 | 345 | 0 | 620000
MTEP21 | West | MidAmerican Energy Company | 20153 | 69 kV Line Rebuilds Blanket 2021 - 2024 | Blanket project to rebuild 69 kV lines due to condition and to improve reliability and operational flexibility. | IA | Other | Age and Condition | Three-year "blanket project" to rebuild existing 69 kV lines due to condition. Specific project locations and scope of work to be determined on an ongoing basis as determined by need. |  |  |  | 2021-12-31 | 69 | 0 | 27700000
MTEP21 | West | MidAmerican Energy Company | 20154 | 69 kV Substation Line Tap Blanket 2021-2024 | Blanket project to add new 69 kV line taps into new or existing substations to serve new distribution substations or to increase reliability. | IL | Other | Load Growth | Three-year "blanket project" to install 69 kV line taps into several new or existing substations to serve customer loads and/or increase system reliability. Specific project locations and scope of work to be determined on an ongoing basis as determined by need. |  |  |  | 2021-12-31 | 69 | 0 | 5150000
MTEP21 | West | MidAmerican Energy Company | 20155 | Relaying, Communication and Control Equipment Replacements 2021-2024 | Blanket project to replace existing relaying, communication equipment and control house equipment to increase reliability and operating flexibility. | IL | Other | Other Local Needs | Three-year "blanket project" to replace existing relaying, communication equipment and control house equipment at several existing substations to increase system reliability and operating flexibility. Specific project locations and scope of work to be determined on an ongoing basis as determined by need. |  |  |  | 2021-12-31 | 345 | 69 | 38999000
MTEP21 | West | MidAmerican Energy Company | 20171 | Red Oak-Emerson 69 kV Structure Replacements | Replace structure to obtain the maximum conductor rating at 212F. | IA | Other | Reliability | Reliability improvement |  |  |  | 2022-04-01 | 69 | 0 | 200000
MTEP21 | West | MidAmerican Energy Company | 20172 | Percival– Hamburg 69 kV Structure Replacements | Replace structure to obtain the maximum conductor rating at 212F. | IA | Other | Reliability | Reliability improvement |  |  |  | 2021-12-31 | 69 | 0 | 60000
MTEP21 | West | MidAmerican Energy Company | 20173 | Quick-Sub 701 161 kV Line and Line Terminals | Construct a new Quick-Sub 701 161 kV line and line terminals.at Quick and Sub 701. | IA | Other | Reliability | Reliability improvement. Serves existing and expanding customer loads. Provides an additional 161 kV line into the Council Bluffs area. Increases reliability. |  |  |  | 2023-06-01 | 161 | 0 | 17000000 | MEC West Region; local reliability with load growth component
MTEP21 | West | MidAmerican Energy Company | 20175 | Remsen Township Substation & Line Taps | Construct a new substation and 345 kV line taps to accommodate wind farm interconnection (J748) | IA | GIP |  | MISO DPP 2017 February Network Upgrade |  |  |  | 2021-09-15 | 345 | 0 | 13200000
MTEP21 | West | MidAmerican Energy Company | 20176 | Hitchcock 69-13.2 kV Substation | Construct a new 69-13.2 kV distribution substation and associated 69 kV line work | IA | Other | Reliability | Reliability improvement. This project will allow to retire the existing Honey Creek Substation after being affected by flooding in the area. |  |  |  | 2022-06-01 | 69 | 0 | 3600000
MTEP21 | West | MidAmerican Energy Company | 20177 | Missouri Valley East 69-13.2 kV Substation | Construct a new 69-13.2 kV distribution substation and associated 69 kV line work | IA | Other | Reliability | Reliability improvement |  |  |  | 2023-06-01 | 69 | 0 | 800000
MTEP21 | West | MidAmerican Energy Company | 20178 | Webster 161 kV Expansion | Expansion of Webster 161 kV to accommodate J524 | IA | GIP |  | MISO DPP 2016 February West Network Upgrade |  |  |  | 2021-12-01 | 161 | 0 | 3050000
MTEP21 | West | MidAmerican Energy Company | 20189 | Washburn: 161 kV Bus A Improvement | Washburn Bus A: Same upgrades needed on Bus A as are being completed on Bus B under T91PK. The 161 kV circuit switcher on 161-69 kV transformer does not interrupt faults | IA | Other | Reliability | Improve reliability |  |  |  | 2021-06-01 | 161 | 0 | 1002400
MTEP21 | West | MidAmerican Energy Company | 20192 | Rock Valley: Replace 69 kV Breakers & Relays | Replace two 69 kV oil circuit breakers and electromechanical line and bus relaying at Rock Valley Substation | IA | Other | Age and Condition | Replace due to condition and operational issues |  |  |  | 2021-12-31 | 69 | 0 | 1100000
MTEP21 | West | MidAmerican Energy Company | 20626 | Se Soteria Substation & 161 kV Line Taps | New 161 kV distribution substation and associated 161 kV line reconfiguration and construction. | IA | Other | Load Growth | Distribution substation is needed to serve new, large customer load |  |  |  | 2022-02-04 | 161 | 13.2 | 25300000
MTEP21 | West | MidAmerican Energy Company | 20627 | Johnson Creek Substation & 161 kV Line Taps | New 161 kV distribution substation and associated 161 kV line reconfiguration and construction. | IA | Other | Load Growth | Distribution substation is needed to serve new, large customer load |  |  |  | 2022-01-01 | 161 | 13.2 | 25300000
MTEP21 | West | MidAmerican Energy Company | 21265 | Sub A Riverside 69 kV Upgrades | Replace 69 kV breakers and protective relaying. Also replace 161-69 kV Transformer Bank 8T1 and 8T2 with a new 161-69 kV, 125 MVA transformer. | IA | Other | Age and Condition | MidAmerican plans to install new 69 kV protection and control equipment in this new control house in 2022 to replace the older equipment located in the existing Sub A 69 kV control house. MidAmerican also plans to replace multiple old oil circuit breakers in the Sub A 69 kV yard as part of this project. Existing Sub A 161-69 kV transformers T1 (manufactured in 1947) and T2 (manufactured in 1961) are operated as a single transformer bank and presently utilize 480 VAC auxiliary power sourced from the Riverside Generating Station plant building. This 480 VAC source will no longer be available in 2022. Given the age of the transformers, replacement of transformers T1 and T2 with a single 161-69 kV, 125 MVA transformer similar to the existing Sub A transformer T6 is preferable to converting transformers T1 and T2 to operate on 120/240 VAC auxiliary power. |  |  |  | 2022-12-31 | 161 | 69 | 4100000
MTEP21 | West | MidAmerican Energy Company | 21266 | Plymouth 161-69 kV Transformer Replacement | Replace the 161/69 kV (150 MVA) transformer at Plymouth substation which failed recently. The replacement transformer will be a spare 161/69 kV 167 MVA with a load tap changer (LTC). Replace the 13 kV tertiary reactors. | IA | Other | Age and Condition | The Plymouth 161-69 kV Transformer AC (150 MVA unit) recently failed and is in the process of being replaced. The replacement transformer will be a spare 161-69 kV, 167 MVA unit with an load tap changer (LTC). Since the replacement transformer has an LTC, the two existing 13 kV reactors connected to the tertiary of the Plymouth transformer will be retired. The new transformer will be purchased to replenish the spare used at Plymouth substation. |  |  |  | 2021-08-31 | 161 | 13 | 3600000
MTEP21 | West | MidAmerican Energy Company | 21430 | Grimes 345/161 kV Transformer Replacement | Replace 345/161 kV (560 MVA) transformer at Grimes substation which failed recently. The replacement transformer will be a spare 345/161 kV 560 MVA transformer. Retire the 13.8 kV tertiary reactors of the transformer. | IA | Other | Age and Condition | The Grimes 345/161 kV transformer recently failed and is in the process of being replaced. The replacement transformer will be a spare 345/161 kV 560 MVA transformer. In addition, one of the 13.8 kV reactors on the tertiary of the failed transformer has a failed RL Switcher and the other 13.8 kV reactor has a failed phase. Given this failed reactor equipment on the tertiary and after reviews by our system control group and planning, we are not replacing the failed reactor equipment when we put the transformer in-service. The equipment will be retired/saved for spares as appropriate, likely later this year. |  |  |  | 2021-07-31 | 345 | 13.8 | 3850000
MTEP21 | West | MidAmerican Energy Company | 21545 | Diamond Trail to Hills 345 kV Line Structure Replacements | Diamond Trail-Hills 345 kV line structure replacements. | IA | Other | Age and Condition | Replace structures based on inspection and condition. |  |  |  | 2022-09-15 | 345 | 0 | 3750000
MTEP21 | East | METC | 17965 | J806 Generator Interconnection | Build a new 138 kV, 3 breaker ring switching station cut in from the METC Rice Creek - Vrooman 138kV circuit. | MI | GIP |  | J806 is a 149 MW Solar Power Plant that requested to interconnect to the METC Rice Creek - Vrooman 138 kV circuit in the DPP-2017-AUG cycle. |  |  |  | 2022-03-31 | 138 | 0 | 12228411
MTEP21 | East | METC | 18239 | 2023 METC Asset Replacement Program | Replace aging and outdated equipment at a pace that will insure each type of equipment is replaced near its projected end of life. | MI | Other | Age and Condition | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. The Asset Replacement program includes a variety of replacement programs for several types of equipment including but not limited to: • Circuit Breakers/switchers • Protective equipment (relays/control) • DC battery and charging systems • Surge Arresters • Instrument Transformers • Disconnect Switches • Wood poles • Miscellaneous line equipment (insulators, cross-arms, etc.) |  |  |  | 2023-12-31 | 345 | 138 | 36000000
MTEP21 | East | METC | 18404 | Nelson Rd - Install 22H9 Breaker | Install a breaker at position 22H9 along with associated disconnect switches to complete row 22 at Nelson Road. | MI | Other | Reliability | To improve system reliability and mitigate the loss of multiple generating sources into the station due to a breaker fault/failure at 24H9. |  |  |  | 2022-06-01 | 345 | 0 | 1530894
MTEP21 | East | METC | 19365 | J806/J857 Stability Mitigation | METC will extend the Marshall – Blackstone 138kV line to loop in J857 Interconnection station. Install two breakers at Stable (the J857 interconnection station) to accommodate the change. | MI | GIP |  | The J806 and J857 interconnections cause stability issues. |  |  |  | 2022-09-01 | 138 | 0 | 14960000
MTEP21 | East | METC | 19385 | J806/J857 Thermal Mitigation | METC will remediate the sag limit on the J806 POI – Denso Jackson 138kV line segment and rebuild approximately 2 miles of the J806 POI – Vrooman 138kV line segment. Replace existing 336 ACSR with 1431 ACSR. | MI | GIP |  | The J806 and J857 interconnections cause thermal overloads. |  |  |  | 2022-12-31 | 138 | 0 | 6308000
MTEP21 | East | METC | 19425 | Gleaner - Hackett - Laundra Sag Remediation | Raise the sag limits on the Gleaner - Hackett and Hackett - Laundra line segments of the Bullock - Saginaw River 138kV line. | MI | GIP |  | J794 increases the flow on the Gleaner - Hackett and Hackett - Laundra line segments of the Bullock - Saginaw 138kV line above the sag limit. |  |  |  | 2021-12-31 | 138 | 0 | 830000
MTEP21 | East | METC | 19445 | Stable - J857 Generator Interconnection | Construct the Stable 138kV as a ring bus station with three 40kA breakers. Loop in the Verona - Foundry 138kV line for transmission service. | MI | GIP |  | J857 is a 124.95 MW solar farm in Calhoun County, MI. |  |  |  | 2022-09-01 | 138 | 0 | 10853508
MTEP21 | East | METC | 19465 | ParrRd-J875-RaisnJ Sag Remediation | Remediate the sag on the Parr Road - J875 Interconnection station and the J875 - Raisin Tap line segment. | MI | GIP |  | J875 is a 150MW solar plant on in the August 2017 DPP study cycle. J875 Generator causes overloads on the line. |  |  |  | 2021-12-31 | 138 | 0 | 338400
MTEP21 | East | METC | 19506 | Riggsville-Livingston 138kV & Mcgulpin-Riggsville 138kV Dual-Pilot Relay Upgrade (J832) | Install dual pilot relaying on the Riggsville-Livingston 138kV & Mcgulpin-Riggsville lines. The installation of dual pilot relaying on these lines requires installing new relaying and wave traps at Mcgulpin, Riggsville, and Livingston as well as removing breaker bypass switches at Riggsville. | MI | GIP |  | This network upgrade is to improve adverse system stability caused by the J832 interconnection customer in the August 2017 MISO DPP Phase 3 study. |  |  |  | 2022-12-13 | 138 | 0 | 1487000
MTEP21 | East | METC | 19546 | J875 Generator Interconnection | Build a new 138 kV, 3 breaker ring switching station cut in from the METC Parr Road - Whiting 138 kV circuit. | MI | GIP |  | J875 is a 150 MW Solar Power Plant that requested to interconnect to the METC Parr Road - Whiting 138 kV circuit in the DPP-2017-AUG cycle. |  |  |  | 2022-11-18 | 138 | 0 | 36523949
MTEP21 | East | METC | 19606 | Thetford Station Eq Upgrade, Reconductor, and Sag (J701,J794,J796,J832) | Sag remediation and reconductoring on the Thetford - Jewell 345kV circuit, as well as upgrading station equipment at Thetford 345kV. The sag remediation requires replacing one (1) 345kV double circuit structure. The reconductor requires replacing approximately 325 feet of 2156 ACSR type conductor with 2-954 ACSR type conductor. The terminal equipment upgrade requires upgrading buswork and a line entrance at Thetford. | MI | GIP |  | Mitigate thermal violations caused by the J701, J794, J796, and J832 interconnection customers in the August 2017 MISO DPP Phase 3 study. To mitigate the thermal violations METC will perform sag remediation on the Thetford - Jewell 345kV line as reconductoring and station equipment upgrades. |  |  |  | 2021-12-31 | 345 | 0 | 849000
MTEP21 | East | METC | 19625 | Bauer - Pontiac 345kV Sag Remediation (J701,J794,J796,J832) | The scope of this network upgrade involves sag remediation on the Bauer - Pontiac 345kV circuit. The sag remediation requires replacing four (4) 345kV double circuit structures. | MI | GIP |  | The scope of this network upgrade is to mitigate thermal violations caused by the J701, J794, J796, and J832 interconnection customers in the August 2017 MISO DPP Phase 3 study. To mitigate the thermal violations METC will perform sag remediation on the Bauer - Pontiac 345kV line. |  |  |  | 2021-12-31 | 345 | 0 | 1879000
MTEP21 | East | METC | 19970 | Rebuild Alma - Vestaburg 138 kV 477 ACSR | Rebuild approximately 0.43 mile of the Alma - Vestaburg 138kV circuit using 954 ACSR on double circuit structures constructed at 138kV Standards with OPGW. Also replace terminal equipment at Alma. | MI | BRP |  | Alma - Vestaburg 138kV line is projected to be overloaded for base case and P1-P7 contingency scenarios during Ludington Pumping and light load conditions. . The identified overloaded equipment on this circuit is the conductor and terminal equipment at Alma. |  |  |  | 2024-12-31 | 138 | 0 | 2800000
MTEP21 | East | METC | 19985 | Murphy 138kV_J1194NU_Install Row12 | Construct Row 12 and install two 63kA breakers at Murphy 138kV. | MI | GIP |  | J1194 is a 224.2 MW wind project in Richland Township, Saginaw county, MI. Generator will connect at position BM12 at Murphy 138kV station. Project is studied in the 2019-DPP-Cycle 1 study cycle. |  |  |  | 2021-11-01 | 138 | 0 | 2000250
MTEP21 | East | METC | 19991 | METC Pole Top Switch Additions/Replacement Program 2022 | Install or replace an existing a new 138 kV, 2-way, full-load-break pole top switch at various tap points. | MI | Other | Reliability | Without pole top switches in place, planned or unplanned outages to a transmission line will cause long outages to customers. |  |  |  | 2022-12-31 | 138 | 0 | 2000000
MTEP21 | East | METC | 20018 | Rebuild Bullock - Shale 138 kV | Rebuild the Bullock to Structure 006A6682 (approximately 5 miles) utilizing 954 ACSR conductor with 230 kV double circuit structure standards with OPGW. Rebuild from Structure 006A6682 to the future Shale Substation (approximately 15 miles) utilizing 954 ACSR conductor with 138 kV double circuit structures standards with OPGW. Upgrade Terminal equipment at Bullock Substation 188 above overhead line conductor rating. | MI | BRP |  | Bullock to Shale 138 kV line is projected to be overloaded for categories P1, P2, P3, P6, and P7. The overloaded equipment identified on this circuit is the overhead conductor and terminal station equipment at Bullock. |  |  |  | 2025-06-01 | 138 | 0 | 33000000
MTEP21 | East | METC | 20033 | Sag Remediate Weadock - Carter Jct 138 kV | ITC is to remove the sag limit on the 336 ACSR and raise the sag limit on the 636 ACSR to 158F on the Carter - Weadock 138 kV Line. | MI | BRP |  | Carter to Weadock 138 kV line is projected to be overloaded for category P6 contingencies in the peak and shoulder peak cases. |  |  |  | 2025-06-01 | 138 | 0 | 888000
MTEP21 | East | METC | 20047 | METC Customer Interconnections - Year 2024 | Customer interconnection requests and retirements less than $1 million with in service dates in the year 2024. | MI | Other | Load Growth | Customer Requests are often in need of interconnection on an expedited basis. This blanket allows interconnection requests of smaller nature to be quickly studied and connected by METC. |  |  |  | 2024-12-31 | 138 | 0 | 2000000
MTEP21 | East | METC | 20049 | Rebuild and Sag Remediate Gallagher - Twining 138kV | The proposed solution is to Raise the sag limit on the 336 ACSR between Gallagher and Withey Lake Jct. and replace the 1/0 Copper on the Withey Lake Jct. - Twinning 138kV line with 477 ACSR utilizing standard 138 kV double circuit structures | MI | BRP |  | Gallagher to Twining 138 kV line is projected to be overloaded for category P6 contingencies in the light load and off-peak cases. |  |  |  | 2025-06-01 | 138 | 0 | 971000
MTEP21 | East | METC | 20053 | Warren 138 kV 188 Bus Upgrade | Upgrade Warren 188 terminal equipment to meet or exceed the rating of a 954 ACSR conductor. | MI | BRP |  | The Warren – Salt River 138 kV line is projected to be overloaded for category P2, P3, P6, and P7 contingencies in light load and several shoulder peak cases. The overloaded equipment identified on this circuit is the overhead conductor. |  |  |  | 2023-12-31 | 138 | 0 | 159000
MTEP21 | East | METC | 20054 | Warren 138 kV 377 Equipment Upgrades | Upgrade terminal station equipment, including a 138 kV breaker, at Warren position 377 to meet or exceed the rating of a 954 ACSR conductor. | MI | BRP |  | The Warren – Clare Jct. 138 kV line is projected to be overloaded for category P1, P2, P3, and P6 contingencies in light load and several shoulder peak cases. |  |  |  | 2023-12-31 | 138 | 0 | 1050000
MTEP21 | East | METC | 20108 | Atlanta-Karn-Thetford Split & Station Reconfiguration (METC) | Split the three-ended Atlanta-Karn-Thetford 138 kV line into Altanta – Karn 138 kV and Atlanta – Thetford 138 kV. | MI | Other | Reliability | Atlanta station is presently configured such that routine NERC required periodic maintenance on some protection systems require the entire station be deenergized for the work to be performed safely. In order to maintain transmission service to the single distribution transformer, a temporary line needs to be constructed to bypass the deenergized Atlanta station. This project will reconfigure the station similar to other ITC stations such that periodic maintenance and other normal work activities can be performed without extensive temporary construction. Adding the section breaker also allows installation of SSVTs to the 120kV buses for station service, allowing for ITC to relocate the backup generator system presently installed. The Atlanta, Karn, and Thetford 138kV line facilities are relayed together; meaning a fault on any one element trips all three and interrupts network transmission flows on the remaining connected elements. The three lines are connect together very near Atlanta station so by bringing the lines the short distance in and out of Atlanta station, we can relay the Karn and Thetford lines individually, which improves system protection as follows: • Less sensitive protection settings on 2-terminal lines, resulting in: ¿ Eliminate risk of overtripping caused by ground miscoordination. ¿ Faster backup clearing times without risk of miscoordination. ¿ Eliminate risk of miscoordination caused by terminals open or with limited infeed. ¿ No concerns with sequential clearing. • The line relaying is newer and will be re-utilized for this 2-terminal line applications with modifications to reduce their complexity to match ITC’s standards: ¿ Increased reliability by reducing risk for human error during operations and maintenance of the schemes. • These 2-terminal lines can utilize double-ended fault locating methods, resulting in the following benefits: ¿ Increased likelihood of locating faults. ¿ Reduce patrol and tower climbing to locate faults. |  |  |  | 2024-12-31 | 138 | 0 | 322000
MTEP21 | East | METC | 20118 | Higgins 138 kV Station Expansion | Reconfigure the Higgins 138 kV station to accommodate the CE request for METC to provide separate and independent exits in the ring bus for 2 new 138/46 kV transformer banks. METC will expand the existing ring bus and install 1 138 kV breaker and associated disconnects. The Mio Dam and Beaver creek lines will be reterminated to improve reliability. | MI | Other | Other Local Needs | Consumers Energy is rebuilding their 46 kV Higgins station and has requested METC provide separate and independent exits for the new transformer banks. |  |  |  | 2023-04-01 | 138 | 0 | 4490498
MTEP21 | East | METC | 20120 | Wackerly 138 kV Station Equipment Upgrades | Replace station equipment in the Wackerly Substation meet or exceed rating of a 795 ACSR conductor. | MI | BRP |  | Equipment at the Wackerly section breaker is projected to be overloaded for category P1, P2, P3, P6 and P7 contingencies in shoulder peak and peak cases. |  |  |  | 2023-12-31 | 138 | 0 | 142000
MTEP21 | East | METC | 20144 | Argenta 2 Transformer Replacement | Replace the Argenta #2 345/138kV transformer. The anticipated replacement is the METC-standard 345/140kV 500MVA transformer. | MI | Other | Age and Condition | The Argenta #2 345/138kV transformer is reaching end of life. This transformer is a 1969 Pennsylvania unit that is leaking oil. |  |  |  | 2025-12-31 | 345 | 138 | 5400000
MTEP21 | East | METC | 20145 | Tallmadge 2 Transformer Replacement | Replace the Tallmadge #2 345/138kV transformer. The anticipated replacement is the METC-standard 345/140kV 500MVA transformer. | MI | Other | Age and Condition | The Tallmadge #2 345/138kV transformer is reaching end of life. This transformer is a 1968 General Electric unit that is leaking nitrogen. |  |  |  | 2025-12-31 | 345 | 138 | 6100000
MTEP21 | East | METC | 20146 | Tittabawassee 1 Transformer Replacement | Replace the Tittabawassee #1 345/138kV transformer. | MI | Other | Age and Condition | The transformer is reaching its end of life. More details to follow asap. |  |  |  | 2023-12-31 | 345 | 138 | 6200000
MTEP21 | East | METC | 20147 | Vergennes 2 Transformer Replacement | Replace the Vergennes #2 345/138kV transformer. The anticipated replacement is the METC-standard 345/140kV 500MVA transformer. | MI | Other | Age and Condition | The Vergennes #2 345/138kV transformer is reaching end of life. This transformer is a 1970 McGraw Edison unit that is leaking oil. Electrical testing in 2009 found that four bushings on this unit have deteriorated as well. |  |  |  | 2023-12-31 | 345 | 138 | 7100000
MTEP21 | East | METC | 20162 | Claremont 138 kV Station Rebuild | The proposed solution is to rebuild Claremont 138 kV station with a new control house at a new site just to the southwest of the existing site utilizing new equipment in a five-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called New Station. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance to be performed again in a safe and efficient manner. | MI | Other | Age and Condition | The Claremont 138 kV station is a late 1940’s legacy station. Much of the equipment has been in-service for several decades and has realized the end of its useful life. This equipment is dated (requires the use of operating practices that do not employ the safety measure designed in modern equipment), a source of failure, emergency maintenance, and in need of a wholesale replacement. The station was designed in accordance with design practices of the era. ITC and the industry’s design practices today - utilizing modern high voltage electrical equipment - produces a reliable, safe, accessible, and operationally flexible station. As it stands today, Claremont station’s design and integrity makes it difficult to perform routine maintenance on equipment and presents challenges when conducting routine operations. Furthermore the present station design is such that a single faulted breaker will deenergize the entire station, dropping network load from 7 lines and 2 sub-transmission transformers. |  |  |  | 2025-12-31 | 138 | 0 | 24227000
MTEP21 | East | METC | 20164 | Wealthy Street 138 kV Station Rebuild | The proposed solution is to rebuild Wealthy Street 138 kV station with a new control house at a new site just to the southwest of the existing site utilizing new equipment in a four-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called New Station. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance to be performed again in a safe and efficient manner. | MI | Other | Age and Condition | The Wealthy Street 138 kV station is an early 1920’s legacy station. Much of the equipment has been in-service for several decades and has realized the end of its useful life. This equipment is dated (requires the use of operating practices that do not employ the safety measure designed in modern equipment), a source of failure, emergency maintenance, and in need of a wholesale replacement. The station was designed in accordance with design practices of the era. ITC and the industry’s design practices today - utilizing modern high voltage electrical equipment - produces a reliable, safe, accessible, and operationally flexible station. As it stands today, Wealthy Street station’s design and integrity makes it difficult to perform routine maintenance on equipment and presents challenges when conducting routine operations. Furthermore the present station design is such that a single faulted breaker will deenergize the entire station, dropping network load from 4 lines and 2 sub-transmission transformers. |  |  |  | 2023-12-31 | 138 | 0 | 24000000
MTEP21 | East | METC | 20711 | Stamping Plant 138kV Station Decommission | Terminate 138kV lines and bypass Stamping Plant 138kV station at structure #068C134. Tie Gaines – Stamping Plant to Stamping Plant – Beals Road to create Gaines – Beals Road 138kV line. Decommission Stamping Plant Station and remove all equipment. | MI | Other | Other Local Needs | The City of Wyoming is requesting ITC to remove the Stamping Plant substation before June 1, 2021. |  |  |  | 2021-06-01 | 138 | 0 | 1254000
MTEP21 | East | METC | 20826 | Arenac CE Interconnection | Arenac Substation is proposed to connect to the Twining 138kV substation. CE to convey Twining 138kV equipment to METC. METC to provide a new 138kV line between Twining and CE's new Arenac Substation. Fiber will be installed for relay communication. | MI | Other | Other Local Needs | CE requested a new Interconnection to facilitate the build of a new 138/46kV Arenac Substation for transfer of CE's existing 46kV Twining equipment. |  |  |  | 2023-01-01 | 138 | 0 | 2094931
MTEP21 | East | METC | 21025 | Foundry Bypass | Disconnect the Stable - Foundry 138kV line at Calhoun. Disconnect the Foundry - Rice Creek line at structure 074B28. Connect the two lines to make Stable - Rice Creek line. Install one 1-way switch at structure 074B28 for Calhoun. | MI | Other | Other Local Needs | CE and METC assets are being decommissioned at Foundry 138kV. Foundry should be bypassed as it serves no purpose. The in-service date is needed to minimize costs associated with J857 interconnection. |  |  |  | 2022-09-01 | 138 | 0 | 1702022
MTEP21 | East | METC | 21046 | Livingston 345kV Reactor 34F Replacement | Replace Livingston 345kV Shunt Reactor #34F with a new reactor | MI | Other | Age and Condition | This reactor has reached it's end of life. |  |  |  | 2023-12-31 | 345 | 0 | 2500000
MTEP21 | East | METC | 21208 | Clinton Station Cut-in | Cut into the Island Rd – Delhi 138 kV line at the Clinton Junction with a new double tap structure and install pole top switches at the Packard and Eaton Rapids taps. Wolverine to utilize existing 795 ACSS conductor on the east side of the structures for the Clinton Rd – Delhi 138 kV circuit and reconductor the line on the west side of the structures utilizing 795 ACSS conductor to complete the Island Rd - Clinton 138 kV circuit | MI | Other | Reliability | The Delhi – Clinton Jct – Island Rd 138 kV line has experienced several misoperations since Clinton Jct was tapped off the line less than 10 years ago. This is a testament to the complexity of three-terminal line relaying. Furthermore, this scheme is so sensitive that it’s picking up and blocking routinely for faults as far away as Fermi. As the carrier equipment degrades over time, we should expect additional misoperations if actions are not taken. • Less sensitive protection settings on 2-terminal lines, resulting in: ¿ Eliminate risk of overtripping caused by ground miscoordination. ¿ Faster backup clearing times without risk of miscoordination. ¿ Eliminate risk of miscoordination caused by terminals open or with limited infeed. ¿ No concerns with sequential clearing. • The line relaying is newer and may be re-utilized for this 2-terminal line applications with modifications to reduce their complexity to match ITC’s standards: ¿ Increased reliability by reducing risk for human error during operations and maintenance of the schemes. • These 2-terminal lines can utilize double-ended fault locating methods, resulting in the following benefits: ¿ Increased likelihood of locating faults. ¿ Reduce patrol and tower climbing to locate faults. ¿ Quicker restoration. |  |  |  | 2025-06-01 | 138 | 0 | 3300000
MTEP21 | East | METC | 21305 | North Belding - Control House Replacement | Install new Control House at North Belding 138kV station. Migrate relaying and vacate old control houses. Install SSVTs and Battery system. | MI | Other | Reliability | Mitigate working space constraints and multiple control houses that can lead to human performance related issues during switching and cutting out protection. Replacement of remaining electromechanical relay schemes to microprocessor relays. |  |  |  | 2023-06-01 | 138 | 0 | 1960830
MTEP21 | West | Minnesota Power (Allete, Inc.) | 18066 | Badoura 115kV Substation Modernization | Relocate existing 115 kV lines into ring bus and remove/retire old substation yard. | MN | Other | Age and Condition | Age & condition |  |  |  | 2023-12-31 | 115 | 0 | 1820000
MTEP21 | West | Minnesota Power (Allete, Inc.) | 18945 | 98 Line Asset Renewal | Structure replacements on Iron Range - Arrowhead 230 kV line | MN | Other | Age and Condition | Age & condition |  |  |  | 2021-03-31 | 230 | 0 | 2130000
MTEP21 | West | Minnesota Power (Allete, Inc.) | 20032 | Canosia Road Substation Expansion | Complete ring bus and add 115/34.5 kV transformer to existing Canosia Road Substation. This project includes the transmission equipment necessary to accommodate the new transformer. | MN | Other | Reliability | Redundancy and load-serving capability for Cloquet area. |  |  |  | 2023-06-01 | 115 | 34.5 | 1500000
MTEP21 | West | Minnesota Power (Allete, Inc.) | 20075 | Forbes 230 kV Modernization | Replace aging 230 kV cap bank and 230 kV circuit breakers at Forbes Substation, as well as a large 230/115 kV autotransformer. Project includes several other asset renewal components and substantial civil work at the site. | MN | Other | Age and Condition | Asset Renewal |  |  |  | 2025-12-31 | 230 | 0 | 7350000
MTEP21 | West | Minnesota Power (Allete, Inc.) | 20081 | Stinson Asset Renewal Project | Replace aging capacitor bank, 115W breaker, switches, PT's, and relay panels. | WI | Other | Age and Condition | Asset renewal. |  |  |  | 2022-12-31 | 115 | 0 | 1530000
MTEP21 | West | Missouri River Energy Services (MRET) | 19845 | Willmar South Breaker Replacement | Replace oil filled breakers due to age and condition | MN | Other | Age and Condition | Breaker replacement |  |  |  | 2021-12-31 | 69 | 0 | 800000
MTEP21 | West | Missouri River Energy Services (MRET) | 19846 | Willmar Plant Sub Relocate | The Willmar Power Plant building is being decommissioned and removed. Substation protection and controls were in the building and will need to be moved. This will require the entire substation to be moved to a new location. | MN | Other | Reliability | New substation location for the Willmar Plant Substation. |  |  |  | 2021-12-31 | 69 | 0 | 3000000
MTEP21 | West | Missouri River Energy Services (MRET) | 19986 | Willmar Sub Upgrades | Upgrading bus jumpers, switches, and oil filled breakers at the Willmar 230/69 kV substation. | MN | Other | Age and Condition | Age and condition of equipment |  |  |  | 2022-12-30 | 230 | 69 | 610000
MTEP21 | West | Missouri River Energy Services (MRET) | 20445 | Atlantic Breaker Replacement | Replace 69 kV oil breaker at NIPCO J8 substation. | IA | Other | Age and Condition | Breaker replacement age and condition. |  |  |  | 2021-12-31 | 69 | 0 | 100000
MTEP21 | Central | Wabash Valley Power Association, Inc. | 20112 | Rebuild Fair Oaks 138/69 kV Substation | Install new 138/69/12 switchable 22.4 MVA transformer. Install a new 69 kV line terminal with auto throwover scheme equipment for a new loop line to Colfax. Expand the fence and install new 69 kV rigid bus. | IN | Other | Age and Condition | Increased load requires more capability. Loop for reliability to area. |  |  |  | 2021-04-30 | 69 | 12 | 4700000
MTEP21 | Central | Wabash Valley Power Association, Inc. | 20113 | Update Colfax South Substation | Install a new 69 kV line terminal with an auto sectionalizing scheme equipment for a new loop line to Fair Oaks. | IN | Other | Age and Condition | Reliability to area |  |  |  | 2021-12-31 | 69 | 12 | 1500000
MTEP21 | Central | Wabash Valley Power Association, Inc. | 20114 | New 69kV Fair Oaks to Colfax South | New 138kV (Operated at 69 kV) 477 ACSR conductor looping Colfax to Fair Oaks for reliability in Jasper and Newton Counties. | IN | Other | Reliability | Reliability in Jasper and Newton Counties |  |  |  | 2021-12-31 | 69 | 12 | 5300000
MTEP21 | Central | Northern Indiana Public Service Company | 20605 | Rebuild Michigan City (Shoreline) 138 kV Substation | Rebuild of Michigan City 138kV substation. | IN | Other | Age and Condition | Age & Condition |  |  |  | 2022-12-31 | 138 | 0 | 16572178
MTEP21 | West | Otter Tail Power Company | 16286 | Donaldson-Hallock 41.6 kV Line Upgrades | Repole and reinsulate 8.8 miles to a 69 kV level on the transmission line between Donaldson-Hallock 41.6 kV for reliability. | MN | Other | Age and Condition | Age and condition of 8.8 miles between Donaldson to Hallock 41.6 kV transmission line will be repoled and reinsulated to a 69 kV level. |  |  |  | 2020-12-15 | 41.6 | 0 | 1400483.7
MTEP21 | West | Otter Tail Power Company | 19929 | OTP Finley to McVille 41.6 kV Line Upgrade | Rebuild 5.75 miles of 41.6 kV line and add automation to existing switches to improve reliability performance and restoration time of this line. | ND | Other | Age and Condition | Structure integrity of existing line is leading to reliability concerns |  |  |  | 2021-12-01 | 41.6 | 0 | 1000000
MTEP21 | West | Otter Tail Power Company | 19930 | OTP Doyon/Bartlett – Rebuild 41.6 kV Line | Rebuild 5.6 miles of 41.6 kV line, replace conductor and reroute existing line out of the water to improve reliability performance and restoration time of this line. | ND | Other | Age and Condition | Structure integrity of existing line is leading to reliability concerns. |  |  |  | 2021-12-01 | 41.6 | 0 | 950000
MTEP21 | West | Otter Tail Power Company | 20485 | OTP Ortonville 115 kV Capacitor Reduction | Reduce capacitor size from 30 MVAR to 17 MVAR. | MN | Other | Reliability | The existing capacitor was too large and voltage jumps exceeded OTP switching criteria. The lower size keeps the voltage jumps within OTP criteria. |  |  |  | 2020-09-24 | 115 | 0 | 1000
MTEP21 | West | Otter Tail Power Company | 20606 | OTP Maple River 345/230/13.8 kV Transformer Replacement | Like-for-like replacement of the failed Maple River 345/230/13.8 kV transformer #1. Additionally, a new control house will be built. | ND | Other | Age and Condition | One of OTP’s transformers failed at Maple River, so a replacement is required. |  |  |  | 2022-02-04 | 345 | 230 | 2600000
MTEP21 | Central | Prairie Power, Inc. | 19847 | New Golden 138/69 kV Substation | New Golden 138/69 kV substation near La Prairie, IL | IL | Other | Reliability | Provide alternative feed to Adams Electric Cooperative and backup St. Anthony transformer. |  |  |  | 2024-12-31 | 138 | 69 | 7425000
MTEP21 | Central | Prairie Power, Inc. | 19848 | New Camden - Rushville 69 kV Line | New ~12-mile Camden to Rushville 69 kV line in AEC | IL | Other | Reliability | Provide alternative feeds to Camden and Rushville substations |  |  |  | 2024-12-31 | 69 | 69 | 7680000
MTEP21 | Central | Prairie Power, Inc. | 19849 | New Rushville - Sugar Grove 69 kV Line | New ~13-mile Rushville to Sugar Grove 69 kV line in AEC | IL | Other | Reliability | Provide alternative feeds to Rushville and Sugar Grove substations |  |  |  | 2024-12-31 | 69 | 69 | 8448000
MTEP21 | Central | Prairie Power, Inc. | 19850 | New Sugar Grove - Mt. Sterling 69 kV Line | New ~9-mile Sugar Grove to Mt. Sterling 69 kV line in AEC | IL | Other | Reliability | Provide alternative feeds for Sugar Grove and Mt. Sterling substations |  |  |  | 2024-12-31 | 69 | 69 | 5548800
MTEP21 | Central | Prairie Power, Inc. | 19851 | New Mt. Sterling - Kellerville 69 kV Line | New ~18-mile Mt. Sterling to Kellerville 69 kV line in AEC | IL | Other | Reliability | Provide alternative feeds to Mt. Sterling and Kellerville substations |  |  |  | 2024-12-31 | 69 | 0 | 11328000
MTEP21 | Central | Prairie Power, Inc. | 19932 | New Disco to Lomax 69 kV Line | New ~15-mile Disco to Lomax 69 kV line in WIEC | IL | Other | Reliability | Provide alternative feeds to Disco and Lomax substations |  |  |  | 2024-12-31 | 69 | 69 | 9862500
MTEP21 | Central | Prairie Power, Inc. | 19933 | New Disco to Powellton 69 kV Line | New ~12-mile Disco to Powellton 69 kV line in WIEC | IL | Other | Reliability | Provide alternative feeds to Disco and Powellton substations |  |  |  | 2024-12-31 | 69 | 69 | 8000000
MTEP21 | Central | Prairie Power, Inc. | 19934 | Add Elvaston 69 kV Breakers | Add breakers on the Elvaston to Powellton line and the Elvaston to Sutter line | IL | Other | Reliability | Provide protection for the Elvaston to Powellton line and Elvaston to Sutter line |  |  |  | 2024-12-31 | 69 | 69 | 350000
MTEP21 | Central | Prairie Power, Inc. | 19935 | New Sutter - Ursa 69 kV Line | New ~21-mile Sutter to Ursa 69 kV line between WIEC and AEC | IL | Other | Reliability | Provide alternative feeds to Sutter and Ursa substations |  |  |  | 2025-12-31 | 69 | 0 | 13312000
MTEP21 | Central | Prairie Power, Inc. | 19937 | New Bluffs 69 kV Breaker Substation | New Bluffs 69 kV Breaker substation located near Bluffs, IL in IEC | IL | Other | Reliability | Provide sectionalizing for Bluffs to Winchester, Bluffs to Naples, and Bluffs to Indian Creek 69 kV lines. |  |  |  | 2023-12-31 | 69 | 69 | 2844450
MTEP21 | Central | Prairie Power, Inc. | 19938 | Rebuild Grand Island - Poplar City 69 kV Line | Rebuild ~1-mile Grand Island to Poplar City 69 kV line in MEC | IL | Other | Age and Condition | Age and Condition. Replace 2/0 line built in 1955 with 556.5 MCM ASCR conductor |  |  |  | 2020-12-31 | 69 | 69 | 557290
MTEP21 | Central | Prairie Power, Inc. | 19939 | Rebuild Grand Island - Topeka 69 kV Line | Rebuild ~5-mile Grand Island to Topeka 69 kV line in MEC | IL | Other | Age and Condition | Age and Condition. Replace 2/0 line built in 1955 with 556.5 MCM ASCR conductor |  |  |  | 2022-05-31 | 69 | 69 | 2407310
MTEP21 | Central | Prairie Power, Inc. | 19940 | Replace Grand Island 138/69 kV Transformer | Replace 56 MVA Delta-Wye 138/69 kV transformer with 84 MVA Wye-Wye 138/69 kV transformer | IL | Other | Reliability | Allow Grand Island transformer to phase with and backup Indian Creek and Fancy Creek transformers |  |  |  | 2024-12-31 | 138 | 69 | 1500000
MTEP21 | Central | Prairie Power, Inc. | 19949 | New ISHI Shelbyville 69 kV Loop | New ~7-mile ISHI Distribution to Johnston to Crest to Airport 69 kV line in SEC | IL | Other | Reliability | Provide alternative feeds to ISHI Distribution, Johnston, Crest, and Airport substations |  |  |  | 2025-12-31 | 69 | 69 | 4064000
MTEP21 | Central | Prairie Power, Inc. | 19951 | Rebuild Pisgah Tap - Berlin 69 kV Line | Rebuild Pisgah Tap to Berlin 69 kV line between IEC and MEC | IL | Other | Age and Condition | Age and Condition. Replace 4/0 line built in 1965 with 336.4 MCM ASCR conductor |  |  |  | 2023-12-31 | 69 | 69 | 7880000
MTEP21 | Central | Prairie Power, Inc. | 20607 | New Illinois Winds Pittsfield 69 kV Generator Interconnection | New Illinois Wind Panther Creek 44.5 MW Wind Farm connecting to the PPI Pittsfield 69 kV bus. | IL | GIP |  | Connect Illinois Winds Panther Creek 44.5 MW Wind Farm to PPI Pittsfield 69 kV bus. Based on the projected 1/31/2023 in-service date, PPI is requesting that this generator interconnection project be placed in MTEP21 |  |  |  | 2023-01-31 | 69 | 0 | 6676401
MTEP21 | South | South Mississippi Electric Power Association | 20305 | MS Solar 4 Switching Station | Construct a new 161kV breaker switching station that taps the Moselle - Columbia 161kV line. | MS | GIP |  | The new 161kV breaker switching station is required as the POI for Interconnection Customer project J1144 (MS Solar 4). |  |  |  | 2022-10-01 | 161 | 0 | 5251585
MTEP21 | East | Wolverine Power Supply Cooperative, Inc. | 20885 | Cimmaron Interconnection | Install tap pole and 2 switches on White Cloud to Hesperia line section to allow Consumers to interconnect service for new Cimmaron substation. | MI | Other | Load Growth | New Load Interconnection |  |  |  | 2022-12-31 | 69 | 0 | 600000
MTEP21 | East | Wolverine Power Supply Cooperative, Inc. | 21205 | Clinton Area Alternative | Wolverine proposes to utilize Wolverine’s existing Clinton station and double circuit line as an alternative to METC’s MTEP Project #20158. In order to address other future drivers, Wolverine also proposes to convert its Bradley to Clinton line from 69kV to 138kV that is additional to METC’s protection needs. See Exhibit 1 for one-line diagram of configuration (Warning – CEII information) The scope of work includes: • Reconfiguring Wolverine’s Clinton Station to create an in-and-out path for METC’s Delhi – Island Road 138kV line and accommodate the converted Bradley– Clinton 138kV line • Replacing 4/0 conductor on one circuit of Clinton’s double circuit line with 795ACSS • Replacing the Vermontville high side to accommodate 138kV operation • Replacing the Hastings high side to accommodate 138kV operation • Replacing the Otsego high side to accommodate 138kV operation • Rebuilding Wolverine’s Eaton Rapids 69 kV line to 138 kV design and relocating from Clinton Station to METC’s Delhi-Island Road line. • Replacing the Eaton Rapids high side to accommodate 138kV operation | MI | Other | Reliability | The southeastern area of Wolverine’s transmission system is in need of several upgrades driven by both reliability and condition. Each driver is disconnected from each other but when put together creates a holistic solution that mitigates the needs for all. Reliability 1. Support METC’s need for improved protection coordination on the Delhi – Island Road 138kV 2. Address the inefficiencies from recurring 69kV to 138kV backflow at Clinton (see Exhibit 2 for 2019 and 2020 flow data) 3. Mitigate voltage constraints under long-term forecasts (10-15 years) Condition 1. Rebuild of the Eaton Rapids line will soon be required due to condition • Current age 67 years, built in 1953 • 7 condemned, 36 damaged poles • 25% of poles in need of replacement |  |  |  | 2025-12-31 | 138 | 0 | 13650000
MTEP21 | West | Northern States Power (Xcel Energy) | 19165 | Fieldon Retirement | This project bypasses and retires the Fieldon series capacitor and removes the substation, whose only function is for the series capacitor. This facility is no longer required and has a significant recurring maintenance cost. | MN | Other | Age and Condition | The system growth in the area has removed the need for the Fieldon series capacitor which has had operational issues in the past and has a significant recurring maintenance cost. |  |  |  | 2022-07-01 | 345 | 0 | 3000000
MTEP21 | West | Northern States Power (Xcel Energy) | 19886 | Minnesota Vallery TR12 ELR | Like for like replacement of Minnesota Valley TR12. Transformer is 68 years old and is experiencing performance issues | MN | Other | Age and Condition | Transformer is 68 years old and has indications of some overheating issues, moisture, bad joints, and active thermal degradation. Not replacing would result in more frequent and long term outages. |  |  |  | 2021-12-15 | 115 | 69 | 1500000
MTEP21 | West | Northern States Power (Xcel Energy) | 19887 | Eau Claire TR10 ELR | End of life, like for like replacement of Eau Claire TR10. | WI | Other | Age and Condition | Eau Claire TR10 is 52 years old and is experiencing performance issues. Potential for more frequent and longer duration outages. |  |  |  | 2021-12-15 | 345 | 161 | 3000000
MTEP21 | West | Northern States Power (Xcel Energy) | 19888 | Northfield to Farmington Line Rebuild | Rebuild approximately 18.6 miles of existing Northfield to Farmington line to current Transmission Design Standards. Reconductor 1.3 miles | MN | Other | Age and Condition | End of life,at risk of imminent failures. Increased outage frequency and duration. Failure could provide risk to public safety |  |  |  | 2022-12-15 | 69 | 0 | 8000000
MTEP21 | West | Northern States Power (Xcel Energy) | 19889 | Black Oak to Sauk Center Line Rebuild | Rebuild and upgrade conductor on approximately 6.64 miles from Black Oak to Sauk Center. | MN | Other | Reliability | Structures exceed planned service life - built in 1951. 4/OA and 3/#6 CU line sections overloading on N-1 contingencies. |  |  |  | 2024-06-01 | 69 | 0 | 4000000
MTEP21 | West | Northern States Power (Xcel Energy) | 19890 | Watkins - Kimball Line Rebuild | Rebuild and upgrade approximately 6.56 miles of existing line. Replace EOL switches and MODs. | MN | Other | Load Growth | 83 year old poles. Age and condition do not support repairs. Load growth requires upgrade of small conductor. Potential for increased outage frequency and duration. Failure could provide risk to public |  |  |  | 2022-12-15 | 69 | 0 | 3200000
MTEP21 | West | Northern States Power (Xcel Energy) | 19891 | Replace Green Isle Substation | Replace existing Green Isle substation with a new 69/13.8 kV substation on a new site. | MN | Other | Load Growth | Addition of industrial load is planned. Existing TR1 has contingency risk post load addition. Existing substation is 4kV and needs to be converted to conform with standards, existing site not sized to fit |  |  |  | 2021-03-15 | 69 | 13.8 | 3500000
MTEP21 | West | Northern States Power (Xcel Energy) | 19892 | Elm Creek TR4 | Install Elm Creek TR4 at 115kV/34.5kV with one new 34.5kV feeders exiting the substation to remediate N-1 overloads and allow proposed new customer load | MN | Other | Load Growth | Extended outage duration under Transformer N-1 contingency to mitigate overloads. New customer load interconnecting to substation. |  |  |  | 2021-12-15 | 115 | 34.5 | 4070000
MTEP21 | West | Northern States Power (Xcel Energy) | 19893 | Great Plains Substation | Construct new 115kV substation in Sioux Falls, SD between West Sioux Falls - Cherry Creek 115kV; 4 rows breaker-and-a-half; 3 TRs, 4 lines, 115 kV cap. | SD | Other | Reliability | Additional capacity needed to continue reliably serving customers in the Southwest area of Sioux Falls. Remediates N-1 distribution risk. |  |  |  | 2022-10-15 | 115 | 13.8 | 10600000
MTEP21 | West | Northern States Power (Xcel Energy) | 19905 | 2589 - Barnes Grove Interconnection | Install 3-way switch on 69kV line between Inver Grove - Keagan Lake Tap to accommodate GRE’s new Barnes Grove interconnection (MTEP 2589) | MN | Other | Load Growth | GRE interconnecting new Barnes Grove substation to serve new customer load |  |  |  | 2021-04-14 | 69 | 0 | 350000
MTEP21 | West | Northern States Power (Xcel Energy) | 19906 | Prentice Cap Bank Replacement | Upgrade the cap bank to 10MVAR and replace the circuit switcher at Prentice substation. | WI | Other | Reliability | Reliability concerns with aging Cap Bank experiencing multiple failures over the years and circuit switcher not rated for -50 deg. C. |  |  |  | 2021-12-15 | 115 | 0 | 1000000
MTEP21 | West | Northern States Power (Xcel Energy) | 19913 | Howard Lake to Big Swan, Delano to Howard Lake, Cokato to Winstead Rebuild | Howard Lake to Big Swan - Rebuild 16.0 miles , Delano to Howard Lake – Rebuild 19.7 miles , Cokato to Winstead – Rebuild 14.3 miles to current 69kV standard for end of life asset renewal | MN | Other | Reliability | Re-occurring system reliability issues increase, Public safety concerns Inability to serve load in long term |  |  |  | 2024-06-15 | 69 | 0 | 28000000
MTEP21 | West | Northern States Power (Xcel Energy) | 19914 | High Bridge-Rogers Lake Bifurcation to Double Circuit | Convert the bifurcated 115 kV line from High Bridge to Rogers Lake to a double circuit 115 kV line to alleviate curtailment on the High Bridge Generating Plant. Construct new breaker positions at High Bridge and Rogers Lake to accommodate the second 115kV circuit | MN | Other | Reliability | Relieve congestion issues historically seen at the High Bridge 115kV substation |  |  |  | 2023-05-01 | 115 | 0 | 3420000
MTEP21 | West | Northern States Power (Xcel Energy) | 19915 | Replace Alma Substation | Replace the existing Alma sub which is at end of life and in a poor access location with new sub with 7MVA TR with two regulated feeders at new site. | WI | Other | Age and Condition | The existing Alma substation is at end of life with 72 year old transformers. Access, space, and clearances are inadequate to rebuild in place |  |  |  | 2022-10-15 | 69 | 12.5 | 3000000
MTEP21 | West | Northern States Power (Xcel Energy) | 19916 | Rebuild Genoa Substation | Rebuild Genoa sub which is at end of life with New sub with 7MVA TR with two feeders on the existing site. | WI | Other | Age and Condition | Genoa has reached end of life. Failing equipment has caused several long outages. |  |  |  | 2022-10-15 | 69 | 13.8 | 2700000
MTEP21 | West | Northern States Power (Xcel Energy) | 20135 | Panther - Big Swan Rebuild | - Rebuilding most of the line to 477 standard due to age and condition - Adding a breaker station at Adams Wind tap to sectionalize the line - Converting the City of Litchfield tap structure to a double circuit structure | MN | Other | Age and Condition | Rebuilding line for age and condition and to support addition of Adams Wind |  |  |  | 2024-12-31 | 69 | 0 | 33300000
MTEP21 | West | Northern States Power (Xcel Energy) | 20229 | J732 Stone Lake XFMR Upgrade | Transformer upgrade for J732 in Aug 17 ATC DPP cycle | WI | GIP |  | Transformer overload with addition of J732 |  |  |  | 2023-11-10 | 345 | 161 | 3600000

## MTEP22
MTEP Year | Planning Region | Utility/TO | Project ID | Project Name | Project Description | State | Project Type | Other Type | System Need / Rationale | Project Driver | Data Center Flag | Load (MW) | Expected ISD | Max kV | Min kV | Estimated Cost ($) | Report Notes
MTEP22 | West | American Transmission Co. LLC | 16766 | Small Capital Project and Asset Renewal Program 2023 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2023. | WI,MI | Other | Age and Condition | Asset Renewal or Reliability |  |  |  | 2026-06-30 | 345 | 69 | 34925540
MTEP22 | West | American Transmission Co. LLC | 16767 | Communications Reliability Program 2023 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2023. | WI,MI | Other | Other Local Needs | other, increased reliability |  |  |  | 2026-06-30 | 0 | 0 | 19593713
MTEP22 | West | American Transmission Co. LLC | 16768 | Line Clearance Mitigation Program 2023 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2023. | WI,MI | Other | Reliability | Line Clearance |  |  |  | 2026-06-30 | 345 | 69 | 3935020
MTEP22 | West | American Transmission Co. LLC | 16769 | Physical Security Program 2023 | Physical Security projects typically have shorter project life cycles. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2023. | WI,MI | Other | Other Local Needs | Physical Security |  |  |  | 2025-01-01 | 345 | 69 | 1859619
MTEP22 | West | American Transmission Co. LLC | 16770 | Load Interconnection Program 2023 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2023. | WI,MI | Other | Load Growth | Load Interconnection - Coordination with LDC |  |  |  | 2026-06-30 | 345 | 69 | 18045914
MTEP22 | West | American Transmission Co. LLC | 18046 | Darlington – Rock Branch, (Y-109), 69kV, Rebuild & OPGW | T-Line Scope o Rebuild approximatley 14 miles of the Y-109 line from Darlington - Rock Branch o Install new conductor IT/Communications o Install fiber and terminate at substations Substation Scope o Fiber terminations at remote ends. o Asset Renewal of substation equipment: -Rock Branch: Replace disconnect switches, jumpers, strain bus and (1) breaker. -Darlington: Replace jumpers and strain bus section. | WI | Other | Age and Condition | Asset Renewal - Line Rebuild |  |  |  | 2025-12-31 | 69 | 0 | 16700000
MTEP22 | West | American Transmission Co. LLC | 18047 | South Beaver Dam - Hubbard, (Y-134), 69kV Rebuild & OPGW | T-Line Scope to replace: • South Beaver Dam SS to Str 230: (~13.2 miles) • Str 230 to Hubbard: (~3.3miles) • Install new conductor and install new OPGW fiber Substation Scope • South Beaver Dam: replace jumpers and 600A switches, fiber terminations • Horicon: replace existing 336 jumpers, fiber terminations. • Hubbard: Fiber terminations, no other work planned. | WI | Other | Age and Condition | Asset Renewal - Line Rebuild |  |  |  | 2026-12-31 | 69 | 0 | 20100000
MTEP22 | West | American Transmission Co. LLC | 18049 | Portage St - 3 Mile 69 kV (6901/ESE_6902), Re-insulate & Underground Fiber | 9 mile SW STA – Portage (6901/6902), 69kV, Re-insulate | MI | Other | Age and Condition | Asset Renewal - Re-insulation |  |  |  | 2025-12-01 | 69 | 0 | 5400000
MTEP22 | West | American Transmission Co. LLC | 19525 | Saratoga SS - Control House and Breaker Asset Renewal | • Replace control building and contents • Replace 69kV oil breakers • Replace 2 CCVT’s • Install normally-open GOAB line switch outside the fence to enable the connection of radial lines Y-301 and Y-302 • Retire inoperable 922-A and 923-A breaker bypass switches which will no longer be required with the installation of the new GOAB • Reconductor 138kV Bus 2 to match the higher capacity X-43 line rating • Install Dual batteries to meet future TPL-002-2 standards | WI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2025-12-01 | 138 | 69 | 8200000
MTEP22 | West | American Transmission Co. LLC | 19962 | Nelson Dewey - Bloomington (Y-184), 69kV, rebuild & OPGW | Rebuild and install OPGW on approximately 15 miles on Y-184 from Nelson Dewey substation to Bloomington substation. Like for like wood pole replacement with wood pecker mesh where necessary. | WI | Other | Age and Condition | Asset Renewal - Line Rebuild |  |  |  | 2025-12-31 | 69 | 0 | 16300000
MTEP22 | West | American Transmission Co. LLC | 19966 | Munising Area Reactive Power Project | Install one +/- 10 MVA, 69-kV STATCOM (Static Synchronous Compensator) at Munising substation | MI | BRP |  | Reliability |  |  |  | 2025-12-31 | 138 | 0 | 10000000
MTEP22 | West | American Transmission Co. LLC | 20805 | Rock County Reliability Project | To address the limited connections, ATC is proposing to develop 345-138 kV connections at Kittyhawk. The specific scope is likely to be: •add two 500-MVA, 345-138 kV transformers at the Kitty Hawk substation •add a 138 kV line between the Kitty Hawk and Town Line Road substations •loop into Kittyhawk existing Paddock-Town Line and Town Line-Bass Creek 138 kV lines •uprate Rock River-Marine 138 kV line •increase ground grid fault capability at several nearby substations. | WI | BRP |  | Reliability A number of factors drive the need for this project resulting in a variety of TPL-001 Planning Event limitations. While many might be addressed by redispatching 345 and 138 kV generation, the future availability of the 138 kV generation is very uncertain. Also, new 345 and 138 generation additions to parts of the system that aggravate the limitations will make it increasingly difficult to find enough generation to redispatch. In addition, there is long-lead time equipment at the Paddock substation that further aggravates the limitations. In 2020 actual system events highlighted this need and make it a near and long term need. All of this points to the need for an additional 345-138 kV source for the Janesville area. The proposed project is at least one alternative to address these needs. |  |  |  | 2024-12-21 | 345 | 69 | 49721000
MTEP22 | West | American Transmission Co. LLC | 21286 | Rocky Run SS Power Transformer Replacement | Replace T1, a 1968 vintage 345/115 kV, 150 MVA power transformer with a 345/115kV, 500 MVA system spare. | WI | BRP |  | Reliability/Asset Renewal - Substation |  |  |  | 2023-12-31 | 345 | 115 | 5408000
MTEP22 | West | American Transmission Co. LLC | 21345 | National - Presque Isle SW YD 138 kV (446), Re-insulate & OPGW | - Reinsulate ~50% of structures on the line with like for like porcelain bells. - Replacement of structures (~15% based on ground inspection) for wood pecker damage - Install OPGW | MI | Other | Age and Condition | Asset Renewal - Transmission Line |  |  |  | 2025-12-31 | 138 | 0 | 8300000
MTEP22 | West | American Transmission Co. LLC | 21346 | Ontonagon - Victoria Hy 69 kV (Ontonagon69 69kV), Re-insulate | -Reinsulate ~65% of structures on the line with like for like porcelain bells. - Replacement of structures (~5% based on ground inspection) for wood pecker damage | MI | Other | Age and Condition | Asset Renewal - Transmission Line |  |  |  | 2024-12-31 | 69 | 0 | 4750000
MTEP22 | West | American Transmission Co. LLC | 21347 | Huiskamp - Ruskin 69 kV (6937), Partial Rebuild | Replace 23 legacy steel lattice towers with 23 new structures. | MI | Other | Age and Condition | Asset Renewal - Transmission Line |  |  |  | 2025-06-30 | 69 | 0 | 7900000
MTEP22 | West | American Transmission Co. LLC | 21348 | Tower Dr - Pulliam 69 kV (P-16/R-70), Partial Rebuild | Reroute approximately .65 miles of double circuit 69 kV transmission line on steel lattice towers due to condition and performance from ice damage including removal of 10 legacy steel lattice towers with replacement with 7 double circuit steel poles and approximately .65 miles of double circuit conductor and replace with T2 4/0 conductor. | WI | Other | Age and Condition | Asset Renewal - Transmission Line |  |  |  | 2024-04-01 | 69 | 0 | 4100000
MTEP22 | West | American Transmission Co. LLC | 21627 | North Lake SS, Power Transformer Asset Renewal | Replace TG2, a 1971 vintage 138/69 kV 47 MVA power transformer with a new 138/69 kV 60 MVA replacement. | MI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2025-12-31 | 138 | 69 | 4221065
MTEP22 | West | American Transmission Co. LLC | 21628 | Rockdale and Christiana SS - Control House and Relay Asset Renewal | • Replace Rockdale 138kV control building and contents, reusing three bus differential panels installed in 2011 as appropriate. • Replace X-65 and X-66 line relay panels at Christiana SS and coordinate with Rockdale work. • Install Dual batteries to meet future TPL-002-2 standards in the Rockdale 138kV building. | WI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2025-12-31 | 345 | 138 | 5800000
MTEP22 | West | American Transmission Co. LLC | 21629 | Oak Creek, Racine SS and Remote Ends, Control Buildings and Relaying Asset Renewal | • Replace control building and contents at Racine and Oak Creek 138kV. • Replace 9 138kV oil breakers at Racine, Dewey and Lincoln • Replace 21 138kV Model ACBL, ATA-2A and MK-40 at Dewey and Racine • Install approximately 35 relay panels • Provide room for WEC distribution equipment at Racine, demo existing building | WI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2025-12-31 | 345 | 138 | 20900000
MTEP22 | West | American Transmission Co. LLC | 21648 | J1000 Comet SS Network Upgrades and Interconnection Facilities | Interconnection Customer shall install a Solar Generating Facility modeled at 50 MW in Grant County, Wisconsin. | WI | GIP |  | Interconnection |  |  |  | 2023-03-27 | 138 | 0 | 6693598
MTEP22 | West | American Transmission Co. LLC | 21812 | J1002 Wautoma SS Network Upgrades and Interconnection Facilities | Interconnection Customer shall install a 99 MW solar facility connecting into the Wautoma SS in Waushara County. | WI | GIP |  | Interconnection |  |  |  | 2023-01-26 | 138 | 69 | 3246667
MTEP22 | West | American Transmission Co. LLC | 21813 | J1003 North Beaver Dam SS Network Upgrades and Interconnection Facilities | Interconnection Customer shall install a 50MW solar farm interconnecting at North Beaver Dam SS in Dodge County. | WI | GIP |  | Interconnection |  |  |  | 2023-06-06 | 138 | 69 | 1031386
MTEP22 | West | American Transmission Co. LLC | 21814 | J986 J1002 MPFCA | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. -J986 is seeking interconnection service for 149.76MW -J1002 is seeking interconnection service for 99 MW | WI | GIP |  | Interconnection |  |  |  | 2023-12-31 | 138 | 69 | 7507240
MTEP22 | West | American Transmission Co. LLC | 21899 | Port Washington – Saukville 138 kV (X-132/X-133) partial rebuild | Full rebuild of 3.5 miles of X-132/X-133 and reconductor only for the remaining 1.4 miles due to newer steel poles -Use ATC standard T2 Dove ACSR 556 conductor -Replace legacy lattice towers, install new OPGW and static line | WI | BRP |  | Reliability |  |  |  | 2025-06-30 | 138 | 0 | 7000000
MTEP22 | West | American Transmission Co. LLC | 21915 | Fitzgerald SS – Transformer and Breaker Asset Renewal | • Replace T1, a 1972 vintage 345/138 kV, 336 MVA power transformer with a new 345/138 kV 500 MVA standard three phase transformer • Replace three 138 kV oil circuit breakers with SF6 gas, eliminating all oil breakers at this station. • Replace one 138 kV 1600 A disconnect switch and associated jumpers • Remove bus arresters off bus 4 and install line arresters | WI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2025-12-31 | 345 | 138 | 7897437
MTEP22 | West | American Transmission Co. LLC | 21916 | Browntown - South Monroe 69 kV (Y-155), Rebuild | Rebuild approximately 8.3 miles on Y-155 from Browntown substation to South Monroe substation. | WI | Other | Age and Condition | Asset Renewal - Transmission Line |  |  |  | 2026-12-31 | 69 | 0 | 10300000
MTEP22 | West | American Transmission Co. LLC | 21917 | West Marinette SS – Transformer and Breaker Asset Renewal | West Marinette SS – Transformer and Breaker Asset Renewal | WI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2025-12-31 | 138 | 69 | 8962353
MTEP22 | West | American Transmission Co. LLC | 21918 | Pine River - Mich Limestone Loading Dock 69 kV (ESE_6906), Rebuild | • T-Line rebuild of approximately 25.5 miles with steel poles and reconductor • Construction: o Utilize two winter cycles for constructability | MI | Other | Age and Condition | Asset Renewal - Transmission Line |  |  |  | 2027-12-31 | 69 | 0 | 31100000
MTEP22 | West | American Transmission Co. LLC | 21923 | Everett GIS Asset Renewal | -Rebuild the GIS substation in the same location and re-use existing HPFF (High-Pressure-FluidFilled) terminations | WI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2025-12-31 | 138 | 0 | 16968398
MTEP22 | West | American Transmission Co. LLC | 21925 | Plymouth #5 - New DIC | Plymouth #5 - New DIC | WI | Other | Load Growth | Load Interconnection |  |  |  | 2025-09-01 | 138 | 0 | 21500000
MTEP22 | West | American Transmission Co. LLC | 21926 | Harbor – Russell Terminal 138 kV (893K11), Rebuild | Norwich - Harbor 138kV, (893K11), underground line replacement | WI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2025-12-31 | 138 | 0 | 37000000
MTEP22 | West | American Transmission Co. LLC | 22045 | J855 J864 J870 J871 MPFCA | Installation of ground conductor, ground rods and possibly ground wells along the perimeter of the Spring Green substaiton. | WI | GIP |  | Interconnection |  |  |  | 2022-12-31 | 138 | 0 | 220000
MTEP22 | West | American Transmission Co. LLC | 22046 | J1188 Sheepkskin SS Network Upgrades and Interconnection Facilities | Installation of a 50MW solar farm located in Rock County, Wisconsin | WI | GIP |  | Interconnection |  |  |  | 2022-04-06 | 138 | 0 | 1129461
MTEP22 | West | American Transmission Co. LLC | 22047 | J1154 Crawfish River Solar Network Upgrades | Installation of a 75MW solar farm located in Jefferson County, Wisconsin. | WI | GIP |  | Interconnection |  |  |  | 2023-05-15 | 138 | 0 | 2343684
MTEP22 | West | American Transmission Co. LLC | 22048 | J986 J1002 J1003 MPFCA | Ground gird mitigation at Roeder substation in Green Lake County, Wisconsin. | WI | GIP |  | Interconnection |  |  |  | 2023-12-31 | 138 | 0 | 220000
MTEP22 | West | American Transmission Co. LLC | 22049 | J1101 Kewaunee SS Network Upgrades and Interconnection Facilities | Installation of a 20MW battery storage project at the J886 Generating Facility. | WI | GIP |  | Interconnection |  |  |  | 2023-08-15 | 345 | 0 | 155000
MTEP22 | West | American Transmission Co. LLC | 22085 | J1002 J1003 MPFCA | Shared work for ground grid upgrades at North Beaver Dam SS, cost shared jointly between J1002 and J1003. J1002 - 5.54% J1003 - 94.46% | WI | GIP |  | Interconnection |  |  |  | 2023-12-31 | 138 | 69 | 550000
MTEP22 | West | American Transmission Co. LLC | 22105 | J1042 North Lake Geneva SS Network Upgrades and Interconnection Facilities | Interconnection Customer shall install a 180MW solar farm interconnecting at North Lake Geneva SS in Walworth County. | WI | GIP |  | Interconnection |  |  |  | 2023-09-15 | 138 | 0 | 1407357
MTEP22 | West | American Transmission Co. LLC | 22145 | J1153 Holland SS Network Upgrades and Interconnection Facilities | Interconnection Customer shall install a 150 MW solar farm interconnecting at Holland SS in Sheboygan County. | WI | GIP |  | Interconnection |  |  |  | 2022-06-14 | 345 | 138 | 8112107
MTEP22 | West | American Transmission Co. LLC | 22146 | J1171 Butternut SS Network Upgrades and Interconnection Facilities | Interconnection Customer shall install a 100 MW solar farm interconnecting at Butternut SS in Dodge County. | WI | GIP |  | Interconnection |  |  |  | 2023-01-26 | 345 | 138 | 3918722
MTEP22 | West | American Transmission Co. LLC | 22225 | J1042 J1188 MPFCA | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. -J1042 is seeking interconnection service for 180 MW -J1188 is seeking interconnection service for 50 MW | WI | GIP |  | Interconnection |  |  |  | 2023-11-01 | 138 | 0 | 4365163
MTEP22 | West | American Transmission Co. LLC | 22986 | Vinburn Substation 69 kV Capacitor Addition | Install a 69 kV capacitor bank configuration and associated automatic control features at Vinburn SS. | WI | BRP | Reliability | Other - Local Needs |  |  |  | 2024-12-31 | 69 | 0 | 3620000
MTEP22 | West | American Transmission Co. LLC | 22987 | Northview SS, DIC, New Substation | *ATC to install a new 138 kV circuit on new ROW (~0.6 miles) to the new substation. *ATC to install two manual load break switches and one manual disconnect switch at the new tap point on line X-107 and 10 new structures and 8 foundations are planned. | WI | Other | Load Growth | Other - Load Interconnection |  |  |  | 2023-06-01 | 138 | 0 | 3220000
MTEP22 | West | American Transmission Co. LLC | 22988 | Gaston Road SS, DIC, Additional Transformer | New DIC, additional transformer | WI | Other | Load Growth | Load Interconnection |  |  |  | 2024-12-31 | 69 | 0 | 3000000
MTEP22 | West | American Transmission Co. LLC | 22989 | Columbus SS, DIC, Transformer Replacement | Columbus SS, new DIC, transformer replacement | WI | Other | Load Growth | Load Interconnection |  |  |  | 2024-06-01 | 69 | 0 | 8782156
MTEP22 | West | American Transmission Co. LLC | 23007 | Cambria SS, DIC, New Substation | Distribution Interconnection, new substation | WI | Other | Load Growth | Load Interconnection |  |  |  | 2024-12-31 | 69 | 0 | 3000000
MTEP22 | West | American Transmission Co. LLC | 23008 | WisDOT I-94 Stadium Group of Projects | WisDOT Road Move: ATC’s 138kV lines and the Park Hill substation have been identified as impacted by the roadway construction in all WisDOT alternatives and will require relocation between the end of Calvary Cemetery and the 28th Street Substation to maintain the transmission network and distribution interconnections. Final transmission line routing and substation site selection to be determined through project investigations and coordination. Asset Renewal Rebuild of Structures 4145-4149: Install structures, OPGW/static, and new conductors. Communications: Install fiber communications between 96th Street Substation to structure 4145 and from the new substation location for the WisDOT road move to Valley Substation. | WI | Other | Age and Condition | Relocation / Age, Condition and Performance |  |  |  | 2026-12-31 | 138 | 0 | 63700000
MTEP22 | West | American Transmission Co. LLC | 23520 | Johnstown SS, DIC, New Substation | DIC, New Substation | WI | Other | Load Growth | Other - Load Interconnection |  |  |  | 2024-05-01 | 69 | 0 | 3000000
MTEP22 | West | American Transmission Co. LLC | 23531 | Cottonwood - Summit Underground Fiber | This project will establish a fiber link between the Cottonwood to Summit substations, which will enhance communications resiliency by interconnecting into ATC’s larger substation fiber network infrastructure at Summit. | WI | Other | Other Local Needs | Other - Communication |  |  |  | 2024-12-31 | 138 | 0 | 3156228
MTEP22 | Central | Ameren Services Company | 20905 | New Mulligan Solar (J1102) at Fogarty | Provide interconnection facilities for J1102 70 MW solar farm to connect at Fogarty. Reroute HOWL-FGTY-1417 to position H4 and install metering on position H2 for the customer to connect at. | IL | GIP |  | This project provides an interconnection point for J1102 to connect at to supply power they generate to MISO customers. |  |  |  | 2021-12-01 | 138 | 0 | 500000
MTEP22 | Central | Ameren Services Company | 21005 | New Ina 138 kV line breaker | Add a line breaker on the Benton NW terminal at Ina. | IL | Other | Reliability | Increased reliability. Adding this line breaker would eliminate a XFMR outage when there is a line outage on the Benton NW-Ina line. |  |  |  | 2023-06-01 | 138 | 0 | 850000
MTEP22 | Central | Ameren Services Company | 21306 | New Whitetail 138 kV Substation | Ameren would construct a new 138 kV substation ring bus configuration on the existing Ameren Monument-Macomb West-1646 138 kV line near structure 97. PPI would construct a 138 kV line to connect their Golden 138/69 kV step down station. This is in support of PPI Interconnection. | IL | Other | Load Growth | Customer interconnection |  |  |  | 2024-12-01 | 138 | 0 | 8000000
MTEP22 | Central | Ameren Services Company | 21326 | New Duff 138 kV Substation | 3-position initial, 4 ultimate ringbus on the Ipava-Meredosia E-1568 138 kV line for PPI Indian Creek 138/69kV substation. This is in support of a PPI Interconnection. | IL | Other | Load Growth | Customer interconnection |  |  |  | 2023-12-01 | 138 | 0 | 8000000
MTEP22 | Central | Ameren Services Company | 21365 | New Puro 138 kV Substation POI (J1453) | J1453 Moraine Sands Wind generator 188.3 MW Interconnection: Install Puro ring bus on Havana-Shockey 138 kV line | IL | GIP |  | Generator interconnection |  |  |  | 2023-06-01 | 138 | 0 | 7200000
MTEP22 | Central | Ameren Services Company | 21385 | Rebuild Austin-Taylorville South 138 kV line (1545) | Rebuild Austin-Taylorville South 138 kV line (1545) | IL | Other | Age and Condition | Aging infrastructure. Initial project to replace shield wire was changed to total rebuild due to condition of structures. |  |  |  | 2023-12-01 | 138 | 0 | 8900000
MTEP22 | Central | Ameren Services Company | 21386 | Rebuild Ruby-Sidney 345 kV line (4560) | Rebuild Ruby-Sidney 345 kV line (4560) | IL | Other | Age and Condition | System repair and maintenance. Initial project to replace insulators was changed to partial rebuild due to condition of structures. |  |  |  | 2023-12-01 | 345 | 0 | 2200000
MTEP22 | Central | Ameren Services Company | 21405 | Rebuild Mattoon East-Charleston NE 138 kV line | Rebuild this line due to the condition of the structures, will add OPGW as part of this. This is the Mattoon East to Charleston NE section of the KANW-MTE8-1 line. | IL | Other | Age and Condition | Age and condition. Maintains the reliability of the Transmission system. |  |  |  | 2023-06-01 | 138 | 0 | 3400000
MTEP22 | Central | Ameren Services Company | 21406 | Rebuild Sparta Tap 138 kV radial line | Rebuild Sparta Tap on the Tibbs-Sparta-1723 138 kV line due to issues found during inspections. | IL | Other | Age and Condition | Age and condition. Maintain the reliability of the Transmission system. |  |  |  | 2023-12-01 | 138 | 0 | 2300000
MTEP22 | Central | Ameren Services Company | 21426 | Reconductor S. Bloomington-W. Washington 138 kV lines (1334 & 1544) | Replace 3.5 miles and 3.48 miles of 477 KCMIL ACSR/T2 30/7 Hen 138 kV line conductor in SBLM-WWSH-1334 and in SBLM-WWSH-1544with a new line conductor having a minimum summer emergency rating of 2000 Amps, respectively. | IL | Other | Load Growth | Customer load |  |  |  | 2022-12-01 | 138 | 0 | 4200000
MTEP22 | Central | Ameren Services Company | 21428 | Rebuild Tanner-Xenia 345 kV line | Rebuild the existing Newton-Xenia-1 345 kV line from Xenia-Str. 44. New conductor will be capable of 3000 A and 2 OPGW shield wires will be installed. | IL | Other | Reliability | Increased reliability. Age and condition. |  |  |  | 2022-12-15 | 345 | 0 | 9100000
MTEP22 | Central | Ameren Services Company | 21645 | New Prairie Solar (J1139) Interconnection at Sidney 138kV | One 138 kV terminal in the Sidney Substation. The terminal will consist of all necessary terminal equipment to connect the J1139 leadline to the Sidney Substation 138 kV bus. | IL | GIP |  | Generator interconnection |  |  |  | 2023-06-01 | 138 | 0 | 500000
MTEP22 | Central | Ameren Services Company | 21646 | Rebuild Sullivan-Casey West 345 kV line | Rebuild the Sullivan-Casey West 345 kV line with conductors capable of 3000 amps Summer Emergency rating and two OPGWs. | IL | Other | Reliability | Increased reliability. Project upgrades the line to structures that meet Ameren's current loading requirements, hardening the circuit against storms and improving resiliency against cascade failure |  |  |  | 2023-12-01 | 345 | 0 | 36100000
MTEP22 | Central | Ameren Services Company | 21647 | Rebuild Casey West-Kansas 345 kV line (4525) | Rebuild the Casey West-Kansas 345 kV line (4525) with conductors capable of 3000 amps Summer Emergency rating and two OPGWs. | IL | Other | Age and Condition | Project upgrades the line to structures that meet Ameren's current loading requirements, hardening the circuit against storms and improving resiliency against cascade failure |  |  |  | 2024-12-01 | 345 | 0 | 25200000
MTEP22 | Central | Ameren Services Company | 21970 | Reconductor Kinmundy-Tanner 138 kV | Reconductor 27.4 miles Kinmundy-Tanner 138 kV line | IL | Other | Reliability | Increased reliability to meet LPC |  |  |  | 2026-06-01 | 138 | 0 | 10000000
MTEP22 | Central | Ameren Services Company | 22325 | New Mogul 345 kV Ring Bus for J1464 | Construct a new 345 kV switching station in Sangamon, Macoupin & Morgan Counties, Illinois to provide a Point of Interconnection for the Generating Facility. The new 345kV Mogul switching station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Austin – Turner 345 kV transmission line and terminate the ends at two of the terminal positions. | IL | GIP |  | Generator interconnection |  |  |  | 2023-10-31 | 345 | 0 | 10300000
MTEP22 | Central | Ameren Services Company | 22385 | New Dion 345 kV Ring Bus for J1115 Greenswitch Wind | The Dion switching station will be a ring bus arrangement with three-line terminal positions and provisions for one additional future terminal position. The existing Latham-Oreana 345 kV transmission line will be cut. | IL | GIP |  | Generator Interconnection |  |  |  | 2024-06-01 | 345 | 0 | 10500000
MTEP22 | Central | Ameren Services Company | 22405 | Add J991 Monarch Solar at Xenia 345 kV | Add 345 kV terminal in the Xenia switching station for the J991 project. | IL | GIP |  | Generator Interconnection |  |  |  | 2023-06-01 | 345 | 0 | 1000000
MTEP22 | Central | Ameren Services Company | 22407 | Add J974 Fulton Wind at MapleRidge 345 kV | Add position to the existing Mapleridge 345 kV switching station for J974 interconnection facilities. | IL | GIP |  | Generator Interconnection |  |  |  | 2023-06-01 | 345 | 0 | 2242000
MTEP22 | Central | Ameren Services Company | 22485 | Add J1094 Tilden Solar at Prest 138 kV | Expand and convert the Prest switching station 138 kV bus from a 6-position ring to a 4-leg breaker and a half (BAAH) configuration to add J1094 Tilden Solar | IL | GIP |  | Generator Interconnection |  |  |  | 2024-01-01 | 138 | 0 | 8520000
MTEP22 | Central | Ameren Services Company | 22566 | New Morganfield 138 kV Ring Bus for J1096 Eldorado Solar | Construct a new 138 kV switching station in Saline County, Illinois to provide a Point of Interconnection for the Generating Facility. The new Morganfield 138 kV J1096 Interconnection Switching Station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Muddy-Norris City North 138 kV transmission line. | IL | GIP |  | Generator Interconnection |  |  |  | 2024-01-01 | 138 | 0 | 6519000
MTEP22 | Central | Ameren Services Company | 18063 | New Mt. Pleasant 345 kV substation | Placeholder | IA | Other | Load Growth | Customer-Driver Request |  |  |  | 2025-12-01 | 345 | 0 | 2600000
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21931 | New Crosstown 69/12 kV Substation | Crosstown 69/12kV Substation Build between Park Tap and Altenburg 69kV substation (Citizens project). | MO | Other | Reliability | Crosstown Substation is needed to help relieve loading on Altenburg, McBride, and Park Substations which are forecast to exceed their OA rating. |  |  |  | 2021-06-01 | 69 | 12 | 800000
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21948 | Upgrade New Bourbon bus tie breaker (B40) | Replace B40 bus tie breaker. | MO | Other | Age and Condition | Replace B40 bus tie breaker that had several issues at New Bourbon. Had trouble while they were operating the breaker to put the station back in service after maintenance. |  |  |  | 2022-05-31 | 69 | 0 | 381780
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21949 | Rebuild T2B 34.5 kV line | Rebuild 34 kV line that feeds the Mosher B,C,&F plants and the Geneva switching station. This includes most of the switches in the line section. | MO | Other | Age and Condition | T2B 34.5 kV line old and in bad shape. |  |  |  | 2024-03-31 | 34.5 | 0 | 4558281
MTEP22 | Central | Ameren Services Company | 21967 | New Dillon 138 kV Capacitor Bank (14 Mvar) | Add a 14 Mvar capacitor bank at Dillon with a separate breaker. The existing 28 Mvar bank will be reduced to 14 Mvar. | MO | BRP |  | This will ensure the entire bank isn't outaged for the one P14 event. This project will also reduce the voltage fluctuations caused by the existing 28 Mvar cap bank. |  |  |  | 2023-06-01 | 138 | 0 | 500000
MTEP22 | Central | Ameren Services Company | 21971 | Upgrade Callaway 345 kV Substation | Add breakers on the high side of safeguard transformer A and B at Callaway 345 kV substation | MO | BRP |  | Generator stability |  |  |  | 2023-06-01 | 345 | 0 | 3000000
MTEP22 | Central | Ameren Services Company | 22365 | New Adna 345 kV Ring Bus for J1107 Lutesville Solar | The Adna switching station will be a ring bus arrangement with three-line terminal positions and provisions for one additional future terminal position. The existing Kelso-Lutesville 345 kV transmission line will be cut. | MO | GIP |  | Generator Interconnection |  |  |  | 2023-11-01 | 345 | 0 | 10837000
MTEP22 | Central | Ameren Services Company | 22406 | Add J994 Guthrie Solar at Guthrie 161 kV | Add 161 kV terminal in the Guthrie substation for J994 project. | MO | GIP |  | Generator Interconnection |  |  |  | 2023-06-01 | 161 | 0 | 1658000
MTEP22 | Central | Ameren Services Company | 22408 | Add J987 Warren Solar at Montgomery 161 kV | Add 161 kV terminal in the Montgomery substation for the J987 | MO | GIP |  | Generator Interconnection |  |  |  | 2023-06-01 | 345 | 161 | 2060000
MTEP22 | Central | Ameren Services Company | 22465 | New Bullion 161 kV Ring Bus for J1087 Kelso Solar | Construct a new 161 kV switching station in Scott County, Missouri to provide a Point of Interconnection for the Generating Facility. The new 161 kV Bullion switching station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Kelso – Miner 161 kV transmission line. | MO | GIP |  | Generator Interconnection |  |  |  | 2024-03-31 | 161 | 0 | 9189000
MTEP22 | Central | Ameren Services Company | 22527 | New Harley 161 kV Ring Bus for J1268 Winfield Solar | Build a 161 kV three position ring bus along the Troy-Pike 161 kV transmission line in Lincoln County, Missouri. This is for Winfield Solar J1268. | MO | GIP |  | Generator Interconnection |  |  |  | 2023-06-01 | 161 | 0 | 10652000
MTEP22 | Central | Ameren Services Company | 22529 | New Vanduser 161 kV Ring Bus for J1034 Ringer Solar | Construct a new 161 kV switching station in Stoddard County, Missouri to provide a Point of Interconnection for the Generating Facility. The new Vanduser 161 kV J1034 Interconnection Switching Station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Morley – Stoddard 161 kV transmission line | MO | GIP |  | Generator Interconnection |  |  |  | 2024-06-01 | 161 | 0 | 6730000
MTEP22 | Central | Ameren Services Company | 22546 | New Rootbeer 345 kV Ring Bus for J976 Split Rail Solar | Construct a new 345 kV switching station in Warren County, Missouri to provide a Point of Interconnection for the Generating Facility. The new Rootbeer 345 kV J976 Interconnection Switching Station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Belleau – Montgomery 345 kV transmission line. | MO | GIP |  | Generator interconnection |  |  |  | 2025-12-01 | 345 | 0 | 10801000
MTEP22 | Central | Ameren Services Company | 22786 | New Wildwood 345/138 kV Transformer No 2 | Upgrade 560 MVA TX to a 700 MVA 345/138 kV Transformer | MO | GIP |  | The larger 345/138kV transformer is needed for system reinforcement upon Rush Island Plant Retirement. |  |  |  | 2024-06-01 | 345 | 138 | 17500000
MTEP22 | Central | Ameren Services Company | 22807 | New Overton 161 kV Capacitor Bank | New 67 MVAR Capacitor at Overton 161 kV | MO | GIP |  | The 345 kV Capacitor Bank is needed for system reinforcement upon the Rush Island Plant Retirement. |  |  |  | 2024-04-01 | 161 | 0
MTEP22 | Central | Ameren Services Company | 22808 | New Rush Island Area Statcoms | Add 250 MVAR Statcom at Bugle, Arnold, Mason and Highway N substations. | MO | GIP |  | The Statcom is needed for system reinforcement due to the Rush Island Plant Retirement. |  |  |  | 2024-12-01 | 161 | 0 | 120000000
MTEP22 | Central | Big Rivers Electric Corporation | 20766 | New Easton Rd 69 kV line | Add 1 mile tap line to serve new distribution substation | KY | Other | Load Growth | The distribution cooperative is constructing a new delivery point to serve member load. |  |  |  | 2022-02-01 | 69 | 0 | 500000
MTEP22 | Central | Big Rivers Electric Corporation | 21685 | New Pratt Paper Load Addition | Conversion of existing switching structure into a switching station and construction of a 8 mile radial transmission line to serve new industrial load. | KY | Other | Load Growth | Conversion of existing switching structure into a switching station and construction of a 8 mile radial transmission line to serve new industrial load. | Paper Mill |  | 30-60 | 2023-07-01 | 161 | 0 | 20200000 | Pratt Paper mill load 30MW (expandable 60MW). 8 mi radial 161kV line (BREC, KY)
MTEP22 | Central | Big Rivers Electric Corporation | 22766 | Replace McCracken-Shell Structure | Raise or replace existing line structures to provide necessary ground clearance. | KY | Other | Reliability | Existing structures are not tall enough to provide needed design clearance. |  |  |  | 2022-10-01 | 69 | 0 | 1500000
MTEP22 | South | Cleco Power LLC | 20163 | Many Area Transmission Expansion | Tap the existing Fisher to Mansfield Compressor 230 kV line 8.3 miles from Fisher. From the Tap point build two new new 2.8 mile 230 kV lines to a new substation (Belmont) tapped into the Pelican to Loring and Loring to Many 138 kV lines. At Belmont substation add a 230/138 kV 300 MVA Auto. | LA | BRP |  | In 2025 a P6 contingency on Many to Fisher 138 kV line followed by a contingency on Carroll to Red River 138 kV line causes an overload greater than 125 % on South Shreveport to Wallace lake 138 kV line. Also voltage violation exist for this contingency. Load shed is the only mitigation for this P6 contingency. With projected industrial load growth in this area this project has been modified to account for the additional load. The original alternative is in the Alternative notes. | Large Industrial (BRP) |  |  | 2025-06-01 | 230 | 138 | 38100000 | BRP driven by projected industrial load growth
MTEP22 | South | Cleco Power LLC | 22205 | Cole Substation | Tap the existing Cooper to Penton 230 kV line 2.4 miles from Cooper and build a new substation (Cole) | LA | Other | Load Growth | This new substation is needed to serve a new industrial customer. |  |  |  | 2023-03-27 | 230 | 0 | 18764954
MTEP22 | South | Cleco Power LLC | 23327 | Marthaville Substation | New load substation tapping the Fisher to Mansfield Compressor 230 kV line | LA | Other | Load Growth | New industrial load |  |  |  | 2023-04-23 | 230 | 0 | 15697000
MTEP22 | South | Cleco Power LLC | 23328 | Vernon Substation | Adding new load substation by tapping the Toledo to Leesville 138 kV line | LA | Other | Load Growth | New industrial load |  |  |  | 2023-04-23 | 138 | 0 | 13650000
MTEP22 | West | Central Minnesota Municipal Power Agency | 21973 | Blue Earth Light and Water- Rice Street Transformer Replacement | Blue Earth Light and Water has a Rice Street sub which carries a 10/14 MVA 69/12.47 kV Transformer. The transformer is showing signs of age as it is 28 years old and needs to be replaced because of potential load growth. | MN | Other | Age and Condition | The Rice street transformer is showing signs of age which is 28 years old and needs tp be replaced. Rice Street carries almost 60% of BELW load. |  |  |  | 2022-05-02 | 69 | 0 | 1250000 | Age & Condition with load growth component
MTEP22 | West | Central Minnesota Municipal Power Agency | 21974 | Blue Earth Light and Water- West Sub Transformer Replacement | Blue Earth Light and Water West Sub Transformer replacement. | MN | Other | Age and Condition | Blue Earth Light and Water has a West sub which carries a 10/14 MVA 69/12.47 kV Transformer. The transformer is showing signs of age as it is 32 years old and needs to be replaced because of potential load growth. |  |  |  | 2022-05-02 | 69 | 0 | 1500000
MTEP22 | West | Central Minnesota Municipal Power Agency | 21975 | Blue Earth Light and Water- New Northeast 69/12.47 kV Sub | Build a new North East 69/12.47kV substation and self-supporting steel pole with 69kV 3-way switch. | MN | Other | Reliability | Following a PSS/E AC Contingency Calculation (ACCC) analysis of the Blue Earth Light & Water (BELW) transmission system, numerous voltage violations (< 0.93 per unit) were noted on BELW facilities as a result of a few different contingencies. The analysis included various load and generation forecasts, and these violations were noted in several years and seasons. The Rice St. and West 69/12.47kV substations do not have enough capacity to add additional load growth in the city. With a potential 3.5 MW approximately new load scheduled to come online, there is a need to build a new North East 69/12.47kV substation to accommodate load growth, load transfers, support transmission system voltage, and add reliability to the BELW transmission and distribution systems. The new substation would connect to the existing 69kV transmission system via a 3-way switch and would be designed to include room for future In/Out circuit breakers. |  |  |  | 2023-01-16 | 69 | 0 | 4100000 | Reliability with load growth driver
MTEP22 | Central | Duke Energy Corporation | 2125 | Upgrade Centerton 138/69kV Bk 1 | Upgrade/replace existing 75MVA 138/69kV bank with 150MVA bank | IN | Other | Reliability | (N-1) A 69kv line outage from Bloomington to Martinsville S.E. Jct. causes an overload on the Centerton 138/69kv Bank (75MVA nameplate, hot spot 91.1MVA). The 138kv winding is 102% of the emergency or hot spot rating. |  |  |  | 2024-09-11 | 138 | 69 | 4010138
MTEP22 | Central | Duke Energy Corporation | 22185 | New J1063 Hardy Hills Solar | J1063 - Hardy Hills Solar | IN | GIP |  | J1063 - GIA |  |  |  | 2023-02-20 | 230 | 0.66 | 3617000
MTEP22 | Central | Duke Energy Corporation | 22206 | Replace Dresser 138kV Breaker | Replace (5) over-dutied Dresser CBs: (13869-9, 13869-10, 138B3-1, 138B3-2, 138138) with higher interruption capacity (63 KIAC rating) | IN | BRP |  | These CBs were identified in the 2021 short circuit study as being over-dutied during certain fault conditions. This is a NERC TPL 001-4 compliance requirement. |  |  |  | 2026-03-20 | 138 | 0 | 562153
MTEP22 | Central | Duke Energy Corporation | 22207 | New WVPA Hendricks Belle Union 138/12kV Distribution Sub | New 138/12 kV - 22.4MVA Belle Union substation for Hendricks Power to be constructed by WVPA. Substation 138kV - 13867 source to be looped through with SCADA controlled switches. | IN | Other | Load Growth | WVPA distribution load growth |  |  | 4 MVA | 2023-12-31 | 138 | 12 | 1408403
MTEP22 | Central | Duke Energy Corporation | 22208 | Rebuild Bedford to Mitchell Lehigh 138kV - 13822 Line | Bedford to Mitchell Lehigh 138kV - Rebuild 13822 line section with 954ACSR@120C; upgrade 1200A Wave trap at Bedford to 2000A; upgrade 954AL bus at Bedford to 1590AL | IN | BRP |  | MTEP21 results show line overload for multiple Cat. P6 pairings; interim operating mitigation to reduce Gibson/Petersburg station gens by 500MWs; if necessary, load shed up to 40MWs from bus 249932 (proposed new load in MTEP19) |  |  |  | 2027-06-01 | 138 | 0 | 17960000 | BRP with new load driver
MTEP22 | Central | Duke Energy Corporation | 22209 | Upgrade Columbus 13830 Line Terminal | Columbus 13830 line terminal: upgrade 300CU bus to 954AL to increase facility rating to 178MVA (line conductor rating) ; P6 - 13828 + 13829 ckts; Relay loadability ok as-is | IN | BRP |  | MTEP21 results show overload of the Columbus 13830 line terminal: P6 - 13828 + 13829 ckts |  |  |  | 2027-06-01 | 138 | 0 | 500000
MTEP22 | Central | Duke Energy Corporation | 22210 | Rebuild Collamer Jct to N.Manchester 69kV (6923) Line | Collamer Jct to N.Manchester 6923 (Pt2) Rebuild with 477ACSR@120C | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2023-05-19 | 69 | 0 | 7300000
MTEP22 | Central | Duke Energy Corporation | 22211 | Rebuild and Reconfigure Huntington 138kV Sub | Huntington 138kV Sub rebuild and reconfigure: establish 4-position 138kV ring bus; replace (2)138/69/12 xfmrs with (2)50MVA 138/69 xfmrs and (1)22.4MVA 138/12 xfmr; establish 4-position 69kV ring bus | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2024-07-19 | 138 | 69 | 28444000
MTEP22 | Central | Duke Energy Corporation | 22212 | Rebuild Morgantown to Samaria Jct 69kV Line | Rebuild 6949 Line from Morgantown to Samaria Jct; 3.63 miles; 954ACSR@120C | IN | Other | Load Growth | Transmission Planning identified contingency overload due to Load Growth; Contingency: Bloomington 230 to Needmore Jct. 6949 Line Outage |  |  |  | 2023-05-01 | 69 | 0 | 2901158
MTEP22 | Central | Duke Energy Corporation | 22213 | Replace Dresser 69kV - 6901 Tower | Dresser 69kV - 6901 Tower Replacements - Replace 1.25 miles of steel lattice towers - six total (802-1012 to 802-1007, including the Wabash River crossing) | IN | Other | Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with Indiana Utility Regulatory Commission. |  |  |  | 2023-07-28 | 69 | 0 | 4780000
MTEP22 | Central | Duke Energy Corporation | 22226 | New Wabash River Station 345kV-230kV Substation | Wabash River Station 345kV-230kV Substation: (1) Add Sandford 345kV 3-CB ring bus in the 34513 Cayuga - Sugar Crk line; (2) build 5.5 mile 345kV - 34556 line to Wabash River Station; (3) add 345/230 xfmr(s) at Wabash River Station | IN | BRP |  | Past MTEP results have shown multiple line and xfmr overloads for multiple categories of TPL contingencies that have been addressed using short term ratings and operating mitigations that are no longer deemed acceptable for the long term. This project would bring a 345kV source into Wabash River Station that would act as a balancing force to the Dresser 345kV source and dramatically reduce contingency flows through the Terre Haute area's 138kV and 230kV systems. |  |  |  | 2026-10-22 | 345 | 230 | 50000000
MTEP22 | Central | Duke Energy Corporation | 22227 | Staunton 230-138kV Xfmr Addition | Staunton sub: add a third parallel 230/138kV transformer | IN | BRP |  | Past MTEP P6 OL of Staunton Bk1 or Bk2 flo 13861 Dresser to Staunton line coupled with the loss of one of the Staunton 230/138 banks - somewhat exacerbated by Wabash River 345/230 project. Interim operating mitigation: open circuit breaker 13801 at Cloverdale (open branch 249708,249731,1). |  |  |  | 2026-12-31 | 230 | 138 | 6000000
MTEP22 | Central | Duke Energy Corporation | 22230 | Upgrade Gibson 34509 Line Terminal | Gibson 345 Switchyard 34509 Line Terminal Upgrades: M210313 - (for Ameren Albion ring bus project) WT / Relays replacement; M210371 - replace (2)345kV CBs, free-standing CTs, and disconnect switches | IN | Other | Age and Condition | M210313 - required for Ameren Albion ring bus project (100% reimbursable); M210371 - CBs, CTs, and Disconnect Switches identified for replacement by Asset Mgmt based on age and condition |  |  |  | 2023-05-01 | 345 | 0 | 2950051
MTEP22 | Central | Duke Energy Corporation | 22245 | Improve 23008 Tipton W-Cammack Rd Line | Noblesville to Tipton West 23008 ckt: reinsulate and implement anti-gallop line conductor modifications | IN | Other | Reliability | TDSIC 2.0 - The assets being addressed in this project fall under one or more of the system programs as outlined in the TDSIC Plan filed with and approved by the Indiana Utility Regulatory Commission. This line has been identified by Duke's R&I Planning group as having an unacceptable outage rate due to faulty insulators and galloping issues. |  |  |  | 2026-11-30 | 230 | 0 | 4716099
MTEP22 | Central | Duke Energy Corporation | 22246 | New IMPA Frankfort 300W 69/12kV Distribution Substation | IMPA Frankfort 300W 69/12kV Distribution Substation | IN | Other | Load Growth | Distribution load growth: wholesale obligation to serve load via IMPA for Frankfort Municipal |  |  |  | 2023-06-01 | 69 | 12 | 5018000
MTEP22 | Central | Duke Energy Corporation | 22265 | Rebuild Purdue NW Tap to Cincinnati St. 138kV - 13820 Line | Rebuild the 13820 line from Purdue NW Tap to Cincinnati St. using 954 ACSR at 120 C | IN | BRP |  | This project is being proposed as a replacement for project 20230 with an additional line section added to the scope and increased costs per the latest Eng'g estimates. With the new West Lafayette Airport sub getting placed in-service on the 13820 line between the Purdue Northwest Tap and West Lafayette Purdue subs, when there is a breaker failure that takes out bus 2 at Westwood, the line segments from the Purdue Northwest Tap to West Lafayette Airport to Purdue to Cincinnati St. are loaded to 99.7% or higher per the MTEP21 - 2023 sum peak _AA model. |  |  |  | 2023-12-31 | 138 | 0 | 45000000
MTEP22 | Central | Duke Energy Corporation | 22425 | New West Lafayette Substation | West Lafayette New Customer: construct 345kV and 138kV facilities to serve new proposed industrial load of approximately 353MVA | IN | Other | Load Growth | New Customer load of 300MW/186MVAR with capacity factor of 50% |  |  | 300 | 2024-12-27 | 345 | 138 | 100000000
MTEP22 | West | Dairyland Power Cooperative | 22531 | Bell Center-Lancaster N6 Rebuild | This project is a rebuild of DPC's existing 69 kV line (N6) connecting the Bell Center and Lancaster transmission substations. The recommended plan is to rebuild 40.51 miles of new 69 kV transmission line on existing right-of-way with 477 ACSR conductor. The recommended plan will address the age and condition issues, constructing the line with new poles and new 477 ACSR conductor. | WI | Other | Age and Condition | DPC’s transmission line in this area was constructed in 1948 and has age and condition issues. |  |  |  | 2025-10-15 | 69 | 0 | 23877825.37
MTEP22 | South | Arkansas Electric Coopertive Corporation | 21565 | Ward Breaker Additions | Install five (5) breakers, one of which will be a transfer breaker, at AECC's Ward 115kV Switching Station. | AR | Other | Reliability | Reliability issues with serving the Ward load. |  |  |  | 2023-12-01 | 115 | 0 | 3000000
MTEP22 | South | Entergy Arkansas | 21805 | 2023 EAL Asset Renewal Program | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. | AR | Other | Age and Condition | The program is needed to replace or repair aging or failing transmission assets across EAL's territory. |  |  |  | 2023-12-31 | 115 | 0 | 28500000
MTEP22 | South | Entergy Arkansas | 21806 | Junction City 115kV: Upgrade CT's | This project will upgrade the existing 600 amp CT's at Junction City to >1000 amps. | AR | Other | Reliability | The CT's at Junction City 115kV is limiting the line section rating and is prohibiting the use of temperature adjusted ratings. This upgrade also mitigates a cascading event during a NERC TPL extreme event. |  |  |  | 2023-12-30 | 115 | 0 | 1415000
MTEP22 | South | Entergy Arkansas | 22530 | Sandy Bayou 500/230kV: New substation | Construct a new 500/230kV substation to serve a new industrial customer. The substation will consist of a 4 breaker 500kV ring bus, two 500/230kV autotransformer banks (7 single-phase 250 MVA units that includes one spare), a two bay breaker and a half 230kV bus with two 230kV sources to the customer. This new substation will be cut into the existing Driver - Shelby 500kV transmission line. | AR | Other | Load Growth | This project is needed to serve a new industrial customer locating in Mississippi county, AR near the Driver - Shelby 500kV transmission line. | Large Industrial |  | 250 MVA | 2024-03-01 | 500 | 230 | 122000000 | EAL $122M; massive industrial customer
MTEP22 | South | Entergy Arkansas | 23154 | Keo 500kV: Expansion for J1258 & J1415 | The KEO 500kV substation will be expanded to interconnect the J1258/J1415 gen-tie 500kV line. The Network Upgrades include a new 500 kV gas circuit breaker, two new 500 kV disconnect switches, relay panels, revising the station RTU configuration, wiring additions to the DFR, and telecommunication additions. | AR | GIP |  | The project is needed to interconnect GIA Projects J1258 and J1415. |  |  |  | 2024-10-15 | 500 | 0 | 8888000
MTEP22 | South | Entergy Arkansas | 23267 | Fountain Hill 115kV: J1281 Cut In Switching Station | Entergy will provide oversight for the construction of the transmission owners interconnection facilities and stand alone network upgrades associated with the interconnection of J1281 on the Crossett - Monticello East 115kV line. The Crossett North 115kV substation will have new line protection installed. The Monticello East 115kV substation will have new line protection installed alond with new CCVT's and a new breaker. | AR | GIP |  | This transmission cut in is needed to interconnect the 75 MW solar project (J1281) per the executed GIA. |  |  |  | 2024-10-31 | 115 | 0 | 3796000
MTEP22 | South | Entergy Arkansas | 23326 | Sunset 230kV: J1215 New Switching Station Cut-In | A new 230kV three breaker ring bus substation will be cut-in to the Woodward - Stuttgart Ricuskey 230kV transmission line. Remote end upgrades will be performed at Stuttgart Ricuskey and Woodward substations. Approximately 2.6 miles of OPGW fiber will be installed between Stuttgart Ricuskey and the new J1215 stations. 230kV Circuit breakers B8414 and B8406 will be replaced at Stuttgart Ricuskey. | AR | GIP |  | This new switching station and remote end upgrades are needed to interconnect J1215 as per the executed generator interconnection agreement. |  |  |  | 2025-02-15 | 230 | 0 | 14695000
MTEP22 | South | Entergy | 13910 | Calhoun: New distribution substation | Construct a 230 kV distribution substation named Calhoun in western Ouachita parish near the town of Calhoun and construct a 230 kV transmission line from the new substation that terminates into the Cadeville substation. | LA | Other | Load Growth | Area distribution load |  |  |  | 2026-06-01 | 230 | 0 | 56800000
MTEP22 | South | Entergy | 21808 | 2023 ENOL Asset Renewal Program | This project is for the ENOL Asset Renewal Program that will be executed in 2023. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. | LA | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | 2023-12-31 | 230 | 69 | 1900000
MTEP22 | South | Entergy | 21809 | 2023 ELL Asset Renewal Program | This project is for the ELL Asset Renewal Program that will be executed in 2023. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. | LA | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | 2023-12-31 | 500 | 69 | 55100000
MTEP22 | South | Entergy | 21811 | Richard 500-138 kV AT1 Relay Improvement SPOF | Ensure the Richard 500-138 kV autotransformer #1 has redundant high-speed protection with independent CT and PT windings. | LA | BRP |  | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. P5 contingency SLG fault on the Richard 500 kV bus with non-redundant relay failure for the Richard 500/138 kV auto #1 protection has the potential to cause 600MW of generation to trip. |  |  |  | 2024-12-31 | 500 | 138 | 10270000
MTEP22 | South | Entergy | 21816 | Drusilla to Jefferson 69 kV: Upgrade Switches | Upgrade switches 9716 and 9717 at Jefferson 69 kV station to 1200 Amps. Upgrade switch 4474 at East 69 kV station to 1200 Amps. Upgrade any remaining terminal equipment to achieve a rating of 1200 Amps on the Drusilla to Jefferson to East 69 kV path. | LA | Other | Reliability | Entergy’s Planning Guidelines. The P2.1 loss of Essen Tap to Tiger 69 kV will overload from Drusilla to Jefferson 69kV line. |  |  |  | 2023-06-01 | 69 | 0 | 2742000
MTEP22 | South | Entergy | 21822 | Hartburg to Rhodes 500 kV River Crossing Tower Replacement | Replace the existing structure with a new structure that will be installed further to the east to avoid future washing out. Access to the structure is especially difficult and will require extensive matting and/or the use of specialized marsh equipment. | LA | Other | Age and Condition | The Sabine River Louisiana side crossing structure (Structure 133) for the Hartburg – Rhodes 500kV line is being washed out by the progression of the Sabine River eastward. |  |  |  | 2023-08-31 | 500 | 0 | 5790000
MTEP22 | South | Entergy | 21832 | Dow Meter to Tiger 230 kV Re-Termination project | Re-terminate the Addis to Tiger and Dow Meter to Addis 230 kV lines to create the Dow Meter to Tiger 230 kV line, which will bypass the Addis 230 kV station. | LA | BRP |  | The 2018 MISO Deliverability study shows an overload on the Addis to Tiger 230 kV line for the P1.2 loss of the Dow Meter to Chenango 230 kV or the Richardson to Iberville 230 kV line in 2023. This project replaces project 15566, which was shown to be ineffective in mitigating deliverability constraints in the area. |  |  |  | 2024-06-01 | 230 | 0 | 5700000
MTEP22 | South | Entergy | 21835 | Kaiser 230-115 kV Autotransformer | Install 300 MVA, 230/115kV Autotransformer to tie Kaiser 230 kV to Conquest 115 kV. Kaiser and Conquest stations are adjacent to each other. Remove Behrman to Pt Nickel 115 kV line from the model. This facility includes an under the Mississippi River section that has failed. The Kaiser Auto alleviates some of the potential radial concerns during outages with this line removed. | LA | Other | Reliability | Enhanced Reliability. P6 Loss of Peters Road-Behrman 230kV and Munster-Oaks 230kV overloads Gretna-Behrman 115kV. This project also alleviates potential radial concerns and higher loadings for the P6 with the Behrman to Port Nickel 115 kV line removal. |  |  |  | 2024-12-01 | 230 | 115 | 26320000
MTEP22 | South | Entergy | 23147 | J1219/J1257 115 kV station(Hickory) | Construct a 115 kV substation between the existing Amite and Chicken Farm 115 kV stations | LA | GIP |  | This station is being constructed to accommodate the interconnection of a solar facility (J1219/1257) |  |  |  | 2024-09-24 | 115 | 0 | 14390000
MTEP22 | South | Entergy | 23308 | J1246 Bayou Labutte 500 kV Interconnection | The Bayou Labutte 500kV substation will be expanded to interconnect the J1246 gen-tie 500kV line. The Network Upgrades include relocation of the Willow Glen 500 kV line position, new 500 kV gas circuit breaker, two new 500 kV disconnect switches, along with other additional station equipment and upgrades at Bayou Labutte. Also Included in the network upgrades for J1246 are the replacement of two 230 kV breakers at the Point Pleasant 230 kV station to 63 kA IPO breakers along with relay upgrades for the associated equipment. | LA | GIP |  | The project is needed to interconnect GIA Project J1246. |  |  |  | 2024-06-01 | 500 | 0 | 14344000
MTEP22 | South | Entergy | 23330 | Rilla 115 kV: Expand Station (J1239) | The Rilla 115 kV station will be expanded to interconnect J1239. | LA | GIP |  | This project is needed to facilitate the interconnection of J1239 100 MW solar generating facility. |  |  |  | 2024-10-15 | 115 | 0 | 7233000
MTEP22 | South | Entergy | 23386 | MPFCA J1281, J1294, J1458 Adams Creek 230 kV and Bogalusa 500-230 kV Upgrades | MPFCA J1281, J1294, J1458 Adams Creek 230 kV and Bogalusa 500-230 kV Upgrades. Replace breakers S4402/S4405 and switches at Adams Creek 230 kV with 4000 Amp equipment. Upgrade bus at Bogalusa 500-230 kV and install slipover current transformers on 230 kV bushings of existing 500-230 kV autotransformers. These upgrades will increase the rating of the circuit between the Adams Creek 230 kV station and the Bogalusa 500-230 kV station to 1281 MVA. | LA | GIP |  | Identified by MISO as required for GIA J1281, J1294, J1458. |  |  |  | 2024-04-04 | 230 | 0 | 3990000
MTEP22 | South | Entergy | 23421 | J1368/J1372 Interconnection: Ventress 230 kV Station | Construct a new Ventress 230 kV substation between the existing Fancy Point and Waterloo 230 kV stations. | LA | GIP |  | This station is being constructed to accommodate the interconnection of a solar facility (J1368/1372) |  |  |  | 2023-04-21 | 230 | 0 | 5354000
MTEP22 | South | Entergy Mississippi | 20063 | Choctaw - TVA French Camp 500 kV: Decommission Line | Decommission and demolish the existing Choctaw-TVA French Camp 500kV line that was recently acquired by Entergy in November of 2019 (~0.75mi). | MS | Other | Reliability | Enhanced Reliability. The current TVA interconnection for the Choctaw power station creates some operational issues that would be removed if the interconnection was terminated. |  |  |  | 2024-12-15 | 500 | 0 | 500000
MTEP22 | South | Entergy Mississippi | 20064 | Choctaw - Wolf Creek 500 kV: Build New Line | Utilize ~0.1mi of existing Choctaw-French Camp 500kV line to tie into Wolf Creek (Choctaw – French Camp 500 kV decommissioned with a separate project). Convert Wolf Creek 500kV switching yard to 4 breaker ring bus to accommodate 2nd line. | MS | Other | Reliability | Enhanced Reliability. Once the existing TVA interconnection is removed from the Choctaw switchyard, the plant will only have one tie to the BES through breaker CC80 into Wolf Creek 500 kV substation. Adding a second interconnection will prevent a single transmission outage from taking the Choctaw Power Station offline and enhance the operational flexibility for the plant. |  |  |  | 2024-12-15 | 500 | 0 | 7100000
MTEP22 | South | Entergy Mississippi | 21815 | 2023 EML Asset Renewal Program | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. | MS | Other | Age and Condition | The AM renewal asset program is to address aging and failing transmission assets across EML's territory. |  |  |  | 2023-12-31 | 500 | 0 | 56009600
MTEP22 | South | South Mississippi Electric Power Association | 22345 | East Winstonville Delivery Point | Tap the Energy owned Delta SES - Shelby 115kV line with switching station and build a 115kV line to the new member East Winstonville delivery point. | MS | Other | Load Growth | Member has requested a new load delivery point near Winstonville, MS. |  |  |  | 2024-07-01 | 115 | 0 | 1862800
MTEP22 | South | Entergy Mississippi | 23268 | Franklin - Ray Braswell 500 kV Upgrade - MPFCA | Multi-Party Facilities Construction Agreement for J1215, J1281, J1294, J1425, J1434, J1440, and J1458 to upgrade the Franklin 500 kV Substation: Replace four (4) 500 kV switches with motor operators, and one (1) 500 kV ground switch. | MS | GIP |  | This network upgrade project is needed to facilitate ERIS/NRIS of J1215, J1281, J1294, J1425, J1434, J1440, and J1458 generating facilities. |  |  |  | 2023-12-19 | 500 | 0 | 1739000
MTEP22 | South | Entergy Mississippi | 23387 | Gerald Andrus - Tinnin 230 kV Cut-in and Line Upgrade (J1458) | Generator Interconnection new Panther Burn 230 kV station on the Gerald Andrus - Tinnin 230 kV line and Network Upgrade rebuild of the Greenville - SE Greenville 115 kV line. | MS | GIP |  | This project is needed for interconnection and ERIS/NRIS as part of the J1458 generator interconnection agreement for the 200 MW solar facility. The NRIS will be limited to 170 MW until the completion of all Network Upgrades and Affected System Upgrades. |  |  |  | 2024-03-13 | 230 | 0 | 10425000
MTEP22 | South | Entergy Mississippi | 23482 | Isola - Belzoni 115 kV Upgrade - MPFCA | MPFCA. Belzoni 115 kV Substation: Replace line terminal bus and insulators for the line terminal to Isola 115 kV to a new through-path rating of 106 MVA. | MS | GIP |  | MPFCA upgrade project needed for GI projects J1294 and J1458. |  |  |  | 2023-11-10 | 115 | 0 | 406000
MTEP22 | South | Entergy Mississippi | 23518 | Tunica - Lula 115 kV Cut-in (J1440) | Generator Interconnection J1440 new Dundee 115 kV station cutting in on the Tunica - Lula 115 kV transmission line. Conditional on Ray Braswell - Franklin 500 kV MPFCA | MS | GIP |  | Needed to facilitate the interconnection of J1440 150 MW generator interconnection project. |  |  |  | 2024-05-23 | 115 | 0 | 13560000
MTEP22 | South | Entergy Mississippi | 23519 | Indianola - Cleveland 115 kV Cut-in (J1294) | Generator Interconnection for J1294 GI on the Indianola - Cleveland 115 kV transmission line. This generation project is conditional on: Ray Braswell – Franklin 500 kV Terminal Equipment Upgrades (DPP 2019 Shared Network Upgrade – MPFCA executed) Isola – Belzoni 115 kV Upgrade (DPP 2019 Shared Network Upgrade – MPFCA executed) Bogalusa – Adams Creek 230 kV Upgrade (DPP 2019 Shared Network Upgrade – MPFCA executed) | MS | GIP |  | Needed for J1294 99 MW generator interconnection. |  |  |  | 2024-05-23 | 115 | 0 | 3870000
MTEP22 | South | Entergy | 15649 | Texas 138 kV: New Distribution Station | Cut the Texas substation in and out of the Lewis Creek to Goree 138 kV line. | TX | Other | Load Growth | Distribution load growth. |  |  |  | 2025-12-01 | 138 | 0 | 69400000
MTEP22 | South | Entergy | 18262 | Tarkington to New Long John 138 kV: Rebuild Line | Rebuild Tarkington to New Long John (L870). | TX | BRP |  | NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. This project replaces the Pony project. The P5 contingency loss of Porter 138 kV bus differential relaying plus a fault causes thermal overloads on the line in multiple sensitivity cases. Tarkington to New Long John 138 kV line also overloads for the loss of Porter to New Caney 138 kV line. |  |  |  | 2024-06-01 | 138 | 0 | 18230000
MTEP22 | South | Entergy | 21810 | 2023 ETI Asset Renewal Program | This project is for the ETI Asset Renewal Program that will be executed in 2023. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2023 asset renewal plans have not yet been finalized. | TX | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | 2023-12-31 | 500 | 69 | 31600000
MTEP22 | South | Entergy | 21841 | Porter to Oak Ridge 138 kV Station Equipment Upgrade | Upgrade Line Bay Bus at Porter 138 kV to achieve a through path rating of 1766 A on the Porter to Oak Ridge 138 kV line. | TX | Other | Reliability | The N-1-1 contingency involving the loss of the Conroe to Forest and Lewis Creek to Alden 138 kV lines could result in non-consequential load loss in the Woodlands area. |  |  |  | 2023-12-01 | 138 | 0 | 459000
MTEP22 | South | Entergy | 21843 | Neches River Crossing Structure Mitigation | Mitigation includes: Replace coffers, de-water and excavate soils Perform structure foundation inspection(s), fortify/repair where possible Restore soils around structure foundations, fill coffers to grade | TX | Other | Age and Condition | Neches River has eroded around the foundations at the base of the structures on Neches to Sabine 138 kV lines 5 and 172. |  |  |  | 2025-06-01 | 138 | 0 | 28000000
MTEP22 | South | Entergy | 21847 | Galaxy: New 138 kV Distribution Station | Cut the Galaxy substation in and out of the Porter to Apollo 138 kV line. | TX | Other | Load Growth | Distribution load growth. |  |  |  | 2026-06-01 | 138 | 0 | 65900000
MTEP22 | South | Entergy | 21850 | District: New 138 kV Distribution Station | Cut the District substation in and out of the Crystal to Security 138 kV line. | TX | Other | Load Growth | Distribution load growth. |  |  |  | 2026-12-01 | 138 | 0 | 85200000
MTEP22 | South | Entergy | 21851 | Falcon: New 138 kV Distribution Station | Cut the Falcon substation in and out of the Luce Bayou to Tarkington 138 kV line. | TX | Other | Load Growth | Distribution load growth. |  |  |  | 2026-12-01 | 138 | 0 | 113800000
MTEP22 | South | Entergy | 22125 | R1003 Generator Interconnection at Sabine 230/138 kV Station (OCAPS) | This project is to perform the required upgrades to accommodate the interconnection at the existing Sabine 230/138 kV station identified in the GIA for R1003(OCAPS) | TX | GIP |  | This project is to support the interconnection of generation interconnection project for R1003(OCAPS) at the Sabine 230/138 kV substation. |  |  |  | 2025-03-01 | 230 | 138 | 14762000
MTEP22 | South | Entergy | 23209 | Legend 230 kV New Customer Connection | Entergy is proposing to construct new 230 kV transmission facilities at the existing Legend 230 kV substation which will serve a new industrial customer in Port Arthur, TX. The proposed new facilities include installing two additional 230 kV breakers into the Legend substation and extending a 230 kV radial transmission line towards the customer’s site. | TX | Other | Load Growth | Entergy has received a request from a customer interested in adding new load to a new station on the transmission system. |  |  |  | 2023-01-31 | 230 | 0 | 4250000
MTEP22 | South | Entergy | 23307 | Flare Hill 230 kV New Customer Substation | Entergy has been notified that a customer is proposing to construct a new 230 kV substation called Flare Hill, which will serve an industrial customer’s new load in Port Arthur, TX. The substation will be cut in on the existing Port Acres to Southside circuit 1. | TX | Other | Load Growth | Entergy has received a request from a customer interested in adding new load to a new station on the transmission system. |  |  |  | 2023-04-30 | 230 | 0 | 980000
MTEP22 | West | Great River Energy | 20666 | Litchfield - Litchfield Tap Double Circuit Rebuild | Rebuild ~2.5 miles of the Litchfield - Litchfield 69 kV tap line to double circuit. | MN | Other | Reliability | Reduce line exposure to the Cedar Mills, Atwater, Litchfield and Grove City substations. The double circuit line reduces the four terminal line to three for better relay coordination. The double circuit line bifurcates the Litchfield Tap – Grove City Tap 69 kV line, which would allow the Big Swan source to be available to serve the Litchfield Muni sub during contingencies on the Panther – Litchfield Muni 69 kV line. The double circuit configuration reduces line exposure to the Cedar Mills, Atwater, Litchfield and Grove City substations. |  |  |  | 2026-12-31 | 69 | 0 | 2281569
MTEP22 | West | Great River Energy | 20707 | Granite Falls - Willmar (WB) Line Upgrade | Upgrade the Granite Falls - Willmar (WB) line to 212 F by replacing 10 structures. | MN | BRP |  | Thermal violations caused by NERC Category P6 events in both 2026 Shoulder High Wind (wind dispatched at 83% of nameplate) and 2026 Spring Light Load (wind dispatched at 70% of nameplate) Sensitivity models. |  |  |  | 2025-06-01 | 230 | 0 | 598979
MTEP22 | West | Great River Energy | 20865 | Shamrock 69 kV Substation | Construct an in/out line to the Wright Hennepin Electric Association's Shamrock substation. The Shamrock substation is a rebuild of the nearby Corcoran substation. The load served at Corcoran will be gradually moved to the new Shamrock substation. | MN | Other | Load Growth | Accommodate a second transformer in the near future (~2023). The existing Corcoran substation is locked with roads that are close to the substation and there is no room to accommodate expansions to meet fast growing electric demand in the area. |  |  |  | 2023-02-21 | 69 | 0 | 1709484.43
MTEP22 | West | Great River Energy | 21065 | Big Swan 5N18 115 kV Breaker Addition | Add the Big Swan 5N18 breaker on the Crow River 115 kV line. | MN | BRP |  | Reduce over tripping for a fault on the Big Swan - Crow River 115 kV line. A fault on the Big Swan – Crow River 115 kV line trips the Big Swan 115/69 kV transformer causing low voltage problems in the 69 kV system. |  |  |  | 2024-11-01 | 115 | 0 | 700000
MTEP22 | West | Great River Energy | 21705 | Mud Lake - Benton County - Monticello Storm Structure Addition | Add 5 storm resistant structures to the Mud Lake - Benton County - Monticello 230 kV line. | MN | Other | Reliability | The storm structures will enhance system reliability by limiting the potential for full failure of all structures within a corridor. History has shown that H-frame structures are at risk of failure during certain weather events resulting in major damage along the corridor. Due to the risk in the number of miles being rebuilt, it was determined that adding storm structures would: • Reduce replacement cost of potentially greater miles of rebuild • Reduce outage time related to rebuilding the system resulting in shorter periods of potential market congestion • Reduce potential safety issues with less wire on the ground • Allowing for less time in getting needed materials within the supply chain |  |  |  | 2022-12-01 | 230 | 0 | 1823350.49
MTEP22 | West | Great River Energy | 21823 | Benson – Morris Storm Structures | Install storm structures in the Benson – Morris 115 kV line. | MN | Other | Reliability | The storm structures will enhance system reliability by limiting the potential for full failure of all structures within a corridor. History has shown that H-frame structures are at risk of failure during certain weather events resulting in major damage along the corridor. Due to the risk in the number of miles being rebuilt, it was determined that adding storm structures would: • Reduce replacement cost of potentially greater miles of rebuild • Reduce outage time related to rebuilding the system resulting in shorter periods of potential market congestion • Reduce potential safety issues with less wire on the ground • Allowing for less time in getting needed materials within the supply chain |  |  |  | 2023-12-01 | 230 | 0 | 1277000
MTEP22 | West | Great River Energy | 21824 | Riverton – Wing River Storm Structures | Install storm structures in the Riverton – Wing River 230 kV line. | MN | Other | Reliability | The storm structures will enhance system reliability by limiting the potential for full failure of all structures within a corridor. History has shown that H-frame structures are at risk of failure during certain weather events resulting in major damage along the corridor. Due to the risk in the number of miles being rebuilt, it was determined that adding storm structures would: • Reduce replacement cost of potentially greater miles of rebuild • Reduce outage time related to rebuilding the system resulting in shorter periods of potential market congestion • Reduce potential safety issues with less wire on the ground • Allowing for less time in getting needed materials within the supply chain |  |  |  | 2023-12-01 | 230 | 0 | 658000
MTEP22 | West | Great River Energy | 21825 | Cormorant – Pelican Rapids Storm Structures | Install storm structures in the Cormorant – Pelican Rapids 115 kV line. | MN | Other | Reliability | The storm structures will enhance system reliability by limiting the potential for full failure of all structures within a corridor. History has shown that H-frame structures are at risk of failure during certain weather events resulting in major damage along the corridor. Due to the risk in the number of miles being rebuilt, it was determined that adding storm structures would: • Reduce replacement cost of potentially greater miles of rebuild • Reduce outage time related to rebuilding the system resulting in shorter periods of potential market congestion • Reduce potential safety issues with less wire on the ground • Allowing for less time in getting needed materials within the supply chain |  |  |  | 2024-06-28 | 115 | 0 | 651387
MTEP22 | West | Great River Energy | 21826 | Bunker Lake - Elk River Storm Structures | Install storm structures in the Bunker Lake - Elk River 230 kV line. | MN | Other | Reliability | The storm structures will enhance system reliability by limiting the potential for full failure of all structures within a corridor. History has shown that H-frame structures are at risk of failure during certain weather events resulting in major damage along the corridor. Due to the risk in the number of miles being rebuilt, it was determined that adding storm structures would: • Reduce replacement cost of potentially greater miles of rebuild • Reduce outage time related to rebuilding the system resulting in shorter periods of potential market congestion • Reduce potential safety issues with less wire on the ground • Allowing for less time in getting needed materials within the supply chain |  |  |  | 2024-06-28 | 230 | 0 | 596365
MTEP22 | West | Great River Energy | 21829 | South Dayton 115 kV Substation | Construct the new Connexus Energy (CE) South Dayton 115 kV in-and-out distribution substation in the Xcel 5522 line. | MN | Other | Load Growth | Connexus Energy’s distribution planning group has calculated the 5-year load projection for Connexus Energy substations in Hennepin County, starting with the South Dayton #1 bank being installed in 2023, as well as a projection of the Connexus Energy load south of the river at the end of the current City of Dayton planning time horizon. This is based on the Metro Council’s “2015 System Statement” for the City of Dayton dated 17 SEP 2015, and CE’s understanding of the City of Dayton area that lies within the Connexus Energy service area. Page 4 of this document shows a household count of 4,400 in 2040 vs. 2,200 in 2020, and most of this increase falls within the Connexus Energy service area. The City of Dayton “2040 Future Land Use Draft” shows Commercial, Mixed Use, and Business Park use within the Connexus Energy service further justifying the load projections. In addition, the City of Maple Grove shows that the Hennepin #4 feeder area adjacent to the substation serves commercial property, which has the potential to re-develop to higher load density as it sits on the Highway 610 corridor. Connexus Energy anticipates both the Hennepin and the South Dayton substations to have a strong potential to double their load over the time window between 2023 and 2040, bringing Connexus Energy’s south of the river load to 23 MW. Project Alternatives: Connexus Energy investigated adding a 2nd transformer at Hennepin Substation, but that substation is remote from the growth area and has severely restricted feeder routes, due to the Elm Creek Park Reserve, and cannot adequately serve the growth area. Connexus Energy studied additional river crossings from Energy Park or Daytonport Substations, but the distances are too long and expensive, and the process to construct additional Mississippi River crossings is very complex. The existing Energy Park Substation river crossing has recently been re-built, and it is dedicated to loads south of the river, but it has limited reach into the growth areas. Overall, the distance from source to load on CE’s 12.47 kV system requires a new delivery point situated in the heart of the load growth area |  |  | 23 | 2023-09-01 | 115 | 0 | 1485000
MTEP22 | West | Great River Energy | 21830 | Shamineau Lake 115 kV Substation | Construct the new Crow Wing Power Shamineau Lake distribution substation. | MN | Other | Load Growth | Crow Wing Power has served the southern Motley / Lincoln area from the Ward delivery point for a while and Crow Wing Power is noticing that it is becoming more difficult to maintain end of the line voltage for its customers. The Ward substation is in Todd-Wadena’s service territory and Crow Wing Power must go 6 miles before they enter their own service territory which makes the voltage issue even more challenging. Having a source closer to their load pocket and within their own service territory will lower the miles per feeder, lowering the exposure for each circuit resulting in better reliability. Additionally, the new source will be closer to the growing load pocket and end of the line voltage will be met. The addition of regulators and capacitor banks isn’t viable since the distribution system already has two sets of regulation. The regulators on the feeders from Ward have been working overtime to keep up with the 34.5kV voltage fluctuations. |  |  |  | 2022-11-21 | 115 | 0 | 792000
MTEP22 | West | Great River Energy | 22025 | Parkwood 115 kV Ring Bus | Rebuild the 115 kV bus at Parkwood substation as a ring bus. | MN | BRP |  | 115 kV line faults cause a trip of a Parkwood 115/69 kV transformer. Parkwood 12WB2 breaker failure causes overload of the Bunker Lake-Village Ten 69 kV line under peak loading conditions. A Parkwood 115/69 kV transformer differential protection activation causes transfer tripping to the remote substations. For the Crooked Lake 115 kV line, this causes the loss of Connexus’ load service at Crooked Lake, which serves a major commercial development. Project Alternatives: Adding 115 kV line breakers. This option is feasible but is not as robust as a ring bus topology. A 115/69 kV transformer trip still will open a 115 kV line and a 12WB2 breaker failure event still trips out the entire 115 kV bus. Rebuilding the Bunker Lake-Village Ten 69 kV line (2.63 miles). This circuit is double circuited with the Blaine-Bunker Lake 230 kV line on steel structures. About 0.50 miles of structures have been replaced as part of past road move projects, but it is unknown if these could be reused. Also, about 0.75 miles of this circuit runs through a residential neighborhood, so access for rebuilding might be challenging. The option, while correcting a NERC Category P24 contingency overload, does not increase the robustness of the Parkwood 115 kV topology. Do nothing and accept the risk of the Parkwood 12WB2 stuck breaker contingency occurring. A P24 contingency is a more extreme contingency than a Category P1 contingency occurring. Should the contingency occur under high system loading conditions, however, the only recourse to alleviate the overload would be load shedding, likely several large commercial districts in Anoka County. This option does not increase the robustness of the Parkwood 115 kV topology. |  |  |  | 2024-11-08 | 115 | 0 | 7620000
MTEP22 | West | Great River Energy | 22026 | Deer River - Jessie Lake - Wirt Tap 69 kV Line Rebuild | Rebuild the Deer River - Jessie Lake - Wirt Tap 69 kV line. | MN | Other | Age and Condition | This line is being rebuilt due to age and condition concerns. Additional benefit is improvement of voltage drop and line losses due to lower impedance of the replacement conductor. |  |  |  | 2025-09-30 | 69 | 0 | 20723354.36
MTEP22 | West | Great River Energy | 22027 | Birch Lake - Pleasant Lake - Wabedo 69 kV Line Rebuild | Rebuild the Birch Lake - Pleasant Lake - Wabedo 69 kV line. | MN | BRP |  | Age and condition. For the loss of the Badoura - Tripp Lake 115 kV line, the voltages in the Blind Lake area go into violation. The existing line is 1/0 and 2/0 ACSR and is planned to be rebuilt with 795 ACSR to help the voltage profile of the Blind Lake area loads. |  |  |  | 2024-06-01 | 69 | 0 | 14419044.49
MTEP22 | West | Great River Energy | 22028 | Denham - Harry Maser 69 kV Line Rebuild | Rebuild the Denham - Harry Maser 69 kV line. | MN | BRP |  | Age and condition. For the loss of the Cromwell - Kettle River 69 kV line, there is a voltage violation at Sturgeon Lake but after rebuilding the existing line from 1/0 ACSR to 477 ACSR we will no longer have this voltage violation. |  |  |  | 2025-05-02 | 69 | 0 | 5112000
MTEP22 | West | Great River Energy | 22029 | Walden 115/41.6 kV LTC | Replace the existing Walden 115/41.6 kV transformer with an LTC transformer. | MN | BRP |  | This project is primarily needed to address low voltage concerns in the area. System planning studies with historical summer peak loads have shown that the Walden to Elbow Lake 41.6 kV system experiences marginal system intact voltage. The study also showed post contingent low voltage planning criteria violations in the Elbow Lake – Walden 41.6 kV system. The most critical contingencies for the area are the Morris to Morris OTP 115 kV line outage and Walden 115/41.6 kV transformer outage. For the loss of Morris to Morris OTP 115 kV line outage, all loads that are served from the Walden 115/41.6 kV transformer experience low voltage that are below GRE’s post contingent low voltage criteria of 0.92 per unit. Even though wide voltage swings are expected between different loading profiles throughout the year in the 41.6 kV system, historical voltage profile of the Walden 41.6 kV bus shows that the Walden 41.6 kV bus experiences high voltage problems that violates GRE’s high voltage criteria of 1.05 per unit. The Walden LTC transformer is required to regulate both the low voltage and high voltage concerns in the area. |  |  |  | 2023-08-31 | 115 | 0 | 2500000
MTEP22 | West | Great River Energy | 22030 | Rost 161/69 kV Substation and Lorain - Rost 69 kV Line | Construct the Rost 161/69 kV substation interconnection in the Heron Lake – Round Lake 69 kV transmission line. Construct approximately 9 miles of 69 kV transmission line from the Lorain substation to the Rost substation. Previously named Worthington Area Projects. | MN | BRP |  | Missouri River Energy Services (MRES), Great River Energy (GRE), and ITC Midwest (ITCM) performed a joint study of the Worthington area in southwestern Minnesota. Existing operational and reliability issues in this area have existed for some time. Various options have been considered for the Worthington load center, approximately 60 MW, and other loads that surround the area. At present, single contingency bus outages at Elk 161/69 kV substation cause the Worthington load to drop. In addition, there is a challenge to take maintenance outages on the 161 kV system from Split Rock to Lakefield Junction, some portions of the 69 kV system, and some portions of the neighboring 345 kV system due to voltage concerns across the area. Reconfiguration of the 69 kV system is a normal occurrence and puts area load at risk if an event were to occur in this temporary configuration. With the load growth occurring in Worthington for Worthington Public Utilities (WPU) over the next few years, the above issues are being exacerbated, and the proposal of a new substation in the Worthington area, prompted a deeper look into the area resulting in the following project need: Phase 1: Approximately 9 mile, 69-kV line from existing MRES Lorain breaker station to new Rost 69 kV breaker substation: Necessity: Establish alternative source beyond Elk to serve the Worthington load center Allow redundant 161/69 kV sources to be connected (Heron Lake and Elk) Lower reliability exposure to multiple 69 kV loads and wind farm connections on long 69 kV corridors Establish new relaying point to enhance relay settings with consideration for the wind farm sources and allow for future wind connections into the substation Benefits: Reduces the dependence of the Worthington load pocket on ITCM’s Elk Substation Increased operational flexibility for Worthington load for prior outages Additional 69-kV source to the Federated Rural Electric Association service territory including breaking up a highly exposed 69 kV line Enhanced relaying for line protection that consist of long distance 69 kV line with many radial taps and four wind farms, all without breaker protection Phase 2: Establish 161/69 kV at Rost with new 161 kV line from new ITC 161 KV Lakefield Corners breaker station Necessity: Low voltage - any outage on the 161-kV between Split Rock Substation (Xcel Energy) and Magnolia Substation leaves the system susceptible to low voltages for faults anywhere between Lakefield Junction and Elk 161-kV. Eliminate considerable operational concerns for prior-outage situation with a second event in the area. 161 kV prior outages of concern from Split Rock to Lakefield Junction including 161 kV substation on the corridor of Magnolia, Elk, Brewster, and Heron Lake. Reduce temporary operating guide and system reconfiguration due to voltage issues caused by a second contingency event. Eliminate significant risk of load loss within a broad area of southwestern Minnesota Benefits: New 161-kV source to the Worthington load pocket, via Rost 69 kV development allowing continued load expansion in the Worthington area Projects address voltage collapse and allows 69-kV system to remain in normal configuration during critical prior outages New Rost 161/69 kV source allows simplification of work at Heron Lake thus resulting in reduced cost at that substation. | Area Load Growth (BRP) |  |  | 2025-10-03 | 161 | 69 | 13368000 | BRP; serves Worthington area load growth
MTEP22 | West | Great River Energy | 22445 | Cedar 115 kV Substation | DEA building new in/out distribution substation. GRE will need to double circuit tap into sub off of DA-DA line. GRE is also responsible for the highside structures and associated equipment. | MN | Other | Load Growth | Cedar Substation – This is a new site located near the intersection of Cedar Ave and Lakeville Blvd. in Lakeville. DEA has talked to engineering and land rights at GRE about the feasibility as this now has passed city council and DEA is purchasing the land and would likely build out this site in 2023. Load growth within the city limits of Lakeville, between Dodd Boulevard, Flagstaff Avenue, and the area south of the existing Dodd Park substation, are forecasted to exceed the available capacity of neighboring Dodd Park, Vermillion River, and Ritter Park substations. Much of the developable land within Lakeville’s 2040 comprehensive plan is proposed as either low density or low/medium density residential housing. Area adjacent to Cedar Avenue, between County Road 50 and 190th Street West, is proposed to be developed as commercial, mixed use, and residential density at or above medium density housing units. The Cedar substation is required to supply new and existing members within both the Lakeville and Farmington city limits an adequate voltage supply during both normal system configurations. The new Cedar substation is also required to provide an adequate contingency supply to southern circuits of the Dodd Park substation, as well as northern and western feeders leaving the Vermillion River substation. Feeders are proposed to be constructed as part of the new Cedar substation as new loads continue to come into the area surrounding the site; specifically residential and mixed use to the north and largely commercial and industrial to the south of the substation location. |  |  |  | 2023-06-01 | 115 | 0 | 2773049.09
MTEP22 | West | Great River Energy | 22528 | Matter 69 kV Substation | Install a manual load break 3-way load break 69kV/1200A switch on a steel pole and foundation on GRE’s DX (Crow River to Victor) line. Install adjacent grading structures if needed. Build HS DE to 115kV. | MN | Other | Load Growth | Delano Municipal Utilities (DMU) desires to establish a distribution substation tapping GRE’s DX line to serve about 5 MW peak load and provide a backup service to its existing Delano Muni distribution substation. DMU will be responsible to install a metering package per GRE’s requirement to allow metering data transfer between DMU’s new substation and GRE. |  |  | 5 | 2024-01-01 | 69 | 0 | 402407
MTEP22 | Central | Hoosier Energy REC, Inc. | 22628 | New HE_Sleepy_Hollow 345/161 Sub | New 345kV ring bus station with 345/161kV transformation and 161 kV transmission line to new station (22646) | IN | Other | Load Growth | Construct new 345kV ring bus station with 345/161 transformation between DEI Prescott and DEI Columbus. Construct new 161kV transmission line to new 161kV station between Decatur and Napoleon. Required to accommodate up to 400 MW load, and maintain N-2 reliability, at new Decatur-Napoleon 161kV station. |  |  | 400 | 2028-06-01 | 345 | 161 | 38000000
MTEP22 | Central | Hoosier Energy REC, Inc. | 22646 | New Decatur-Napoleon 161KV Station | New 161 kV transmission station between Decatur and Napoleon | IN | Other | Load Growth | New customer request interconnection to 161kV line. Construct new 161kV station about 1.5 miles south of Decatur station to accommodate interconnection. Initial load about 25 MW, growing up to 400 MW through 2032. |  |  | 25 | 2024-10-01 | 161 | 0 | 26000000
MTEP22 | Central | Hoosier Energy REC, Inc. | 22648 | New HE_Prescott_161kV_Line | New 161kV line from DEI Prescott to new 161kV station | IN | Other | Load Growth | Expand DEI Prescott ring-bus and construct new 345/161 substation. Construct 161kV line from Prescott to new Decatur-Napoleon Station (22646). Required to accommodate up to 400 MW load, and maintain N-2 reliability, at new Decatur-Napoleon 161kV station. |  |  | 400 | 2026-06-01 | 345 | 161 | 45000000
MTEP22 | Central | Hoosier Energy REC, Inc. | 22666 | New HE_Batesville_161kV_Line | New 161kV line from DEI Batesville to new 161kV station (22646) | IN | Other | Load Growth | Expand DEI Batesville ring-bus and construct new 345/161 substation. Construct new 161kV line from DEI Batesville to new 161kV station between Decatur and Napoleon. Required to accommodate up to 400 MW load, and maintain N-2 reliability, at new Decatur-Napoleon 161kV station. |  |  | 400 | 2027-06-01 | 345 | 161 | 45000000
MTEP22 | Central | Hoosier Energy REC, Inc. | 23266 | New HE_AboutBit 115 MVA Load | Extend a new 69kV transmission line from an available bay position at Merom transmission station (Bus # 248774) to the new customer. The 69kV line will split at about 0.3 miles from Merom station, extending to two separate substations. Total estimated load is 115 MVA (20 MVA on substation 1 and 95 MVA on substation 2). | IN | Other | Load Growth | Hoosier Energy has received a request from a customer to add 115 MVA load to the 69kV transmission system, about 1 mile south of Merom station. An agreement targeting an in-service date of January 2023 was reached between Hoosier Energy and the customer in June 2022. The project is to be constructed prior to the MTEP23 cycle. | Large Industrial |  | 115 MVA | 2023-01-01 | 69 | 0 | 1200000 | 115 MVA industrial load ~1mi from Merom (Hoosier Energy, IN)
MTEP22 | Central | Henderson Municipal Power & Light | 22228 | Upgrades HMPL Transmission Due to I-69 DOT Project | Rerouting of HMPL 69kV transmission lines (HMPL Sub 6 to HMPL Sub 1, HMPL Sub 6 to (BREC) HMPL6 Tap, HMPL Sub 6 to HMPL Sub 3, and HMPL Sub 3 to (BREC) Wolf Hills Tap) due to I-69 KY DOT project. | KY | Other | Reliability | HMPL needs to reroute its transmission lines due to the KY I-69 DOT project. |  |  |  | 2022-06-30 | 69 | 0 | 3800000
MTEP22 | Central | Indianapolis Power & Light Company | 21836 | Replace Sunnyside 345 kV and 138 kV Breakers | Replacement of three (3) 345 kV breaker #21, #22 & #23 and two (2) 138 kV breakers #1, & #3 | IN | Other | Age and Condition | Age and condition |  |  |  | 2024-12-31 | 345 | 0 | 5100000
MTEP22 | Central | Indianapolis Power & Light Company | 21838 | Replace Southwest 138 kV Breakers | Replacement of five (5) 138 kV breakers #4, #5, #3, #26, #27 | IN | Other | Age and Condition | Age and Condition |  |  |  | 2024-12-31 | 138 | 0 | 4500000
MTEP22 | Central | Indianapolis Power & Light Company | 21839 | Replace West 138 kV Breakers | Replacement of three (3) 138 kV breakers #1, #4, #7 | IN | Other | Age and Condition | Age and Condition |  |  |  | 2024-12-31 | 138 | 0 | 2400000
MTEP22 | West | ITC Midwest | 21828 | Agency Street New Control Enclosure & Relay Replacements | The relays at Agency Street are approaching their 20 year end of life. ITC will install a new control enclosure with all new relays to provide ITC a separate control enclosure from IPL and minimize required outages and outage times for the relay replacements. All necessary outages should be coordinated with IPL. Also coordinate with IPL on location of new control building as this is an IPL owned site. | IA | Other | Age and Condition | The relays at Agency Street are approaching their 20 year end of life. |  |  |  | 2024-12-31 | 69 | 69 | 2090891
MTEP22 | West | ITC Midwest | 21842 | Jasper County Control Enclosure and Relay Replacements | A new Control Enclosure is required at the Jasper County Substation due to age and condition. ITC will install a new Control Enclosure with all new relays. | IA | Other | Age and Condition | The existing control enclosure and relays are at the end of their respective lives and in need of replacement. |  |  |  | 2024-12-31 | 161 | 161 | 2486897
MTEP22 | West | ITC Midwest | 21929 | Forks Switching Station & Forks-Rost 161kV Circuit | As part of a joint study to serve load expansion in Worthington, MN, ITC will construct a 161kV circuit between new Forks switching station and GRE Rost substations. | MN | BRP |  | Part of a joint study to serve load expansion in Worthington, MN. MRES submitted a load addition on the Southeast side of the city of Worthington, MN. As part of this load addition study, GRE and ITC Midwest analyzed the existing operation and reliability concerns/violations. | Area Load Growth (BRP) |  |  | 2026-12-31 | 161 | 161 | 13456200 | BRP; part of Worthington load expansion
MTEP22 | West | ITC Midwest | 21930 | Millstream 69kV Switching Station | ITC has been working with Amana Society on way to improve reliability to their substation, and ITC will be building a new 69 kV switching station called “Millstream” adjacent to the existing Amana Society substation to improve area transmission system reliability. | IA | Other | Reliability | ITC has been working with Amana Society on way to improve reliability to their substation, and ITC will be building a new 69 kV switching station called “Millstream” adjacent to the existing Amana Society substation to improve area transmission system reliability. |  |  |  | 2024-12-31 | 69 | 69 | 7748400
MTEP22 | West | ITC Midwest | 21933 | Fox Lake Relay, Breaker, & SCADA Replacements | ITC will replace all of its relays and SCADA equipment as well as remove the existing carrier equipment/wave trap at the Fox Lake substation. Circuit Breaker 736 will also be replaced at Fox Lake substation. | MN | Other | Age and Condition | Relays and SCADA equipment are near the end of their lifespan and will need replacement due to aging. Circuit breaker 736 will also need replacement due to aging condition. |  |  |  | 2025-12-31 | 161 | 161 | 2651016
MTEP22 | West | ITC Midwest | 21935 | Hayward Transformer Replacement | ITC will replace the two 161/69kV transformers at Hayward Substation with a single 150 MVA 161/69kV unit. To make room for the new 161kV bus tie breaker. ITC will move the Glenworth – Hayward 161kV terminal to the opposite side of the Hayward – Murphy Creek 161kV terminal. | MN | Other | Age and Condition | At Hayward Substation there are two 75MVA 161/69kV transformers that are beginning to gas. Both units are over 50 years of age, and the DGA results show that the paper cellulose insulation is at the end of life. |  |  |  | 2025-12-31 | 161 | 69 | 6744271
MTEP22 | West | ITC Midwest | 21936 | Centerville Cooper Creek 69kV Interconnection | IPL will be building a new 69/25x12.5 kV substation named “Centerville Cooper Creek” adjacent to the existing Centerville North substation on the location of the old combustion turbines. This new substation will replace the existing IPL/ITC Centerville North Substation and accommodate future area load growth as well as IPL’s future conversion to 25 kV distribution. IPL will be installing two 12/20 MVA transformers at the new Centerville Cooper Creek substation. For the ITC owned portion of Centerville North, ITC will build a new 69 kV substation with two single boxes, two line breakers, and a bus tie breaker. Once the new Centerville Cooper Creek substation is in-service, the existing Centerville North substation will be retired. | IA | Other | Load Growth | Load serving, future conversion and retirement of existing Centerville North substation. |  |  | 20 MVA | 2025-12-31 | 69 | 69 | 3708274
MTEP22 | West | ITC Midwest | 21937 | Chariton North 69kV Substation Interconnection | IPL will be building a new 69/26.2 kV Substation named Chariton North. IPL will be installing one 69/26.2 kV 20/33 MVA or 30/50 MVA transformer initially but is planning the substation to accommodate a second 69/26.2 kV 20/33 MVA or 30/50 MVA transformer when all the load is added. All the ITC 69 kV substation equipment will be capable of 1200A or greater. The 69 kV lines to the new substation will be T2-4/0 or larger and will be the standard 69 kV construction. | IA | Other | Load Growth | Customer Interconnection |  |  | 33 MVA | 2024-12-30 | 69 | 69 | 6836817
MTEP22 | West | ITC Midwest | 21939 | Cedar Rapids Hunter Field Substation Expansion | IPL has notified ITC that it will be adding a 3rd 161x69/24.9 kV transformer at the Hunter Field Substation. ITC will need to add an additional breaker and bus to connect the new IPL transformer at Hunter Field. All new ITC equipment to be designed to 161 kV specs to allow future conversion of the substation to 161 kV operation. Substation will initially be operated at 69 kV. | IA | Other | Reliability | Customer requested and system reliability. |  |  |  | 2024-12-31 | 69 | 69 | 1284996
MTEP22 | West | ITC Midwest | 21940 | Turkey River to Guttenburg 69kV Rebuiild | The 9.04 mile Turkey River – Guttenberg 69 kV line is at the end of its useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Turkey River and Monona. | IA | Other | Age and Condition | Age & Condition, end of useful life. |  |  |  | 2025-12-31 | 69 | 69 | 10376400
MTEP22 | West | ITC Midwest | 21941 | Guttenburg to Garnavillo 69kV Rebuild | The 11.23 mile Guttenberg - Garnavillo 69 kV line along with the 0.18 mile tap to Garnavillo are at the end of their useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Guttenberg and Monona. | IA | Other | Age and Condition | Age & Condition, end of useful life. |  |  |  | 2028-12-31 | 69 | 69 | 14391600
MTEP22 | West | ITC Midwest | 21942 | Garnavillo to Elkader 69kV Rebuild | The 7.63 mile Garnavillo - Elkader 69 kV line is at the end of its useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Garnavillo and Elkader. | IA | Other | Age and Condition | Age & Condition, end of useful life. |  |  |  | 2028-12-31 | 69 | 69 | 10012800
MTEP22 | West | ITC Midwest | 21943 | Rose Hollow Add 161kV Terminal for North Gate line | MidAmerican has notified ITC that they will be building a new 161 kV line from their exiting North Gate substation to the ITC Rose Hollow substation. Per the terms of the agreement with MidAmerican, ITC will need to install a new 161 kV terminal at Rose Hollow for the new line to North Gate. | IA | Other | Reliability | Customer requested |  |  |  | 2024-12-31 | 161 | 161 | 984000
MTEP22 | West | ITC Midwest | 21946 | Pelican-Triboji 69kV Rebuild | Two sections of the Pelican-Triboji 69kV line are near end of life and in poor condition. The line between Pelican and structure 162 (~1.04 miles) and the line between Triboji and structure 72 (~4.45 miles) will be rebuilt to current 69kV standards. All new line should be rated 600A or higher. All necessary outages should be coordinated with IPL and CBPC. | IA | Other | Age and Condition | Two sections of the Pelican-Triboji 69kV line are near end of life and in poor condition. |  |  |  | 2023-12-31 | 69 | 69 | 6462000
MTEP22 | West | ITC Midwest | 21976 | Jasper to Laurel 161kV Line Rebuild | ITC will rebuild approximately 10 miles of the Jasper to Laurel 161kV line. The 161kV line conductor will be capable of 1600A or greater. | IA | Other | Age and Condition | The existing control enclosure and relays are at the end of their respective lives and in need of replacement. |  |  |  | 2027-12-30 | 161 | 161 | 18781720
MTEP22 | West | ITC Midwest | 21977 | J1050 Generator Interconnection - TOIF | The Interconnection Customer, Great Pathfinder Wind, LLC, has proposed connection of a 225 MW wind powered generating facility to the Doud 161 kV bus. A breaker position in the Doud 161 kV ring bus will be added to accommodate the interconnection. TOIF cost to include dead end, line disconnect switch, arresters, PT’s, relay panel, and other associated equipment. The IC has requested ITCM to begin design under an E&P agreement to better accommodate their requested in service date while the MISO process is still ongoing. | IA | GIP |  | Customer requested - GIA |  |  |  | 2022-08-22 | 161 | 161 | 403313
MTEP22 | West | ITC Midwest | 21978 | J1050 Generator Interconnection - Network Upgrade | The Interconnection Customer, Great Pathfinder Wind, LLC, has proposed connection of a 225 MW wind powered generating facility to the Doud 161 kV bus. A breaker position in the Doud 161 kV ring bus will be added to accommodate the interconnection. Network Upgrade cost to include the new breaker position, switch and associated equipment. The IC has requested ITCM to begin design under an E&P agreement to better accommodate their requested in service date while the MISO process is still ongoing. | IA | GIP |  | Customer requested - GIA |  |  |  | 2022-08-22 | 161 | 161 | 408428
MTEP22 | West | ITC Midwest | 21980 | ITC Midwest Asset Replacement Program 2024 | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA,MN,IL | Other | Age and Condition | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance have increased potential for misoperations and higher maintenance costs associated with their ongoing use. |  |  |  | 2024-12-31 | 345 | 69 | 37080000
MTEP22 | West | ITC Midwest | 21982 | Southern Dubuque 161/69kV Source & Bunker Hill 69kV Loop | ITC Midwest will construct a new 161/69kV substation on the south side of Dubuque. Then a new right of way 69 kV line ~2.65 miles to the existing Bunker Hill substation in the center of Dubuque. The new line will provide the 2nd 69kV line to the radial Bunker Hill 69kV sub. Alliant Energy will expand the Bunker Hill site to allow for a 2nd distribution transformer and ITC to have two 69 kV line breakers and a 69 kV bus tie breaker. The new ITC 161/69kV sub will be capable of two 150 MVA 161/69kV transformers (one initially). The 161kV will be constructed with the standard 161 kV ring convertible to breaker and 1/2 with just the single transformer and the two 161kV line taps initially. The 69kV will need to allow for a potential 2nd 150 MVA transformer and 69kV bus tie breaker, but will initially be just a single 69kV line to feed the Bunker Hill loop. | IA | Other | Load Growth | Alliant Energy has requested that ITC provide a network feed for the radial Dubuque 8th Street-Bunker Hill 69 kV line. The Bunker Hill site is centrally located with all other transmission lines more or less bordering the edges of the city of Dubuque. The Bunker Hill substation can not serve existing distribution load during summer months and Alliant Energy must move several distributions feeders to other distribution sources. The new 69kV source will initially be just the new 69 kV loop to Bunker Hill, but will also be effective at serving future load along the Southwest Arterial, a recently completed 4 lane bypass connecting the major highways heading south and west from Dubuque. |  |  | 150 MVA | 2025-12-31 | 161 | 69 | 19306266
MTEP22 | West | ITC Midwest | 21987 | J1181 GIA - TOIF Lasalle 345 kV Switching Station | ITC is entering into a Generator Interconnection Agreement with Invenergy for the interconnection of project J1181, a 200 MW wind-powered generating facility to a new, 3 breaker, 3 terminal 345 kV “Lasalle” switching station along the Hazleton to Mitchell 345 kV line. Invenergy’s collector substation will be located in close proximity to the new Lasalle switching station. Invenergy has requested an October 31, 2022 in service date for the project. Under the terms of the GIA, Invenergy will transfer property for Lasalle 345 kV station to ITC, and Invenergy will also provide a topographical survey and soil borings for the ITC facilities. Lasalle switching station will be constructed with 3,000A capability. | IA | GIP |  | Customer requested - GIA |  |  |  | 2023-08-31 | 345 | 345 | 892270
MTEP22 | West | ITC Midwest | 21989 | J1181 GIA - TO Funded 345 kV Network Upgrades | ITC is entering into a Generator Interconnection Agreement with Invenergy for the interconnection of project J1181, a 200 MW wind-powered generating facility to a new, 3 breaker, 3 terminal 345 kV “Lasalle” switching station along the Hazleton to Mitchell 345 kV line. Invenergy’s collector substation will be located in close proximity to the new Lasalle switching station. Invenergy has requested an October 31, 2022 in service date for the project. Under the terms of the GIA, Invenergy will transfer property for Lasalle 345 kV station to ITC, and Invenergy will also provide a topographical survey and soil borings for the ITC facilities. Lasalle switching station will be constructed with 3,000A capability. | IA | GIP |  | Customer requested - GIA |  |  |  | 2023-08-31 | 345 | 345 | 12653333
MTEP22 | West | ITC Midwest | 21991 | J836 GIA - TOIF - Ledyard 345 kV | 7-21-21: ITCM and Duke Energy have entered into a MISO Generator Interconnection Agreement. Initial sketch provided Design work for TOIF under an Engineering and Procurement Agreement. The work under the E&P Agreement included design of TOIF and Network Upgrades necessary for the expansion of Ledyard 345 kV to a 4-terminal, 4-breaker ring bus configuration. | IA | GIP |  | Customer requested - GIA |  |  |  | 2022-08-26 | 345 | 345 | 1146492
MTEP22 | West | ITC Midwest | 21992 | J836 TO Funded Generator Interconnection - Ledyard 345 kV | ITCM and Duke Energy have entered into a MISO Generator Interconnection Agreement for upgrade of Ledyard 345 kV switching station. The work under the Agreement will include design of TOIF and Network Upgrades necessary for the expansion of Ledyard 345 kV to a 4-terminal, 4-breaker ring bus configuration. Design work for TOIF and Network Upgrade commenced under an Engineering and Procurement Agreement, and the GIA provides for continuation and completion of the work at Ledyard. | IA | GIP |  | Customer requested - GIA |  |  |  | 2022-07-01 | 345 | 345 | 1814497
MTEP22 | West | ITC Midwest | 21996 | J1084 Generator Interconnection TOIF | TOIF includes facilities and equipment at the 345 kV substation dedicated to the 345 kV radial line and Generating Facility | IA | GIP |  | Customer requested - GIA |  |  |  | 2023-10-01 | 345 | 345 | 661704
MTEP22 | West | ITC Midwest | 21997 | J1084 Generator Interconnection Network Upgrades | Rock Creek 345 kV ring bus will be expanded with a 345 kV breaker and other necessary equipment to interconnect the new terminal for project J1084. | IA | GIP |  | Customer requested - GIA |  |  |  | 2023-10-01 | 345 | 345 | 1294462
MTEP22 | West | ITC Midwest | 21998 | J1164 Generator Interconnection TOIF | Magnolia 161 kV substation currently has no circuit breakers protecting the Magnolia to Elk 161 kV line and the Magnolia to Rock County 161 kV line. The Facilities Study for J1164 identified Network Upgrades and TOIF necessary for the interconnection of project J1164 to ITCM’s Magnolia 161 kV substation. Project J1164’s impact to the transmission system is currently being evaluated as part of the DPP 2018 April West Area Study, which has not been finalized pending results of an Affected System Study. | MN | GIP |  | To interconnect project J1164 to the ITC Midwest (“ITCM”) system at the interconnection customer’s requested point of interconnection, ITCM will upgrade Magnolia 161 kV substation to a 4 terminal ring bus configuration. The interconnection customer, MISO and ITCM entered into an Engineering and Procurement Agreement for initial design work for the Magnolia 161 kV expansion, and it is expected that a Generator Interconnection Agreement (“GIA”) will be entered into by the interconnection customer, MISO and ITCM soon. Network Upgrades and Transmission Owner Interconnection Facilities (“TOIF”) are expected to be constructed at Magnolia substation for project J1164, an 80 MW, solar-powered generating facility under a Generator Interconnection Agreement (“GIA”) as a condition of the project’s Interconnection Service. |  |  |  | 2024-08-01 | 161 | 161 | 475538
MTEP22 | West | ITC Midwest | 21999 | J1164 Generator Interconnection Network Upgrades | Magnolia 161 kV substation currently has no circuit breakers protecting the Magnolia to Elk 161 kV line and the Magnolia to Rock County 161 kV line. The Facilities Study for J1164 identified Network Upgrades and TOIF necessary for the interconnection of project J1164 to ITCM’s Magnolia 161 kV substation. Project J1164’s impact to the transmission system is currently being evaluated as part of the DPP 2018 April West Area Study, which has not been finalized pending results of an Affected System Study. | MN | GIP |  | To interconnect project J1164 to the ITC Midwest (“ITCM”) system at the interconnection customer’s requested point of interconnection, ITCM will upgrade Magnolia 161 kV substation to a 4 terminal ring bus configuration. The interconnection customer, MISO and ITCM entered into an Engineering and Procurement Agreement for initial design work for the Magnolia 161 kV expansion, and it is expected that a Generator Interconnection Agreement (“GIA”) will be entered into by the interconnection customer, MISO and ITCM soon. Network Upgrades and Transmission Owner Interconnection Facilities (“TOIF”) are expected to be constructed at Magnolia substation for project J1164, an 80 MW, solar-powered generating facility under a Generator Interconnection Agreement (“GIA”) as a condition of the project’s Interconnection Service. |  |  |  | 2024-08-01 | 161 | 69 | 8833588
MTEP22 | East | ITC Transmission | 15875 | Kentucky - Luzon 120 kV Sag Remediation | Completely remove the sag limit on the Kentucky – Luzon 120 kV line. | MI | BRP |  | The Kentucky – Luzon 120 kV line is projected to be overloaded for several shutdown-plus-contingency that involve the loss of the Brownstown – Swan Creek 120 kV line. The identified overloaded equipment on this circuit is the sag limit. The thermal violations are found in peak and off peak conditions. |  |  |  | 2024-06-01 | 120 | 0 | 500000
MTEP22 | East | ITC Transmission | 17999 | Re-conductor Corktown - Waterman 120 kV UG | The proposed solution is to re-conductor approximately 3.7 miles of the Corktown – Waterman 120 kV underground cable utilizing 5000 Kcmil underground cable. | MI | BRP |  | The Corktown – Waterman 120 kV underground cable is projected to marginally overload. |  |  |  | 2024-06-01 | 120 | 0 | 7000000
MTEP22 | East | ITC Transmission | 20182 | Northeast 120kV 55 MVAR Reactor | Install a 120 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Northeast 120 kV bus. | MI | Other | Reliability | The Northeast, Mack, Warren, Stephens and various 120 kV buses on ITCT system has been experienced high voltages during light load conditions and Real-time Operations has challenging mitigating the issues. The Power Factor (PF) was modified in the planning models to reflect the PF seen in real-time operations. |  |  |  | 2024-12-31 | 120 | 0 | 1320000
MTEP22 | East | ITC Transmission | 20183 | Stephens 345kV 55 MVAR Reactor | Install a 345 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Stephens 345kV bus. | MI | Other | Reliability | The Northeast, Mack, Warren, Stephens and various 120 kV buses on ITCT system has been experienced high voltages during light load conditions and Real-time Operations has challenging mitigating the issues. The Power Factor (PF) was modified in the planning models to reflect the PF seen in real-time operations. |  |  |  | 2024-12-31 | 230 | 0 | 3500000
MTEP22 | East | ITC Transmission | 20185 | Warren 120kV 55 MVAR Reactor | Install a 120 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Warren 120kV bus. | MI | Other | Reliability | The Northeast, Mack, Warren, Stephens and various 120 kV buses on ITCT system has been experienced high voltages during light load conditions and Real-time Operations has challenging mitigating the issues. The Power Factor (PF) was modified in the planning models to reflect the PF seen in real-time operations. |  |  |  | 2024-12-31 | 120 | 0 | 1700000
MTEP22 | East | ITC Transmission | 20186 | Mack 120kV 55 MVAR Reactor | Install a 120 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Mack 120kV bus. | MI | Other | Reliability | The Northeast, Mack, Warren, Stephens and various 120 kV buses on ITCT system has been experienced high voltages during light load conditions and Real-time Operations has challenging mitigating the issues. The Power Factor (PF) was modified in the planning models to reflect the PF seen in real-time operations. |  |  |  | 2024-12-31 | 120 | 0 | 1700000
MTEP22 | East | ITC Transmission | 20525 | ITCT Line Relocation Blanket | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI | Other | Other Local Needs | ITCT has transmission lines and underground cables in road right of way, without easement. The State of Michigan and local municipalities have road improvement projects which require ITCT to relocation portions of our transmission lines, often with a very short time to comply. This blanket is for smaller projects (each less than $1 million) with in service dates too soon to run through the normal MTEP process. |  |  |  | 2022-12-31 | 345 | 120 | 2000000
MTEP22 | East | ITC Transmission | 21166 | Maple - J1062 Generator Interconnection | Build a new 345kV 3 breaker substation cut-in from the Lemoyne - Majestic 345kV circuit, and removal of terminal equipment at Majestic 345kV substation. | MI | GIP |  | J1062 is a 150 MW Solar Power Plant connecting to the ITCT Lemoyne - Majestic 345 kV circuit in the DPP-2018-APR Cycle. |  |  |  | 2023-06-01 | 345 | 0 | 16434520
MTEP22 | East | ITC Transmission | 21726 | Warren 120kV Pos JJ Station Equipment Upgrade | Replace station equipment at Warren to meet or exceed 528 MVA (2540 Amps) | MI | BRP |  | The station equipment at Warren Pos JJ is projected to be overloaded for P21 contingency during peak load condition. |  |  |  | 2026-06-01 | 120 | 0 | 160000
MTEP22 | East | ITC Transmission | 21745 | Cato - Waterman 120 kV Re-conductor | The Cato – Waterman 120 kV underground cable is projected to overload for P11 and P6 contingencies during peak load. The limiting elements on this circuit are the cable conductor. | MI | BRP |  | The proposed solution is to re-conductor approximately 4.43 miles utilizing 1600MM2 CU XLPE underground cable. |  |  |  | 2026-06-01 | 120 | 0 | 15000000
MTEP22 | East | ITC Transmission | 21958 | Augusta 2 120kV PTS Additions | Install 2 new 120 kV, 1-way, full-load-break 2,000 A GOAB switches near the Augusta 2 Tap. | MI | Other | Reliability | Installing pole-top switches, or replacing them as appropriate, at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. This significantly reduces service interruptions to the customers during planned maintenance work or restoration from the aftermath extreme weather events. Even if an automatic load throw-over (ATO) scheme is present at a station which is tapped off two circuits, that customer or distribution station can still benefit from having pole top switches installed at the tap points on those circuits because in the event of a double circuit tower (DCT) outage, an ATO will not be able to restore service to the customer if both circuits are on the same structure. Installing pole top switches on those circuits will enable us to still serve that customer even during that scenario by sectionalizing the circuit. If nothing is done, this will reduce our ability to sectionalize the circuits with tapped customers and may increase restoration time to the tapped stations in the event of an outage. |  |  |  | 2024-12-31 | 120 | 0 | 1300000
MTEP22 | East | ITC Transmission | 22013 | ITCT Pole Top Switch Additions/Replacement Program 2023 | Install or replace an existing pole top switch with a new 120 kV, 1-way full-load-break pole top switch at tap points. | MI | Other | Reliability | The ITCT system has many 120 kV load interconnection taps that do not have pole-top switches installed on either one or both sides of the tap or have switches that are not operable. Without pole-top switches, this reduces the flexibility to isolate faults or planned outages of a section of the line (for repair work or maintenance purposes. As a consequence, all distribution or industrial load that is tapped and served from the line will be out of service along with it until the faulted section can be repaired. Since there are no switches installed at these junctions or the switches are not operable, it is impossible to sectionalize a faulted part of the circuit to restore power to customers while the crew is working on bringing that section of the line back in-service again. The transmission circuits are often long transmission lines which have more exposure to weather related forces (e.g. ice, snow, wind, extreme temperatures, and lightning strikes). |  |  |  | 2023-12-31 | 138 | 0 | 2400000
MTEP22 | East | ITC Transmission | 22016 | 2025 ITCT Customer Interconnections | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $1 Million that have an in service date within the year 2025 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $1 Million a separate project will be submitted for approval. | MI | Other | Load Growth | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. These projects are strictly in response to customer interconnection requests. They are not being proposed to address any specific ITCT system reliability concerns. |  |  |  | 2025-12-31 | 120 | 0 | 2000000
MTEP22 | East | ITC Transmission | 22017 | 2024 ITCTransmission Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | Other | Age and Condition | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. |  |  |  | 2024-12-31 | 345 | 120 | 37140000
MTEP22 | West | Montana-Dakota Utilities Company | 20946 | Poplar2 115/60 kV | Build a Poplar Oil Field 115/60 kV sub and a 115 kV line from the Poplar Trans sub to the Poplar Oil Field sub to tie into the 60 kV system near MDU's Poplar Oil Field load. | MT | Other | Load Growth | Load growth; extend 115 kV to Poplar Oil Field to support load growth on the 60 kV system and mitigate 60 kV voltage violations under Poplar 60 kV line-end outage contingency or loss of existing 115/60 kV transformer at Poplar. |  |  |  | 2024-12-31 | 115 | 60 | 8525000
MTEP22 | West | Montana-Dakota Utilities Company | 21889 | Hettinger 115/69/41.6 | Rebuild Hettinger Substation 115/69/41.6 due to age and condition | ND | Other | Age and Condition | Age and condition |  |  |  | 2024-12-31 | 115 | 0 | 6500000
MTEP22 | West | Montana-Dakota Utilities Company | 21894 | Retire Tioga 1 | Retire Tioga 1, expand Tioga 2 to move the 60 kV lines from Tioga 1 to Tioga 2 along with a 115/60 kV transformer, move 115 kV lines position in station and add another 115 kV breaker. | ND | Other | Age and Condition | Retire old sub and expand a newer substation |  |  |  | 2024-12-31 | 115 | 60 | 7050000
MTEP22 | West | MidAmerican Energy Company | 21871 | Sub E East Moline 69 kV Upgrades | Replace aged equipment at Sub E East Moline. Project includes installing a new control building, replacing 69 kV oil circuit breakers, and replacing 69 kV cap-and-pin switches and insulators. | IL | Other | Age and Condition | Lifecyle management of older equipment |  |  |  | 2024-12-31 | 69 | 0 | 7000000
MTEP22 | West | MidAmerican Energy Company | 21872 | Sub E East Moline-Sub 37 69 kV OPGW Installation | Install OPGW on the Sub E East Moline-Sub 37 69 kV Line | IL | Other | Other Local Needs | Fiber path needed for communication and protective relaying |  |  |  | 2024-12-31 | 69 | 0 | 1000000
MTEP22 | West | MidAmerican Energy Company | 21873 | Sub 39-Sub 28 161 kV OPGW Installation | Install OPGW on the 161 kV line from Sub 39-Sub 28 | IL | Other | Other Local Needs | Fiber path needed for communication and protective relaying |  |  |  | 2021-12-31 | 161 | 0 | 700000
MTEP22 | West | MidAmerican Energy Company | 21874 | Sub 17 Expansion to Add 345-161 kV Transformer | Convert Sub 17 161 kV yard to a ring bus. Loop the Sub 49-Beaver Channel 161 kV line into Sub 17. Add a new short 345 kV line connecting Cordova and Sub 17 and a new 345-161 kV transformer at Sub 17. | IL | BRP |  | Local 161 kV bus voltages identified as being below planning criteria minimum for NERC TPL-001 Category P6 N-1-1 contingencies in the MTEP21 reliability assessment. |  |  |  | 2024-12-31 | 345 | 161 | 23000000
MTEP22 | West | MidAmerican Energy Company | 21893 | Neal North 161-69 kV Transformer Replacement | Replace Neal North 161-69 kV Transformer AC2 (83.3 MVA unit) which recently failed with a spare unit. Purchase a new 161-69 kV transformer at Neal North as a spare unit. | IA | Other | Reliability | The Neal North 161-69 kV Transformer AC2 (83.3 MVA unit) recently failed and is in the process of being replaced. The replacement transformer will be a spare 161-69 kV, 83.3 MVA unit with an load tap changer (LTC). The replacement of Neal North transformer with spare unit and purchase of new spare transformer will be completed by the end of this year. |  |  |  | 2021-09-30 | 161 | 69 | 1600000
MTEP22 | West | MidAmerican Energy Company | 21895 | Sycamore 161-69 kV Transformer Replacement | Replace the failed 161-69 kV transformer at Sycamore substation with a spare unit. Purchase a new 161-69 kV spare transformer at Sycamore substation. | IA | Other | Reliability | The 161-69 kV transformer at Sycamore substation failed recently and is in the process of being replaced. The transformer will be replaced with a spare unit of same size. A new 161-69 kV spare transformer will be purchased at Sycamore substation. |  |  |  | 2021-12-31 | 161 | 69 | 3000000
MTEP22 | West | MidAmerican Energy Company | 21896 | NE 94th Avenue 161-13.2 kV Substation | Construct NE 94th Ave 161-13.2 kV substation and taps | IA | Other | Load Growth | Reliability improvement and serve load |  |  |  | 2023-06-01 | 161 | 13.2 | 6700000
MTEP22 | West | MidAmerican Energy Company | 21897 | Berwick 161-13.2 kV Substation | Construct Berwick 161-13.2 kV substation and taps | IA | Other | Load Growth | To serve growing load. |  |  |  | 2025-06-01 | 161 | 13.2 | 6700000
MTEP22 | West | MidAmerican Energy Company | 21898 | Increase Bus Withstand Capabiities | At Raun 161 kV, Neal North 161 kV, CBEC 161 kV, Sycamore 161 kV and Sycamore 69 kV, replace insulators, install new bus supports and/or replace bus to increase bus withstand capabilities | IA | Other | Reliability | Fault current can exceed existing bus capabillities. |  |  |  | 2023-12-01 | 161 | 69 | 6500000
MTEP22 | West | MidAmerican Energy Company | 21901 | Raun Substation: 345 kV Switch Replacements | Replace 10 switches due to condition | IA | Other | Age and Condition | Reliability improvement |  |  |  | 2022-12-01 | 345 | 0 | 900000
MTEP22 | West | MidAmerican Energy Company | 21902 | Anthon Substation | Construct a new 69-12.47 kV distribution substation and associated 69 kV line work. | IA | Other | Load Growth | Serve load |  |  |  | 2023-12-01 | 69 | 0 | 1500000
MTEP22 | West | MidAmerican Energy Company | 21904 | Sioux Center Substation | Construct a new 69-12.47 kV distribution substation and associated 69 kV line work. | IA | Other | Load Growth | Serve load |  |  |  | 2023-12-01 | 69 | 0 | 600000
MTEP22 | West | MidAmerican Energy Company | 21906 | Sheldon-Boyden 69 kV Line Uprate | Replace structures and jumpers on Sheldon-Boyden 69 kV line to increase line rating | IA | Other | Age and Condition | Reliability improvement |  |  |  | 2022-12-01 | 69 | 0 | 600000
MTEP22 | West | MidAmerican Energy Company | 21907 | Replace structures on Templeton-Audubon North-Exira 69 kV line to increase line rating | Replace terminal equipment at Audubon North and replace structures on Templeton-Audubon North-Exira 69 kV line to increase the line rating | IA | Other | Reliability | Reliability improvement |  |  |  | 2023-06-01 | 69 | 0 | 1650000
MTEP22 | West | MidAmerican Energy Company | 21908 | Carroll County-Auburn-Sherwood 69 kV Line Rebuild & Terminal Upgrades | Rebuild 69 kV lines from Carroll County to Auburn and Auburn to Sherwood and replace line structures. | IA | Other | Age and Condition | Several line structure issues have been found during annual inspection. Also this facility gets congested occasionally. The project will fix the issues in line structures and will relive the congestion as well. |  |  |  | 2024-12-01 | 69 | 0 | 7700000
MTEP22 | West | MidAmerican Energy Company | 21909 | Sac City Switching Station & Rebuild of Sac County-Odebolt-Schaller 69 kV Line | Construct new Sac City switching station to interconnect two MidAmerican 69 kV lines and one Corn Belt 69 kV line | IA | BRP |  | Low voltage can occur for loss of Sac County 161-69 kV Transformer |  |  |  | 2024-12-01 | 69 | 0 | 20000000
MTEP22 | West | MidAmerican Energy Company | 21910 | Hills 345 kV Equipment Replacements | Replace 345 kV Breakers and switches at Hills substation due to condition and operational issues. Replace relaying on two Hills lines and remote ends. The project will be completed in conjunction with MTEP Project 20121 | IA | Other | Age and Condition | Reliability improvement |  |  |  | 2022-12-31 | 345 | 0 | 5400000
MTEP22 | West | MidAmerican Energy Company | 21911 | IC Enron Substation: 161 kV Line Switch Additions | Add line switches at IC Enron Substation. | IA | Other | Age and Condition | Reliability Improvement |  |  |  | 2022-12-31 | 161 | 0 | 300000
MTEP22 | West | MidAmerican Energy Company | 21912 | Substation J 161 kV Capacitor Bank Replacement | Replace 161 kV Capacitor due to condition and operational failures. | IA | Other | Age and Condition | Reliability improvement |  |  |  | 2022-12-31 | 161 | 0 | 500000
MTEP22 | West | MidAmerican Energy Company | 21913 | Northgate Substation: Ring bus expansion and 161 kV tie line to ITCM’s Rose Hollow Substation | Expand Northgate Substation to a ring bus configuration and build 161 kV tie line from Northgate Substation to ITCM owned Rose Hollow Substation | IA | Other | Reliability | Reliability improvement |  |  |  | 2024-12-01 | 161 | 0 | 3500000
MTEP22 | West | MidAmerican Energy Company | 21914 | Butler 161-69 kV Transformer | Install 161-69 kV, 125 MVA Transformer at Butler Substation to accommodate a networked 69 kV system between MidAmerican’s Butler, New Hartford and Shell Rock Substations and Corn Belt’s Donald Feldman Switching Station. MTEP21. The project also include upgrading 34.5 kV lines from Butler to New Hartford and New Hartford to Shell Rock to 69 kV lines. | IA | BRP |  | Satisfy MidAmerican's 69 kV n-1-1 voltage reliability criteria |  |  |  | 2024-12-01 | 161 | 69 | 25700000
MTEP22 | West | MidAmerican Energy Company | 22305 | Lakefield Jct to Obrien 345 kV Line Structure Replacements | The project will replace some line structure on MidAmerican owned part of Lakefield to Obrien 345 kV line. This project will increase the line rating of MidAmerican portion of Lakefield to Obrien 345 kV. | IA | Other | Other Local Needs | The Lakefield to Obrien 345 kV line congestion was studied as part of MidAmerican's local stakeholder planning process using PROMOD models. The project show good benefits to MidAmerican LBA. |  |  |  | 2022-12-31 | 345 | 0 | 2200000
MTEP22 | West | MidAmerican Energy Company | 22746 | Overland Trail to Fallow Avenue 345 kV line structure replacements | Replace five line structures on Overland Trail to Fallow avenue 345 kV line. | IA | Other | Age and Condition | These structures were damaged due to storm and will be replaced by the end of year 2022. |  |  |  | 2022-12-31 | 345 | 0 | 1250000
MTEP22 | West | MidAmerican Energy Company | 22747 | Interstate Containment Structures Installation Blanket | Based on recent experience from storms and its effects on transportation, installation of containment structures on either side of heavily traveled interstate and similar highway crossings is planned. The structures will reduce the likelihood of failure. If a severe storm occurs, the containment structures will reduce cascading and enable faster cleanup of the highway because the conductor can be cut free as it will not be under high tension. | IA | Other | Other Local Needs | The wood H-frame or monopole structures will be replaced with steel structures. New structures are planned at two 345 kV crossings, three 161 kV crossing, and five 69 kV crossings. |  |  |  | 2022-12-31 | 345 | 0 | 13000000
MTEP22 | West | MidAmerican Energy Company | 23366 | Powell Creek 161-13 kV Substation | Construct a new Powell Creek 161-13 kV distribution substation tapping the Buena Vista-Sac County 161 kV line. | IA | Other | Load Growth | Serve new customer load |  |  |  | 2024-01-02 | 161 | 13 | 5500000
MTEP22 | West | MidAmerican Energy Company | 23480 | Substation 18: Replace Failed 161/69 kV Transformer 1 | Replace transformer that was failed in May 2022. Purchase replacement spare transformer for the unit being replaced at Sub. 18 | IA | Other | Age and Condition | Replace failed transformer at Sub. 18 |  |  |  | 2022-09-30 | 161 | 69 | 3400000
MTEP22 | West | MidAmerican Energy Company | 23516 | Enterprise Way South Substation | Construct new 161-13.2 kV distribution substation bisecting the existing Sub 56-Enterprise Way 161 kV line. | IA | Other | Load Growth | Serve new customer load |  |  |  | 2024-09-01 | 161 | 0 | 3500000
MTEP22 | East | METC | 15910 | Marquette - Bingham 138 kV Rebuild | Rebuild 18.76 miles of the Marquette – Bingham circuit using 954 ACSR conductor with double-circuit steel structures. | MI | Other | Reliability | The Marquette – Bingham 138 kV Rebuild project is being re-submitted to MTEP22 due to the age and condition of the circuit. This project was first submitted to MTEP19 and was recommended to Appendix B by MISO. Based on the latest METC circuit rating data (updated in March 2020), this line is the 17th worst performing circuit (top 20 worst circuits) on the system. The Marquette – Bingham 138 kV line outages effect three (3) major customers: Ventra (American Bumper Sub), MWC (formerly Glanbia, Technical Drive Sub Ckt #1) and Proliant (Technical Drive Ckt #2). The sentiment of these customers is that they feel there are frequent outages. The Technical Drive substation customers have experienced two major outages since the sub was built in early 2020. |  |  |  | 2025-12-31 | 138 | 0 | 27600000
MTEP22 | East | METC | 20906 | Styx - J984 Generator Interconnection | Build a new 345kV three breaker ring bus station and cut-in the Murphy - Nelson Road 345kV line. Remote relay upgrades at Murphy 345kV and Nelson Road 345kV substations, as well as jumper work at Slate 345kV substation. | MI | GIP |  | J984 is a 200MW Wind Power Plant in the DPP-2018-April Cycle connecting to the METC Murphy - Nelson Road 345 kV circuit. |  |  |  | 2023-01-31 | 345 | 0 | 15319904
MTEP22 | East | METC | 20965 | METC Line Relocation Blanket | Relocation portions of transmission lines located in public right of way at the government entity's mandate. | MI | Other | Other Local Needs | ITCT has transmission lines and underground cables in road right of way, without easement. The State of Michigan and local municipalities have road improvement projects which require ITCT to relocation portions of our transmission lines, often with a very short time to comply. This blanket is for smaller projects (each less than $1 million) with in service dates too soon to run through the normal MTEP process. |  |  |  | 2022-12-31 | 345 | 138 | 2000000
MTEP22 | East | METC | 21145 | J996 Generator Interconnection | Build a new 138 kV, 3 breaker ring switching station cut in from the METC Beecher - Morocco 138 kV circuit. | MI | GIP |  | J996 is a 80 MW Solar Power Plant that requested to interconnect to the METC Beecher - Morocco 138 kV circuit in the DPP-2018-APRIL cycle |  |  |  | 2023-03-31 | 138 | 0 | 6618732
MTEP22 | East | METC | 21146 | J1172 Generator Interconnection | Build a new 138 kV, 3 breaker ring switching station cut in from the METC Dort - Garfield 138 kV circuit. | MI | GIP |  | J1172 is a 50 MW Solar Power Plant that requested to interconnect to the METC Dort - Garfield 138 kV circuit in the DPP-2018-APRIL cycle. |  |  |  | 2023-11-15 | 138 | 0 | 10889470
MTEP22 | East | METC | 21185 | Muskrat - J1043 Generator Interconnection | Build a new three breaker ring bus station and cut-in the Vergennes - Nelson Road 345kV line. Install remote relay upgrades at Vergennes 345kV and Nelson Road 345kV substations. | MI | GIP |  | J1043 is a Wind farm capable of 374.4 MW of generation in the DPP-2018-April cycle connecting to the METC Vergennes - Nelson Road 345kV circuit |  |  |  | 2024-05-31 | 345 | 0 | 9585454
MTEP22 | East | METC | 21445 | Donaldson Creek - White Lake 138 kV Rebuild (J1071) | Rebuild approximately 18.43 miles of the 336 ACSR conductor utilizing 954 ACSR on standard 138 kV double circuit structures with OPGW. Upgrade 336 ACSR Line Drop and 336 ACSR Bus at White Lake Position 188, as well as the 336 ACSR line drop at Donaldson Creek position BM11 to meet or exceed the summer emergency rating of the new conductor. | MI | GIP |  | The MISO East 2019 DPP cycle determined that the Donaldson Creek - White Lake 138kV line is limited by the 336 ACSR conductor as a result of the J1071 generation interconnection. |  |  |  | 2024-06-01 | 138 | 0 | 30142027
MTEP22 | East | METC | 21446 | J1071 Generator Interconnection | Install 138kV breaker at position 13W8. Install 138kV disconnect switches at positions 13W8 & 13M6. | MI | GIP |  | J1071 is a 100 MW Solar Power Plant that requested to interconnect to the METC Donaldson Creek 138kV substation in the DPP-2018-APRIL cycle. |  |  |  | 2023-12-31 | 138 | 0 | 1159555
MTEP22 | East | METC | 21485 | Lawndale - Murphy 138kV Sag Remediation | The proposed solution is to remove sag limits on the Lawndale to Murphy 138 kV line to conductor limit. | MI | BRP |  | Lawndale to Murphy 138 kV line is projected to be overloaded for P1, P2, P3, P6, and P7 contingencies in peak and off-peak scenarios. This consequently causes the Lawndale to Murphy 138kV line section to exceed its summer emergency limit. The overloaded equipment identified on this circuit is the overhead conductor, 795 ACSR 26/7. |  |  |  | 2025-12-31 | 138 | 0 | 931000
MTEP22 | East | METC | 21505 | Houghton Lake Interconnection | Create a three-breaker ring bus switching station. Install three 138kV breakers, buswork, and associated disconnects. Loop in the METC Bard Rd - Higgins 138kV circuit to the new switching station. Connect CE Houghton Lake Substation to new switching station. | MI | Other | Load Growth | Consumers Energy has provided notification for a new 138kV substation to be located approximately 12.5 miles west of the METC Bard Rd - Higgins point of interconnection. Houghton Lake station will serve 13.5 MW and 7.9 MVAR of load transferred from the CE Houghton Heights Substation. The new switching station is needed to service the new CE substation. |  |  | 5 | 2025-06-01 | 138 | 0 | 6161060
MTEP22 | East | METC | 21706 | Mill Creek Interconnection | Install tap pole and two 1-way switches to facilitate the Mill Creek tap on the Mcgulpin-Riggsville line. | MI | Other | Load Growth | WPSC has provided a formal interconnection request for transmission service tapped from the Mcgulpin - Riggsville 138kV line. WPSC will construct Mill Creek substation as a 138/13.08 kV distribution station with a single transformer and high-side protection. Mill Creek station will serve 1.62 MW and 0.7 MVAR of new load and 1.39 MW of transferred load from the WPSC Cheboygan Station. |  |  | 62 | 2023-06-30 | 138 | 0 | 1822800
MTEP22 | East | METC | 21890 | Gallagher - Ogemaw 138 kV Sag Remediation | Remediate sag on the 336 ACSR conductor on the Gallagher to Ogemaw 138 kV circuit up to at least 60 MVA summer emergency rating. | MI | BRP |  | The Gallagher - Ogemaw 138 kV circuit is projected to be overloaded for P2, P5, and P6 contingencies during peak load conditions. The identified overloaded equipment on this circuit is the sag limit on the Gallagher – Ogemaw 138 kV sections. |  |  |  | 2026-06-01 | 138 | 0 | 660000
MTEP22 | East | METC | 21945 | Parr Road-Whiting 138kV Rebuild | Rebuild approximately 12 miles from Parr Rd - Tangent (J875 Generator Interconnection) and approximately 28.6 miles from Raisin Tap - Whiting on 138kV future double circuit steel poles with 1431 ACSR conductor with OPGW (coordinating with J875 Generator Interconnection project). | MI | Other | Reliability | The METC system relies heavily on both wood poles and steel lattice towers, many of which are 70 years of age or older. METC transmission structures may experience increasing failure rates that could degrade reliability on the system. Maintenance, partial rebuild, or complete rebuild activities need to be undertaken on aging circuits throughout the system in order to maintain acceptable levels of system reliability. ITC performed an analysis in 2020 to assess the METC and ITCT circuits based on 4 main factors: recent outage history, current maintenance needs, age and type of structures and circuit importance. The objective of the analysis was to assist ITC staff in identifying circuits that should be considered for rebuilding. While there is not a specific criteria used to determine when these assets reach their end of life, utilizing the factors described above helps to prioritize replacement of aging infrastructure across the ITC systems. Based on that criteria, the Parr Rd - Whiting 138kV line is being recommended for a full rebuild. Currently based on the 2020 analysis, this line is in the top 10 worst performance circuit on the ITC systems. Upon further investigation, approximately 80% of this circuit is found to be structurally overloaded. This can lead to reduced life expectancy, more frequent maintenance, and pose an elevated safety risk particularly during reactive maintenance and system restoration. Additionally, this compromised design renders the circuit inflexible for marginal improvements and limited preventative maintenance. METC is recommending this circuit be rebuilt in order to maintain acceptable levels of system performance and to improve system reliability. Most poles are expected to reach their maximum life span in the next 5-10 years. Furthermore, approximately 80% of the circuit is found to be structurally overloaded. |  |  |  | 2025-05-15 | 138 | 0 | 53580500
MTEP22 | East | METC | 21947 | Roedel Road 138 kV PTS Replacements | The proposed solution is to replace 3185 and 3198 pole top switches with 2 new 138kV, 1-way, full-load-break 2,000 A GOAB switch near the Roedel Road Tap. | MI | Other | Reliability | Installing pole-top switches, or replacing them as appropriate, at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. This significantly reduces service interruptions to the customers during planned maintenance work or restoration from the aftermath extreme weather events. Even if an automatic load throw-over (ATO) scheme is present at a station which is tapped off two circuits, that customer or distribution station can still benefit from having pole top switches installed at the tap points on those circuits because in the event of a double circuit tower (DCT) outage, an ATO will not be able to restore service to the customer if both circuits are on the same structure. Installing pole top switches on those circuits will enable us to still serve that customer even during that scenario by sectionalizing the circuit. If nothing is done, this will reduce our ability to sectionalize the circuits with tapped customers and may increase restoration time to the tapped stations in the event of an outage. |  |  |  | 2024-12-31 | 138 | 0 | 1200000
MTEP22 | East | METC | 21952 | Dutton 138 kV PTS Replacements | Replace 3004, 3017 and 3493 pole top switches with 3 new 138kV, 1-way, full-load-break 2,000 A GOAB switch near the Dutton Tap. | MI | Other | Reliability | Installing pole-top switches, or replacing them as appropriate, at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. This significantly reduces service interruptions to the customers during planned maintenance work or restoration from the aftermath extreme weather events. |  |  |  | 2024-12-31 | 138 | 0 | 1700000
MTEP22 | East | METC | 21984 | METC Pole Top Switch Additions/Replacement Program 2023 | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. | MI | Other | Reliability | The METC system has many 138 kV load interconnection taps that do not have pole-top switches installed on either one or both sides of the tap or have switches that are not operable. Without pole-top switches, this reduces the flexibility to isolate faults or planned outages of a section of the line (for repair work or maintenance purposes. As a consequence, all distribution or industrial load that is tapped and served from the line will be out of service along with it until the faulted section can be repaired. Since there are no switches installed at these junctions or the switches are not operable, it is impossible to sectionalize a faulted part of the circuit to restore power to customers while the crew is working on bringing that section of the line back in-service again. The transmission circuits are often long transmission lines which have more exposure to weather related forces (e.g. ice, snow, wind, extreme temperatures, and lightning strikes). |  |  |  | 2023-12-31 | 138 | 0 | 2400000
MTEP22 | East | METC | 21990 | Cut Iosco – Karn into Twining 138 kV | Cut the Iosco – Karn 138 kV circuit into the Twining 138 kV substation. This will require expand the Twining 138 kV substation and constructing approximately 0.15 miles of new right of way to bring the line into the substation. | MI | Other | Reliability | This project aims to increase reliability and address operational issues in Northern Michigan. The Iosco – Karn 138 kV circuit is 82 mile long and can only be safely removed from service during off peak times. Taking Iosco – Karn out of service can only be performed outside of summer months due to area voltages and overloads on the CE 46kV system. Splitting this line in half would reduce the number of required outages to perform maintenance. If at any time the line is lost for any reason during the summer, METC is in an extreme rush to return the line to service. Splitting this circuit in half would provide operational flexibility and increase reliability. The Twining substation also struggles with taking outages during the summer peak load. This project would provide more connections at the station for operational flexibility when taking outages. |  |  |  | 2026-06-01 | 138 | 0 | 4100000
MTEP22 | East | METC | 21993 | METC Pole Top Switch Additions/Replacement Program 2024 | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. | MI | Other | Reliability | The METC system has many 138 kV load interconnection taps that do not have pole-top switches installed on either one or both sides of the tap or have switches that are not operable. Without pole-top switches, this reduces the flexibility to isolate faults or planned outages of a section of the line (for repair work or maintenance purposes. As a consequence, all distribution or industrial load that is tapped and served from the line will be out of service along with it until the faulted section can be repaired. Since there are no switches installed at these junctions or the switches are not operable, it is impossible to sectionalize a faulted part of the circuit to restore power to customers while the crew is working on bringing that section of the line back in-service again. The transmission circuits are often long transmission lines which have more exposure to weather related forces (e.g. ice, snow, wind, extreme temperatures, and lightning strikes). |  |  |  | 2024-12-31 | 138 | 0 | 2400000
MTEP22 | East | METC | 21995 | 2025 METC Customer Interconnections | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $1 Million that have an in service date within the year 2025 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $1 Million a separate project will be submitted for approval | MI | Other | Load Growth | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. These projects are strictly in response to customer interconnection requests. They are not being proposed to address any specific ITCT system reliability concerns. |  |  |  | 2025-12-31 | 138 | 0 | 2000000
MTEP22 | East | METC | 22000 | 2024 METC Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | Other | Age and Condition | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. |  |  |  | 2024-12-31 | 138 | 0 | 39400000
MTEP22 | East | METC | 22001 | Westwood 138 kV Interconnection | Install a 138 kV breaker and associated equipment at Plum station to accommodate Wolverine’s interconnection request. | MI | Other | Load Growth | Wolverine Power Cooperative requests for a new 138 kV interconnection to METC’s Plum station. |  |  |  | 2024-12-31 | 138 | 0 | 3700000
MTEP22 | East | METC | 22020 | Leoni – Parr Rd 138kV Rebuild | Rebuild approximately 19 miles from Leoni to Parr Rd utilizing 1431 ACSR on standard 138 kV double circuit steel poles with OPGW. | MI | Other | Age and Condition | The majority (approximately 80%) of the Leoni - Parr Rd 138 kV circuit contains structures that are 70 years of age and have reached their end of life. Approximately 20% of those structures is tagged for replacement. The most recent inspection determined that several structures were marked “urgent” for replacements (needed ASAP or within 2 years) due to the amount of internal decay found. Furthermore, an investigation on the conditions of the structures determined that over 65% of the circuit contains structures that are structurally overloaded. Structures that are overloaded can lead to reduce life expectancy, more frequent maintenance, and pose an elevated safety risk particularly during reactive maintenance and system restoration. Additionally, this compromised design renders the circuit inflexible for marginal improvements and limited preventative maintenance. Therefore, METC recommends that this circuit be rebuilt to maintain acceptable levels of system reliability and performance. |  |  |  | 2025-12-31 | 138 | 0 | 32630000
MTEP22 | East | METC | 22021 | Chopin – Dupont – White Lake 138kV Rebuild | Rebuild approximately 21 miles of the Chopin – Dupont – White Lake 138 kV Circuit from around structure 003F410 to Dupont utilizing 954 ACSR conductor on standard 138 kV double circuit structures with OPGW and relocate Cobb - White Lake and Dupont White Lake lines to the other side of the new 138 kV standard structures utilizing 954 ACSR conductor. | MI | Other | Age and Condition | Cobb – Dupont – White Lake 138 kV Approximately 70% of the structures on the Cobb – Dupont – White Lake 138 kV circuit consists of wood pole structures from its original construction of 1962 and is at or approaching its end of life. About 35% of these structures are slated to be replaced. Furthermore, as much as 67% of the structures in this circuit were identified to be structurally overloaded. Cobb – White Lake 138 kV Approximately 90% of the structures on the Cobb – White Lake 138 kV circuit consists of wood pole structures from its original construction of 1953 and is at or approaching its end of life. About 34% of these structures are slated to be replaced. Furthermore, as much as 87% of the structures in this circuit were identified to be structurally overloaded Structures that are overloaded can lead to reduce life expectancy, more frequent maintenance, and pose an elevated safety risk particularly during reactive maintenance and system restoration. Additionally, this compromised design renders the circuit inflexible for marginal improvements and limited preventative maintenance. Furthermore, many of the structures between the two circuits are in extremely poor conditions (See example pictures in the “Other Project Justification” section below). Therefore, METC recommends that these circuits be rebuilt in order to maintain acceptable levels of system reliability and performance. Since extensive replacements are necessary on both circuits, METC determined the best path forward is to rebuild one circuit with double circuit structures and place the other circuit on the empty side. |  |  |  | 2025-12-31 | 138 | 0 | 39018000
MTEP22 | East | METC | 22586 | Buskirk - New CE Interconnection | METC to construct a new 138 kV switching station, Buskirk, with three 138 kV breakers in a ring-bus configuration, expandable for a fourth line exit, and cut the Buck Creek-Hazelwood 138 kV line in. | MI | Other | Age and Condition | Consumers Energy requested to interconnect a new 138/46 kV bulk power substation (Buskirk), proposed to be located adjacent to the existing Titus Lake substation. Consumers Energy plans to retire and decommission Wayland 138/46 kV bulk power substation once Buskirk is energized. |  |  |  | 2024-12-31 | 138 | 0 | 7800000
MTEP22 | East | METC | 22627 | Day - New WPSC Interconnection | Tap the Deja Jct. – Derby Jct. section of Eureka – Vestaburg 138kV line, approximately 2.5 miles West of Deja Tap. Transmission tap will be ~ 4 miles long. Install tap pole at the tap location, install two new 138 kV, 1-way, full-load-break 2000 A. | MI | Other | Load Growth | WPSC interconnection request for transmission service tapped from the Deja Jct. – Derby Jct. section of Eureka – Vestaburg 138kV line. WPSC will construct Day substation as a distribution station with a single transformer and associated high-side protection. Wolverine has submitted the following MTEP project into the portal database for the WPSC owned portion of facilities: Day Interconnection – MTEP21 Target A, project #21665 |  |  |  | 2024-06-01 | 138 | 0 | 1132000
MTEP22 | East | METC | 23246 | CE - Riverbend Tap (Saginaw River - Twining 138 kV) | Install a tap pole and two 1-way, 2000 Amp switches near structure #229 on the Saginaw River-Twining 138 kV line to connect Consumer Energy’s new Riverbend substation. | MI | Other | Load Growth | Consumers Energy requested to tap METC's Saginaw-Twining 138 kV line to connect its new Riverbend substation. The new Riverbend substation will serve 4.25 MW load, 1.35 MW of it is being transferred from the existing Bessinger substation (46kV). |  |  | 25 | 2023-12-31 | 138 | 0 | 1160000
MTEP22 | West | Minnesota Power (Allete, Inc.) | 17868 | Duluth Loop 115 kV Project | Construct new 115 kV lines: Hilltop - Haines Road 115 kV and Haines Road - Ridgeview 115 kV Combine existing Arrowhead - Haines Road 115 kV and Haines Road - Swan Lake 115 kV lines to create Arrowhead - Swan Lake 115 kV Line Expand Ridgeview Substation to a ring bus which will allow 2 additional transmission line connections Add 115 kV line entrance at Hilltop and add a breaker at Haines Road | MN | BRP |  | Voltage collapse for loss of connection to Arrowhead Substation, thermal overloads on Arrowhead - Colbyville 115 kV for loss of Arrowhead - Haines Road 115 kV and vice versa |  |  |  | 2026-12-31 | 115 | 0 | 46900000
MTEP22 | West | Minnesota Power (Allete, Inc.) | 18058 | Square Butte - Arrowhead HVDC Line Hardening | Structure replacements to improve HVDC line resiliency and restorability at critical locations, including transportation and infrastructure crossings. | ND | Other | Reliability | Resiliency |  |  |  | 2023-12-31 | 250 | 0 | 14000000
MTEP22 | West | Minnesota Power (Allete, Inc.) | 20074 | Two Islands 115 kV Project | Construction of new 115 kV switching station near the existing Tac Harbor Substation. Route North Shore-Tac Harbor and Mesaba Junction-Tac Harbor Ckt #1 & Ckt #2 into the new switching station. One capacitor bank will be added to the switching station and it will connect to a new GRE 115/69 kV Two Islands Substation | MN | Other | Reliability | Safety, expandability, and outage constraint concerns with the existing Tac Harbor substation design. |  |  |  | 2024-12-31 | 115 | 0 | 14100000
MTEP22 | West | Minnesota Power (Allete, Inc.) | 20077 | Hilltop 230 kV Reliability Project | Upgrade Hilltop 1TR to 373 MVA base 230/115 kV transformer. Add 230 kV breaker to high side of transformer. Disconnect Hilltop Tap from 3-Terminal 230 kV line and extend this tap 0.7 Miles to a new line entrance at Arrowhead 230 kV. | MN | BRP | Reliability | Additional transformation capacity needed at Hilltop. Breaking up the existing 3-terminal 230 kV line connected to Hilltop will resolve existing relaying and reliability concerns. |  |  |  | 2024-12-31 | 230 | 115 | 13100000
MTEP22 | West | Minnesota Power (Allete, Inc.) | 21605 | Hibbing Transmission Exits | Rebuild two 115 kV lines coming into Hibbing Substation on double circuit structures and realign entrances to coordinate with Hibbing Substation Modernization Project (MTEP #18064) | MN | Other | Age and Condition | Asset renewal - age & condition - non-standard framing of existing 115 kV lines. Also, a need to realign at the substation exits in response to relocations within the substation itself. |  |  |  | 2025-12-31 | 115 | 0 | 2000000
MTEP22 | West | Minnesota Power (Allete, Inc.) | 21606 | West Cohasset Project | Add new 115-23 kV transformer at existing Boswell SES substation and rename substation | MN | Other | Load Growth | New customer load interconnection to 23 kV system |  |  |  | 2024-12-31 | 115 | 23 | 500000
MTEP22 | West | Minnesota Power (Allete, Inc.) | 21608 | 105 & 106 Line Upgrade | Rebuild and upgrade the two short parallel Blackberry - Iron Range 230 kV Lines | MN | BRP | Reliability | Increased capacity |  |  |  | 2024-12-31 | 230 | 0 | 1500000
MTEP22 | West | Minnesota Power (Allete, Inc.) | 21686 | Mesaba Junction 137 Line Extension | Add breaker and transmission line entrance to Mesaba Junction Switching Station. Extend existing Embarrass - Babbitt 115 kV Line to switching station and establish a normal open between the Babbitt Tap and the Argo Tap | MN | BRP |  | Provides redundancy to an industrial load pocket that requires near-constant availability. Improves reliability by providing to independent sources to the Babbitt area. Enables asset renewal by allowing the existing Embarrass-Babbitt 115kV Line to be taken out of service and improved. |  |  |  | 2024-12-31 | 115 | 0 | 9000000
MTEP22 | West | Minnesota Power (Allete, Inc.) | 21763 | North Shore Transformer Addition | Add 115/14 kV transformer to existing North Shore Switching Station. Relocate 13K cap bank to make room for transformer | MN | Other | Age and Condition | Age & condition - project enables retirement of the existing Silver Bay Hillside Substation |  |  |  | 2022-12-31 | 115 | 0 | 250000
MTEP22 | West | Minnesota Power (Allete, Inc.) | 21766 | 126 Line Asset Renewal | Replace transmission line structural components on Little Fork - I.Falls 115 kV Line, replace Little Fork 126L breaker, and replace relay panels on both ends of 126 Line | MN | Other | Age and Condition | Age & condition |  |  |  | 2023-12-31 | 115 | 0 | 900000
MTEP22 | East | Michigan Public Power Agency | 21761 | Zeeland Riley Transformer Addition | Install a second 138/69 kV Transformer at Riley Substation | MI | Other | Load Growth | With the voltage conversion of the Wolverine transmission system to 138kV, there should be a focus on maintaining sufficient backup capacity in the 138kV:69kV connection. With the loss of one of the two 138kV:69kV transformers in the 2021 projected load scenario, internal generation would be needed to maintain load levels below rated capacity for the remaining transformer. An additional 83.3MVA 138kV:69kV transformer installed at Riley Substation would provide sufficient capacity for an N-1 contingency through 2035 load projections. |  |  | 3 MVA | 2022-09-30 | 138 | 69 | 1465000
MTEP22 | West | Missouri River Energy Services (MRET) | 21938 | Worthington Sub 2 Breaker | A breaker will be added to Worthington Public Utilities(WPU) Sub #2. The breaker will protect for a fault between Sub #2 and Elk. | MN | Other | Reliability | The normally open line between WPU Sub #1 and Sub #2 as a result of the MTEP 20608 Worthington Substation project. A breaker will be added to minimize load exposure to a single fault. |  |  |  | 2023-04-01 | 69 | 0 | 375000
MTEP22 | West | Missouri River Energy Services (MRET) | 23346 | Hutchinson Substation | This project will add a second 115/69 kV transformer to the existing City of Hutchinson MN, Hutchinson Substation. The project will also rebuild the Hutchinson 115 kV into a four position ring bus. | MN | Other | Load Growth | There are existing operational concerns in the area that require generation to be ran system intact. The City of Hutchinson expects a large expansion of existing customer load over the next couple of years, which will exacerbate the operational concern. |  |  |  | 2025-12-31 | 115 | 69 | 8000000
MTEP22 | Central | Northern Indiana Public Service Company | 21167 | New Menges Ditch 138/69 kV Substation | New 138/69kV Substation source from AEP's E. Elkhart substation. | IN | Other | Reliability | New 69kV source needed in the Bristol area. |  |  |  | 2025-12-31 | 138 | 69 | 42368620
MTEP22 | Central | Northern Indiana Public Service Company | 21168 | New Hiple to Northport 138kV Line | New Hiple to Northport 138kV line | IN | Other | Reliability | Support to East 69kV Network. Relieves overload of 6990 seen in system outage studies. |  |  |  | 2024-12-31 | 138 | 0 | 27527004
MTEP22 | Central | Northern Indiana Public Service Company | 21867 | Rebuild Marktown 138 kV Substation | Rebuild Marktown 138kV Substation | IN | Other | Age and Condition | Age & Condition |  |  |  | 2024-12-31 | 138 | 0 | 30190251
MTEP22 | Central | Northern Indiana Public Service Company | 21870 | Rebuild S.Chalmers -Oakdale 69 kV_Circuit 6972 | Rebuild circuit 6972, South Chalmers to Oakdale substations | IN | Other | Age and Condition | Age & Condition |  |  |  | 2022-12-31 | 69 | 0 | 4917926
MTEP22 | Central | Northern Indiana Public Service Company | 21875 | Rebuild Lagrange 69 kV line-Circuit 6980 | Rebuild 3.4 miles of circuit 6980 | IN | Other | Age and Condition | Age and Condition |  |  |  | 2023-12-31 | 69 | 0 | 3014269
MTEP22 | Central | Northern Indiana Public Service Company | 21876 | Upgrade Transmission Substation - 2022 Program | Transmission Age & Condition Projects | IN | Other | Age and Condition | Age & Condition |  |  |  | 2022-12-31 | 345 | 69 | 26223459
MTEP22 | Central | Northern Indiana Public Service Company | 21878 | Upgrade transmission lines - 2022 program | Rebuilds/upgrades 69 kV and up line based on age and condition, including structures, conductor, switches and communication upgrades (fiber) | IN | Other | Age and Condition | Age & Condition |  |  |  | 2022-12-31 | 138 | 34 | 36772890
MTEP22 | Central | Northern Indiana Public Service Company | 21879 | Upgrade Transmission Substation - 2023 Program | Upgrades/replacements 69 kV and up Substation based on age and condition, including but not limited to switches, breakers, transformers, and protection and communication equipment. | IN | Other | Age and Condition | Age & Condition |  |  |  | 2023-12-31 | 345 | 34 | 42330170
MTEP22 | Central | Northern Indiana Public Service Company | 21880 | Upgrade transmission lines - 2023 program | Rebuilds/upgrades 69 kV and up line based on age and condition, including structures, conductor, switches and communication upgrades (fiber) | IN | Other | Age and Condition | Age and Condition |  |  |  | 2023-12-31 | 345 | 34 | 19261989
MTEP22 | Central | Northern Indiana Public Service Company | 21881 | Upgrade Transmission Substation - 2024 Program | Upgrades/replacements 69 kV and up Substation based on age and condition, including but not limited to switches, breakers, transformers, and protection and communication equipment. | IN | Other | Age and Condition | Age & Condition |  |  |  | 2024-12-31 | 345 | 34 | 32711473
MTEP22 | Central | Northern Indiana Public Service Company | 21882 | Upgrade transmission lines - 2024 program | Rebuilds/upgrades 69 kV and up line based on age and condition, including structures, conductor, switches and communication upgrades (fiber) | IN | Other | Age and Condition | Age & Condition |  |  |  | 2024-12-31 | 345 | 34 | 31312504
MTEP22 | Central | Northern Indiana Public Service Company | 21883 | Upgrade Transmission Substation - 2025 Program | Upgrades/replacements 69 kV and up Substation based on age and condition, including but not limited to switches, breakers, transformers, and protection and communication equipment. | IN | Other | Age and Condition | age & condition |  |  |  | 2025-12-31 | 345 | 34 | 26977092
MTEP22 | Central | Northern Indiana Public Service Company | 21884 | Upgrade transmission lines - 2025 program | Rebuilds/upgrades 69 kV and up line based on age and condition, including structures, conductor, switches and communication upgrades (fiber) | IN | Other | Age and Condition | Age & Condition |  |  |  | 2025-12-31 | 345 | 34 | 30216017
MTEP22 | Central | Northern Indiana Public Service Company | 21885 | Upgrade Transmission Substation - 2026 Program | Upgrades/replacements 69 kV and up Substation based on age and condition, including but not limited to switches, breakers, transformers, protection and communication equipment. | IN | Other | Age and Condition | Age & Condition |  |  |  | 2026-12-31 | 345 | 34 | 54852316
MTEP22 | Central | Northern Indiana Public Service Company | 21886 | Upgrade transmission lines - 2026 program | Rebuilds/upgrades 69 kV and up lines based on age and condition, including structures, conductor, switches and communication upgrades (fiber). | IN | Other | Age and Condition | Age & Condition |  |  |  | 2026-12-31 | 345 | 34 | 68286845
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21950 | New Timmons 69/12 kV substation | Build the new Timmons 69/12 kV 14.4 MVA sub. | IN | Other | Load Growth | Build new substation to serve member load |  |  | 4 MVA | 2023-12-31 | 69 | 12 | 5301167
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21954 | New Rosebud 69/12kV Sub | Building new Rosebud 69/12 substation to feed load normally fed from existing Parr substation. | IN | Other | Load Growth | Transfer of load from Old substation |  |  |  | 2022-11-29 | 69 | 12 | 4947000
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21955 | Upgrade Fair Oaks 2nd bank 138/69/12 kV transformer | Add second 138/69/12kV 22.4MVA transformer to Fair Oaks substation to handle new load in area | IN | Other | Load Growth | Add second 138/69/12kV 22.4MVA transformer to Fair Oaks substation to handle new load in area |  |  | 4 MVA | 2024-10-17 | 69 | 12 | 4176754
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21956 | New Yellow River 69 kV Sub | Build a new 69kv/12.5 kV 14.4 MVA substation near the Knox Industrial Park. Install 13 MVAR cap bank. Build 0.5 miles of 69 kV to new sub. | IN | Other | Load Growth | New Ind park load |  |  | 4 MVA | 2023-12-31 | 69 | 12 | 5255244
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21957 | Upgrade Oregon 69 kV Sub | Replace existing 7 MVA substation transformer at the KVREMC owned Oregon Substation to a 14 MVA. Add a backup transmission line for Oregon Substation and tap the nearby 69105 (0.25mi). New ATO scheme to be installed on KVL property on transmission line poles and to be owned by WVPA. | IN | Other | Load Growth | Substation needs to supply new load in area. |  |  | 7 MVA | 2023-12-31 | 69 | 12 | 1338591
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21959 | Upgrade Moody 69 kV sub | Purchase the Moody Substation from NIPSCO and replace the transformer (14.4MVA from Fair Oaks), regulators, fuses, and jumpers. Add oil containment around a new foundation. | IN | Other | Age and Condition | Substation needed upgrade. Old and needed larger transformer |  |  |  | 2022-09-01 | 69 | 12 | 1500000
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21961 | New Marco 69/12 kV substation | Build new Marco substation near the existing NIPS Argos substation. 69/12kV 14.4MVA Xfmr, design for 4 ckts used initially. Will replace Marshall MP. Add external control Hut for Fiber connections (Rochester Fiber). Build short tap from Nipsco 6968 to new sub | IN | Other | Load Growth | Backup of existing load and added load. |  |  | 4 MVA | 2022-12-30 | 69 | 12 | 4947000
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21962 | New Berthaville 69/12 kV sub | New Berthaville substation needed south of Goodland for new dairy farm and added load near Newton office. 14.4 MVA transformer, 4 distr exits, 69kV with manual switch to Nipsco 6964 line. | IN | Other | Load Growth | New Berthaville substation needed south of Goodland for new dairy farm and added load in area. |  |  | 4 MVA | 2022-09-30 | 69 | 12 | 4200000
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21964 | Upgrade Colfax 138/69/12 kV substation | Add 2nd transformer to Colfax substation. 138/69/12kV 22.4MVA transformer. Substation work to make space for new transformer. | IN | Other | Load Growth | Added load in area |  |  | 4 MVA | 2023-11-30 | 69 | 12 | 5000000
MTEP22 | Central | Wabash Valley Power Association, Inc. | 21965 | Upgrade Otter sub eqmnt | Otter substation in Steuben has an inoperable switch and transrupter that need replaced. Replacing switch with a load break manual switch and replacing the transrupter with a S&C Circuit Switcher. | IN | Other | Age and Condition | Old equipment |  |  |  | 2023-07-31 | 69 | 12 | 872640
MTEP22 | Central | Northern Indiana Public Service Company | 22630 | J1067 Network Upgrades | Network upgrades necessary to connect J1067 to interconnect at NIPSCO's Reynolds to Burr Oak 345kV line | IN | GIP |  | Network upgrades necessary to connect J1067 to interconnect at NIPSCO's Reynolds to Burr Oak 345kV line |  |  |  | 2023-10-20 | 345 | 0 | 23632643
MTEP22 | Central | Northern Indiana Public Service Company | 22649 | J968 J1069 Network Upgrades | New 345kV breaker in Bay 6 at Reynolds substation to accommodate new lead line into northern position, plus all associated equipment | IN | GIP |  | Network upgrades necessary for J968 and J1069 to connect to NIPSCO's Reynolds 345kV substation |  |  |  | 2023-04-30 | 345 | 0 | 2204486
MTEP22 | West | Otter Tail Power Company | 20385 | OTP Buffalo to Alice 115 kV Rebuild | Rebuild 7 miles of 115 kV line due to poor performance. | ND | Other | Reliability | Rebuild 7 miles of 115 kV line due to poor performance. |  |  |  | 2024-11-01 | 115 | 0 | 2000000
MTEP22 | West | Otter Tail Power Company | 20565 | Forman 230/115 kV uprate | Increase the capacity of the the Forman 230/115 kV transformer and the Forman - Forman WAPA 115 kV line. | ND | MPFP |  | A Market Participant has requested that these facilities capacity be increased. |  |  |  | 2024-10-09 | 230 | 115 | 6162000
MTEP22 | West | Otter Tail Power Company | 21427 | OTP Max Water Treatment Plant 41.6 kV | Project Description: This project will consist of: 1. Add one 41.6 kV circuit breaker at Max. | ND | Other | Load Growth | A new water treatment plant is interconnecting to OTP's system in Max, ND. This new load addition is driving the need for transmission upgrades in the Max, ND and Parshall, ND 41.6 kV areas. |  |  |  | 2022-08-31 | 41.6 | 0 | 350000
MTEP22 | West | Otter Tail Power Company | 22606 | OTP Jamestown, ND Load Addition | OTP has a new customer requesting to be served in Jamestown, ND. The customer facility will have a demand of 100 MWs. OTP will serve the new customer from the 41.6 kV tertiaries of both the existing Jamestown 345/115/41.6 kV transformers. The load will be split 50/50 between each of the transformers. OTP will install a new 115/41.6 kV 24 MVA transformer at the Jamestown 345 kV substation. The 115 kV bus will be expanded to allow for the new 115/41.6 kV transformer. The existing 41.6 kV load will be moved to be served off the new 115/41.6 kV 24 MVA transformer. | ND | Other | Load Growth | The new 115/41.6 kV transformer will serve the existing 41.6 kV load, allowing additional capacity on the 41.6 kV tertiaries of the Jamestown 345/115/41.6 kV transformers to serve the new customer. | Load Growth |  | 24 MVA | 2023-11-01 | 115 | 41.6 | 2268000 | OTP EPR project
MTEP22 | West | Otter Tail Power Company | 23148 | OTP Fergus Falls & Canby Area MPFPs | OTP has been requested by a Market Participant (Market Participant Funded Project - MPFP) to increase the capacity of the following Facilities: 1. Canby - Granite Falls 115 kV 2. Hoot Lake - Fergus Falls 115 kV 3. Hoot Lake - Fergus Falls SE 115 kV The Market Participant has requested an in-service date of 1/1/2023. | MN | MPFP |  | A Market Participant has requested that the capacity of the facilities below be increased: 1. Canby - Granite Falls 115 kV 2. Hoot Lake - Fergus Falls 115 kV 3. Hoot Lake - Fergus Falls SE 115 kV |  |  |  | 2023-06-30 | 115 | 0 | 1705000
MTEP22 | Central | Prairie Power, Inc. | 19945 | New Topeka-Bishop 69 kV Line | New Topeka--Bishop 69 kV line (~8-mile) w/ 556 MCM in MEC | IL | Other | Reliability | Provide alternative feeds to Topeka and Bishop substations. Part of 69 kV path from Forest City to Grand Island, |  |  |  | 2025-12-31 | 69 | 0 | 5120000
MTEP22 | Central | Prairie Power, Inc. | 19950 | New St. David-Wee-Ma-Tuk-Canton 69 kV line | New St. David-Wee-Ma-Tuk-Canton 69 kV line (10.4-mile) in Spoon River Electric Cooperative | IL | Other | Reliability | Provide alternative feeds to St. David, Wee-Ma-Tuk, and Canton substations |  |  |  | 2023-12-31 | 69 | 0 | 5596000
MTEP22 | Central | Prairie Power, Inc. | 19952 | Rebuild Walkerville-Eldred 69 kV line | Rebuild Rebuild Walkerville-Eldred 69 kV line (7.3-mile) in Illinois Electric Cooperative | IL | Other | Age and Condition | Age and Condition. Replace 4/0 line built in 1967 with 336.4 MCM ASCR conductor |  |  |  | 2024-12-31 | 69 | 0 | 3942000
MTEP22 | Central | Prairie Power, Inc. | 21746 | New Bluff Hall-E. Hannibal 69 kV line | New Bluff Hall-E. Hannibal 69 kV line (~9-mile) 69 kV Line | IL | Other | Reliability | Provide backup feed to E. Hannibal and Barry substations. |  |  |  | 2024-12-31 | 69 | 69 | 4184000
MTEP22 | Central | Prairie Power, Inc. | 21747 | New Barry 69 kV Substation | New Barry 69 kV Transmission Substation near Barry, IL. Terminals to Bluff Hall, Liberty, Pittsfield, and Barry Distribution substation. | IL | Other | Load Growth | Provide service to new load (Cannibis facility) at Barry Distribution substation. |  |  |  | 2022-12-31 | 69 | 69 | 1600000
MTEP22 | Central | Prairie Power, Inc. | 21748 | Rebuild Barry-E. Hannibal Tap 69 kV line to double circuit | Rebuild Barry-Old E. Hannibal Tap 69 kV line to double circuit. Split the Pittsfield to Liberty 69 kV line into a Pittsfield to Barry circuit and a Liberty to Barry circuit. Incudes new 0.3 mile line from Barry toward E Hannibal tap. Rebuilding only a portion of E Hannibal tap to Barry North and South. | IL | Other | Load Growth | Provide network service to Barry substation. |  |  |  | 2022-12-31 | 69 | 0 | 3762000
MTEP22 | Central | Prairie Power, Inc. | 21749 | New Trailblazer 69 kV Substation | New Trailblazer 69 kV breaker substation near Marblehead, IL. | IL | Other | Reliability | Trailblazer Breaker Station will sectionalize 69 kV lines to St, Anthony, Liberty and Barry. |  |  |  | 2024-12-31 | 69 | 69 | 2935000
MTEP22 | Central | Prairie Power, Inc. | 21750 | New Rock Creek 69 kV Substation | New Rock Creek 69 kV breaker station near Ursa substation in Adams Electric Cooperative. Breaker station will have terminals looking towards Elvaston, Golden, and Payson. | IL | Other | Reliability | Sectionalize three terminal line to Ursa, Big Neck, and Burton. |  |  |  | 2025-12-31 | 69 | 69 | 2935000
MTEP22 | Central | Prairie Power, Inc. | 21751 | New Panther 138/69 kV Substation | New Panther 138/69 kV substation near Pana, IL in Shelby Electric Cooperative. | IL | Other | Reliability | Provide backup for ISHI 138/69 kV substation. Allow for networking of several Shelby Electric Cooperative substations including Pana, Herrick and ISHI. Allow for upgrading of 34.5 kV system in area to 69 kV. |  |  |  | 2025-12-31 | 138 | 69 | 8425000
MTEP22 | Central | Prairie Power, Inc. | 21752 | New Panther-Pana Tap 69 kV line | New Panther-Pana Tap 69 kV line (~2.5-mile) in Shelby Electric Cooperative | IL | Other | Reliability | Provide new feed for Shelby Electric Cooperative's Pana distribution substation, including conversion from 34.5 kV to 69 kV. Part of line connecting Panther to ISHI. |  |  |  | 2025-12-31 | 69 | 69 | 2250000
MTEP22 | Central | Prairie Power, Inc. | 21753 | New Pana Tap-Lakewood 69 kV line | New Pana Tap-Lakewood 69 kV line (~12-mile) in Shelby Electric Cooperative | IL | Other | Reliability | Provide new feed to Lakewood and Herrick substations in Shelby Electric Cooperative including conversion from 34.5 kV to 69 kV. Part of line connecting Panther to ISHI. |  |  |  | 2025-12-31 | 69 | 69 | 7680000
MTEP22 | Central | Prairie Power, Inc. | 21754 | New ISHI-Herrick 69 kV line | New ISHI-Herrick 69 kV line (~9.7-mile) in Shelby Electric Cooperative. This is part of the line from Panther to ISHI. | IL | Other | Reliability | Provide new feed for Herrick substation including conversion from 34.5 kV to 69 kV. This line is part of the line from Panther to ISHI substations. |  |  |  | 2025-12-31 | 69 | 0 | 5474000
MTEP22 | Central | Prairie Power, Inc. | 21755 | Rebuild Hadley Breaker-Barry 69 kV line | Rebuild portion of Hadley Breaker-E. Hannibal Tap 69 kV line (0.54-mile) in Illinois Electric Cooperative. | IL | Other | Age and Condition | Age and condition. Replace 4/0 line built in 1967 with 336.4 ACSR line. |  |  |  | 2025-12-31 | 69 | 69 | 270000
MTEP22 | Central | Prairie Power, Inc. | 21756 | Rebuild Hadley Breaker-Hadley 69 kV line | Rebuild Hadley Breaker-Hadley 69 kV line (1.61-mile) in Illinois Electric Cooperative | IL | Other | Age and Condition | Age and condition. Replace 4/0 ACSR line built in 1967 with 336.4 ACSR line, |  |  |  | 2025-12-31 | 69 | 69 | 805000
MTEP22 | Central | Prairie Power, Inc. | 21757 | Rebuild Barry-Liberty 69 kV line | Rebuild portion of Barry-Liberty 69 kV line (6.35-mile) between Illinois Electric Cooperative and Adams Electric Cooperative. | IL | Other | Age and Condition | Age and condition. Replace 4/0 line built in 1967 with 336.4 MCM ACSR line. |  |  |  | 2023-12-31 | 69 | 69 | 3175000
MTEP22 | Central | Prairie Power, Inc. | 21758 | Rebuild Kampsville-Kampsville River Crossing 69 kV line | Rebuild Kampsville-Kampsville River Crossing 69 kV line (0.7-mile) in Illinois Electric Cooperative | IL | Other | Age and Condition | Age and condition. Replace 4/0 line originally built in 1949 with 336.4 MCM ACSR conductor. |  |  |  | 2025-12-31 | 69 | 69 | 350000
MTEP22 | Central | Prairie Power, Inc. | 21760 | New Rushville 69 kV Substation | New 69 kV Rushville breaker substation in Adams Electric Cooperative. Terminals will look to Golden and Liberty. | IL | Other | Reliability | Sectionalize the line between Golden and Liberty which will contain five substations on the Adams East Loop: Camden, Rushville, Mt. Sterling, Sugar Grove and Kellerville. |  |  |  | 2024-12-31 | 69 | 69 | 2935000
MTEP22 | Central | Prairie Power, Inc. | 21788 | Rebuild Andrew-Barclay 69 kV line | Rebuild Andrew-Barclay 69 kV line (~7.5-mile) in Menard Electric Cooperative. Replace 4/0 ACSR line built in 1964 with 556.5 MCM ACSR conductor. | IL | Other | Age and Condition | Age and condition. Upgrade rating of East Lanesville to Andrew path to accommodate CWLP imports. |  |  |  | 2024-12-31 | 69 | 69 | 3755000
MTEP22 | Central | Prairie Power, Inc. | 21789 | Rebuild Lanesville-Barclay 69 kV Line | Rebuild ~11.5-mile Lanesville to Barclay 69 kV line in Menard Electric Cooperative. Replace 4/0 ACSR line built in 1964 with 556.5 MCM ACSR conductor. | IL | Other | Age and Condition | Age and condition. Increase rating of East Lanesville to Andrew path to accommodate CWLP imports. |  |  |  | 2025-12-31 | 69 | 69 | 5745000
MTEP22 | Central | Prairie Power, Inc. | 21791 | Rebuild E. Lanesville-Lanesville 69 kV line | Rebuild E. Lanesville-Lanesville 69 kV line (~0.9-mile) in Menard Electric Cooperative. Replace 336.4 MCM ACSR line built in 1981 with 556.5 MCM ACSR conductor. | IL | Other | Reliability | Upgrade rating of East Lanesville to Andrew path to improve CWLP import capability. |  |  |  | 2024-12-31 | 69 | 69 | 450000
MTEP22 | Central | Prairie Power, Inc. | 21792 | Rebuild Fancy Creek-Andrew 69 kV line | Rebuild Fancy Creek-Andrew 69 kV line (~4.5-mile) in Menard Electric Cooperative. Replace 336.4 MCM ACSR line built in 1969 with 556.5 MCM ACSR conductor. | IL | Other | Age and Condition | Age and condition. Upgrade Fancy Creek to Andrew path to accommodate CWLP imports. |  |  |  | 2026-12-31 | 69 | 69 | 2250000
MTEP22 | Central | Prairie Power, Inc. | 21793 | New Forest City-Bishop 69 kV line | New Forest City-Bishop 69 kV line (~2-mile) in Menard Electric Cooperative. | IL | Other | Reliability | Provide alternative feed to Bishop substation. Part of Forest City to Grand Island 69 kV path. |  |  |  | 2025-12-31 | 69 | 0 | 1415000
MTEP22 | Central | Prairie Power, Inc. | 21794 | New Forest City 138/69 kV Substation | New 138/69 kV substation near Forest City, IL in Menard Electric Cooperative. This substation will connect to the Ameren Havana to Cincinnati 138 kV line at Winnebago on the high side and to the Menard Electric Cooperative Forest City to Bishop 69 kV line on the low side with an 84 MVA transformer, | IL | BRP |  | Backup Grand Island transformer for Menard Electric Cooperative, Provide alternative feed to Ameren's Mason City 138 kV substation for P6 loss of Havana - Cane 138 kV and Quiver - Mason City 138 kV. |  |  |  | 2025-12-31 | 138 | 69 | 7725000
MTEP22 | Central | Prairie Power, Inc. | 21795 | New Middletown 69 kV Substation | New 69 kV breaker substation near Middletown, IL in Menard Electric Cooperative. Substation will have terminals looking to Fancy Creek, Grand Island, Forest City, and Middletown Distribution substation. | IL | Other | Reliability | Sectionalize 69 kV lines Middletown - Fancy Creek, Middletown - Grand Island, and Middletown - Forest City. |  |  |  | 2025-12-31 | 69 | 69 | 2107000
MTEP22 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 22002 | Francisco Gen Interconnection (J1074) | Francisco Substation modifications needed for the interconnection of Queue project J1074 | IN | GIP |  | Needed to interconnect generation customer for Queue project J1074 |  |  |  | 2022-12-15 | 138 | 0 | 1805104
MTEP22 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 22004 | Replace Southwind 69/12 kV T2 transformer | Replace 69/12 kV distribution transformer T2 at the Southwind substation | IN | Other | Reliability | Increase distribution capacity at substation |  |  |  | 2023-06-01 | 69 | 12 | 2000000
MTEP22 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 22005 | Replace Duff 345/138 kV substation 345 kV breakers | Replace two 345 kV breakers (#s 3200 and 3300) at the Duff 345/138 kV substation | IN | Other | Reliability | Increase the rating on the Duff - Francisco 345 kV transmission line |  |  |  | 2023-06-01 | 345 | 0 | 1500000
MTEP22 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 22006 | New Anderson Road 69/12 kV Substation | Build new 69/12 kV distribution substation | IN | Other | Load Growth | Address load growth |  |  |  | 2023-06-01 | 69 | 12 | 8500000
MTEP22 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 22007 | Rebuid Warrick North 138 kV switching station | Expand Warrick North 138 kV switching station from ring bus to breaker and a half to allow for new terminal for large industrial customer. | IN | Other | Load Growth | Create new terminal for transmission line to large industrial customer. |  |  |  | 2023-07-01 | 138 | 0 | 3500000
MTEP22 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 22008 | New Kaiser Aluminum 138 kV Sub | Build new 138 kV substation for new large industrial customer. | IN | Other | Load Growth | New large industrial customer interconnection at Kaiser Aluminum 138 kV | Large Industrial (Kaiser Aluminum) |  |  | 2023-07-01 | 138 | 15 | 12000000
MTEP22 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 22009 | New Midwest Fertilizer 138 kV Sub | Build new 138 kV substation on existing 138 kV line for large industrial customer | IN | Other | Load Growth | Large industrial customer - Midwest Fertilizer 138 kV | Large Industrial (Midwest Fertilizer) |  |  | 2023-12-01 | 138 | 12 | 8000000
MTEP22 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 22010 | Scott Gen Interconnection (J856) | New 138 kV terminal at existing Scott 138/69 kV substation to facilitate generation interconnection Queue project J856 | IN | GIP |  | Generation interconnection project |  |  |  | 2023-10-01 | 138 | 0 | 1552504
MTEP22 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 22011 | New Warrick N. - Kaiser 138 kV Line | New 138 kV line from existing Warrick North 138 kV switching station to new Kaiser 138 kV substation to serve large industrial customer. | IN | Other | Load Growth | New customer |  |  |  | 2023-07-01 | 138 | 0 | 2300000
MTEP22 | East | Wolverine Power Supply Cooperative, Inc. | 15652 | Rebuild Atlanta to Gaylord 138kV | Rebuild 22 miles to Wolverine's 138 kV standard | MI | Other | Age and Condition | Condition Based - Replace aging infrastructure. • Built in 1978, current age 44 years • 5 Condemned poles, 144 Damaged poles, 133 Good poles • 53% of poles in need of replacement |  |  |  | 2024-12-31 | 138 | 0 | 16500000
MTEP22 | East | Wolverine Power Supply Cooperative, Inc. | 21425 | Mills Creek Interconnection | Add .9 Miles Transmission and 138kV BUS to accommodate load interconnection. | MI | Other | Load Growth | New interconnection/Load growth |  |  |  | 2022-12-31 | 138 | 0 | 1000000
MTEP22 | East | Wolverine Power Supply Cooperative, Inc. | 21665 | Day Interconnection | New ROW and line for interconnection | MI | Other | Load Growth | Interconnection Request |  |  |  | 2024-06-01 | 138 | 0 | 3500000
MTEP22 | East | Wolverine Power Supply Cooperative, Inc. | 21785 | Grawn Station Protection System Update | Replace obsolete electromechanical relays that require replacement by modern digital relays. | MI | Other | Age and Condition | Protection system is obsolete and requires updated electronics. |  |  |  | 2024-12-31 | 69 | 0 | 1500000
MTEP22 | East | Wolverine Power Supply Cooperative, Inc. | 21787 | Westwood 138kV Interconnection | The Westwood Transmission station was fully rebuilt in 2009 and can accommodate the addition of a new 138kV/69kV power transformer. This project includes adding the power transformer, bus equipment, and protection systems, to accommodate the addition of a 138kV line terminal. | MI | Other | Age and Condition | Mitigate potential overloads seen on the Alba Transformer and allow for the retirement of the Alba Station. Address age and condition based issues seen at Alba station due to its age in excess of 60 years. Eliminate the three terminal protection scheme between Alba, Van Tyle, and Stoever. |  |  |  | 2024-12-31 | 138 | 69 | 18000000
MTEP22 | West | Northern States Power (Xcel Energy) | 20505 | Blue Earth-South Bend Area Upgrades | Rebuild approx. 30 miles of 161 kV line and upgrade South Bend TR6 to a 336 MVA transformer. | MN | BRP |  | Address Thermal violations in multiple sensitivity cases. |  |  |  | 2025-04-15 | 161 | 115 | 40000000
MTEP22 | West | Northern States Power (Xcel Energy) | 21285 | Elm Creek TR10 | Install second 345/115 kV transformer at Elm Creek sub Route SHC-CNC #1 345 kV Line Into Elm Creek Sub Add 50 MVAR reactor to existing TR9. | MN | Other | Reliability | Additional load serving capability in the area Removes need to shed load under contingency Eliminates need for line rebuilds in the area, which would otherwise be required. |  |  |  | 2023-06-01 | 345 | 115 | 9750000
MTEP22 | West | Northern States Power (Xcel Energy) | 21833 | Mallard Facility Rebuild | Joint NSP - Central Power facility rebuild. NSP substation grading and fencing, 3 new box structures, control and wiring modifications to accommodate Central Power equipment moves | ND | Other | Age and Condition | Central Power has failing 43.8kV control circuits and 115-43.8kV facilities approaching end of life. |  |  |  | 2023-05-15 | 115 | 0 | 2340000
MTEP22 | West | Northern States Power (Xcel Energy) | 21834 | Boyd Sub Removal | Retire end of life Boyd sub and install two 5 MVAR capacitor banks at nearby Bateman sub. | WI | Other | Reliability | Project is required to keep the system within NSP Planning Criteria limits. |  |  |  | 2022-06-01 | 69 | 0 | 500000
MTEP22 | West | Northern States Power (Xcel Energy) | 21845 | NSPM Metro Steel Pole Replacement | Address painted poles concerns between Riverside Sub and Main Street Sub. Approximately 4-mile of triple circuit structure(35-structures) to be either replaced, painted or a combination of replace/paint | MN | Other | Age and Condition | The existing structures were installed in the 1980’s and are experiencing paint peeling & steel deterioration |  |  |  | 2024-12-15 | 115 | 0 | 20000000
MTEP22 | West | Northern States Power (Xcel Energy) | 21846 | Hyland Lake TR1 and TR2 Upgrade | Upgrade TR1 and TR2 to 115/13.8 kV 70 MVA transformers at Hyland Lake Substation. Install high-side line breaker. Install new feeder bay. | MN | Other | Reliability | HYL TR1 and TR2 have load at risk under contingency. |  |  |  | 2022-10-15 | 115 | 13.8 | 6670000
MTEP22 | West | Northern States Power (Xcel Energy) | 21848 | Willmar 230/115kV Interconnection | Build new dead-end structure to re-terminate the 0823 line to a southern position at the Willmar sub to accommodate GRE's substation reconfiguration | MN | Other | Reliability | Projected needed to address multiple N-2 low voltage and thermal violations in the area. |  |  |  | 2022-07-09 | 115 | 0 | 800000
MTEP22 | West | Northern States Power (Xcel Energy) | 21853 | North Fork Sub Expansion | Retire the Flambeau breaker station and will add MOD’s to the switches at North Fork substation | WI | Other | Reliability | This project is needed to retire a substation at the ends of its life, consolidate assets at one substation and to remove old EEE equipment from the old Energy Supply building on site while keeping customer reliability high. |  |  |  | 2023-12-01 | 34.5 | 0 | 1500000
MTEP22 | West | Northern States Power (Xcel Energy) | 21866 | Sleepy Eye Cap Bank Retirement | This cap bank is no longer needed to support the area and will be retired to prevent unnecessary maintenance costs on the system. | MN | Other | Other Local Needs | A retirement project is needed to reduce unnecessary maintenance costs. |  |  |  | 2023-06-01 | 69 | 0 | 100000
MTEP22 | West | Northern States Power (Xcel Energy) | 21868 | Canistota Junction Cap Bank Retirement | This cap bank is no longer needed to support the area and will be retired to prevent unnecessary maintenance costs on the system. | MN | Other | Other Local Needs | A retirement project is needed to reduce unnecessary maintenance costs. |  |  |  | 2023-06-01 | 69 | 0 | 100000
MTEP22 | West | Northern States Power (Xcel Energy) | 21869 | BRI CHB 34.5kV Cap Bank Retirement | Retire 34.5kV cap banks at Buffalo Ridge/Chanarambe feeders BRI311, BRI312, and CHB341. | MN | Other | Other Local Needs | A retirement project is needed to reduce unnecessary maintenance costs. |  |  |  | 2023-06-01 | 34.5 | 0 | 250000
MTEP22 | West | Northern States Power (Xcel Energy) | 21877 | Coon Creek Substation 345kV Breaker Additions | Install three 345kV circuit breakers at the Coon Creek (CNC) substation to provide a better isolation between the Main Bus 1 & 2 to the line 1 & 2. | MN | Other | Reliability | Three breakers needed to isolate the SHC-CNC “Line 1” and “Line 3” from the 345kV Main Bus 1 and 2, which will prevent loss of large portions of substation during existing breaker trip. |  |  |  | 2023-12-31 | 345 | 0 | 2700000
MTEP22 | West | Northern States Power (Xcel Energy) | 21887 | Rogers Lake Breaker Addition | Install two breakers at Rogers Lake to separate Airport – Rogers Lake 115 kV line and Rogers Lake TR2 | MN | Other | Reliability | Eliminate single breaker failure and eliminate distribution exposure by terminating the line and TR2 into individual positions in the breaker and a half scheme at RLK. |  |  |  | 2022-02-01 | 115 | 0 | 1860000
MTEP22 | West | Northern States Power (Xcel Energy) | 21888 | Line 0761 Rebuild | Wreck-out 19.7 miles of existing 69kV on line 0761 rebuild to current 69kV Standards | MN | Other | Age and Condition | Rebuilding line for age and condition. Built in 1960, refurbished in 2011. |  |  |  | 2022-12-15 | 69 | 0 | 8500000
MTEP22 | West | Northern States Power (Xcel Energy) | 21891 | Line 0726 Rebuild | NSM 0726-69kV Line Major line rebuild from Pipestone to Tracy Switching Station. | MN | Other | Age and Condition | Rebuilding line for age and condition |  |  |  | 2024-12-21 | 69 | 0 | 17150000
MTEP22 | West | Northern States Power (Xcel Energy) | 21892 | West Shakopee Interconnection | City of Shakopee T-L Interconnection Request. In-and-out off NSP’s Scott County - Dean Lake 115kV transmission line. Joint substation, NSP will own the high side. | MN | Other | Load Growth | Needed to accommodate the rapidly developing load growth along the western edge of the City of Shakopee’s territory. |  |  |  | 2023-06-01 | 115 | 0 | 3000000
MTEP22 | West | Northern States Power (Xcel Energy) | 22629 | Wheaton Sub Tie | Project will tie Wheaton generation bus 1 to bus 2, effectively moving TR3 to the same bus as TR1 and TR2. | WI | Other | Other Local Needs | This project will allow for operational flexibility between the two Wheaton buses. |  |  |  | 2023-06-01 | 161 | 0 | 1500000
MTEP22 | West | Northern States Power (Xcel Energy) | 22686 | Briggs Road - Lacrosse Upgrade | Reconductor of Briggs Road - Mayfair - LaCrosse line for age and condition. Upgrade to larger size to remediate N-1-1 thermal overloads. | WI | BRP |  | Line being reconductored for age and condition. Upgrading to large conductor to remediate N-1-1 overloads. |  |  |  | 2023-05-15 | 161 | 0 | 4000000
MTEP22 | West | Northern States Power (Xcel Energy) | 23452 | Brookings - Lyon, Hampton - Helena 2nd 345kV Circuits | Install second 345 kV circuit between the Brookings County and Lyon County substations. Install second 345 kV circuit between the Hampton Corner and Helena substations. Perform substation upgrades associated with installation of line. | MN | Other | Reliability | Adds second circuit that eliminates current system conditions that impede deliverability of existing resources to demand centers in primarily off-peak periods of high renewable production which results in a reduction of available generation capacity at times of higher than average maintenance and construction outages. |  |  |  | 2025-09-01 | 345 | 0 | 48700000

## MTEP23
MTEP Year | Planning Region | Utility/TO | Project ID | Project Name | Project Description | State | Project Type | Other Type | System Need / Rationale | Project Driver | Data Center Flag | Load (MW) | Expected ISD | Max kV | Min kV | Estimated Cost ($) | Report Notes
MTEP23 | Central | Duke Energy Corporation | 3382 | Vincennes Vigo St. 138kV Dist Sub | Build new radial 138kV line and add breaker at Vincennes 138kV sub to convert Vigo St. sub from 34kV to 138kV | IN | Other | Other Local Needs |  |  |  |  | 2026-07-14 | 138 |  | 10932000
MTEP23 | South | Entergy | 9764 | Dixie Baker to Baker 69 kV: Reconductor Line | Upgrade the Dixie Baker to Baker 69 kV line section. This includes a reconductor/rebuild and upgrading substation equipment. | LA | Other | Reliability |  |  |  |  | 2026-06-01 | 69 |  | 12800000
MTEP23 | South | Entergy Arkansas | 12055 | Gum Springs 115kV: Build Breaker Station | Create a new 115kV switching station by tapping the Arkadelphia North – Richwood 115kV and the Arkadelphia West – Dalark 115kV line sections. | AR | Other | Reliability |  |  |  |  | 2026-06-01 | 115 |  | 14950800
MTEP23 | South | Entergy | 12084 | Dixie Baker to Zachary 69 kV: Upgrade Line | Upgrade the ~3.3 mile long line section. | LA | Other | Reliability |  |  |  |  | 2027-06-01 | 69 |  | 18900000
MTEP23 | South | Entergy | 12098 | Delmont to Hazel 230 kV: Upgrade Line | Upgrade the Delmont to Hazel 230 kV conductor, bus work at both the stations, line bay bus ,jumpers and any station equipment to a minimum of 1600 A. | LA | BRP | [5 empty] | 2026-06-01 | 230 |  | 15600000
MTEP23 | South | South Mississippi Electric Power Association | 12210 | South Hattiesburg Industrial Delivery Point | In order to serve the South Hattiesburg and Hattiesburg Industrial delivery points economically and reliably, service will be established by tapping L161 and constructing a 161kV breaker switching station. A new distribution station will be constructed adjacent to the 161kV switching station and the existing distribution feeders from both delivery points will be routed to the new station. | MS | Other | Other Local Needs |  |  |  |  | 2025-06-01 | 161 |  | 13884200
MTEP23 | South | South Mississippi Electric Power Association | 12222 | Maxie Delivery Point | In order to serve the Maxie delivery point economically and reliably, service will be established by a short transmission feed by tapping the Cooperative Energy Lines 37 and 38 that are near the delivery point. | MS | Other | Other Local Needs |  |  |  |  | 2023-06-01 | 69 |  | 1939497
MTEP23 | South | Entergy | 15654 | Delhi - Tallulah 115 kV rebuild | Rebuild 20.7 miles of 115kV line from Delhi to Tallulah. Operate the series reactor at Delhi as normally open. | LA | BRP | [5 empty] | 2026-12-01 | 115 |  | 39900000
MTEP23 | South | Entergy Mississippi | 15708 | North Jackson 115 kV: Install Circuit Breakers | Install Transmission Breakers at North Jackson 115 kV substation. | MS | Other | Reliability |  |  |  |  | 2025-12-15 | 115 |  | 7300000
MTEP23 | East | METC | 15752 | Redstone – Tittabawassee 138 kV Rebuild | Rebuild ~13.4 miles of the ~21.5 mile-long Redstone – Tittabawassee 138 kV line from 336 ACSR to 1431 ACSR using future double-circuit construction with OPGW. | MI | BRP | [5 empty] | 2027-06-01 | 138 |  | 22170000
MTEP23 | East | ITC Transmission | 15872 | Brownstown-Monroe #2 345 kV Sag Remediation | Remediate the sag on the Brownstown - Monroe #2 345 KV line to at least 1400 MVA and upgrade switches at Monroe "FT" and "FM" positions. | MI | Other | Other Local Needs |  |  |  |  | 2026-12-31 | 345 |  | 2582000
MTEP23 | South | Entergy | 18236 | Winnsboro to Gilbert 115 kV: Rebuild Line | Rebuild approximately 9.5 miles of 115 kV line from Winnsboro to Gilbert. | LA | BRP | [5 empty] | 2026-12-01 | 115 |  | 20900000
MTEP23 | South | Entergy | 18247 | Gilbert to Wisner 115 kV: Rebuild Line | Rebuild Gilbert to Wisner 115 kV line. The line will be built using a double circuit configuration but only strung on one side. The unused side will be reserved for a future 230 kV line. | LA | BRP | [5 empty] | 2027-12-15 | 115 |  | 11900000
MTEP23 | South | Entergy | 18266 | New Long John to Dayton 138 kV: Rebuild line | Rebuild New Long John to Dayton Bulk 138 kV line. | TX | BRP | [5 empty] | 2026-06-01 | 138 |  | 24900000
MTEP23 | Central | Big Rivers Electric Corporation | 19007 | Upgrade Kansas 69 kV line | Create double circuit from existing radial 69 kV tap | KY | Other | Load Growth |  |  |  |  | 2024-10-01 | 69 |  | 900000
MTEP23 | South | Entergy Arkansas | 19911 | Dumas - Reed 115kV: Rebuild Line | Rebuild the 15 mile 115kV line from Dumas - Reed to a minimum through path rating of 259 MVA. | AR | BRP | [5 empty] | 2025-06-01 | 115 |  | 18600000
MTEP23 | Central | Prairie Power, Inc. | 19947 | New Allen-Mason City 69 kV Line | New Allen-Mason City 69 kV line | IL | Other | Reliability |  |  |  |  | 2027-12-31 | 69 |  | 6367500
MTEP23 | Central | Prairie Power, Inc. | 19948 | New Mason City-Middletown 69 kV Line | New Mason City-Middletown 69 kV line | IL | Other | Reliability |  |  |  |  | 2027-12-31 | 69 |  | 9197500
MTEP23 | West | American Transmission Co. LLC | 19963 | Kirkwood SS, Power Transformer and Breaker Asset Renewal | Replace T31, a 1974 vintage 138/69 kV 93 MVA power transformer with the onsite 138/69 kV 100 MVA system spare. • Replace station service transformers of 100 kVA • Replace all relays, RTU, batteries and charger and install new DC panel in existing building • Install battery monitoring solution instead of dual batteries to fit in existing building • Install new 138 kV and 69 kV bus tie breakers and associated disconnect switches • Replace two 69 kV and two 138 kV oil circuit breakers and replace with SF6 gas breakers • Remove and retire disconnect switches no longer in use and bypass switches • Replace one 69 kV disconnect switch due to condition • Replace capacitor cans and protection voltage transformers on existing 19.2 MVAR bank • Install new 138 kV 16.33 MVAR capacitor bank • Install new 138 kV bus PT’s and new 69 kV bus PT’s • Install new line side disconnects • Replace existing CCVT and wave trap • Replace brown glass insulation • Add corona rings to existing line dead-end polymer insulators | WI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 138 |  | 14100000
MTEP23 | West | American Transmission Co. LLC | 20201 | Small Capital Project and Asset Renewal Program 2024 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2024. | WI,MI | Other | Age and Condition |  |  |  |  | 2026-06-30 | 345 |  | 47000000
MTEP23 | West | American Transmission Co. LLC | 20202 | Communication Reliability Program 2024 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2024. | WI,MI | Other | Other Local Needs |  |  |  |  | 2026-06-30 | 0 |  | 11000000
MTEP23 | West | American Transmission Co. LLC | 20203 | Line Clearance Mitigation Program 2024 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2024. | WI,MI | Other | Reliability |  |  |  |  | 2026-06-30 | 345 |  | 10000000
MTEP23 | West | American Transmission Co. LLC | 20204 | Load Interconnection Program 2024 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2024. | WI,MI | Other | Load Growth |  |  |  |  | 2025-06-30 | 345 |  | 16000000
MTEP23 | East | ITC Transmission | 21725 | Horn - Trenton Channel 120 kV Sag Remediation | Fully remediate the sag on the Horn – Trenton Channel 120 kV circuit up to the conductor limit. Upgrade station equipment at Trenton Channel position HG. | MI | BRP | [5 empty] | 2026-12-31 | 120 |  | 320000
MTEP23 | South | Entergy Arkansas | 21807 | Brinkley East 230/115kV Auto: Change Tap Setting | Change the high side taps on the Brinkley East 230/115kV Auto to 242 kV [230kV Auto completed on 3/8/2022]. | AR | BRP | [5 empty] | 2023-03-01 | 230 |  | 15000
MTEP23 | South | Entergy | 21844 | Deer to Doucette 138 kV: Upgrade Station Equipment and Line | Rebuild the ~6 mile Deer to Doucette 138 kV line. | TX | BRP | [5 empty] | 2025-12-01 | 138 |  | 18400000
MTEP23 | West | American Transmission Co. LLC | 21921 | Groenier – Rosholt (ALTE) Tap, 69 kV (Y-71), Partial Rebuild and Rerate | Sectionalize of tap near existing Rosholt (ALTE) Substation with 3-Way T-Line switch. Assumed rebuild section off center due to radial connection. Bury distribution to resolve rerate issues. | WI | Other | Age and Condition |  |  |  |  | 2025-12-31 | 69 |  | 16500000
MTEP23 | Central | Wabash Valley Power Association, Inc. | 21927 | New Kinsey 69/12 kV Substation | Construct New Kinsey 69/12 kV Substation (5/7 MVA). | MO | Other | Reliability |  |  |  |  | 2025-02-06 | 69 |  | 1200000
MTEP23 | Central | Wabash Valley Power Association, Inc. | 21928 | New Valley View-Salem Bulk 69 kV line | Construct New Valley View-Salem Bulk 69 kV line. Construct 69 kV from Salem Bulk 69 kV Substation to Sprott substation, Sprott to Kinsey substation, Kinsey to Valley View substation. Construct with 477 kcm ACSR, 21 miles total. | MO | Other | Reliability |  |  |  |  | 2025-02-06 | 69 |  | 44520000
MTEP23 | West | American Transmission Co. LLC | 21985 | Chandler-Delta 69 kV (Delta1), Rebuild and OPGW | Rebuild approximately 5.5 miles of 69 kV line Delta1 from Delta SS to Chandler SS and install OPGW. | MI | Other | Age and Condition |  |  |  |  | 2026-06-30 | 69 |  | 11600000
MTEP23 | East | ITC Transmission | 22014 | ITCT Pole Top Switch Additions/Replacement Program 2024 | Installing pole-top switches, or replacing them as appropriate, at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. This significantly reduces service interruptions to the customers during planned maintenance work or restoration from the aftermath extreme weather events. | MI | Other | Reliability |  |  |  |  | 2024-12-31 | 120 |  | 2400000
MTEP23 | Central | Ameren Services Company | 22066 | Replace Mason 345/138 kV Transformer No. 1 | Replace Mason 345/138 kV Transformer #1 with a 700 MVA Unit | MO | Other | Reliability |  |  |  |  | 2026-12-01 | 345 |  | 7800000
MTEP23 | East | METC | 22147 | Blackstone-Stable- J1310 Generator Interconnection | Build a new 138 kV 3 Breaker ring substation cut in from the Blackstone - Stable 138 kV line. System changes will require relay upgrades at Stable 138kV and Blackstone 138kV stations. | MI | GIP | [5 empty] | 2024-10-01 | 138 |  | 14648128
MTEP23 | East | METC | 22165 | Brooks Industrial Mud Lake - J1430 Interconnection - NU | Build J1430 interconnection station as a breaker and half station with three breakers in a ring bus configuration. Brooks Industrial - Mud Lake 138kV line will be extended to loop in the J1430 Interconnection 138kV station. Relay upgrades will be required at Mud Lake, Stable, Marshall, and Brooks Industrial 138kV stations. | MI | GIP | [5 empty] | 2023-08-01 | 138 |  | 8609509
MTEP23 | Central | Ameren Services Company | 22186 | Upgrade South Ottawa 138 kV Substation to Ring Bus | Create a 5 position 6 ultimate ring bus at the existing South Ottawa substation | IL | Other | Reliability |  |  |  |  | 2025-06-01 | 138 |  | 9300000
MTEP23 | Central | Ameren Services Company | 22266 | Rebuild Clinton-Oreana and Clinton-Goose Creek 345 kV lines | Rebuild existing double-circuit towers on the Clinton-Oreana-4571/Clinton-Goose Creek-4545 345 kV line due to deteriorated condition. Include the reroute of the 4571 line in to Leghorn. | IL | Other | Age and Condition |  |  |  |  | 2024-12-01 | 345 |  | 34300000
MTEP23 | West | American Transmission Co. LLC | 22587 | North Central WI Reliability Project | Address reliability concerns in the 115kV system in North Central Wisconsin for multiple P6 outage combinations. Scope: • Construct new 115kV source between Hilltop and Pine substations • OPGW to be installed on new line • Asset renewal work on relays at Hilltop, Maine, and Pine substation • Upgrade Pine SS Bus #51 to match rating of new line | WI | BRP | [5 empty] | 2028-06-01 | 115 |  | 47900000
MTEP23 | Central | Ameren Services Company | 22667 | New PPI - Forest City 138 kV Interconnection | Construct a new 138 kV substation in ring bus configuration on the existing Ameren Havana-Cincinnati-1352 138 kV line. A position will feed PPI Forest City 138/69 kV | IL | Other | Reliability |  |  |  |  | 2025-12-01 | 138 |  | 8500000
MTEP23 | Central | Ameren Services Company | 22706 | New Huck Finn Solar 345 kV interconnection (J956) | Connect a 200MW solar farm via 345 kV leadline from Interconnection Customer collector substation to existing Spencer Creek switching station. | MO | GIP | [5 empty] | 2024-06-01 | 345 |  | 4200000
MTEP23 | Central | Ameren Services Company | 22728 | Reconfigure Decatur North—27th St. 138 kV substation | Rebuild this station to a 7 position BAAH, minimum 8 position ultimate BAAH. New name is Boxcar. | IL | Other | Reliability |  |  |  |  | 2025-06-01 | 138 |  | 19800000
MTEP23 | Central | Ameren Services Company | 22787 | Upgrade Warson 161 kV substation | Line BKRs on 4 line terminals, High Side interrupting devices on XFMRs 1,2,3,4, Add bus tie 2-3 BKR | MO | Other | Reliability |  |  |  |  | 2026-12-01 | 138 |  | 8000000
MTEP23 | Central | Ameren Services Company | 22789 | Upgrade Canton South 138 kV substation | New ring bus at Canton South | IL | Other | Age and Condition |  |  |  |  | 2026-06-01 | 138 |  | 3250000
MTEP23 | Central | Ameren Services Company | 22790 | Reconfigure Moreau 161 kV substation | Construct a four position (six ultimate) 161 kV ring bus at Moreau. New name is Jays. | MO | Other | Reliability |  |  |  |  | 2026-12-01 | 161 |  | 8500000
MTEP23 | Central | Ameren Services Company | 22791 | New McBaine 161 kV substation | New switching station at McBaine tap off LYMT-OVRT-3. New name is Katy. | MO | Other | Reliability |  |  |  |  | 2026-12-01 | 161 |  | 14400000
MTEP23 | Central | Ameren Services Company | 22801 | Rebuild Sioux-Meppen North-Hull 138 kV line | Rebuild the Sioux-Meppen North-4 from Str. 180-Meppen North and the entire Meppen North-Hull-1494 138 kV line to upgrade aging infrastructure and improve system reliability. | MO,IL | Other | Age and Condition |  |  |  |  | 2026-12-01 | 138 |  | 77700000
MTEP23 | Central | Ameren Services Company | 22806 | Upgrade Rush Island 345 kV Substation | Upgrade the Rush Island 345 kV bus to 3000A capability | MO | Other | Reliability |  |  |  |  | 2024-04-01 | 138 |  | 1500000
MTEP23 | Central | Northern Indiana Public Service Company | 22809 | J1058 Network Upgrades 345 kV | New Substation(Dinwiddie) and 345kV line to Connect J1058 to NIPSCO's Schahfer to St. John line | IN | GIP | [5 empty] | 2025-06-01 | 345 |  | 24060403
MTEP23 | Central | Ameren Services Company | 22813 | Reconductor Coffeen North-Roxford 345 kV line | Reconductor the 51 mile Coffeen North-Roxford-4551 345 kV line with conductor capable of carrying 3,000 amps during Summer Emergency conditions. | IL | Other | Age and Condition |  |  |  |  | 2025-12-01 | 345 |  | 25000000
MTEP23 | Central | Ameren Services Company | 22814 | Upgrade Guthrie 161 kV substation | Add a 161 kV line breaker to the 161 kV GUTH-LYMT-3 line at Guthrie. | MO | Other | Reliability |  |  |  |  | 2024-12-01 | 161 |  | 2000000
MTEP23 | Central | Ameren Services Company | 22815 | Upgrade Hunter 161 kV substation | Add Line breakers on H2 and H10; High Side Interrupting Devices on XFMR 1, 2, 3 | MO | Other | Age and Condition |  |  |  |  | 2025-12-01 | 161 |  | 3000000
MTEP23 | Central | Ameren Services Company | 22816 | Rebuild Louisville - Newton 138 kV line | Replace the 134 original vintage wood structures on the Louisville-Newton-1 138 kV line due to age and condition. Replace the existing conductor with ones capable of carrying 2,000 amps under Summer Emergency conditions. Replace both shield wires with 72-fiber OPGW. | IL | Other | Age and Condition |  |  |  |  | 2024-12-01 | 138 |  | 32000000
MTEP23 | Central | Ameren Services Company | 22817 | Rebuild Mount Vernon West-Xenia 345 kV line (4591) | Rebuild the existing 37 mile Mount Vernon West-Xenia-4591 345 kV line due to replace decayed and severely woodpecker damaged wood poles. Newly rebuilt line will utilize conductors capable of 3000 amps at Summer Emergency conditions and 2 OPGW's. | IL | Other | Age and Condition |  |  |  |  | 2026-12-01 | 345 |  | 51000000
MTEP23 | Central | Ameren Services Company | 22846 | Upgrade Sioux 138 kV Substation | Upgrade 15H posn to higher ampacity to increase available capacity of the 700MVA Auto XFMR | MO | Other | Age and Condition |  |  |  |  | 2026-12-01 | 138 |  | 10500000
MTEP23 | East | ITC Transmission | 22847 | Kings Point - New DTE 120kV Interconnection | DTE requested a new LDC 120kV substation interconnection, called Kings Point. ITCT will construct a new 120 kV station and cut the Boyne - Golf 120 kV line in to accommodate this new interconnection. The configuration for ITCT’s 120 kV station will be a straight bus station with one 40kA section breaker and two 40kA line breakers. ITCT will relocate a ~ 2.1 miles section of the Boyne-Golf 120kV circuit by utilizing DTE’s existing 40kV circuit on the North side of 21 Mile Rd, East side of N. Gratiot Ave, and South side of Hall Rd to rebuild this ~2.1 miles to 120kV with 40kV underbuilding to loop the Boyne-Golf line into the new 120kV substation. | MI | Other | Load Growth |  |  |  |  | 2027-03-31 | 120 |  | 20000000
MTEP23 | Central | Ameren Services Company | 22848 | Rebuild Hutsonville-Heath 138 kV line (1311) | Rebuild the Hutsonville-Heath-1311 138 kV line from Hutsonville-Str. 95 with conductors capable of 2000 amps at Summer Emergency and OPGW. | IL | Other | Reliability |  |  |  |  | 2025-06-01 | 138 |  | 12500000
MTEP23 | Central | Ameren Services Company | 22851 | Rebuild Mount Vernon West-West Frankfort East 345 kV line (4561) | Rebuild the existing 36 mile Mount Vernon West-West Frankfort East-4561 345 kV line. Newly rebuilt line will utilize conductors capable of 3000 amps at Summer Emergency conditions and 2 OPGW's. | IL | Other | Age and Condition |  |  |  |  | 2025-06-01 | 345 |  | 48000000
MTEP23 | Central | Ameren Services Company | 22866 | Upgrade St Francois 345 kV substation | Install a new circuit breaker at St. Francois 345 kV Sub position V43 to complete the ring bus. Replace 138 kV breakers. Upgrade relaying. | MO | Other | Reliability |  |  |  |  | 2027-06-01 | 345 |  | 12700000
MTEP23 | Central | Ameren Services Company | 22868 | Upgrade Quincy South 138 kV substation | Replace 1753 and 1823 BKRs, Replace 1751 line switch. | IL | Other | Age and Condition |  |  |  |  | 2024-12-01 | 138 |  | 3000000
MTEP23 | Central | Ameren Services Company | 22869 | Rebuild Clark 138/161 kV Substation to 138 kV BAAH | Rebuild Clark 138/161 kV Substation to have a 138 kV BAAH bus with 8 positions (4 existing lines, 2 XFMRs, bring in RIV-ALFM-6636) and a 161 kV ring bus with 6 positions (2 existing lines, 2 XFMRs, and new line position to Viburnum). Rebuild the existing Clark-Viburnum 161 kV line to be double circuit 161 kV lines. Add a 161 kV terminal at Viburnum Substation. Route the RIV-ALFM-6636 138 kV line into the new Clark 138 kV BAAH bus. New name is Clemens. Install 161kV PCB (or CS) on XFMR 3. Install 138kV PCB on XFMR 3. Replace existing differential relaying with new 161kV bus diff, XFMR diff, and 138kV bus diff. | MO | BRP | [5 empty] | 2027-12-01 | 161 |  | 44350000
MTEP23 | Central | Ameren Services Company | 22870 | Reconfigure Mason-Carrollton-Sioux 138 kV lines | Split the ~2 mile Mason-Carrollton-8/Carrollton-Sioux-8 138 kV lines into two separate circuits to avoid the loss of a single structure causing a long-term outage on both Carrollton supplies. | MO | Other | Reliability |  |  |  |  | 2025-06-01 | 138 |  | 5000000
MTEP23 | West | Great River Energy | 22871 | Cedar Lake Line Rebuild | Relocate the existing Cedar Lake tap line to a new route to accommodate Hampton Corners - Helena 345 kV addition to the Hampton Corners - Chub Lake - Helena structures. | MN | Other | Other Local Needs |  |  |  |  | 2025-08-01 | 69 |  | 12772504.79
MTEP23 | Central | Ameren Services Company | 22873 | Upgrade Oran 161 kV substation | Add 161 kV ring bus to split the Kelso- Morley-3 line into two lines | MO | Other | Reliability |  |  |  |  | 2026-06-01 | 161 |  | 7800000
MTEP23 | West | Minnesota Power (Allete, Inc.) | 22885 | Brainerd Crypto | Mitigation solutions to accommodate a 70 MW Load addition at Brainerd 115 kV bus, including a second 20 MVAR capacitor bank and thermal upgrade of the Brainerd - Riverton 115 kV Line | MN | Other | Load Growth | Mitigation for 70 MW cryptocurrency mining load at Brainerd 115 kV bus; second 20 MVAR capacitor bank and thermal upgrade of Brainerd-Riverton 115 kV line | Crypto Mining | Crypto | 70 | 2025-12-31 | 115 |  | 2750000 | Cryptocurrency mining 70 MW load at Brainerd 115 kV (Minnesota Power). EPR project
MTEP23 | Central | Ameren Services Company | 22888 | Upgrade Edwards 345 kV substation | Install a new 345 kV Ring Bus near Edwards Switchyard to support the transmission system in the Peoria area. Reroute ~0.75 miles of the existing Mapleridge-Tazewell-4528 345 kV line on the west side of Edwards Switchyard to avoid conflicts with the existing 138 kV crossings. Remove the existing failed 345 kV underground cable between Str. 123 and 124. Design and build the rerouted line to support 2 - 345 kV circuits to support MISO planning needs. All new conductors should be minimum 3000 amp Summer Emergency rated. | IL | Other | Reliability |  |  |  |  | 2027-06-01 | 345 |  | 32000000
MTEP23 | Central | Ameren Services Company | 22890 | Upgrade Selma 161 kV substation | Add line breakers to Selma-Rivermines-2 & DPFE-Selma-1 Add High Side Interrupting devices to XFMR 1 & 2 | MO | Other | Reliability |  |  |  |  | 2025-12-01 | 138 |  | 3000000
MTEP23 | Central | Ameren Services Company | 22891 | Rebuild Tibbs-Steeleville 138 kV line | Repair issues found during inspections. Replace existing 477 ACSR conductor in line. | IL | Other | Reliability |  |  |  |  | 2024-12-01 | 138 |  | 37000000
MTEP23 | West | Minnesota Power (Allete, Inc.) | 22909 | 40 Line Rebuild | Rebuild Badoura - Dog Lake 115 kV Line, new 795 ACSR and OPGW will be installed | MN | Other | Age and Condition |  |  |  |  | 2024-12-31 | 115 |  | 17307658
MTEP23 | Central | Ameren Services Company | 22926 | Upgrade Dardenne 161 kV substation | Add line breakers to Dardenne | MO | Other | Reliability |  |  |  |  | 2027-12-01 | 138 |  | 5000000
MTEP23 | Central | Ameren Services Company | 22927 | Convert Viaduct 115 kV facilities to 161 kV | Convert 115 kV facilities at Viaduct to 161 kV. Eliminate Viaduct 161 to 115kV transformer T1 by bypassing it, and by changing the taps on Viaduct XFMR 1 from 115 to 161kV. Replace 115kV OCB #5210 with a 161kV puffer breaker. | MO | Other | Age and Condition |  |  |  |  | 2024-12-01 | 161 |  | 5000000
MTEP23 | Central | Ameren Services Company | 22946 | New Alta - Pioneer 138 kV Line | Construct a new 138 kV line from Alta to Pioneer. Rebuild Alta 138 kV substation as a 4-position initial, 6-position ultimate 138 kV ring bus. Rebuild Pioneer 138 kV substation as 5-position initial, 6-position ultimate 138 kV ring bus. TP5161 was created to rebuild Pioneer as a ring bus to address aging infrastructure. The aging infrastructure will be addressed by this project. | IL | Other | Reliability |  |  |  |  | 2025-12-01 | 138 |  | 26700000
MTEP23 | Central | Ameren Services Company | 22947 | Upgrade Lakeshire 138 kV substation | Add line breaker to Pos. J (Baum-Wat-1) | MO | Other | Age and Condition |  |  |  |  | 2025-12-01 | 138 |  | 3400000
MTEP23 | Central | Ameren Services Company | 22966 | New Baldwin Area Reactive Support | Add 4 138 kV dynamic reactive 250 Mvar each located at Turkey Hill, Moro, Jarvis, and Granite City 23rd Street. | IL | Other | Reliability |  |  |  |  | 2027-06-01 | 138 |  | 170000000
MTEP23 | Central | Ameren Services Company | 23006 | Upgrade Pilot Knob 161 kV substation | Add circuit switcher for XFMR 1 and line breaker for 161 kV FLET –PKNB -2 | MO | Other | Reliability |  |  |  |  | 2025-12-01 | 161 |  | 4000000
MTEP23 | Central | Ameren Services Company | 23026 | New South Central Illinois Transmission Expansion | Construct a new 138 kV substation as an ultimate six-position ring bus requiring one 3000 A 138 kV breaker initially adjacent to the Continental Tire facility. Construct a ~3.5 mile 138 kV line from Mt. Vernon 42nd St. to the new substation ~0.3 miles NE of the Continental Tire facility with minimum 2000 A summer emergency capability. Add a new 3000 A 138 kV breaker at Mt. Vernon 42nd St. for this new 138 kV line position | IL | Other | Reliability |  |  |  |  | 2028-06-01 | 138 |  | 167850000
MTEP23 | Central | Ameren Services Company | 23072 | Rebuild Newton-Tanner 345 kV line | Rebuild the Newton-Tanner 345 kV line with conductors capable of 3000 amps Summer Emergency rating and two OPGWs. | IL | Other | Reliability |  |  |  |  | 2026-12-01 | 138 |  | 29000000
MTEP23 | Central | Ameren Services Company | 23087 | Rebuild Troy-Pike 161 kV line | Add Dual OPGW to the TROY-PIKE-1 Line from Pike to the Auburn tap (Structure 309 or so). Adding OPGW to the TROY-PIKE-1 line will require the line to be rebuilt. Since the line is being rebuilt, dual OPGW is to be added. At the Auburn tap the OPGW will be terminated to allow a connection to the AECI Fiber on their portion of the TROY-PIKE-1 line and brought the rest of the way to the new Harley Substation. | MO | Other | Reliability |  |  |  |  | 2024-12-01 | 161 |  | 16000000
MTEP23 | Central | Ameren Services Company | 23088 | Upgrade Quincy East 138 substation | Replace BKR 1442 Replace switch 1456. | IL | Other | Age and Condition |  |  |  |  | 2024-06-01 | 138 |  | 1500000
MTEP23 | Central | Indianapolis Power & Light Company | 23107 | New J993 Brickyard Solar 345 kV | Interconnection Customer shall install a 217 MVA solar facility. | IN | GIP | [5 empty] | 2023-12-01 | 345 |  | 20000000
MTEP23 | South | South Mississippi Electric Power Association | 23126 | J1249 Morrow Repower | A single steam turbine unit will be repowered at Plant Morrow for combined cycle operation utilizing a new natural gas fired combustion turbine (CT). In order to support a single unit repower at Plant Morrow with a max net capacity, Cooperative Energy has identified the need for transmission and substation projects on its system. | MS | GIP | [5 empty] | 2023-02-08 | 161 |  | 15903000
MTEP23 | West | Otter Tail Power Company | 23129 | OTP Casselton 115 kV Capacitor Addition | The project consists of expanding the existing 115 kV bus at OTP's Casselton, ND substation with two additional 115 kV breakers to allow for another position in the substation. A new 115 kV 15 MVAR capacitor and breaker will be added into the new position created in the Casselton 115 kV bus. | ND | Other | Load Growth |  |  |  |  | 2024-06-01 | 115 |  | 1200000
MTEP23 | West | Otter Tail Power Company | 23146 | OTP Big Stone Network Upgrades - J722 | J722, a 200 MW wind project, has requested to interconnect into OTP's Big Stone South 230 kV substation as part of the MISO August 2017 DPP study cycle. J722 has been assigned to complete the following network upgrades on OTP's transmission system to interconnect at Big Stone South 230 kV. 1. Increase capacity on the Big Stone South - Big Stone 230 kV circuits #1 and #2. 2. Increase capacity on the Big Stone - Blaire 230 kV circuit. | SD | GIP | [5 empty] | 2023-05-31 | 230 |  | 1756087
MTEP23 | Central | Ameren Services Company | 23152 | New Copley 138-12 kV Substation | Build a new four position 138 kV Ring bus needed to connect two 13/12 kV transformers | MO | Other | Load Growth |  |  |  |  | 2024-12-01 | 138 |  | 20000000
MTEP23 | East | ITC Transmission | 23171 | J1319 Generator Interconnection | J1319 generator will utilize the existing POI established for J327 Deerfield Wind Energy at the ITCT Rapson 120 kV substation. | MI | GIP | [5 empty] | 2023-02-28 | 0
MTEP23 | Central | Ameren Services Company | 23207 | Rebuild Mattoon West-Tuscola West 138 kV line | Rebuild the 24.6 mile Mattoon West-Tuscola West-1 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL | Other | Reliability |  |  |  |  | 2025-12-01 | 138 |  | 18500000
MTEP23 | Central | Ameren Services Company | 23286 | New [PPI] Paragon 138 kV substation | Add interconnection point to the Pana substation for PPI's new bulk substation which will be called Paragon (name changed from Panther) | IL | Other | Load Growth |  |  |  |  | 2025-06-01 | 138 |  | 900000
MTEP23 | Central | Ameren Services Company | 23306 | Rebuild Stoddard-Essex 161 kV line | Rebuild the 5.4 mile Stoddard-Essex-3 161 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | MO | Other | Reliability |  |  |  |  | 2025-06-01 | 161 |  | 3300000
MTEP23 | East | METC | 23329 | R1009 Replacement Generator Interconnection | R1009 generator will replace existing Hillman generating unit and utilize the existing POI established for Hillman Cogeneration connected at the METC Airport-Mio Dam 138 kV line (Progress Street Tap). | MI | GIP | [5 empty] | 2023-12-31 | 0
MTEP23 | West | Northern States Power (Xcel Energy) | 23347 | Blue Lake Substation - FRM13 | Replace ammeter on Blue Lake 345kV breaker 8M33 to increase rating on the Blue Lake - Scott County 345 kV line. | MN | Other | Reliability |  |  |  |  | 2022-09-02 | 345 |  | 127000
MTEP23 | South | Entergy Mississippi | 23348 | Grenada Industrial 115 kV: New Station | Entergy is proposing to construct a new 115 kV substation (Grenada Industrial 115 kV Substation) which will serve the industrial customer’s 10 MW of new load and future area load growth in Grenada, MS and the industrial park. Entergy will construct a new (4) breaker ring bus substation with (1) – 40 MVA, LTC 115/13.8 kV transformer. The new substation will have (1) main and (3) feeder breakers. The new substation will cut into the current Grenada – Tillatoba 115 kV line. | MS | Other | Load Growth |  |  |  | 10 | 2024-12-01 | 115 |  | 32610000
MTEP23 | Central | Prairie Power, Inc. | 23350 | New Forest City-Allen Tap 69 kV Line | New Forest City-Allen Tap 69kV line | IL | Other | Reliability |  |  |  |  | 2027-12-31 | 69 |  | 2880000
MTEP23 | Central | Ameren Services Company | 23351 | New Bugle 138 kV Capacitor (120 Mvar) | 120 Mvar Capacitor at Bugle | MO | Other | Reliability |  |  |  |  | 2024-12-01 | 138 |  | 26000000
MTEP23 | Central | Ameren Services Company | 23367 | New Lincoln Land Energy Center 345 kV substation (J955) | Project will connect to the existing Austin substation this requires us to install a new 345 kV breaker position. This is a 1165 MW combined cycle project. | IL | GIP | [5 empty] | 2024-12-01 | 345 |  | 2700000
MTEP23 | Central | Ameren Services Company | 23388 | New Firebrick Wind Farm (J1026) | J1026 is seeking interconnection service for 380 MW for Wind facility. The Connection will be made at the 345 kV Spencer Creek Substation | MO | GIP | [5 empty] | 2024-06-01 | 345 |  | 1700000
MTEP23 | Central | Duke Energy Corporation | 23406 | Upgrade Bedford 345 kV - 138 kV Bus 9 | Bedford 345 KV - Upgrade 138KV Bus 9 - from (1)954acsr@120C (overhead line rating) to (2)954ACSR@120C | IN | BRP | [5 empty] | 2027-06-01 | 138 |  | 532500
MTEP23 | Central | Duke Energy Corporation | 23407 | Upgrade Bloomington 230 - Bk1 138kV Bus | Bloomington 230 - Upgrade Bk1 138KV Bus - from 300CU to 954AL | IN | BRP | [5 empty] | 2024-06-01 | 230 |  | 387100
MTEP23 | Central | Prairie Power, Inc. | 23427 | New Disco-Carthage 69 kV Line | New Disco-Carthage 69 kV line | IL | Other | Reliability |  |  |  |  | 2026-12-31 | 69 |  | 8320000
MTEP23 | Central | Prairie Power, Inc. | 23428 | New Golden-Denver 69 kV Line | New Golden-Denver 69 kV line | IL | Other | Reliability |  |  |  |  | 2026-12-31 | 69 |  | 12800000
MTEP23 | Central | Prairie Power, Inc. | 23429 | Upgrade Feldon 69 kV Substation | Two new motor-operated SCADA-controlled switches on the Hardin Tap to Eldred 69 kV line. | IL | Other | Reliability |  |  |  |  | 2023-07-01 | 69 |  | 100000
MTEP23 | Central | Ameren Services Company | 23430 | New Zachary generation interconnection FCAs (J1025-J1182) | Install a 2nd Zachary 345/161 kV transformer, construct a 2nd Zachary - Adair 161 kV transmission line, and re-route existing Appanoose-Adair 161 kV Transmission line. | MO | GIP | [5 empty] | 2025-12-01 | 345 |  | 17000000
MTEP23 | Central | Ameren Services Company | 23431 | Upgrade Decatur-Main St. 138 kV line (J955) | Replace two Wood structures and re-frame 3 others to increase capacity of the Decatur - Main St. 138 kV line. | IL | GIP | [5 empty] | 2024-12-01 | 138 |  | 500000
MTEP23 | West | Northern States Power (Xcel Energy) | 23446 | W3502 Rebuild and Connection to W3503 | Construct a new line from the end of the existing line W3502 to Xcel’s W3503 1.3 miles to the east. The new connection would be made with a group of one way pole mounted switches. The new connection will allow the sections between the substations to be sequentially rebuilt. The existing line W3502 will be rebuilt to serve as a redundant connection. | WI | Other | Age and Condition |  |  |  |  | 2024-06-15 | 69 |  | 3000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23447 | W3441 Extension to W3510 | Extend the line from Birchwood substation to the east to connect to Xcel line W3510 in the vicinity of the town of Wieger, a distance of about 13 miles. Install motor operated switches at Birchwood to sectionalize the line. Install manual switches at the connection to W3510. The line would initially be operated as a normally open second source to Birchwood. | WI | Other | Reliability |  |  |  |  | 2025-12-01 | 69 |  | 9000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23448 | W3430 Rebuild | Rebuild 2 ¼ miles from Luck - Luck (DPC) to 69 kV standard. | WI | Other | Age and Condition |  |  |  |  | 2023-06-01 | 69 |  | 1000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23449 | W3429 Clear Lake to STR 214 Rebuild | Rebuild 10 miles of line W3429 from Clear Lake to Structure 214 to 69 kV standard and add OPGW. | WI | Other | Age and Condition |  |  |  |  | 2024-07-31 | 69 |  | 5250000
MTEP23 | West | Northern States Power (Xcel Energy) | 23450 | STY Install TR3 & 115kV Bus Tie | Install new 115kV bus tie and associated disconnect switches and bus work and re-terminate 0818/5529 at Rogers Lake Sub. | MN | Other | Reliability |  |  |  |  | 2024-12-15 | 115 |  | 5300000
MTEP23 | West | Northern States Power (Xcel Energy) | 23451 | Pine Lake - Stanton 69kV Rebuild | Rebuild 16.1 miles from Pine Lake - Stanton to 69kV standard. | WI | Other | Reliability |  |  |  |  | 2023-09-01 | 69 |  | 9500000
MTEP23 | West | Northern States Power (Xcel Energy) | 23453 | Line 0811 - Riverside Substation - FRM13 | Replace switches 5M330B, 5M331B, 5M329A, 5M330A, 5M329B, 5M331A, aux current transformers on 5M304 and 5M305, and two sections of busbar. | MN | Other | Reliability |  |  |  |  | 2022-12-31 | 115 |  | 900000
MTEP23 | West | Northern States Power (Xcel Energy) | 23454 | Line 0838 - Red Rock Substation - FRM13 | Replace bushing current transformers on breaker K2, switches K2B1, 946B, K2B2, 946A, and meters on 946 and K2. | MN | Other | Reliability |  |  |  |  | 2022-12-31 | 115 |  | 650000
MTEP23 | West | Northern States Power (Xcel Energy) | 23455 | Parkers Lake TR09 ELR | Replace Parkers Lake 345/115 kV TR09 (3 phases). | MN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 345 |  | 6000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23456 | Lake Yankton TR02 ELR | Replace Lake Yankton 115/69 kV TR02. | MN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 115 |  | 1500000
MTEP23 | West | Northern States Power (Xcel Energy) | 23457 | Hydro Lane TR05 ELR | Replace Hydro Lane 115/69 kV TR05. | WI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 115 |  | 3000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23458 | Line 0893 NSS-BCK Rebuild | Rebuild 3.4 miles of 115 kV line between North Star Steel and Battle Creek substations. Portions of this line are double circuited with 0892, this project will separate the two circuits. | MN | Other | Age and Condition |  |  |  |  | 2023-12-15 | 115 |  | 3437000
MTEP23 | West | Northern States Power (Xcel Energy) | 23459 | Line 0749 Waseca - ITC Tap Rebuild | Rebuild 6.7 miles of 69 kV line 0749 from Waseca - ITC Tap and add OPGW. | MN | Other | Age and Condition |  |  |  |  | 2024-06-15 | 69 |  | 6000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23460 | Line 0714 Medelia - Watonwan Rebuild | Rebuild 22 miles of line 0714 69 kV from Medelia - Watonwan. | MN | Other | Age and Condition |  |  |  |  | 2024-12-31 | 69 |  | 11000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23461 | Line 0708 STR 78 to 476 Rebuild | Rebuild 16 miles of line 0708 69 kV from Eagle Lake - Waterville and add OPGW. | MN | Other | Age and Condition |  |  |  |  | 2024-12-31 | 69 |  | 9000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23462 | Line 0718 Arlington - Winthrop Rebuild | Rebuild 15 miles line 0718 69 kV from Arlington - Winthrop. | MN | Other | Age and Condition |  |  |  |  | 2024-06-15 | 69 |  | 9000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23463 | Nighthawk Breaker Station | New 4-line terminal breaker station connecting to Minnesota Valley – Troy 69 kV transmission line (0724), Crook’s substation, and the SMBSC plant. | MN | Other | Reliability |  |  |  |  | 2024-06-01 | 69 |  | 5000000
MTEP23 | West | ITC Midwest | 23464 | Abbott-Traer 161kV 15 mile Rebuild | Due to aging condition, ITC will rebuild the Abbott – Traer 161kV circuit with T2-Grosbeak. | IA | Other | Age and Condition |  |  |  |  | 2027-12-31 | 161 |  | 16836000
MTEP23 | West | Northern States Power (Xcel Energy) | 23466 | W3351 88kv Rebuild STR 336 to Saxton Pump | Rebuild line W3551 from structure 336 to Saxton Pump. Design the 88kv circuit to be 115kv capable. Include provision for a 34.5 kv under build circuit to connect to W3628 north of Saxton Pump. | WI | Other | Age and Condition |  |  |  |  | 2024-12-31 | 88 |  | 8000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23467 | Line 0859 Str 16 to Chemolite rebuild | Rebuild 6.9 miles of line 0859 115 kV from Chemolite substation to structure 16. | MN | Other | Age and Condition |  |  |  |  | 2024-12-31 | 115 |  | 9000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23468 | Chisago County Substation - FRM13 | Replace primary and secondary 115 kV bus 1 differential relays for TR05 and TR06. | MN | Other | Reliability |  |  |  |  | 2022-08-01 | 115 |  | 200000
MTEP23 | West | Northern States Power (Xcel Energy) | 23469 | Scott County Substation - FRM13 | Replace busbar. | MN | Other | Reliability |  |  |  |  | 2022-12-31 | 115 |  | 200000
MTEP23 | Central | Ameren Services Company | 23470 | New Northeast Missouri Wind interconnection (J1025) | Construct the new 345 kV Fabius substation in Knox County, Missouri to provide a Point of Interconnection for the Generating Facility with a terminal that will consist of all necessary terminal equipment to connect the J1025 leadline to 345kV Fabius substation bus. J1025 is a 300 MW Wind project interconnecting to the Zachary-Maywood 345 kV line | MO | GIP | [5 empty] | 2024-06-01 | 345 |  | 11000000
MTEP23 | Central | Northern Indiana Public Service Company | 23471 | Upgrade Roxana to Mittal 2 138 kV Line | Reconductor 2 miles of the Roxana to Mittal 2 138kV OH Conductor. Upgrade Roxana terminal connections. | IN | BRP | [5 empty] | 2025-05-31 | 138 |  | 5648342
MTEP23 | Central | Northern Indiana Public Service Company | 23472 | Upgrade Leesburg Substation 138 kV | Leesburg substation upgrade to eliminate common breaker betweeen Leesburg Transformer and Circuit 13821. | IN | BRP | [5 empty] | 2026-12-31 | 138 |  | 2392215
MTEP23 | West | Northern States Power (Xcel Energy) | 23473 | Line 0892 RRK-BCK Rebuild | Rebuild 3.4 miles of 115 kV line between Red Rock and Battle Creek substations. Portions of this line are double circuited with 0893, this project will separate the two circuits. | MN | Other | Age and Condition |  |  |  |  | 2023-12-15 | 115 |  | 5237000
MTEP23 | West | Northern States Power (Xcel Energy) | 23474 | Line 0736 Arden Hills - Lawrence Creek Rebuild | Rebuild 33 miles of line 0736 69 kV from Arden Hills - Lawrence Creek and add OPGW. | MN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 69 |  | 20000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23475 | Line 0721 STR 71 to 476 Rebuild | Rebuild 22 miles line 0721 69 kV from Structure 71 - Structure 476. | MN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 69 |  | 11000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23476 | Line 0822 Empire to STR 107 Rebuild | Rebuild 7 miles of line 0822 115 kV from Empire to Str 107 and add OPGW. | MN | Other | Age and Condition |  |  |  |  | 2024-12-31 | 115 |  | 6000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23477 | Line 0772 Prairie to MNPC Connection Rebuild | Rebuild 12 miles of line 0772 69 kV from Prairie - Emerado. | ND | Other | Age and Condition |  |  |  |  | 2025-12-31 | 69 |  | 6000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23479 | Iron River Substation Rebuild | Rebuild the existing Iron River substation to include a 115 kV ring bus and new 115/34.5 kV transformer. | WI | Other | Age and Condition |  |  |  |  | 2024-06-01 | 115 |  | 7000000
MTEP23 | East | ITC Transmission | 23481 | S1007 Surplus Generator Interconnection | S1007 Surplus generator will utilize the existing POI established for J202 Starkey Wind Farm at the ITCT Dixon 120 kV substation. | MI | GIP | [5 empty] | 2023-09-01 | 0
MTEP23 | West | ITC Midwest | 23483 | J1174 GIA - Bluebill TOIF | A new Bluebill 345 kV switching station will be constructed to interconnect projects J1174 and J1175. The Bison – Colby 345 kV line will be tapped and re-routed to new positions in the Bluebill station. The TOIF will include dead-end, disconnect switch, arresters, PT’s, relay panel, and associated equipment. | IA | GIP | [5 empty] | 2025-06-30 | 345 |  | 864989
MTEP23 | West | ITC Midwest | 23484 | J1175 GIA - Bluebill TOIF | A new Bluebill 345 kV switching station will be constructed to interconnect projects J1174 and J1175. The Bison – Colby 345 kV line will be tapped and re-routed to new positions in the Bluebill station. The TOIF will include dead-end, disconnect switch, arresters, PT’s, relay panel, and associated equipment. | IA | GIP | [5 empty] | 2025-06-30 | 345 |  | 864989
MTEP23 | West | ITC Midwest | 23485 | J1174 & J1175 MPFCA - Network Upgrades | A new Bluebill 345 kV switching station will be constructed to interconnect projects J1174 and J1175. The Bison – Colby 345 kV line will be tapped and re-routed to new positions in the Bluebill station. ITC will TO self-fund the Network Upgrades and will earn a return of and return on investment under a FSA for 90% of the cost. 10% of the Network Upgrades costs will be recovered under Attachment GG. | IA | GIP | [5 empty] | 2025-06-30 | 345 |  | 16216106
MTEP23 | West | Northern States Power (Xcel Energy) | 23486 | Inver Hills Substation - FRM13 | Replace busbar. | MN | Other | Reliability |  |  |  |  | 2023-03-01 | 115 |  | 200000
MTEP23 | West | Northern States Power (Xcel Energy) | 23487 | Kohlman Lake Substation - FRM13 | Replace meter on breaker 5P106. | MN | Other | Reliability |  |  |  |  | 2022-12-31 | 115 |  | 50000
MTEP23 | West | Northern States Power (Xcel Energy) | 23488 | Prairie Substation - FRM13 | Replace meter on breaker 5G8. | ND | Other | Reliability |  |  |  |  | 2022-12-31 | 115 |  | 50000
MTEP23 | West | Northern States Power (Xcel Energy) | 23489 | Wilmarth Substation - FRM13 | Replace bushing current transformer on breaker 5S11 as well as switches 8S26B1, 8S25B, 8S25A, 8S26B1. | MN | Other | Reliability |  |  |  |  | 2022-12-31 | 115 |  | 550000
MTEP23 | West | Northern States Power (Xcel Energy) | 23490 | Crystal Cave TR01 ELR | Replace Crystal Cave 161/115 kV TR01. | WI | Other | Age and Condition |  |  |  |  | 2024-12-31 | 161 |  | 3500000
MTEP23 | West | Northern States Power (Xcel Energy) | 23491 | Parkers Lake TR10 ELR | Replace Parkers Lake 345/115 kV TR10 with a single 3 phase transformer. | MN | Other | Age and Condition |  |  |  |  | 2022-12-31 | 345 |  | 3500000
MTEP23 | West | Northern States Power (Xcel Energy) | 23492 | Pine Lake TR03 ELR | Replace Pine Lake 161/115 kV TR03. | WI | Other | Age and Condition |  |  |  |  | 2027-12-31 | 161 |  | 3500000
MTEP23 | West | Northern States Power (Xcel Energy) | 23493 | Monticello TR06 & TR10 ELR | Replace Monticello 345/230 kV TR06 and 345/115 kV TR10. | MN | Other | Age and Condition |  |  |  |  | 2025-09-16 | 345 |  | 7000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23494 | Prairie Island TR10 ELR | Replace Prairie Island 345/161 kV TR10 | MN | Other | Age and Condition |  |  |  |  | 2024-12-15 | 345 |  | 3500000
MTEP23 | West | Northern States Power (Xcel Energy) | 23495 | Pipestone TR05 & TR06 ELR | Replace Pipestone TR05 and TR06 115/69 kV transformers. | MN | Other | Age and Condition |  |  |  |  | 2024-12-31 | 115 |  | 3000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23496 | Inver Grove TR02 ELR | Replace Inver Grove 115/69 kV TR02. | MN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 115 |  | 2500000
MTEP23 | West | Northern States Power (Xcel Energy) | 23497 | Lake Pulaski TR05 ELR | Replace Lake Pulaski 115/69 kV TR05. | MN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 115 |  | 2500000
MTEP23 | West | Northern States Power (Xcel Energy) | 23498 | Minnesota Valley TR11 ELR | Replace Minnesota Valley 115/69 kV TR11. | MN | Other | Age and Condition |  |  |  |  | 2027-12-31 | 115 |  | 2500000
MTEP23 | West | Northern States Power (Xcel Energy) | 23499 | Osprey TR05 ELR | Replace Osprey 115/69 kV TR05. | WI | Other | Age and Condition |  |  |  |  | 2027-12-31 | 115 |  | 3500000
MTEP23 | Central | Ameren Services Company | 23500 | New Morris Solar interconnection (J1182) | One 345 kV terminal in the Zachary substation. The terminal will consist of all necessary terminal equipment to connect the J1182 leadline to the Zachary substation bus. J1182 is a 250 MW Solar project interconnecting to the Zachary substation 345 kV bus | MO | GIP | [5 empty] | 2024-11-01 | 345 |  | 2593000
MTEP23 | West | Northern States Power (Xcel Energy) | 23501 | Line 0840 Elliot Park Pumping Plants | Upgrades to pumping station for HPFF. | MN | Other | Reliability |  |  |  |  | 2025-06-01 | 115 |  | 5000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23502 | Line 0771 Rebuild | Rebuild 2 miles of line 0771 from Young America - Carver County 69 kV substations and add OPGW. | MN | Other | Age and Condition |  |  |  |  | 2024-06-30 | 69 |  | 1500000
MTEP23 | West | Northern States Power (Xcel Energy) | 23503 | Line 0719 Winthrop to STR 45 Rebuild | Rebuild 1.5 miles of line 0719 69 kV from Winthrop - Structure 45. | MN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 69 |  | 2000000
MTEP23 | Central | Ameren Services Company | 23504 | Rebuild Vermillion-Tilton Energy Center 138 kV line (1572) | Rebuild the 11.4 mile Vermillion-Tilton Energy Center-1572 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL | Other | Reliability |  |  |  |  | 2024-12-01 | 138 |  | 13000000
MTEP23 | Central | Ameren Services Company | 23505 | Relocate Bosco 138 kV substation (fka Murdock) | Relocate station due to the contamination, build a ring bus at a new location. | IL | Other | Age and Condition |  |  |  |  | 2025-06-01 | 138 |  | 14400000
MTEP23 | West | Northern States Power (Xcel Energy) | 23506 | Gingles TR05 ELR | Replace Gingles 115/69 kV TR05. | WI | Other | Age and Condition |  |  |  |  | 2025-12-31 | 115 |  | 2500000
MTEP23 | West | Northern States Power (Xcel Energy) | 23508 | Line 5503 Cherry Creek - Great Plains - West Sioux Falls Rebuild | Rebuild 2 miles 115 kV Cherry Creek - Great Plains. Rebuild 1 mile 115 kV Great Plains - West Sioux Falls (single circuit portion) as bifurcated double circuit. Rebuild 0.7 mile 115 kV Great Plains - West Sioux Falls (double circuit portion). | SD | Other | Age and Condition |  |  |  |  | 2024-06-01 | 115 |  | 5000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23509 | Junction Mill Substation | Build new Junction Mill substation near 3-terminal 115kV connection with Glenmont, River Falls and Crystal Cave lines. In addition, this substation will install a new 115/69kv transformer and change the operating voltage of the River Falls tap to 69kV. The transformation at the River Falls substation will be removed as well any 115kV equipment. | WI | Other | Reliability |  |  |  |  | 2024-06-01 | 115 |  | 12000000
MTEP23 | West | ITC Midwest | 23510 | Rock Creek T3 Replacement | The existing Rock Creek T3 transformer is at the end of its useful life and in need of replacement. T3 will be replaced with a new 150 MVA 161/69 kV transformer with LTC. In addition, there is an 800 amp relay thermal limit on T3, so the existing relaying needs to be upgraded to remove the 800 amp thermal limit to allow full use of the 150 MVA transformer rating. | IA | Other | Age and Condition |  |  |  |  | 2025-12-31 | 161 |  | 4267194
MTEP23 | West | ITC Midwest | 23511 | Grinnell South 69kV Substation & 20MVAR Cap | IPL has notified ITC that they will be rebuilding the Grinnell South substation in a new location directly south of the existing substation location which will replace the existing Grinnell South substation. ITC will construct the 69 kV portion of Grinnell South in the new location including two busses, two line breakers, and a bus tie breaker. ITC will also install a new 69 kV capacitor bank at the new Grinnell South substation to provide improved area voltage support for existing and potential additional future load growth in the area. | IA | Other | Load Growth |  |  |  |  | 2025-12-31 | 69 |  | 5637400
MTEP23 | West | Northern States Power (Xcel Energy) | 23512 | Prairie View Substation | Rebuild the Wheaton Substation on a new location with a 4-row breaker and a half 161 kV configuration in order to separate it from the Generation facility. | WI | Other | Age and Condition |  |  |  |  | 2026-06-01 | 161 |  | 17000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23513 | Emerald Substation | Line W3209 – Replace 3 way switch with new 161kv to 115kv substation. Rebuild 1 mile of double circuit 161-115kv line to single circuit 115kv line. Retire Pine Lake 161kv to 115kv yard. | WI | Other | Reliability |  |  |  |  | 2025-06-15 | 161 |  | 12000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23514 | Sauk Centre North Interconnection | Build three 1-way switches on line 0794 to accommodate new Sauk Centre Municipal distribution substation. | MN | Other | Load Growth |  |  |  |  | 2024-12-31 | 69 |  | 800000
MTEP23 | West | Northern States Power (Xcel Energy) | 23515 | Eau Claire TR09 Replacement | Upgrade Eau Claire TR09. | WI | Other | Reliability |  |  |  |  | 2025-06-01 | 345 |  | 8000000
MTEP23 | Central | Ameren Services Company | 23526 | Reconfigure Warrenton 161 kV substation | Install a 161 kV Ring bus at Warrenton Substation | MO | Other | Reliability |  |  |  |  | 2024-12-01 | 161 |  | 15000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23527 | Line W3428 Clear Lake - New Richmond Rebuild | Rebuild 19.8 miles of line W3428 from Clear Lake - New Richmond. | WI | Other | Age and Condition |  |  |  |  | 2023-03-15 | 69 |  | 10000000
MTEP23 | West | Northern States Power (Xcel Energy) | 23528 | Gaiter Lake Substation | Build new Gaiter Lake substation in Waseca to pick up load off of Clarks Grove, Meridan, and Waseca substations. Retire Clarks Grove and Meridan substations. | MN | Other | Age and Condition |  |  |  |  | 2025-10-15 | 69 |  | 7800000
MTEP23 | Central | Prairie Power, Inc. | 23532 | New Pleasant View-Ishi 69 kV Line | New Pleasant View to Ishi 69 kV line in SEC. This line has three line segments: 1) New Pleasant View-Moweaqua 69 kV Line 2) New Moweaqua-Yantisville 69 kV Line 3) New Yantisville-Henton 69 kV Line | IL | Other | Reliability |  |  |  |  | 2029-12-31 | 69 |  | 23498000
MTEP23 | West | ITC Midwest | 23546 | Jefferson County 161kV Substation Rebuild | The relaying and SCADA equipment at the Jefferson County substation is nearing the end of its useful lifespan. In addition, the existing 161/69 kV transformer does not have a high side protective device, there is not adequate space to add it, and the existing 161 kV bus configuration does not allow the flexibility needed. Due to this, ITC will rebuild the 161 kV bus at Jefferson to a 3 position ring bus configuration and will replace all existing relays at the station except on two 69 kV lines going towards NEMO. ITC will also replace and upgrade existing SCADA equipment and add 69 kV line PTs on all lines except those going towards NEMO. | IA | Other | Reliability |  |  |  |  | 2025-12-31 | 161 |  | 7922995
MTEP23 | West | Northern States Power (Xcel Energy) | 23547 | 21829 - South Dayton Interconnection | New GRE interconnection (MTEP ID 21829). Xcel will own high side of new sub with an in-and-out configuration on the Elm Creek - Champlin Tap 115kV line. | MN | Other | Load Growth |  |  |  |  | 2023-06-15 | 115 |  | 5000000
MTEP23 | Central | Prairie Power, Inc. | 23567 | Rebuild Pearl-Kampsville 69 kV Line | Rebuild Pearl-Kampsville 69 kV line | IL | Other | Age and Condition |  |  |  |  | 2029-12-31 | 69 |  | 7285000
MTEP23 | Central | Indianapolis Power & Light Company | 23568 | Replace Southwest 138 kV #16 Breaker | Replacement of one (1) 138 kV breaker at Southwest #16 | IN | BRP | [5 empty] | 2025-12-31 | 138 |  | 900000
MTEP23 | Central | Big Rivers Electric Corporation | 23569 | New [BREC] McCracken-[GLH] Joppa 161 kV Tie Line | This relatively small and confined project will consist of one additional terminal at an existing Big Rivers’ substation (Big Rivers owned), 2 miles of 161 kV transmission line (Big Rivers owned), and a three bay switching station (GLH owned). Without this proposed project transmission voltages are very near a contingent TPL violation with normal forecasted load levels. Loads associated with extreme weather or a small load increase in this region will cause a contingent TPL violation. In addition to the TPL violation relief and providing needed capacity in the western part of Big Rivers system, the proposed project will alleviate the need to purchase transmission service from TVA. During contingent conditions, the majority of Jackson Purchase Energy (distribution cooperative served by Big Rivers) is dependent on one 161 kV interconnection with TVA. Therefore, Big Rivers must purchase transmission service as available from TVA during various planned and unplanned outage scenarios. The proposed project will provide a second MISO source to this load and alleviate the reliance on TVA transmission service and eliminate the need to purchase such service. This project will coincide with project ID 23827 submitted by GridLiance Heartland. | KY | Other | Reliability | Additional terminal at Big Rivers substation, 2 miles 161 kV line; addresses TPL violations caused by extreme weather and/or small load increase |  |  |  | 2025-07-02 | 161 |  | 5300000 | BREC/GLH; local reliability with load increase component
MTEP23 | West | MidAmerican Energy Company | 23570 | Valley Trail 161 kV Substation | Construct Valley Trail 161-13.2 kV Sub and Line Taps | IA | Other | Load Growth |  |  |  |  | 2026-06-01 | 161 |  | 9500000
MTEP23 | West | MidAmerican Energy Company | 23571 | Humboldt 69 kV Reconfiguration | Network Humboldt Central Substation and establish tie with Corn Belt's Weaver Switching Station | IA | Other | Reliability |  |  |  |  | 2027-12-01 | 69 |  | 9900000
MTEP23 | West | MidAmerican Energy Company | 23572 | Franklin: Replace 161 kV Breaker 9210 | Franklin: Replace 161 kV Breaker 9210 | IA | Other | Other Local Needs |  |  |  |  | 2023-12-01 | 161 |  | 500000
MTEP23 | West | MidAmerican Energy Company | 23573 | Black Hawk: 161-69 kV, 167 MVA Transformer | Replace existing 161-69 kV, 50 MVA Transformer | IA | Other | Reliability |  |  |  |  | 2025-12-01 | 161 |  | 9000000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23574 | Pellston to Cross Village | Rebuild and upgrade 9 miles of 69kV line to 138 kV standard with steel poles, 336ACSS conductor, and OPGW. | MI | Other | Age and Condition |  |  |  |  | 2028-12-31 | 69 |  | 9500000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23575 | Pellston Relocation and Upgrades | Project will replace capacity limiting equipment and existing protection system at the Pellston substation and relocate the Pellston to Cross Village line to improve reliability on that line. | MI | Other | Reliability |  |  |  |  | 2027-12-31 | 69 |  | 1600000
MTEP23 | West | MidAmerican Energy Company | 23590 | Granger Substation 161 kV Line Breakers | Install 161 kV line breakers and associated relaying | IA | Other | Reliability |  |  |  |  | 2027-12-01 | 161 |  | 2100000
MTEP23 | West | MidAmerican Energy Company | 23591 | Nashua Tap-Plainfield Junction 69 kV Rebuild | Replace conductor on section of Nashua Tap-Plainfield Junction 69 kV line using existing right of way | IA | Other | Age and Condition |  |  |  |  | 2024-12-31 | 69 |  | 2500000
MTEP23 | West | MidAmerican Energy Company | 23592 | Floyd Substation: Add 69 kV Bus PTs, Remove Wave Trap and Incorporate Fiber | Add 69 kV Bus PTs; remove wave trap and employ fiber for Floyd-Emery 161 kV line relaying | IA | Other | Reliability |  |  |  |  | 2024-12-31 | 161 |  | 350000
MTEP23 | West | MidAmerican Energy Company | 23593 | Charles City North add 69 kV Breakers | Charles City North Add 69 kV Breakers | IA | Other | Reliability |  |  |  |  | 2027-12-31 | 69 |  | 800000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23594 | Scottville RTU Upgrade | Replace communication equipment at the Scottville substation. | MI | Other | Age and Condition |  |  |  |  | 2025-12-31 | 69 |  | 40000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23595 | Weidman RTU Upgrade | Replace communication equipment at the Weidman substation. | MI | Other | Age and Condition |  |  |  |  | 2025-12-31 | 69 |  | 40000
MTEP23 | West | Montana-Dakota Utilities Company | 23596 | Glenham rebuild | Rebuilding the current Glenham substation 230/115/41.6 kV. | SD | Other | Age and Condition |  |  |  |  | 2025-10-31 | 230 |  | 23500000
MTEP23 | West | MidAmerican Energy Company | 23608 | E. 29th & Hubbell 69 kV Expansion and Line Tap | Expand substation steel for a second 69 kV line tap | IA | Other | Reliability |  |  |  |  | 2024-06-01 | 69 |  | 500000
MTEP23 | West | MidAmerican Energy Company | 23609 | Delaware Substation 161 kV Line Breakers | Install 161 kV line breakers and associated relaying | IA | Other | Reliability |  |  |  |  | 2025-06-01 | 161 |  | 1900000
MTEP23 | West | MidAmerican Energy Company | 23610 | Washburn: 161-69 kV, 125 MVA Transformer | Replace existing 161-69 kV, 50 MVA Transformer | IA | Other | Reliability |  |  |  |  | 2026-12-01 | 161 |  | 7500000
MTEP23 | West | ITC Midwest | 23611 | J982 Affected System Upgrades | MISO Facilities Study for Affected System upgrades for project J982, a 300 MW wind-powered generating facility with proposed interconnection on MEC’s Obrien County – Kossuth 345kV circuit. The system impact study has indicated the interconnection of project J982 will require sag mitigation on the Fox Lake to Rutland 161 kV circuit. | MN | GIP | [5 empty] | 2023-09-01 | 161 |  | 338000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23612 | Altona Protection System Upgrade | Replace the control building to install modern digital relays and install an additional circuit breaker to increase reliability on Altona to Morley transmission line. | MI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 1500000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23613 | 2025 WPSC Fiber Retrofit | Installation of fiber on recently rebuilt (post 2006) 138kV structures utilizing ADSS (All Dielectric Self Supporting) and OPGW (Optical Ground Wire). | MI | Other | Reliability |  |  |  |  | 2025-12-31 | 69 |  | 5000000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23614 | Casnovia to Cedar Springs Rebuild | Rebuild and upgrade 11 miles of 69kV line to 138 kV standard with steel poles, 795ACSS conductor, and OPGW. | MI | Other | Age and Condition |  |  |  |  | 2027-12-31 | 69 |  | 9250000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23615 | Copemish Protection System Upgrade | Replace the circuit breaker and its associated controls and protective relaying, bringing the station to Wolverine’s standard for 138kV transmission operation. | MI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 1500000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23616 | Gaylord Protection System Upgrade | Upgrade existing electromechanical relays with digital relays. | MI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 138 |  | 800000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23617 | Hayes Junction to Hayes Rebuild | Rebuild and upgrade 12 miles of 69kV line to 138 kV standard with steel poles, 336ACSS conductor, and OPGW. | MI | Other | Age and Condition |  |  |  |  | 2028-12-31 | 69 |  | 11850000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23618 | Lake County Protection System Upgrade | Upgrade Lake County Protection system with new line relays. | MI | Other | Reliability |  |  |  |  | 2024-12-31 | 138 |  | 75000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23619 | Mulliken Jct to Grand Ledge Rebuild | Rebuild and upgrade 4 miles of 69kV line to 138 kV standard with wood poles, 336ACSS conductor, and OPGW. | MI | Other | Age and Condition |  |  |  |  | 2027-12-31 | 69 |  | 4250000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23620 | North Shade Protection System Upgrade | Upgrade existing electromechanical relays with digital relays. | MI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 1250000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23621 | Redwood RTU Upgrade | Replace communication equipment at the Redwood substation. | MI | Other | Age and Condition |  |  |  |  | 2024-12-31 | 69 |  | 150000
MTEP23 | West | MidAmerican Energy Company | 23628 | Waverly Junction: Reconfigure 69 kV Terminals | Reconfigure 69 kV line terminals to eliminate tapped substation transformer | IA | Other | Reliability |  |  |  |  | 2024-06-01 | 69 |  | 1300000
MTEP23 | West | MidAmerican Energy Company | 23629 | Charles City South-Nashua Tap 69 kV Rebuild | Rebuild Charles City South-Nashua Tap 69 kV Line on new Right of Way | IA | Other | Age and Condition |  |  |  |  | 2025-12-01 | 69 |  | 7700000
MTEP23 | West | MidAmerican Energy Company | 23630 | Wida-Streeter 69 kV Rebuild | Replace conductor on MidAmerican section of Wida-Streeter 69 kV line. | IA | Other | Age and Condition |  |  |  |  | 2024-04-01 | 69 |  | 1000000
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 23631 | Petosky Protection System Upgrade | Upgrade existing electromechanical relays with digital relays. | MI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 1000000
MTEP23 | Central | Ameren Services Company | 23632 | New Beehive-Dupo Ferry 138 kV line | Install new Beehive to Dupo Ferry 138 kV line. Add breaker to new Dupo Ferry ring bus. Add position at Beehive. | IL | Other | Reliability |  |  |  |  | 2024-12-01 | 138 |  | 6300000
MTEP23 | West | Montana-Dakota Utilities Company | 23633 | Ellendale load addition | MDU has new customer requesting service at Ellendale, ND for total demand of 180 MW. MDU will serve the customer from the existing Ellendale 2 transformer's 34.5 kV tertiary. An overhead line will be built from the tertiary of the transformer to the customers sub. | ND | Other | Load Growth | MDU new customer requesting service at Ellendale ND for total demand of 180 MW; served from existing Ellendale 2 transformer 34.5 kV tertiary | Data Center | Y | 180 | 2023-02-15 | 34.5 |  | 3060359.76 | Ellendale: new 180MW customer (MDU ND). $3M. Precursor to data center projects
MTEP23 | West | Montana-Dakota Utilities Company | 23634 | Wishek rebuild | Will be expanding the 230 kV to add new wind farm and rebuilding the 115 and 41.6 kV. | ND | Other | Age and Condition |  |  |  |  | 2025-12-31 | 230 |  | 18650000
MTEP23 | Central | Ameren Services Company | 23635 | New Baldwin Solar Interconnection (J1202) | Install one 345 kV terminal in the Baldwin substation. The terminal will consist of all necessary terminal equipment to connect the J1202 leadline to the Baldwin substation 345 kV bus. | IL | GIP | [5 empty] | 2024-06-01 | 345 |  | 150000
MTEP23 | West | ITC Midwest | 23636 | ITCM Customer Interconnects (short lead time) 2025 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL | Other | Load Growth |  |  |  |  | 2025-12-31 | 345 |  | 3600000
MTEP23 | Central | Ameren Services Company | 23637 | New Hennepin Solar Interconnection (J1200) | Install one 138 kV terminal in the Putnam substation. The terminal will consist of all necessary terminal equipment to connect the J1200 leadline to the Putnam substation 138 kV bus. Install upgrades at Putnam substation. Raise existing PUTN-HKOK-1556, PUTN-HENN-1771, PUTN-HENN-1765, PUTN-ESK-1757, and PUTN-BURE-1552 transmission lines | IL | GIP | [5 empty] | 2024-06-01 | 138 |  | 1800000
MTEP23 | West | MidAmerican Energy Company | 23655 | Shenandoah: Replace 69 kV Breakers 601 & 602 | Replace 69 kV breakers at Shenandoah Substation | IA | Other | Age and Condition |  |  |  |  | 2024-12-01 | 69 |  | 600000
MTEP23 | West | MidAmerican Energy Company | 23675 | Avoca: Install 69 kV Breaker on 161-69 kV Transformer 8T3 and 161 kV & 69 kV Breaker Replacements | Install a 69 kV breaker on the low-side of Avoca 161-69 kV Transformer 8T3, replace/rolocate Avoca Breakers 622 and 623 to accommodate new 69 kV breaker and replace Breakers 801, 802 and 620 due to condition | IA | Other | Reliability |  |  |  |  | 2025-12-01 | 161 |  | 4100000
MTEP23 | Central | Ameren Services Company | 23676 | New Coffeen Solar Interconnection (J1201) | Install one 138 kV terminal in the Coffeen North substation. The terminal will consist of all necessary terminal equipment to connect the J1201 leadline to the Coffeen North substation 138 kV bus. Raise existing Coffeen North-Pana 345kV Transmission line. 44.2 MW solar generator | IL | GIP | [5 empty] | 2024-06-01 | 345 |  | 1500000
MTEP23 | West | ITC Midwest | 23677 | ITC Midwest Asset Replacement Program 2025 | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA,MN,IL | Other | Age and Condition |  |  |  |  | 2025-12-31 | 345 |  | 38400000
MTEP23 | Central | Ameren Services Company | 23678 | New Duck Creek Solar Interconnection (J1199) | Install one 345 kV terminal in the Duck Creek substation. The terminal will consist of all necessary terminal equipment to connect the J1199 leadline to the Duck Creek substation 345 kV bus. Upgrade control and relay fiber panel at the Duck Creek substations as well as the remote end substatio | IL | GIP | [5 empty] | 2024-06-01 | 345 |  | 2500000
MTEP23 | West | Great River Energy | 23679 | Cromwell Breaker Replacement | Replace 115 kV circuit breakers 13L and 26L. | MN | Other | Age and Condition |  |  |  |  | 2023-11-01 | 115 |  | 1359267.96
MTEP23 | West | Great River Energy | 23680 | Frog Creek Breaker Replacement | Replace Circuit Switcher FC161-10 at Frog Creek substation with breaker and add disconnect switches. Replacement of Panel #2 relaying to also be included. | MN | Other | Age and Condition |  |  |  |  | 2025-01-31 | 69 |  | 1030196.45
MTEP23 | West | Great River Energy | 23681 | Riverton Breaker Replacement | This project will remove 69kV bus differential relaying, replace GE-T60 with SEL-487E using existing panel 7, protect the 69kV bus zone with the transformer relays, replace Riverton IR8600 RTU with Cybectec RTU, replace Westinghouse 3-phase 115kV PT with 3 single phase CCVTs on 115kV bus, and replace the 115-kV 25WB1 oil breaker. In addition to this work there will also be some 69-kV and 115-kV bus work and jumper modifications. | MN | Other | Reliability |  |  |  |  | 2024-06-30 | 115 |  | 849708.75
MTEP23 | West | Great River Energy | 23682 | Princeton Breaker Addition | Add breaker and relaying to address incomplete topology and relaying load limit issue at Princeton. The plan to accommodate this work is to bring the OL line around to the west bay of the four structure and place breaker in PT occupied bay. Bus PT’s will be replaced and relocated to a different location on site to accommodate the breaker addition in west bay. This project will also require that we rebuild to OL line tapping into the north by bringing it in to the west bay with the characteristics of the new line rebuild plan of the OL line. | MN | Other | Other Local Needs |  |  |  |  | 2024-06-21 | 69 |  | 763118.2
MTEP23 | West | MidAmerican Energy Company | 23683 | Sheldon: 69 kV Breaker and Relay Replacements | Replace Sheldon 69 kV Breakers 7730, 7740, 7880 and 7890 and associated disconnect switches and relaying | IA | Other | Age and Condition |  |  |  |  | 2024-10-01 | 69 |  | 2800000
MTEP23 | West | ITC Midwest | 23684 | Kittyhawk 69kV Substation Interconnection | IPL has notified ITC that they will be rebuilding the Kittyhawk substation in the existing location to allow the addition of a 2nd IPL distribution transformer. ITC will construct the 69 kV portion of Kittyhawk which will include two busses/single box structures, two line breakers, and a bus tie breaker. | IA | Other | Load Growth |  |  |  |  | 2025-12-31 | 69 |  | 3902741
MTEP23 | West | MidAmerican Energy Company | 23685 | Neal North-Southbridge Tap-Knox-State Steel Tap 69 kV Line Rebuild | Rebuild approximately 9 miles of line | IA | Other | Age and Condition |  |  |  |  | 2024-12-05 | 69 |  | 8600000
MTEP23 | West | MidAmerican Energy Company | 23686 | Obrien County-Hospers 161 kV Line, Obrien County 345-161 kV Transformer Addition & Hospers 161-69 kV Transformer Addition | Construct new 161 kV line from Obrien County Substation to Hospers Substation, expand Obrien County Substation to install 345-161 kV, 560 MVA transformer and 161 kV bus and expand Hospers Substation to install 161-69 kV, 167 MVA transformer and 161 kV bus | IA | BRP | [5 empty] | 2026-12-01 | 345 |  | 45000000
MTEP23 | West | MidAmerican Energy Company | 23687 | Storm Lake Industrial 69 kV Line Taps | Construct 69 kV line taps into new Storm Lake Industrial 69-13.8 kV Substation | IA | Other | Load Growth |  |  |  |  | 2026-12-01 | 69 |  | 800000
MTEP23 | West | MidAmerican Energy Company | 23688 | Macksburg - Winterset 161 kV Reconductor | Reconductor the 161 kV line from Macksburg to Winterset. Line identified as a constraint in the MTEP22 generator deliverability analysis. | IA | BRP | [5 empty] | 2027-06-01 | 161 |  | 12500000
MTEP23 | West | MidAmerican Energy Company | 23689 | Sub 93 Louisa: Replace 345 kV Breaker 934 | Replace 345 kV breaker in Sub 93 (Louisa) ring. | IA | Other | Age and Condition |  |  |  |  | 2023-04-07 | 345 |  | 390000
MTEP23 | West | MidAmerican Energy Company | 23690 | Quad Cities Enron Substation: Install 161 kV Line Switches | Install new 161 kV line switches on both sides of the QEN Quad City Enron substation to increase switching flexibility. | IA | Other | Reliability |  |  |  |  | 2025-12-31 | 161 |  | 500000
MTEP23 | West | MidAmerican Energy Company | 23691 | Riverdale 161-13.2 kV Substation | Construct new 161-13.2 kV substation and 161 kV line taps. | IL | Other | Reliability |  |  |  |  | 2026-12-31 | 161 |  | 4100000
MTEP23 | West | MidAmerican Energy Company | 23692 | Sub 28 Add 161 kV Line Breakers and Install New Control Building | Install new 161 kV line breakers and new control building to replace existing control enclosure. | IL | Other | Reliability |  |  |  |  | 2027-12-31 | 161 |  | 3700000
MTEP23 | West | ITC Midwest | 23693 | J1132 GIA Network Upgrades | Expansion of the Creston Roundhouse 69kV bus with an additional box structure. | IA | GIP | [5 empty] | 2024-06-01 | 69 |  | 316693
MTEP23 | West | MidAmerican Energy Company | 23694 | Wall Lake 161 kV Terminal Equipment Upgrades | Replace limiting jumpers on Wright - Wall Lake and Wall Lake - Franklin 161 kV line terminals. | IA | Other | Other Local Needs |  |  |  |  | 2026-12-31 | 161 |  | 100000
MTEP23 | East | ITC Transmission | 23697 | Beck - Stephens 120 kV Sag Remediation | Remediate the sag limit on the Beck - Stephens 120 kV circuit up to a minimum summer emergency rating of 242 MVA. | MI | BRP | [5 empty] | 2026-12-31 | 120 |  | 540000
MTEP23 | West | MidAmerican Energy Company | 23699 | Gifford Road 161-13.2 kV Substation and 161 kV Line Taps | Construct Gifford Road 161-13.2 kV Sub and Line Taps | IA | Other | Load Growth |  |  |  |  | 2026-09-01 | 161 |  | 5500000
MTEP23 | West | ITC Midwest | 23701 | J1135 GIA Huntwoods 69 kV TOIF | Install equipment dedicated to the J1135 generating facilities. The J1135 line will be connected to a new breaker position on the Huntwoods 69 kV bus. TOIF cost to include the new breaker, switches, relay panel and any new associated equipment. | IA | GIP | [5 empty] | 2027-06-01 | 69 |  | 558384
MTEP23 | West | MidAmerican Energy Company | 23703 | J982 POI New 345 kV Interconnection Substation and 345 kV Line Taps | Construct new 345 kV POI substation and 345 kV line taps for J982 wind farm. | IA | GIP | [5 empty] | 2025-06-01 | 345 |  | 15250000
MTEP23 | East | METC | 23704 | Abbe Jct - Mio 138kV Sag Remediation | Remediate sag on the 266.8 ACSR up to conductor’s limit on the Abbe Jct. – Mio Dam section of the Airport – Mio Dam 138 kV circuit. | MI | BRP | [5 empty] | 2026-12-31 | 138 |  | 1700000
MTEP23 | West | Minnesota Power (Allete, Inc.) | 23707 | Maturi Substation Expansion | The Maturi Expansion Project will add three circuit breakers to allow for the transmission line to be looped in and out of the Maturi Substation. | MN | Other | Other Local Needs |  |  |  |  | 2025-12-31 | 115 |  | 3580000
MTEP23 | West | Minnesota Power (Allete, Inc.) | 23708 | Mahtowa Substation Expansion | The Mahtowa Expansion project will add 3-115 kV circuit breakers to reconfigure the existing Mahtowa Substation into a 3 position ring bus. | MN | Other | Age and Condition |  |  |  |  | 2027-12-31 | 115 |  | 2500000
MTEP23 | East | METC | 23709 | Campbell – Blendon 138kV Loop Into Tyler | Loop the Campbell - Blendon 138kV line into Tyler to create Campbell - Tyler and Tyler - Blendon 138kV lines. Install (3) new breakers at Tyler and OPGW from Port Sheldon to Campbell. | MI | BRP | [5 empty] | 2027-06-01 | 138 |  | 6916517
MTEP23 | West | Missouri River Energy Services (MRET) | 23710 | Atlantic 161 kV Breaker Replacement | Replace two 161 kV oil filled breakers with SF6. | IA | Other | Age and Condition |  |  |  |  | 2024-01-01 | 161 |  | 800000
MTEP23 | West | Northern States Power (Xcel Energy) | 23712 | Lyon County Substation - FRM13 | Replace 5N130 actuator secondary current limitation to increase TR9 rating back up to it's transformer limits. | MN | Other | Reliability |  |  |  |  | 2023-09-01 | 345 |  | 300000
MTEP23 | Central | Wabash Valley Power Association, Inc. | 23714 | Rebuild Citizens 69kV Line (Groups C & E) | Rebuild 69kV line group on CEC 69 kV System - Phase 2 | MO | Other | Age and Condition |  |  |  |  | 2024-12-31 | 69 |  | 675000
MTEP23 | Central | Wabash Valley Power Association, Inc. | 23715 | New Charmin Bulk 161 kV Sub. Breakers | Add breakers to Charmin Bulk to have 2 separate 161kV feeds from Trail of Tears. | MO | Other | Reliability |  |  |  |  | 2024-02-28 | 161 |  | 4485000
MTEP23 | West | Great River Energy | 23717 | Deer River Breaker Replacement | Replace breakers 21NB1,2 & 3. Oil containment and SSVT relocation project is be combined with this project to create more efficiencies with project execution. Replace bus PTs as well due to relay prioritization recommendation. Replace single phase 115kV CCVT with 3 single-phase CCVTs. Move Zemple line relays to the 115kV CTs (current transformers) and CCVTs. Replace EEE and internal equipment, address bus work and jumper issues, and fix wood high side dead-end. | MN | Other | Age and Condition |  |  |  |  | 2025-04-09 | 69 |  | 3823670.01
MTEP23 | West | Great River Energy | 23718 | Rush City Ring Bus Upgrade | This project will establish a 230 kV ring bus topology at Rush City. For GRE to address the rating exceedances experienced with the current shared breaker position, GRE will add breakers and associated equipment/relaying/etc. to the 230-kV Rush City bus between the Linwood, Red Rock, and Rock Creek lines | MN | BRP | [5 empty] | 2025-03-27 | 230 |  | 4013958.83
MTEP23 | West | MidAmerican Energy Company | 23719 | Oakland: Add 69 kV, 12 MVAR Capacitor Bank and 69 kV Line Breakers | Install 69 kV, 12 MVAR capacitor bank and install 69 kV line breakers at Oakland Substation. | IA | Other | Reliability |  |  |  |  | 2026-06-01 | 69 |  | 5000000
MTEP23 | West | MidAmerican Energy Company | 23720 | Hickory Avenue-Sioux Center 69 kV Line & Substation Line Terminals | Construct new 69 kV line from Hickory Avenue Substation to Sioux Center Substation. Expand Hickory Avenue and Sioux Center Substations to install new 69 kV line terminals. | IA | BRP | [5 empty] | 2025-06-01 | 69 |  | 12000000
MTEP23 | West | MidAmerican Energy Company | 23721 | Monona: Replace 161 kV Transformer | Replace the existing Monona 161-69 kV transformer with a 125 MVA unit. Convert Monona 161 kV bus to a ring bus configuration. Also, replace two 69 kV breakers and upgrade associated terminal equipment | IA | Other | Reliability |  |  |  |  | 2025-12-01 | 161 |  | 7000000
MTEP23 | West | ITC Midwest | 23722 | J1132 GIA TOIF | TOIF includes facilities and equipment dedicated to the Generating Facility including; 69kV switch | IA | GIP | [5 empty] | 2024-06-01 | 69 |  | 40968
MTEP23 | West | MidAmerican Energy Company | 23723 | Edgington 161-13.2 kV Substation | Construct new 161-13.2 kV sub and 161 kV line taps. Install fiber for communication and protective relaying. | IL | Other | Reliability |  |  |  |  | 2027-12-31 | 161 |  | 10500000
MTEP23 | West | MidAmerican Energy Company | 23724 | Pomeroy 161 kV Substation 69 kV Breaker Replacement and Addition | Replace 69 kV breaker 7290. Convert 34.5 kV system to 69 kV due to condition. Expand Pomeroy 69 kV bus to accommodate additional 69 kV line terminal and add 69 kV bus differential relaying. | IA | Other | Age and Condition |  |  |  |  | 2023-12-31 | 161 |  | 600000
MTEP23 | West | MidAmerican Energy Company | 23725 | Palo Alto 345 kV Substation Expansion for J877 | Add one new 345 kV line terminal at Palo Alto substation for J877 solar farm generator tie line. | IA | GIP | [5 empty] | 2025-07-01 | 345 |  | 3800000
MTEP23 | West | MidAmerican Energy Company | 23726 | Raun - Remsen 345 kV Line Uprate for DPP 2018 | Replace line structures to increase line rating. | IA | GIP | [5 empty] | 2024-12-01 | 345 |  | 1200000
MTEP23 | West | MidAmerican Energy Company | 23727 | Sub 56 161 kV Substation Expansion for J1131 | Add one new 161 kV line terminal at Sub 56 for J1131 solar farm generator tie line. | IA | GIP | [5 empty] | 2027-09-01 | 161 |  | 2025000
MTEP23 | West | Northern States Power (Xcel Energy) | 23728 | Owen Area Substation | Install new Owen Area Substation and convert Owen Distribution to 23.9 kV. | WI | Other | Load Growth |  |  |  |  | 2026-10-15 | 69 |  | 7854000
MTEP23 | West | MidAmerican Energy Company | 23739 | Sub 42: Install 69 kV Line Switches | Install new 69 kV line switches on both sides of the Sub 42 substation to increase switching flexibility. | IL | Other | Reliability |  |  |  |  | 2027-12-31 | 69 |  | 800000
MTEP23 | West | MidAmerican Energy Company | 23740 | Webster: Replace 161 kV Breaker 9250 | Replace 161 kV breaker 9250 in Webster substation | IA | Other | Other Local Needs |  |  |  |  | 2026-12-31 | 161 |  | 300000
MTEP23 | West | MidAmerican Energy Company | 23741 | Wright 161 kV Terminal Equipment Upgrades | Replace 1200A substation terminal equipment on Webster - Wright and Wall Lake- Wright 161 kV line terminals. | IA | Other | Other Local Needs |  |  |  |  | 2026-12-31 | 161 |  | 150000
MTEP23 | East | METC | 23743 | Deja Junction - Vestaburg 138 kV Rebuild | Rebuild 4.3 miles section between Deja Jct. and Vestaburg of the Eureka - Vestaburg 138kV line. | MI | BRP | [5 empty] | 2027-06-01 | 138 |  | 8822000
MTEP23 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 23748 | Rebuild Y74-1 NE - Modification 69 kV | Rebuild ~1.75 miles of 69 kV line to increase rating for local operational flexibility and contingency support | IN | Other | Other Local Needs |  |  |  |  | 2024-12-31 | 69 |  | 710600
MTEP23 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 23749 | Rebuild Y39 Cato - Winslow 69 kV | Rebuild ~9.5 miles of 69 kV due to aging infrastructure and pole condition (conductor size not changing) | IN | Other | Age and Condition |  |  |  |  | 2024-12-31 | 69 |  | 14130000
MTEP23 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 23751 | Replace Maryland 69/12 kV T1 and New 69/12 kV T2 transformers | Replace existing 69/12 kV distribution T1 at Maryland due to age, and add new 69/12 kV T2 for distribution system contingency support | IN | Other | Reliability |  |  |  |  | 2024-12-31 | 69 |  | 3900000
MTEP23 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 23755 | Replace Point Dist. 69/12 kV Transformer | Replace existing 69/12 kV distribution transformer due to age and condition | IN | Other | Age and Condition |  |  |  |  | 2024-12-31 | 69 |  | 12257000
MTEP23 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 23756 | Replace Yankeetown 69/12 kV Transformer | Replace existing 69/12 kV distribution transformer T1 due to age and condition | IN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 69 |  | 1102500
MTEP23 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 23757 | New Garvin 69/12 kV Transformer | Add second 69/12 kV distribution transformer to provide distribution system support and contingency | IN | Other | Reliability |  |  |  |  | 2024-12-31 | 69 |  | 2500000
MTEP23 | Central | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. | 23758 | New Bergdolt 138/12 kV Transformer | Add second 138/12 kV distribution transformer at the Bergdolt sub to provide distribution system and contingency support | IN | Other | Reliability |  |  |  |  | 2024-12-31 | 138 |  | 2500000
MTEP23 | West | Northern States Power (Xcel Energy) | 23760 | Nobles County Substation - FRM13 | Upgrade flexible busbar to increase ratings of TR9 and TR10. | MN | Other | Reliability |  |  |  |  | 2023-09-01 | 345 |  | 450000
MTEP23 | West | Great River Energy | 23761 | NW Litchfield Substation Tap | Tap Xcel’s Grove City – Litchfield Mun 69 kV line and Construct about 3 miles of 69 kV radial line to the high side of Meeker’s new NW Litchfield distribution substation. Install metering and telecom at the new sub. | MN | Other | Load Growth |  |  |  |  | 2027-01-04 | 69 |  | 2969551
MTEP23 | West | Great River Energy | 23762 | Trimont Substation Retirement | Retire GRE assets in the Trimont SMEC distribution substation. | MN | Other | Other Local Needs |  |  |  |  | 2024-04-30 | 69 |  | 243446.12
MTEP23 | West | Great River Energy | 23763 | Laketown Substation Tap | Install 3-way MOD 2000 A 115 kV switch on GRE’s MV-VTT and construct about 3 mile 115 kV transmission line from the three way switch to the high side of MVEC’s Laketown distribution substation. | MN | Other | Load Growth |  |  |  |  | 2028-09-26 | 115 |  | 6308542
MTEP23 | West | Great River Energy | 23764 | Stinson Breaker Addition | Add low side breaker and SEL-487E secondary transformer relay. Move 69kV line relays to the 69kV CTs. New panel will be installed with SEL-487E and breaker controls. | MN | Other | Reliability |  |  |  |  | 2025-09-02 | 69 |  | 664368
MTEP23 | Central | Gridliance | 23765 | Rebuild Joppa-Joppa TS-Grahamville 161 line (854) | Rebuild the GridLiance Heartland portion of Joppa - Joppa TS - Grahamville 161 kV Ckt 854 three terminal line | KY,IL | Other | Age and Condition |  |  |  |  | 2026-12-31 | 161 |  | 21900000
MTEP23 | Central | Indianapolis Power & Light Company | 23766 | New IU Health Substation 138 kV | New 138 kV, two 40 MVA transformer, three-breaker straight bus substation to serve customer load | IN | Other | Load Growth |  |  |  | 40 MVA | 2023-12-31 | 138 |  | 15000000
MTEP23 | Central | Wabash Valley Power Association, Inc. | 23779 | Rebuild Citizens 69kV Line (Groups A & B) | Rebuild 69kV line group on CEC 69 kV System - Phase 1 | MO | Other | Age and Condition |  |  |  |  | 2023-12-31 | 69 |  | 1600000
MTEP23 | Central | Wabash Valley Power Association, Inc. | 23780 | Relocate T23 69kV for Ameren Wittenberg-Whipple Line | Relocate T23 69kV to allow for Ameren's new 138kV Line (Wittenberg - Whipple) | MO | Other | Reliability |  |  |  |  | 2023-12-31 | 69 |  | 4588146
MTEP23 | West | Great River Energy | 23781 | Shannon Breaker Addition | Add low side breaker and SEL-487E secondary transformer relay. Move 69kV line relays to the 69kV CTs. New panel will be installed with SEL-487E and breaker controls. Replace RTU. Replace two (2) 69kV Bus PTs (G.E. Superbute) | MN | Other | Reliability |  |  |  |  | 2024-10-15 | 69 |  | 596069
MTEP23 | West | Great River Energy | 23782 | Dotson Corners Breaker Replacement | Replace 69kv oil breakers 860, 861, and 862 and associated equipment. | MN | Other | Age and Condition |  |  |  |  | 2026-07-18 | 69 |  | 778017
MTEP23 | West | Great River Energy | 23783 | Maple Lake Breaker Replacement | Replace 69kV relaying & Breakers 1NB4 & 5 at the Maple Lake sub and associated equipment. | MN | Other | Age and Condition |  |  |  |  | 2025-02-28 | 69 |  | 1158346
MTEP23 | West | Great River Energy | 23784 | Blackberry Breaker Addition | Remove existing switch 20NSM1 from Blackberry and replace with a circuit breaker and disconnect. OR Retain existing switch 20NSM1 at Blackberry and add a circuit breaker between the 115/69 kV transformer and switch 20NSM1. | MN | Other | Other Local Needs |  |  |  |  | 2025-09-01 | 69 |  | 704466
MTEP23 | East | METC | 23785 | J1550 Generator Interconnection | Install a new 138kV switching station. Install five 138kV breakers rated at 40kA and two bus sections. Cut the METC Batavia - Barton Lake and Batavia - J1320 (Coldwater) 138 kV circuits into the new 138 kV switching station. | MI | GIP | [5 empty] | 2025-03-03 | 138 |  | 15666608
MTEP23 | South | South Mississippi Electric Power Association | 23786 | Ft Redwood - Rawhide 115kV Line | Tap the Entergy MS owned Flowers - Tinsley 115kV line and construct a new Cooperative Energy owned 115kV breaker switching station near Rawhide Road in Warren, MS. Construct a new 115kV line from a new Cooperative Energy owned breaker 115kV switching station near the Ft Redwood substation to the new Cooperative Energy owned switching station near Rawhide Road. Rebuild the existing Cooperative Energy owned Redwood - Ft Redwood 115kV line to support the industrial customer's full load during unplanned on-site generation outages. | MS | BRP | [5 empty] | 2026-06-01 | 115 |  | 13492500
MTEP23 | West | Great River Energy | 23799 | Benton County 115 kV Breaker Replacement | Replace 115kV breakers 5N52 and 5N53. | MN | Other | Age and Condition |  |  |  |  | 2023-11-16 | 115 |  | 526695.97
MTEP23 | West | Great River Energy | 23800 | Gilman - Milaca 69 kV Line Rebuild | Rebuild the JC line (18.93 miles) and switch SS2888 to 69kV with 477 ACSS . | MN | Other | Reliability |  |  |  |  | 2026-08-21 | 69 |  | 12048956
MTEP23 | West | Great River Energy | 23801 | Cotton Substation Tap Rebuild | LCP is rebuilding the existing Cotton Distribution site to the north, the 115 kV (TT Line) will need to adjust to terminate on LCP’s new high side structure. The EEE from Goodland distribution substation will be placed at the new Cotton substation. | MN | Other | Reliability |  |  |  |  | 2023-09-29 | 115 |  | 468450.72
MTEP23 | West | Great River Energy | 23802 | West Otsego Substation Tap | Install a 3-way 69 kV switch on GRE’s Otsego to Albertville 69 kV line and construct about 0.5 miles of 69 kV tap line to the high side of Wright Hennepin’s West of Otsego area substation. | MN | Other | Load Growth |  |  |  |  | 2025-10-31 | 69 |  | 1283329
MTEP23 | West | Great River Energy | 23803 | Big Swan Capacitor Bank Addition | Add a new 40 MVAr capacitor on the extended 115-kV bus and replace 69-kV bus relaying, station power, and battery bank. | MN | BRP | [5 empty] | 2024-11-01 | 115 |  | 2633876.19
MTEP23 | West | Great River Energy | 23804 | Kimball Substation Tap | Install a 3-way 69 kV, 1200 A switch on Xcel Energy’s Kimball – Watkins 69 kV line and construct about 2 miles of 69 kV line with 477 ACSR conductor to the high side of Meeker’s new Kimball area distribution substation. | MN | Other | Reliability |  |  |  |  | 2025-07-29 | 69 |  | 1036304.63
MTEP23 | West | Great River Energy | 23805 | Searles Capacitor Bank Retirement | Retire the 5.4 MVar Searles Capacitor Bank and associated components. | MN | Other | Other Local Needs |  |  |  |  | 2023-08-31 | 69 |  | 116968.65
MTEP23 | West | Otter Tail Power Company | 23806 | OTP Lake Preston, SD Load Addition | OTP has a new customer requesting to be served in Lake Preston, SD. OTP will serve the new customer by extending a 115 kV line from our Hetland 115 kV substation to a new Lake Preston 115/34.5 kV substation. A new 115 kV line will be extended from the new Lake Preston 115/34.5 kV substation to Xcel's Brookings County 345/115 kV substation to create a 115 kV looped network. Capacitors will be installed at the new Lake Preston 115/34.5 kV substation for additional voltage support. The Facilities will consist of the following: 1. Hetland 115 kV substation termination addition 2. Approximate 9.5 mile 115 kV line from Hetland 115 kV substation to a new Lake Preston 115/34.5 kV substation 3. A new Lake Preston 115/34.5 kV substation with capacitors installed at the 115 kV level 4. Approximate 45 mile 115 kV line from the new Lake Preston 115/34.5 kV substation to Xcel's Brookings County 345/115 kV substation | SD | Other | Load Growth | Serve new customer load in SD by extending 115 kV from Hetland to new Lake Preston 115/34.5 kV; then 45-mi 115 kV to Brookings County 345/115 kV | Large Load |  |  | 2024-12-31 | 115 |  | 42600000 | Lake Preston: new customer load in SD, ~55mi new 115kV line (OTP). $42.6M
MTEP23 | East | METC | 23807 | Alma - Vestaburg 138 kV Reconductor | Reconductor from Vestaburg to structure #2W8472 (~16.24 miles) from 954 ACSR to 954 ACSS. Also, upgrade 1590 SAC buses and 1200A switches at Alma position “477” to at least 455 MVA for summer emergency rating. | MI | BRP | [5 empty] | 2027-06-01 | 138 |  | 16660000
MTEP23 | West | Great River Energy | 23819 | Eidswold Substation Tap | New 115/12.47 kV substation for Dakota Electric Association (DEA) in the Elko New Market area. | MN | Other | Load Growth |  |  |  |  | 2024-11-22 | 115 |  | 207813.44
MTEP23 | South | South Mississippi Electric Power Association | 23820 | Gloster 13.8kV Delivery Point | A new 13.8kV feeder breaker will be added at the Entergy Mississippi LLC owned Gloster substation in order to serve Cooperative Energy's distribution member's new customer. | MS | Other | Load Growth |  |  |  |  | 2024-06-01 | 115 |  | 483800
MTEP23 | West | Great River Energy | 23821 | Penelope Capacitor Bank Retirement | Retire the 5.4 MVar Penelope Capacitor Bank and associated components. | MN | Other | Other Local Needs |  |  |  |  | 2023-08-18 | 69 |  | 121351
MTEP23 | West | Great River Energy | 23822 | Matawan - St. Olaf Lake 69 kV Rebuild | Rebuild SW-MB line segments 1 and 2 (11.01 miles) (Matawan switches to St. Olaf Lake switches) to 69 kV minimum conductor size 477 ACSR would meet voltage and thermal considerations per planning. | MN | Other | Age and Condition |  |  |  |  | 2026-09-07 | 69 |  | 7309835
MTEP23 | West | Great River Energy | 23823 | Burnsville Capacitor Bank Retirement | Remove existing cap bank and 5M201. Relocate breaker 5M198 to 5M201 location. Leave A3 for future termination. | MN | Other | Other Local Needs |  |  |  |  | 2025-12-31 | 69 |  | 1022278
MTEP23 | West | Great River Energy | 23824 | Virginia Breaker Addition | Add low side breaker and SEL-487E secondary transformer relay. Move 69kV line relays to the 69kV CTs. New panel will be installed with SEL-487E and breaker controls. Replace RTU. Replace three (3) 69kV Bus Pts (G.E. Superbute) | MN | Other | Reliability |  |  |  |  | 2024-11-11 | 69 |  | 555894.89
MTEP23 | Central | Indianapolis Power & Light Company | 23825 | Reconfigure Rockville 138 kV substation | Conversion of Rockville 138 kV to a ring bus configuration | IN | BRP | [5 empty] | 2024-12-01 | 138 |  | 8500000
MTEP23 | Central | Gridliance | 23826 | Rebuild Joppa - Grahamville 161 line (804) | Rebuild the GridLiance Heartland portion of Joppa - Grahamville 161 kV Ckt 804 line | KY,IL | Other | Age and Condition |  |  |  |  | 2026-12-31 | 161 |  | 21900000
MTEP23 | Central | Gridliance | 23827 | New 3-breaker ring bus substation | Build new 3-breaker ring bus switching station near Heath, KY bisecting Joppa - Shawnee 161 kV ckt 1 line with one terminal for connection with Big Rivers Electric McCracken station. Additionally, add 1-161 kV breaker at Joppa TS station and remove existing Joppa - Joppa TS - Shawnee 161 kV ckt 1 three terminal in Illinois by bringing line in and out of Joppa TS station. | KY | Other | Reliability |  |  |  |  | 2026-12-31 | 161 |  | 15900000
MTEP23 | East | ITC Transmission | 23828 | Hurst 120 kV 33.3 MVAR Capacitor | Install a 33.3 MVAR capacitor at bus 102, position HJ, with a new 120 kV, 40 kA synchronous breaker and associated disconnect switch. Install a 3000 A, 40 kA breaker at position HK on the Hurst – Genoa 120 kV circuit. | MI | BRP | [5 empty] | 2025-06-01 | 120 |  | 3125000
MTEP23 | East | METC | 23829 | Tompkins 345/138 kV Transformer #1 Replacement | Replace the 345/138 KV transformer #1 at Tompkins with a new, standard transformer of similar size. | MI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 345 |  | 5231640
MTEP23 | East | METC | 23830 | MCV 138 kV Station Equipment Upgrade | Upgrade thermal relay at position "3141" to at least 620 MVA. | MI | BRP | [5 empty] | 2026-12-31 | 138 |  | 190000
MTEP23 | Central | Indianapolis Power & Light Company | 23831 | New Gillette 138 kV Substation | New 138 kV, two 40 MVA transformer, three-breaker straight bus substation to serve customer load | IN | Other | Load Growth |  |  |  | 40 MVA | 2024-11-01 | 138 |  | 15000000
MTEP23 | Central | Indianapolis Power & Light Company | 23832 | New 138/13.2 Transformer at Thompson Substation | One new 138/13.2 kV 40 MVA distribution transformer with one new 138 kV breaker | IN | Other | Load Growth |  |  |  | 40 MVA | 2023-11-01 | 138 |  | 16000000
MTEP23 | Central | Duke Energy Corporation | 23833 | New Edinburgh Industrial Park 69/12kV sub | DEI to construct high-side and loop 69kV lines into a new IMPA-owned Edinburgh Industrial Park substation; one 69/12kV 20MVA transformer; SCADA controlled MOLB 69kV line switches; two 69kV buses with a manually operated 69kV bus tie switch; 69kV connections from the 6950 and 69146 ckts. | IN | Other | Reliability | DEI to construct high-side and loop 69 kV lines into new IMPA-owned Edinburgh Industrial Park substation; one 69/12 kV 20MVA transformer | Industrial Park |  | 20 MVA | 2025-06-01 | 69 |  | 4570000
MTEP23 | Central | Indianapolis Power & Light Company | 23834 | New Valley Avenue 138 kV Substation | New 138 kV, two 40 MVA transformer, three-breaker straight bus substation to serve customer load | IN | Other | Load Growth |  |  |  | 40 MVA | 2024-12-31 | 138 |  | 15000000
MTEP23 | East | METC | 23835 | Pere Marquette Transformer 2 Replacement | Replace 345/138KV transformer 2 at Pere Marquette with a new, standard transformer of similar size. Install a 345 kV breaker and associated switch on the high side of the transformer. Also, install a 138 kV switch on the low side of the transformer. | MI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 345 |  | 8500000
MTEP23 | West | American Transmission Co. LLC | 23836 | Perch Lake - National 138kV (468) Partial Retirement Project | Reconfigure 138kV line 468, from Perch-Lake to Presque Isle, by terminating into National SS to establish a new Perch Lake – National line. The remaining 23mi of line from National to Presque Isle will be retired. | MI | Other | Reliability |  |  |  |  | 2025-11-01 | 138 |  | 10400000
MTEP23 | West | American Transmission Co. LLC | 23837 | Northeast - Revere Dr. 69kV (C-103), Uprate or Rebuild | Scope to include partial rebuild • Substation scope is for Revere Drive • Fiber optic installation | WI | Other | Age and Condition |  |  |  |  | 2030-01-31 | 69 |  | 8600000
MTEP23 | West | American Transmission Co. LLC | 23838 | High Falls – Mountain 69kV (Y-77), Rebuild & OPGW | Rebuild ~16.4 miles with new wire mesh wrapped wood pole structures and steel poles on foundation. - T2 4/0 Conductor and 48 Fiber OPGW. Conductor would meet and exceed planning needs. - Assumed to obtain Certificate of Authority (CA) application by rebuilding off center (30’ shift) and obtaining new 80’ easements typically. This is due to radial connection and uncertainty at this time if outage and distribution could be taken out for period of time. This may not be necessary once project gets into details and could result in savings as listed under alternatives. • Real Estate, Environmental, Vegetation - Majority of existing easements are 80' in width with VM and access rights. 2 DNR parcels will require permit/easement. - Project assumes new easements at $800k due to shift in ROW, rest through NEPA permit. - Shifting centerline will require going through the NEPA process (schedule impacts), likely an Environmental Assessment (EA), with a resulting Special Use Permit from the Chequamegon-Nicolet National Forest. - Federal forest lands currently limit herbicide spray, resulting in brush growing up along the Rights-of-Way. Within 2 years of next cycle and in decent shape with prior aerial saw work. | WI | Other | Age and Condition |  |  |  |  | 2028-12-31 | 69 |  | 33000000
MTEP23 | West | Otter Tail Power Company | 23842 | OTP Wilmot - Peever Jct. 41.6 kV | Rebuild 4 miles of 41.6 kV line between Wilmot 41.6 kV and Peever Jct. 41.6 kV. | SD | Other | Reliability |  |  |  |  | 2024-12-31 | 41.6 |  | 1125000
MTEP23 | Central | Ameren Services Company | 23844 | Replace Pole and Insulator Program - MTEP23 | Pole and Insulator Replacements requested by Maintenance. | IL,MO | Other | Age and Condition |  |  |  |  | 2025-12-01 | 345 |  | 20000000
MTEP23 | Central | Ameren Services Company | 23845 | Replace Breakers and Relays Program - MTEP23 | Breaker and Relay Upgrades Requested by Maintenance (Missouri and Illinois) | IL,MO | Other | Age and Condition |  |  |  |  | 2025-12-01 | 345 |  | 5000000
MTEP23 | Central | Ameren Services Company | 23846 | New Seminary - Wittenberg - Grand Tower 138 kV line | This project will include building a new Perryville (Seminary) - Wittenberg - Grand Tower 138 kV line. | MO | BRP | [5 empty] | 2026-12-31 | 138 |  | 68000000
MTEP23 | East | METC | 23847 | Bingham - Looking Glass 138 kV Rebuild | Rebuild approximately 19.3 miles of the Bingham – Looking Glass 138 kV circuit to 1431 ACSR conductor utilizing 138 kV double- circuit structures with OPGW. Leave the East side of the double-circuit structures vacant. Connect OPGW at Bingham 138 kV position WM6. | MI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 138 |  | 35395000
MTEP23 | Central | Duke Energy Corporation | 23848 | Rebuild WVPA Montclair to Montclair Jct. 69kV | WVPA Montclair to Montclair Jct. 69134 69kV Rebuild: rebuild 69kV line section | IN | Other | Reliability |  |  |  |  | 2023-12-18 | 69 |  | 8888000
MTEP23 | West | Great River Energy | 23849 | Big Swan - Wakefield Storm Structures | Install (2) new storm structures every 5 miles along the ME-BW line between structures 306 and 415 as there are no full stop deadends in this section of line. Possible locations are structures 340 or 349 and 374 or 383. | MN | Other | Reliability |  |  |  |  | 2024-10-31 | 115 |  | 526381
MTEP23 | Central | Duke Energy Corporation | 23850 | Rebuild WVPA Lee Hanna to Lee Hanna Jct 69 kV (Phase 3) | Rebuild 5.6 miles of 69 kV to match line conductor for Fortville to Mohawk line. (954 ACSR) | IN | Other | Reliability |  |  |  |  | 2023-10-31 | 69 |  | 3274000
MTEP23 | Central | Indianapolis Power & Light Company | 23852 | New Petersburg Energy Center 138 kV (R1011) | Interconnection Customer shall install a 279.45 MVA generator facility. | IN | GIP | [5 empty] | 2025-12-31 | 345 |  | 35000000
MTEP23 | East | ITC Transmission | 23853 | Wayne Transformer 301 Replacement | Replace 345/120kV transformer 301 at Wayne station with a new transformer rated at least 750 MVA for summer emergency. | MI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 345 |  | 5635000
MTEP23 | South | Entergy Arkansas | 23855 | Keo 500kV Bus Reconfigure | Reconfigure the Keo 500 kV substation so that the Keo – White Bluff & Keo - Wrightsville 500kV lines are not lost for a P2.3 internal breaker fault. | AR | BRP | [5 empty] | 2027-12-01 | 500 |  | 15015000
MTEP23 | West | American Transmission Co. LLC | 23856 | Benson Lake SVC SCM Layer Asset Renewal | Replace hardware and software of the Benson Lake SVC plant System Control and Monitoring (SCM) Layer with supported hardware and software with a design life of 10 years. | WI | Other | Age and Condition |  |  |  |  | 2026-12-01 | 20.5 |  | 4500000
MTEP23 | West | American Transmission Co. LLC | 23857 | Pine Hy Tap – Pine Hy 69kV (ASPY31-1), Rebuild & OPGW | Install 6.3 miles of new single circuit line on existing ROW. | MI | Other | Age and Condition |  |  |  |  | 2027-12-31 | 69 |  | 11500000
MTEP23 | West | American Transmission Co. LLC | 23858 | Wick Drive – Black Earth 69kV, (Y-62), OPGW Addition & Partial Rebuild | Installation of 6 miles OPGW with (57) Structure Replacements and (2.2) miles of new (T2-477 HAWK) conductor added to scope between the Wick Drive to Mazomanie Tap substations • 55 replacements assumed due to engineering usage analysis of 1985 and earlier structures. Of the 55 replacements, 22 also are legacy with asset renewal condition need. • 2 additional structures from WKS-MAZT to replace due to ground clearance for new T2-477. • OPGW Termination from Wick Drive and Black Earth substation Dead-End structures into the control houses • Substation Router Configuration to route SCADA and Relay communications on to ATC’s private fiber network infrastructure • Real Estate Easements Required to address gaps and areas of inadequate width. (~$500k) | WI | Other | Other Local Needs |  |  |  |  | 2026-12-31 | 69 |  | 7000000
MTEP23 | West | Otter Tail Power Company | 23859 | OTP Granville - Granville Station 41.6 kV | Rebuild of 41.6 kV line between Granville 41.6 kV and Granville Station 41.6 kV. | ND | Other | Reliability |  |  |  |  | 2023-12-31 | 41.6 |  | 1000000
MTEP23 | West | Otter Tail Power Company | 23860 | OTP Grenville - Veblen 41.6 kV | Rebuild of 41.6 kV line between Grenville 41.6 kV and Veblen 41.6 kV. | SD | Other | Reliability |  |  |  |  | 2025-11-30 | 41.6 |  | 4600000
MTEP23 | Central | Duke Energy Corporation | 23861 | Upgrades Columbus 345 kV Sub Breaker | Columbus 345 Sub Breaker Upgrades: Replace (3) 138kV CBs on Xfmr Banks 1, 2, and 3 with higher fault interrupting capacity | IN | BRP | [5 empty] | 2026-12-31 | 138 |  | 1500000
MTEP23 | Central | Duke Energy Corporation | 23862 | Upgrade Bedford 345 kV Sub - 138-138 Bus Tie | Bedford 345 KV Sub 138-138 bus tie path - Upgrade 138kV bus (increase to 2-1590AL), CTs (reconnect at 2000A:5A ratio), and (2) switches (replace with 3000A) | IN | BRP | [5 empty] | 2032-04-01 | 138 |  | 667000
MTEP23 | Central | Duke Energy Corporation | 23863 | Upgrade Cayuga to Nucor 34501 Line Terminal 345 kV | Cayuga to Nucor 34501 Line Terminal Bus Upgrades: Upgrade 2500AL bus to 2-1590AL at both line terminals | IN | BRP | [5 empty] | 2027-04-01 | 345 |  | 320000
MTEP23 | Central | Duke Energy Corporation | 23864 | New Bloomington Area 138kV Source | Construct new 345/138kV substation on the west side of Bloomington with (1) 138kV line to Bloomington Rogers St. | IN | BRP | [5 empty] | 2028-06-01 | 345 |  | 44500000
MTEP23 | East | METC | 23865 | Elephant - Phase 1 | CE has requested a new 103 MW (expanding to 206 MW) Industrial interconnection near METC's Mecosta substation. To accommodate this request, METC would install a new, 3-row, 138 kV substation near the customer site, and loop the existing Chase-Mecosta 138 kV line approx. 1.5 miles into the new substation. A 138 kV, 54 MVAR cap bank would be installed at the new substation. METC would also rebuild the entire Chase-Mecosta 138 kV circuit (approx. 17.6 miles), and rebuild a 7.8 mile segment of the Croton-Mecosta 138 kV line. | MI | Other | Other Local Needs |  |  |  |  | 2025-03-01 | 138 |  | 56025000
MTEP23 | West | Otter Tail Power Company | 23866 | OTP Veblen 41.6 kV Breaker Replacement | Replacement of Veblen 41.6 kV breaker. | SD | Other | Age and Condition |  |  |  |  | 2023-12-31 | 41.6 |  | 450000
MTEP23 | Central | Duke Energy Corporation | 23867 | Rebuilding WVPA Anderson Grain 69/12kV Sub | Relocate transmission and add in&out with SCADA switches for new Anderson Grain substation. Install 69kV ckt switcher and relaying for high side protection. | IN | Other | Age and Condition |  |  |  |  | 2024-08-07 | 69 |  | 1750000
MTEP23 | Central | Duke Energy Corporation | 23868 | New WVPA IPC to 69162 Tap loop 69 kV | Build 69 kV from IPC to 69162 Tap 2.8 miles. Add 2 ATO switchs at IPC tap & 3 switches at 69162 line tap. 90 amps minimum. 477 ACSR. | IN | Other | Reliability |  |  |  |  | 2023-12-31 | 69 |  | 6000000
MTEP23 | West | Great River Energy | 23869 | Ramsey Breaker Replacement | Replace breaker 33RB1 | MN | Other | Age and Condition |  |  |  |  | 2024-06-28 | 230 |  | 471468
MTEP23 | South | Entergy | 23870 | 2024 ETI Asset Renewal Program | This project is for the ETI Asset Renewal Program that will be executed in 2024. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. | TX | Other | Age and Condition |  |  |  |  | 2024-12-31 | 500 |  | 34240000
MTEP23 | Central | Duke Energy Corporation | 23871 | New WVPA NSC Lick Creek 69/12kV Sub. | Build new WVPA NSC (Ninestar Connect) Lick Creek substation; Install 22.4MVA 69/12kV sub with 3-way switches at line jct.; preliminary plan is to be fed from the 69198 ckt. | IN | Other | Load Growth |  |  |  | 4 MVA | 2026-10-31 | 69 |  | 6923547
MTEP23 | East | METC | 23872 | Kraft 138 kV Station Equipment Upgrade | Upgrade existing 500 circuit switcher, two line switches with new breakers at Kraft 138kV station and remove N.O. 3317 PTS. | MI | Other | Reliability |  |  |  |  | 2026-12-31 | 138 |  | 6075105
MTEP23 | West | American Transmission Co. LLC | 23874 | Harrison Tap – Iola 69kV (Y-70), Rebuild & OPGW | Rebuild approximately 11 miles of 69 kV with new wood monopoles wrapped with mesh. | WI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 16000000
MTEP23 | West | American Transmission Co. LLC | 23875 | Madison Area Relay Projects | Asset Renewal of Blount control building and contents. Retire the existing 69kV control building at Sycamore. Install new relaying at Blackhawk(MGE), Blount, East Campus, Ruskin, Sycamore, Walnut GIS and Wingra SS. | WI | Other | Age and Condition |  |  |  |  | 2026-12-01 | 138 |  | 21900000
MTEP23 | West | American Transmission Co. LLC | 23876 | Cornell Tap – Watson Tap 69kV (Chandler), Partial Rebuild | Rebuild approximately 18 miles of 69kV Chandler line between Cornell Tap and Watson Tap. | MI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 30000000
MTEP23 | West | Minnesota Power (Allete, Inc.) | 23877 | Nelson Lake 230 kV Substation | New 230 kV switching station tying together MP Square Butte East - Bison and GRE Square Butte - Stanton 230 kV lines | ND | Other | Reliability |  |  |  |  | 2026-06-01 | 230 |  | 25000000
MTEP23 | East | ITC Transmission | 23880 | 2023 ITCT Line Relocation Blanket | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI | Other | Other Local Needs |  |  |  |  | 2023-12-31 | 345 |  | 2400000
MTEP23 | South | Entergy | 23881 | Holiday to Lafayette 69 kV: Reterminate into Elks | Re-terminate the Holiday to Lafayette 69 kV line into the LUS Elks 69 kV substation, creating an Elks to Holiday 69 kV path. Demolish the unused portions of the Holiday - Lafayette 69 kV line. Upgrade/Rebuild Holiday to Elks line. | LA | Other | Reliability |  |  |  |  | 2025-06-01 | 69 |  | 29400000
MTEP23 | South | Entergy | 23882 | Barnett Oil Mill 69 kV Relocation | Build new 69kV T-line from Barnett Oil Mill Sub to a tap point on the existing CLECO Guidry to South Park 69kV line . Install new 3-way motor operated GOAB switch cut-in to CLECO T-line. Demolish the L-658 69kV T-line from the BROM Tap to the Barnett Oil Mill substation. Some of the L-658 structures support CLECO distribution facilities, that distribution will be relocated and/or rebuilt. | LA | Other | Reliability |  |  |  |  | 2025-06-01 | 69 |  | 23700000
MTEP23 | West | Great River Energy | 23883 | Cedar Mountain Capacitor Bank Addition | Installation of (2) 75 MVar capacitor banks, installation od of 3 new 345kV breakers to complete the breaker and a half | MN | GIP | [5 empty] | 2024-05-31 | 345 |  | 4025164
MTEP23 | East | ITC Transmission | 23884 | 2025 ITCTransmission Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | Other | Age and Condition |  |  |  |  | 2025-12-31 | 345 |  | 44250000
MTEP23 | East | METC | 23885 | 2026 METC Customer Interconnections | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in service date within the year 2026 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million a separate project will be submitted for approval | MI | Other | Other Local Needs |  |  |  |  | 2026-12-31 | 138 |  | 2500000
MTEP23 | Central | Duke Energy Corporation | 23886 | New J1234 - J1235 IN Solar 1 | J1234 - J1235 IN Solar 1 - 150MW net solar farm (100 MW for J1234 and 50 MW for J1235) | IN | GIP | [5 empty] | 2023-12-31 | 138 |  | 17232683
MTEP23 | Central | Duke Energy Corporation | 23887 | J1378 Crossroads Solar | J1378 Crossroads Solar - 200MW: 230kV connection at existing Veedersburg West sub | IN | GIP | [5 empty] | 2024-11-15 | 230 |  | 5992933
MTEP23 | Central | Duke Energy Corporation | 23892 | Reconfigure Shelbyville Northeast 138kV Ring bus | Shelbyville Northeast: build 138kV ring bus; replace CIR 6946, 6976, 69183, 13803, 13865 relays, replace OCBs 6946, 6976, 69183, 69138-1, 13803, replace Bank 1 ground switch with circuit switcher, and station battery. | IN | Other | Reliability |  |  |  |  | 2026-06-30 | 138 |  | 10800000
MTEP23 | Central | Indianapolis Power & Light Company | 23893 | New Winding Ridge 138 kV Substation | New 138 kV, two 40 MVA transformers, 8 breaker, breaker and a half substation to serve AES-IPL customer load and provide transmission service to TOs whom have requested as such | IN | Other | Load Growth |  |  |  | 40 MVA | 2024-12-31 | 138 |  | 15000000
MTEP23 | East | ITC Transmission | 23894 | Jewell 301 Transformer Replacement | Replace the 345/230 KV transformer #301 at Jewell with a new, standard transformer of similar size. | MI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 345 |  | 6600000
MTEP23 | West | American Transmission Co. LLC | 23895 | McCue SS Control House and Relay Asset Renewal | Replace control building and contents • Install relay panels, no remote end work needed • Replace Siemens Station Manager RTU • Replace 69kV OCB Westinghouse model 690-GS-2500 • Replace existing 69kV cap bank with 16.3MVAR in the same bus position, replace zero crossing breaker. • Retire or replace 796-A when reconductoring the 69kV bus • Provisions to meet battery standard TPL-001-5 requirements with either dual battery or monitoring. • Install 138kV line side disconnects if practical • Install 138kV line breaker and relaying for the section of 138kV bus that leaves the McCue yard to feed Kennedy SS • Replacement of 954.0 kcmil AAC 37 Magnolia bus and jumpers in MCU 69 kV Bus 1 and 2 | WI | Other | Age and Condition |  |  |  |  | 2026-12-01 | 138 |  | 9500000
MTEP23 | West | Otter Tail Power Company | 23896 | OTP Devils Lake, ND 115 kV Delivery | OTP is converting the 4.16 kV distribution system in the town of Devils Lake, ND to a 12.5 kV system. With this conversion, the town will be removed from our 41.6 kV system and be served via the 115 kV system. In order to move the town to the 115 kV system, a new 115 kV delivery will be established by tapping the Devils Lake East to Sweetwater 115 kV line with a two way switch. 2 miles of 115 kV line will be constructed from the new switch over to the town of Devils Lake where a new 115/12.5 kV distribution substation will be established which will include a 115 kV breaker on the high side of the 115/12.5 kV transformer. | ND | Other | Load Growth |  |  |  |  | 2026-12-31 | 115 |  | 1550000
MTEP23 | West | American Transmission Co. LLC | 23897 | Ohmstead SS Control House and Relay Asset Renewal | Replace control building and contents • Install approximately 5 relay panels, no remote end work needed • Replace Siemens Station Manager RTU • Replace one Bus power potential transformer • Add 4 new 138kV line side disconnects • Provisions to meet battery standard TPL-001-5 requirements with either dual battery or monitoring | WI | Other | Age and Condition |  |  |  |  | 2026-12-01 | 138 |  | 5700000
MTEP23 | South | Entergy Arkansas | 23898 | McNeil 500kV Relay Improvement SPOF | Ensure the McNeil – El Dorado 500 kV line, the McNeil 500/115 kV auto and the McNeil – Etta 500 kV line have redundant high-speed protection. This includes protection schemes with independent CT and PT winding inputs. Ensure dual battery installations or monitoring sufficient to FERC 754 guidelines. | AR | BRP | [5 empty] | 2026-12-01 | 500 |  | 3970000
MTEP23 | South | Entergy Arkansas | 23899 | 2024 EAL Asset Renewal Program | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. | AR | Other | Age and Condition |  |  |  |  | 2024-12-31 | 500 |  | 24638000
MTEP23 | South | Entergy Arkansas | 23900 | Dell 161kV Breaker Upgrades | Upgrade Dell 161 kV Breakers B2240, B2205, and B2235 with a 63kA breaker. | AR | BRP | [5 empty] | 2025-06-01 | 161 |  | 2515000
MTEP23 | West | American Transmission Co. LLC | 23901 | Shoto SS, Power Transformer Asset Renewal | Replace T1, a 1972 vintage 69/138 kV 84 MVA power transformer with a new 69/138 kV 100 MVA replacement. • Install oil containment system for the new transformer. • Install online monitoring to the new transformer and existing T2 transformer. • Replace fuses and assemblies, capacitors, protection voltage transformers, and reactors on existing capacitor bank and rack for a life extension of the existing asset. • Investigate and provide mitigation as needed to existing ground grid per current guidelines | WI | Other | Age and Condition |  |  |  |  | 2026-12-01 | 138 |  | 6200000
MTEP23 | West | American Transmission Co. LLC | 23902 | SS Physical Security Switch and SS Asset Renewal Enhancement | o Replace the existing Cisco 2520 switches at approximately 28 substation control house locations including dedicated firewall additions at the enhanced security sites o Replace the existing Cisco 3750/3850 physical security switches at approximately 56 control house locations o Install station wi-fi functionality at approximately 67 control house locations o Replace the existing network speakers and network door video stations at approximately 67 control house locations o Migrate mission critical equipment from AC inverted power to the station DC power at approximately 67 control house locations o Implement rogue device detection at approximately 67 control house locations | WI,MI | Other | Age and Condition |  |  |  |  | 2025-12-01 | 345 |  | 10000000
MTEP23 | West | American Transmission Co. LLC | 23903 | North Beaver Dam SS Asset Renewal | Reconfigure 138 kV bus layout • Install a fire wall between ATC and Alliant power transformers • Install online monitoring per approved 2020 program to T31 power transformer • Replace one 1980’s vintage 138 kV circuit switcher with a circuit breaker. • Replace control building which will include relay replacements, RTU replacement, and battery replacement • Replace 69kV 10.8 MVAR fused capacitor bank with a 12.25 MVAR fuseless bank • Install future 138kV bus-tie disconnect switches and a set of 138kV bus PTs to allow for bus sectionalizing • Install new line side disconnect switch on the X-47 terminal, does not currently exist • Upgrade jumpers per Planning requirements on the Y-59 line to meet future transmission line renewal needs • Upgrade strain bus in the 69 kV bus per Planning requirements to meet future needs | WI | Other | Age and Condition |  |  |  |  | 2026-12-01 | 138 |  | 16100000
MTEP23 | West | American Transmission Co. LLC | 23904 | South Beaver Dam – North Beaver Dam, 69kV (Y-59) Line Rebuild & OPGW | Rebuild line and install OPGW on 4.1 miles and install 0.9 miles of OPGW on remaining section. Assumes newer legacy vintage structures can remain. | WI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 11200000
MTEP23 | West | American Transmission Co. LLC | 23905 | Waupun - South Fond du Lac 69kV (Y-25), Partial Rebuild | Replace remaining legacy monopoles poles (~60%) as ~40% were replaced in 2011. Replace conductor and static with new material. | WI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 22600000
MTEP23 | West | American Transmission Co. LLC | 23906 | South Fond du Lac SS, Power Transformer and Breaker Asset Renewal | South Fond du Lac: - Replace 2 power transformers with new single larger voltage transformer - Install new bus for auxiliary station service - Install new motor operated switches - Relocation one gas circuit breaker to a new position to support new transformer location - Retire 3 CCVTs and relocate 1 CCVT - Install motor operators on 2 line disconnect switches - Retire one oil circuit breaker and replace with gas breaker - Replace portions of strain bus with rigid bus and replace bus PTs to support new transformer location - Retire a portion of strain bus and replace bus PTs - Replace 8 disconnect switches to support bus rebuilds and breaker replacement - Replace 4 disconnect switches Columbia: - Purchase a new spare transformer | WI | Other | Age and Condition |  |  |  |  | 2026-12-01 | 345 |  | 9500000
MTEP23 | West | American Transmission Co. LLC | 23911 | Shoto – Northeast 69kV (K-11), Rebuild | Line rebuild • Substation work at Northeast • Fiber optic installation | WI | Other | Age and Condition |  |  |  |  | 2030-10-31 | 69 |  | 5400000
MTEP23 | West | American Transmission Co. LLC | 23912 | East Krok SS Transformer Replacement | This project will replace the existing East Krok Transformer 1 with a new 138/69kV 100 MVA transformer. | WI | BRP | [5 empty] | 2027-12-31 | 138 |  | 8700000
MTEP23 | West | American Transmission Co. LLC | 23913 | Northern Adams County Area Network Improvement Project | Construct 9.2 miles of 69 kV single circuit transmission line (5 miles between Badger West and Y-302, and 4.2 miles between Y-302 and Colburn). • Expand Badger West substation with three 138 kV breakers, a 138/69 kV, 100/167/187 MVA base transformer, a new ATC control building, and one 69 kV line breaker. • Modify X-43 at Badger West to cross over the new 69kV t-line. | WI | Other | Load Growth |  |  |  | 187 MVA | 2027-05-01 | 69 |  | 39900000
MTEP23 | West | American Transmission Co. LLC | 23915 | Delta County, DIC, Upgrades | ATC will construct a 138 kV, four-breaker ring configuration substation, with ultimate provisions for a six-position 138 kV ring bus. • ATC will loop the existing Holmes-Old Mead Rd 138 kV line (OMDG81) into the new 138 kV substation, raising the OMDG81 line over the existing Old Mead Rd-Delta OMDY51 line. • ATC will retire a portion of the existing Old Mead Rd-Mead Paper 69 kV line (OMDY71), retire OMDY51/OMDY71 bypass equipment and retire the remaining portion of OMDY71 in place. • ATC will remove a 69 kV breaker and OMDY71 line MOD at Old Mead Rd. • ATC will replace 31 structures on the Arnold-Perkins 138 kV double circuit lines (ARNG81/29051). • ATC will implement reverse power blocking and/or LTC tap limiting on the Chandler and Old Mead Rd 138/69 kV transformer LTC controls. | MI | Other | Load Growth |  |  |  |  | 2027-01-31 | 138 |  | 21000000
MTEP23 | West | Otter Tail Power Company | 23917 | OTP Fordville - Fordville Jct. 41.6 kV | Rebuild of 41.6 kV line between Fordville 41.6 kV and Fordville Jct. 41.6 kV. | ND | Other | Reliability |  |  |  |  | 2025-11-30 | 41.6 |  | 1450000
MTEP23 | West | Otter Tail Power Company | 23918 | OTP Michigan - Mapes 41.6 kV | Rebuild of the 41.6 kV line between Michigan 41.6 kV and Mapes 41.6 kV. | ND | Other | Reliability |  |  |  |  | 2023-12-31 | 41.6 |  | 1000000
MTEP23 | West | Missouri River Energy Services (MRET) | 23919 | Morris to Grant County to East Fergus Falls Upgrade | Increase the rating of 115 kV lines from Morris to Grant County to East Fergus Falls. | MN | MPFP | [5 empty] | 2024-07-01 | 115 |  | 1336540
MTEP23 | West | Great River Energy | 23920 | Missouri River Line Crossing Relocation | Replace/relocate 5 towers and reconductor the river crossing to avoid structure/line segments from falling into Missouri river. | MN | Other | Reliability |  |  |  |  | 2023-10-13 | 230 |  | 3122886.14
MTEP23 | West | Great River Energy | 23921 | Pilot Knob to Deerwood Area Projects | Rebuild the Pilot Knob Substation to a breaker and a half configuration due to age and condition of the current equipment. Upgrade the DA-PD line from Deerwood to Pilot Knob substation to increase the capacity. Upgrade to be built to 115kV standards but operated at 69kV. Retire the underground portion of the DA-PLX at Pilot Knob and replace with overhead Retire the DA-RE line from Pilot Knob road to Black Hawk Road Retire the DA-PKX from Pilot Knob to Cliff Road Retire SS-2820 and replace with a turning structure. Retire SS-2819 | MN | Other | Age and Condition |  |  |  |  | 2027-05-21 | 115 |  | 29572823.69
MTEP23 | Central | Duke Energy Corporation | 23922 | Rebuild WVPA Bringhurst 69/12kV Sub | Rebuild Bringhurst 69/12kV substation. 4.5MVA loading on 6.25MVA existing bank.Possibly bring #1 & #2 sectionalizing line switches inside of substation for an in&out. WVPA owns the loop through portion of the substation. | IN | Other | Age and Condition |  |  |  |  | 2024-04-03 | 69 |  | 5800000
MTEP23 | Central | Duke Energy Corporation | 23923 | New WVPA Vandalia 69/12 kV Substation | Vandalia (Fillmore) Substation - Incorporate SCADA operated 69 kV flow-through switches into 6996 line between Greensboro and Amo. | IN | Other | Reliability |  |  |  |  | 2024-07-15 | 69 |  | 5450000
MTEP23 | South | Entergy | 23924 | Mossville 69 kV Upgrade Breaker 17955 | Breaker number 17955 at the Mossville 69 kV substation will be replaced due to the short circuit analysis. | LA | Other | Reliability |  |  |  |  | 2024-06-01 | 69 |  | 3600000
MTEP23 | Central | Duke Energy Corporation | 23925 | New Slugger 138kV Load | Project Slugger - large new customer load - early phases to be served from 138kV system followed by 345/138kV transformation as load projections increase. | IN | Other | Load Growth | Large new customer load - early phases from 138 kV, then 345/138 kV as load grows | Large Industrial |  |  | 2029-12-31 | 345 |  | 123500000 | DEI $123.5M; ISD 12/31/2029; major new industrial customer
MTEP23 | South | Entergy Mississippi | 23932 | 2024 EML Asset Renewal Program | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. | MS | Other | Age and Condition |  |  |  |  | 2024-12-31 | 500 |  | 50427385
MTEP23 | South | Entergy | 23933 | Sabine 230-138 kV Auto Upgrade | Replace the existing 300 MVA 230-138 kV Sabine Autotransformer with a 500 MVA unit. | TX | Other | Reliability |  |  |  |  | 2026-06-01 | 230 |  | 15500000
MTEP23 | South | Entergy | 23934 | 2024 ELL Asset Renewal Program | This project is for the ELL Asset Renewal Program that will be executed in 2024. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. | LA | Other | Age and Condition |  |  |  |  | 2024-12-31 | 500 |  | 43882621
MTEP23 | West | Otter Tail Power Company | 23936 | OTP Milbank, SD Load Addition | OTP has received a new load request in Milbank, SD. In order to serve this new load a new 115 kV line will be constructed from Big Stone 230/115 kV substation to Milbank, SD where a new 115/12.5 kV substation will be built to offload the existing 41.6 kV system. An additional 115 kV line will be built from the new Milbank, SD substation to a new 115 kV switching station that will be located on the Big Stone - Marietta 115 kV line. The Facilities will consist of the following: 1. Expansion of the Big Stone 115 kV bus to accommodate an additional 115 kV terminal 2. Approximate 12.5 mile 115 kV line from Big Stone 115 kV to a new Milbank 115/12.5 kV substation 3. A new Milbank 115/12.5 kV substation 4. Approximate 15 mile 115 kV line from the new Milbank 115/12.5 kV substation to a new switching station located on the Big Stone - Marietta 115 kV line 5. A new 115 kV switching station on the Big Stone - Marietta 115 kV line | SD | Other | Load Growth | Serve new 4.5 MW load at Milbank SD plus 9.5 MW electric boiler conversion; new 12.5-mi 115 kV line; new Milbank 115/12.5 kV substation | Load Growth + Electrification |  | 9.5 | 2026-12-31 | 115 |  | 32300000 | Milbank: 9.5MW electric boiler, expand Big Stone 115kV (OTP). $32.3M
MTEP23 | South | Entergy | 23937 | Willow Glen 138 kV Reconnect Bus | Construct rigid bus to tie in the Willow Glen 138 kV southwest bus and southeast bus together. | LA | BRP | [5 empty] | 2023-03-10 | 138 |  | 2900000
MTEP23 | South | Entergy | 23938 | Port Hudson - Jackson 69 kV: Switch upgrades | This project is to upgrade switches on the Port Hudson to Jackson 69 kV line to increase the through path rating of the line. | LA | Other | Reliability |  |  |  |  | 2024-12-01 | 69 |  | 3900000
MTEP23 | South | Entergy | 23939 | Blount to Devil Swamp New 69 kV line | Construct new 2.8 mile line from the existing Blount to Devil Swamp 69 kV stations. | LA | Other | Reliability |  |  |  |  | 2025-06-01 | 69 |  | 32300000
MTEP23 | South | Entergy | 23940 | Tiger 69 kV: Bus upgrades | Upgrade the Tiger 69 kV bus tie, including breakers and switches, to increase through path rating. | LA | Other | Reliability |  |  |  |  | 2025-06-01 | 69 |  | 1494000
MTEP23 | South | South Mississippi Electric Power Association | 23941 | Silver Creek Delivery Point | In order to serve the Silver Creek delivery point economically and reliably, service will be established by tapping the Cooperative Energy owned Line 571 115kV line. A 115kV GOAB will be installed at the tap point and a new 115kV tap line will be constructed to the delivery point. | MS | Other | Other Local Needs |  |  |  |  | 2024-06-01 | 115 |  | 2075000
MTEP23 | West | Otter Tail Power Company | 23942 | OTP Gackle - Jamestown 41.6 kV | Reconductor and rebuild sections of the 41.6 kV line between Gackle 41.6 kV and Jamestown 41.6 kV. | ND | Other | Reliability |  |  |  |  | 2024-11-30 | 41.6 |  | 1000000
MTEP23 | West | Otter Tail Power Company | 23943 | OTP Pickert - McVille 41.6 kV | Rebuild portions of the 41.6 kV line between Pickert 41.6 kV and McVille 41.6 kV. | ND | Other | Reliability |  |  |  |  | 2024-11-30 | 41.6 |  | 3800000
MTEP23 | West | Otter Tail Power Company | 23944 | OTP Wabek - Parshall 41.6 kV | Rebuild and Reconductor the 41.6 kV line between Parshall 41.6 kV and Wabek 41.6 kV | ND | Other | Reliability |  |  |  |  | 2027-12-31 | 41.6 |  | 930000
MTEP23 | South | Entergy | 23946 | MTEP23 ELL Capacitor Bank Retirements | Retire the Snakefarm 115 kV and Jaguar 69 kV capacitor banks. | LA | Other | Age and Condition |  |  |  |  | 2023-12-31 | 230
MTEP23 | East | ITC Transmission | 23947 | 2026 ITCT Customer Interconnections | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in service date within the year 2026 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million a separate project will be submitted for approval. | MI | Other | Load Growth |  |  |  |  | 2026-12-31 | 120 |  | 2500000
MTEP23 | East | METC | 23948 | 2025 METC Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | Other | Age and Condition |  |  |  |  | 2025-12-31 | 345 |  | 41750000
MTEP23 | East | METC | 23949 | METC Pole Top Switch Additions/Replacement Program 2025 | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. | MI | Other | Age and Condition |  |  |  |  | 2025-12-31 | 138 |  | 2400000
MTEP23 | East | METC | 23950 | 2023 METC Line Relocation Blanket | Relocation of portions of transmission lines located in public right of way at the government entity's mandate. | MI | Other | Other Local Needs |  |  |  |  | 2023-12-31 | 345 |  | 2400000
MTEP23 | South | Entergy | 23952 | SETEX Area Reliability Project | Construct Babel, a new 500 kV 4 breaker ring substation on the Layfield to Hartburg 500 kV line near the Toledo Bend Reservoir. Install two 70 MVAR Reactors • East of Lewis Creek, construct a 500-230-138 kV Station named Running Bear. • Install a 500-230 kV and 230-138 kV Autotransformer • Cut the Lewis Creek to Peach Creek and Lewis Creek to Porter 230 kV lines into Running Bear 230 kV • Cut the Lewis Creek to Texas, Lewis Creek to Sheawill, and Lewis Creek to Caney Creek 138 kV lines into Running Bear 138 kV. Upgrade Running Bear to Caney Creek 138 kV. • Construct a new ~150-mile 500 kV line from Babel 500 kV to Running Bear 500 kV station. | TX | BRP | [5 empty] | 2030-12-19 | 500 |  | 1111000000
MTEP23 | Central | Duke Energy Corporation | 23953 | Rebuild WVPA Greencastle 69/12kV Substation | Rebuild the existing 69-12.47 kV Greencastle Substation with 69 kV flow-through in another location due to size of site. Replace bank with 14.4 MVA. | IN | Other | Age and Condition |  |  |  |  | 2024-05-31 | 69 |  | 4828000
MTEP23 | West | Otter Tail Power Company | 23955 | OTP Wilton 41.6 kV Breaker Addition | Install a new line sectionalizing 41.6 kV breaker at Wilton, ND. | ND | Other | Reliability |  |  |  |  | 2024-12-31 | 41.6 |  | 250000
MTEP23 | South | Entergy | 23957 | Amite South Reliability Project - Phase 2 | Construct a 14-mile 230 kV line from the Willow Glen substation to the Conway substation. • Station work at both Willow Glen and Conway including additional breakers to accommodate the new line. • Construct a new 500 kV Station near Conway and install a 1200 MVA 500-230 kV Autotransformer. • Build approximately 5 miles of 500 kV to cut the Willow Glen to Waterford 500 kV station into the new Conway 500 kV station. | LA | Other | Reliability |  |  |  |  | 2026-06-30 | 500 |  | 290000000
MTEP23 | South | Entergy | 23960 | 2024 ENOL Asset Renewal Program | This project is for the ENOL Asset Renewal Program that will be executed in 2024. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2024 asset renewal plans have not yet been finalized. | LA | Other | Age and Condition |  |  |  |  | 2024-12-31 | 230 |  | 2190124
MTEP23 | Central | Duke Energy Corporation | 23962 | Rebuild 6958 Line 69 kV for FAA | 6958 Line Rbld as required by FAA - Rebuild 39 Structures and replace conductor from HE Whitehall to structure 815-1069-01. Replace individual poles 815-1060 and 815-1061. Install monitored FAA warning lights on 37 of the poles. Install 36 marker balls on the static wire. | IN | Other | Reliability |  |  |  |  | 2025-06-01 | 69 |  | 3385000
MTEP23 | Central | Duke Energy Corporation | 23963 | Rebuild 6932 Potato Crk to Thorntown 69 kV | 6932 Rebuild Potato Crk to Manson Jct to Clarks Hill to Thorntown with 954ACSR conductor | IN | GIP | [5 empty] | 2024-05-17 | 69 |  | 41811862
MTEP23 | Central | Duke Energy Corporation | 23964 | New Kokomo Fusion Phase 1 - 230/69 kV Sub | Kokomo Project Fusion Phase 1 - 110MW new load: new 230/69kV substation inserted in the 23022 ckt. with breaker and 1/2 layout (between Greentown and Kokomo Webster St.); (2) 150MVA -230/69kV transformers; (14) 69kV breakers in a breaker and 1/2 layout; loop 69172 ckt. (between Kokomo East and Kokomo Chrysler North) through new sub; also loop the 69174 ckt. (between Kokomo Touby Pike Tap 1 and Chrysler North Jct.); (3) 60MVA - 69/34.5kV transformers; As of 9/14/23: Customer has Phase 2 plans to increase the load here: scope/cost increase in Phase 1 to partially prepare for Phase 2 (MTEP24 project - 155MWs load addition) - includes 2nd 230/69kV transformer in parallel at existing Kokomo Webster St. | IN | Other | Load Growth | Kokomo Project Fusion - new 230/69 kV substation for large new customer load; (2) 150MVA 230/69 kV transformers, (14) 69 kV breakers | Large Industrial (Stellantis/EV) |  | 110 | 2025-06-01 | 230 |  | 92073454 | DEI $92.1M; ISD 6/1/2025; likely Stellantis EV manufacturing
MTEP23 | Central | Duke Energy Corporation | 23965 | Replace 13832 Line Structure 138 kV | Replace 14 structures in the 13832 line: 849-2103 thru 2106, and 849-2113 thru 2122 | IN | Other | Age and Condition |  |  |  |  | 2024-05-01 | 138 |  | 2566706
MTEP23 | Central | Duke Energy Corporation | 23966 | Reconfigure Greensburg 138kV Ring Bus | Greensburg 138kV expand sub and reconfigure to (4) breaker ring bus | IN | Other | Reliability |  |  |  |  | 2023-06-01 | 138 |  | 5884000
MTEP23 | Central | Duke Energy Corporation | 23967 | J1295 Gibson Solar | J1295 Gibson Solar farm 280MW +/- w/ 345kV POI between Gibson and Francisco in ckt. 34516 (3-breaker ring); Includes required relay work at Gibson | IN | GIP | [5 empty] | 2024-06-01 | 345 |  | 17700000
MTEP23 | Central | Duke Energy Corporation | 23968 | New Greensfork East 69/12kV Sub | Greensfork East new 69/12kV - 22.4MVA Sub: looped-through feed from 69100 ckt. | IN | Other | Load Growth |  |  |  | 4 MVA | 2028-08-08 | 69 |  | 1440000
MTEP23 | Central | Duke Energy Corporation | 23969 | New Williamsport 69/12kV Sub | Williamsport new 69/12kV - 22.4MVA sub: looped-through feed from the 6936 ckt. | IN | Other | Load Growth |  |  |  | 4 MVA | 2026-10-02 | 69 |  | 3152000
MTEP23 | Central | Duke Energy Corporation | 23970 | Rebuild 69100 Greensfork to HE Jacksonburg Jct 69kV | Rebuild 69100 from Greensfork #1 switch (pole #862-3176) to Jacksonburg Jct switch (pole #862-3074) using light duty steel poles, 477ACSR and OPGW | IN | Other | Reliability |  |  |  |  | 2025-10-09 | 69 |  | 10800000
MTEP23 | Central | Ameren Services Company | 23971 | Upgrade Effingham NW-Neoga 138 kV line | Upgrade terminal equipment at Hannibal West, replace two structures and shunts in Neoga – Effingham NW 138 kV line. These are Non-SSR related needs. | MO | Other | Reliability |  |  |  |  | 2024-12-01 | 138 |  | 1750000
MTEP23 | East | ITC Transmission | 23976 | ITCT Pole Top Switch Additions/Replacement Program 2025 | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. | MI | Other | Reliability |  |  |  |  | 2025-12-31 | 120 |  | 2400000
MTEP23 | West | Otter Tail Power Company | 23977 | OTP Cooperstown 41.6 kV | Reroute and rebuild 5 miles of 41.6 kV line near Cooperstown 41.6 kV. | ND | Other | Reliability |  |  |  |  | 2024-11-30 | 41.6 |  | 1150000
MTEP23 | Central | Duke Energy Corporation | 23978 | New Bargersville North 69kV Switching Station | Build new Bargersville North 69kV three breaker ring bus switching station in the 69102 line | IN | Other | Reliability |  |  |  |  | 2025-12-31 | 69 |  | 11659302
MTEP23 | Central | Duke Energy Corporation | 23979 | New Trafalgar 69 kV Ring Bus | Convert the existing Trafalgar 69 kV switching station to a three breaker ring bus | IN | Other | Reliability |  |  |  |  | 2026-03-03 | 69 |  | 9980000
MTEP23 | Central | Duke Energy Corporation | 23980 | New Glenwood West 10.5MVA 69/12kV Sub | Glenwood West (new) - Install 10.5MVA, 69-12kV non-LTC transformer; build/re-route the existing 6920 line to loop through the new substation with ATO/TLS switches | IN | Other | Reliability |  |  |  |  | 2023-12-29 | 69 |  | 1400000
MTEP23 | Central | Duke Energy Corporation | 23981 | New Saint Paul Northwest 10.5MVA 69/12kV Sub | Saint Paul Northwest (new) - Install 10.5MVA, 69-12kV non-LTC transformer; build/re-route the existing 6937 line to loop through the new substation with ATO/TLS switches | IN | Other | Reliability |  |  |  |  | 2025-11-06 | 69 |  | 1377000
MTEP23 | Central | Ameren Services Company | 23982 | New Newton Solar Interconnection (J1198) | Install one 345 kV terminal in the Newton substation. The terminal will consist of all necessary terminal equipment to connect the J1198 leadline. | IL | GIP | [5 empty] | 2025-12-01 | 345 |  | 1500000
MTEP23 | Central | Ameren Services Company | 23983 | New Bison 345 kV Substation for J1289 Lotus Wind E&P | A 200 MW wind project interconnecting the Ameren Illinois system along the Turner - Austin 345 kV line. | IL | GIP | [5 empty] | 2024-11-01 | 345 |  | 12000000
MTEP23 | West | Cedar Falls Utilities | 23993 | Streeter-Wida Rebuild | Rebuild of the eastern half of CFU's part of the Streeter Switch Substation to MEC's WIDA substation. This will include reconductor and structures. | IA | Other | Load Growth |  |  |  |  | 2024-04-01 | 69 |  | 2000000
MTEP23 | Central | Northern Indiana Public Service Company | 24032 | Upgrade J1482 Network 138kV | 138kV substation and line work to connect J1482 to Springboro to Monticello 138kV line | IN | GIP | [5 empty] | 2024-05-01 | 138 |  | 17892294
MTEP23 | South | Cleco Power LLC | 24033 | J1286 Manuel Expansion | Expand Manuel Substation for the interconnection of J1286 Generation Plant | LA | GIP | [5 empty] | 2025-04-01 | 138 |  | 2831239
MTEP23 | Central | Ameren Services Company | 24052 | New Nile 138 kV Substation for J1208-J1209 Chariot Solar I & ll | A 160 MW solar project connecting to a new switching station in Saline County, Illinois. | IL | GIP | [5 empty] | 2025-12-01 | 138 |  | 9250000
MTEP23 | South | Entergy | 24053 | J1431 Interconnection Project at Vacherie 230 kV | Facilities required for the interconnection of J1431 at the existing Vacherie 230 kV substation. | LA | GIP | [5 empty] | 2024-05-01 | 230 |  | 1420000
MTEP23 | East | ITC Transmission | 24072 | Resource Equipment Removal and Bypass | Remove ITC assets at Resource substation. Bypass Resource substation to form a direct Alfred to Frisbie 120 kV circuit. | MI | Other | Reliability |  |  |  |  | 2026-12-31 | 120 |  | 3530000
MTEP23 | West | Montana-Dakota Utilities Company | 24092 | Baker upgrades MP funded | Market Funded project to upgrade terminal equipment at Baker. | ND | MPFP | [5 empty] | 2023-12-31 | 230 |  | 50000
MTEP23 | West | American Transmission Co. LLC | 24093 | Rocky Run SS T2 and T4 Power Transformer Replacement | Planning Scope: o Remove Rocky Run 345/115kV transformers T2 and T4. Replace with on-site spare 500MVA 345/115kV transformer in the T4 position. o Upgrade two (2) 345kV bus switches and five (5) 115kV bus switches. o Remove breaker 4-2 and shorten 345kV ring bus. o Purchase new 500MVA 345/115kV system spare. Asset Renewal Scope: o Replace W-8 secondary relay SEL-321 (component replacement). o Replace all physical security cameras. | WI | BRP | [5 empty] | 2027-06-01 | 345 |  | 17600000
MTEP23 | South | Entergy | 24094 | J1463 Interconnection: Bueche 230 kV Station | This project is to support the interconnection of solar project J1463 at the new Bueche 230 kV station on the 230 kV line 731 (Addis to Big Cajun). | LA | GIP | [5 empty] | 2023-11-01 | 230 |  | 128000
MTEP23 | South | Cleco Power LLC | 24112 | J1205 Perkins Substation | Tap the existing Centennial to West Bay 138 kV line and build a new Perkins Substation. J1205 Generation Plant will interconnect to this substation. | LA | GIP | [5 empty] | 2023-10-31 | 138 |  | 2607000
MTEP23 | South | Cleco Power LLC | 24113 | J1424 Singer Substation | Tap the existing Cooper to Penton 230 kV line and add Singer Substation. This substation is needed for J1424's generation interconnection. | LA | GIP | [5 empty] | 2024-09-15 | 230 |  | 2967565
MTEP23 | South | Cleco Power LLC | 24114 | J1367 Caneland Expansion | Expand Caneland 230 kV substation for the interconnection of J1367 Generation Plant | LA | GIP | [5 empty] | 2024-09-29 | 230 |  | 5163000
MTEP23 | East | ITC Transmission | 24115 | Mack - Northeast 120kV UG Cable Relocation | Relocation and replacement of 1230 ft. of 1500kcmil CU cable with 2100 ft. of 2500kmil CU cable of the Mack-Northeast 120 kV circuit to accommodate future interstate infrastructure improvements directed by the Michigan Department of Transportation (MDOT). | MI | Other | Other Local Needs |  |  |  |  | 2024-06-03 | 120 |  | 5540000
MTEP23 | Central | Ameren Services Company | 24133 | J1360 Goose Creek Wind PGIA | A 300 MW wind project connecting at the existing Goose Creek substation in McLean County, IL. Install Gas circuit breaker and relocate Rising Line terminal. Reterminate the Goose Creek-Rising 345 kV transmission line to provide a position for J1360 | IL | GIP | [5 empty] | 2024-06-01 | 345 |  | 4200000
MTEP23 | South | Entergy | 24134 | Mustang 138 kV New Customer Substation | Entergy is proposing to construct a new 138 kV substation called Mustang, which will serve an industrial customer’s 150 MW of new load near Orange, TX. The new Mustang 138 kV station is being laid out as a four bay breaker and a half station with twelve breakers initially installed and cut in on the existing Orange to Bunch Gully 138 kV circuit. | TX | Other | Load Growth |  |  |  | 150 | 2024-10-30 | 138 |  | 28000000
MTEP23 | South | Entergy | 24152 | Moscow 138 kV Customer Load Addition Project | Entergy is proposing to construct new 138 kV transmission facilities at the existing Moscow 138 kV substation which will serve an existing industrial customers new load. The proposed new facilities include installing two 138 kV breakers at the Moscow substation and a new capacitor bank. | TX | Other | Load Growth |  |  |  |  | 2023-06-30 | 138 |  | 10470000
MTEP23 | Central | Henderson Municipal Power & Light | 24172 | Re-route HMPL Sub 4 to HMPL Sub 4 Tap 161 kV Transmission Line | HMPL plans to reroute the HMPL Sub 4 to HMPL Sub 4 Tap 161 kV transmission line due to Big Rivers Electric Corporation (BREC) Pratt Paper transmission project (MISO Project ID 21685). | KY | Other | Reliability |  |  |  |  | 2023-07-01 | 161 |  | 155000
MTEP23 | South | Arkansas Electric Coopertive Corporation | 24192 | UIG | NUCOR is expanding their operations by adding to two locations manufacturing facilities to produce liquid products for both their operations and the market. AECC and Mississippi County Electric will be building out the AECC Barfield substation by adding a new 25 MVA; 161/13.8 kV transformer to support 20 MW of new load. AECC and Mississippi County Electric will also be building out the AECC Hickman North substation by adding a new 40 MVA; 161/13.8 kV transformer to support 30 MW of new load. This project will be submitted as an Expedited Process project. This project should be in MTEP23. | AR | Other | Load Growth |  |  |  | 20 | 2025-04-01 | 0
MTEP23 | West | MidAmerican Energy Company | 24212 | Badger Creek Substation | Construct Badger Creek Substation that will bisect the existing Arbor Hill-Raccoon Trail 345 kV line. Construct a new 345 kV line from Badger Creek Substation to the Raccoon Trail Substation. | IA | Other | Other Local Needs |  |  |  |  | 2025-12-01 | 345
MTEP23 | West | Missouri River Energy Services (MRET) | 24232 | ALP SE Substation | Alexandria Light & and Power (ALP) will build a new distribution substation on the southeast part of town. The substation will tap and existing 115 kV line with an in and out substation. The substation will have a 115 kV to distribution transformer. | MN | Other | Load Growth |  |  |  |  | 2025-12-31 | 115 |  | 1358000
MTEP23 | South | Entergy | 24252 | MPFCA J1246, J1367, J1465: Install 2nd Bayou Labutte 500-230 kV Autotransformer and Construct New Wise to Bayou Labutte 230 kV Line | Install 2nd 500-230 kV Autotransformer at Bayou Labutte 500 kV, including all associated station and relay work. Construct new Wise to Bayou Labutte 230 kV line, including all associated station and relay work. | LA | GIP | [5 empty] | 2025-09-20 | 500 |  | 45202000
MTEP23 | South | Entergy | 24253 | MPFCA J1246, J1421, J1463: Willow Glen 230 kV Breaker Replacements | Replace sixteen 230 kV breakers at Willow Glen 230 kV station with IPO circuit breakers rated at 80 kA. | LA | GIP | [5 empty] | 2025-08-09 | 230 |  | 16510000
MTEP23 | South | Entergy | 24254 | J1465 138 kV Interconnection Station | This project is to support the interconnection of J1465 on 138 kV line between existing Livonia and Colonial Springs stations. | LA | GIP | [5 empty] | 2025-06-01 | 138 |  | 14400000
MTEP23 | South | Entergy | 24272 | J1421 230 kV Interconnection Project | This project is to support the interconnection of solar project J1421 at a new station cut in between Colfel and Moler 230 kV stations. Convert Moler 230 kV into a four breaker ring bus. Upgrade the Coly to Moler 230 kV line as identified during the MISO DPP cycle. | LA | GIP | [5 empty] | 2026-03-01 | 230 |  | 32259000
MTEP23 | Central | Indianapolis Power & Light Company | 24273 | New - 138kV - Airtech Substation | New 138kV, two 20 MVA transformer, three-breaker substation | IN | Other | Load Growth |  |  |  | 20 MVA | 2026-12-31 | 138 |  | 10700000
MTEP23 | East | METC | 24275 | Morocco - J1226 GIA NU | Install two 345 kV breakers rated at 40 kA and associated disconnect switches to complete row 36 in Morocco Substation. Install one 345 kV breaker rated at 40 kA and associated disconnect switch to complete row 34 in Morocco Substation. | MI | GIP | [5 empty] | 2024-06-06 | 345 |  | 4260888
MTEP23 | East | METC | 24276 | Vergennes - Marquette - J1255 GIA (Hawley) NU | J1255 is a 200MW solar project connecting in Keene Township on the Vergennes - Marquette 138kV. Build the J1255Interconnection 138kV station as a breaker and half station with three 40kA breakers in a ring bus configuration. Extend the Marquette - Vergennes 138kV line to loop in the station. Connect the generators at position WM12 as TOIF. Generators are part of the DPP 2019 Cycle 1. | MI | GIP | [5 empty] | 2025-12-31 | 138 |  | 6939380
MTEP23 | East | METC | 24277 | Gaines - Thompson Road 138kV - J1292 GIA (Peddler) NU | Build a new 138 kV 3 breaker ring substation cut in from the Gaines - Thompson Road 138kV line. | MI | GIP | [5 empty] | 2025-12-31 | 138 |  | 6934580
MTEP23 | West | Northern States Power (Xcel Energy) | 24278 | Edina Switch Replacement | Project will replace 115kV switch at Edina, which is limiting the rating of the Edina - St. Louis Park 115kV line. | MN | BRP | [5 empty] | 2023-12-31 | 115 |  | 135000
MTEP23 | East | METC | 24279 | Claremont - Cornell #2 - J1297 GIA (Hathon) NU | J1297 is a 170MW solar project interconnecting in Venice Township, Shiawassee, MI. METC will need to build a new 138kV breaker and half station with three 40kA breakers. METC will need to extend the Claremont - Cornell #2 138kV line 0.1 miles to loop in the J1297 Interconnection station for transmission service. Loop in the Cornell - Goss 138kV line to mitigate anti - islanding at Bell Road. J1297 is queued within the DPP 2019 Cycle 1. | MI | GIP | [5 empty] | 2026-01-28 | 138 |  | 18106637
MTEP23 | East | ITC Transmission | 24280 | Greenwood - J1331 GIA NU | Add row P and install two 120 kV breakers rated at 40 kA and four disconnect switches at Greenwood Substation. | MI | GIP | [5 empty] | 2025-02-28 | 120 |  | 2881189
MTEP23 | East | METC | 24282 | Leoni - Parr Road - J1472 GIA(Vargo) NU | J1472 is a generation interconnection request for 100 MW Solar Power Plant proposing to connect to the METC Leoni – Parr Road 138kV Line. J1472 is queued within the DPP 2019 Cycle 1. | MI | GIP | [5 empty] | 2025-03-31 | 138 |  | 7130467
MTEP23 | West | Great River Energy | 24285 | Benton County Solar Farm | The existing 115kV Benton County substation is built as a two row breaker-and-a-half breaker station. A new breaker and a half row would be built out to accommodate the interconnection of the 100 MW solar farm for J1426. The network upgrades at the substation will include the installation of a new 115kV Breaker, Line arrestors, line CCVTs, Primary/Secondary Relay Panels, Metering, new metering CTs, and disconnects in the breaker-and-a-half row. | MN | GIP | [5 empty] | 2025-08-01 | 115 |  | 2386979
MTEP23 | Central | Indianapolis Power & Light Company | 24293 | New - 138 kV - New Pleasant Acres Substation | New 138 kV, two 22.4 MVA transformers, 3 breaker, straight bus substation to serve WVPA load | IN | Other | Load Growth |  |  |  | 4 MVA | 2025-12-31 | 138 |  | 10000000
MTEP23 | East | METC | 24294 | Mio Dam - Twining - J1210 GIA (Quarry) - NU | Construct new Quarry 138 kV station. Install five 138 kV breakers rated at 40 kA, associated disconnects, and two new bus sections. Loop in the Mio Dam – Twining circuit to the new Quarry station. Loop in the Iosco – Karn circuit to the new Quarry station. Remove Twining 177 sparing and install approximately 4.3 miles of fiber on the Quarry – Twining circuit. | MI | GIP | [5 empty] | 2025-03-31 | 345 |  | 11049936
MTEP23 | East | METC | 24295 | Marshall - Blackstone (Stable) - J1248 GIA (Bearcat) NU | J1248 is a 100.9MW solar farm connecting on the Marshal - Stable 138kv line in Calhoun County, MI. Construct J1248 as a breaker and half station with three 40kA breakers in a ring bus configuration. Construct BM14 as a TOIF to connect J1248. Generator is part of the DPP 2019 Cycle 1. | MI | GIP | [5 empty] | 2025-11-30 | 138 |  | 9711426
MTEP23 | West | American Transmission Co. LLC | 24296 | Valders SS, New 138/69 kV Substation | Construct a new 138/69 kV Valders Substation with 100 MVA transformer looping in Forest Junction - Howards Grove 138 kV (971K51) and Custer - St Nazianz - New Holstein 69 kV (P-68) lines. | WI | Other | Reliability |  |  |  |  | 2028-07-31 | 138 |  | 24200000
MTEP23 | South | Entergy | 24298 | J1442 Interconnection Project on Livingston to Rich 138 kV line | This project is to construct the interconnection station for the solar project J1442 on the Livingston to Rich 138 kV line. | TX | GIP | [5 empty] | 2025-05-01 | 138 |  | 15590000
MTEP23 | East | ITC Transmission | 24299 | J1196 Generator Interconnection TOIF | Install required entrance structures and 345 kV disconnect switch at the new Wedge station. | MI | GIP | [5 empty] | 2025-03-31 | 345
MTEP23 | East | METC | 24300 | J1320 Generator Interconnection TOIF | Install required line entrance structures and 138 kV disconnect at new Byers switching station. | MI | GIP | [5 empty] | 2025-12-10 | 138
MTEP23 | East | METC | 24301 | Leoni - Parr Road - J1472 GIA(Vargo) TOIF | Install a line entrance structure and a switch for the generator to connect at position WM13. | MI | GIP | [5 empty] | 2024-11-29 | 138
MTEP23 | East | ITC Transmission | 24313 | Greenwood-Rapson(Banner)-J1196 GIA(Wedge) NU | Construct new Wedge 345 kV station. Install three 345 kV breakers rated at 40 kA with associated disconnects and two new bus sections. Cut the ITCT Greenwood – Rapson (Banner) 345 kV circuit into the new Wedge station. | MI | GIP | [5 empty] | 2025-03-31 | 345 |  | 12620784
MTEP23 | East | METC | 24314 | Thetford-J1203 GIA NU | Install three 345 kV breakers rated at 40 kA and associated disconnect switches and complete row 29 in the METC Thetford Substation. | MI | GIP | [5 empty] | 2025-05-05 | 345 |  | 4245703
MTEP23 | West | Northern States Power (Xcel Energy) | 24315 | Dubay Lake Substation | Install new 115/34.5kV substation in the Dayton area to meet area load growth. | MN | Other | Load Growth |  |  |  |  | 2025-06-16 | 115 |  | 12400000
MTEP23 | East | METC | 24317 | DuPont - Cobb - J1375 GIA (Lamos) NU | Construct the new Lamos 138 kV station. Extend the White Lake – DuPont – Cobb 138 kV line to loop in the new Lamos 138 kV station. Install three 138 kV breakers rated at 40 kA and two new bus sections at the new Lamos station. Loop the White Lake – Du Pont – Cobb 138 kV line into the White Lake 138 kV station. Install approximately 3.1 miles of fiber from White Lake to Lamos Switching Station. Implement anti-islanding protection for identified islanding scenarios. Replace an existing bus at White Lake Substation. Install new bus and 500 tie-breaker with associated disconnects at White Lake Substation. Install 677 and 777 breakers with associated disconnects at White Lake Substation. Cut White Lake – Cobb circuit and reconnect to the new bus at White Lake. | MI | GIP | [5 empty] | 2025-05-12 | 138 |  | 14998507
MTEP23 | East | METC | 24318 | Eureka - Vestaburg - J1379 GIA NU | Install a new 138kV switching station. Install four 138kV breakers rated at 40kA and two bus sections. Cut the METC Eureka - Vestaburg 138 kV circuit into the new 138 kV switching station. Rebuild the METC Eureka - Vestaburg 138 kV line from Deja to Eureka. Rebuild the METC Eureka - North Belding 138 kV line. Add a new 138 kV line from the new switching station to North Belding. | MI | GIP | [5 empty] | 2024-05-31 | 138 |  | 50088736
MTEP23 | East | METC | 24319 | Delhi-Thompkins #2 J1399 (Edgar) NU | J1399 Interconnection is a 90MW solar project in Lesli Township, MI. Build the J1399 Interconnection station as a breaker and half station with three 40kA breakers in a ring bus configuration. Extend the Delhi – Tompkins 138kV line to loop in the J1399 Interconnection station. J1399 is queued within the DPP 2019 Cycle 1. | MI | GIP | [5 empty] | 2025-12-31 | 138 |  | 10010107
MTEP23 | East | ITC Transmission | 24333 | Majestic-Milan - J1224 & J1329 GIA (Neblo) NU | Build a new 345 kV 3 Breaker ring substation cut in from the Majestic-Milan 345kV line. System changes will require relay upgrades at Majestic 345 kV and Milan 345 kV stations. | MI | GIP | [5 empty] | 2025-12-29 | 345 |  | 13156394
MTEP23 | West | American Transmission Co. LLC | 24373 | Manogue Rd SS DIC, New Substation | New tapped substation to serve 4.3 MVA motor load between the existing Edgerton Business Park and Russell substations on the 138 kV Line X-31. Line breakers will be installed at the Edgerton Business Park Substation on the Rockdale-Edgerton Business Park-ANR Manogue Rd-Russell 138kV (X-31) line due to high network flow. | WI | Other | Load Growth |  |  |  | 3 MVA | 2025-08-01 | 138 |  | 7100000
MTEP23 | West | Northern States Power (Xcel Energy) | 24374 | Steep Bank Lake Line Swap | Move J460 Steep Bank Lake interconnection to new 345kV second circuit being built between Brookings County - Lyon County (MTEP ID 23452). | MN | Other | Reliability |  |  |  |  | 2025-09-02 | 345 |  | 300000
MTEP23 | East | ITC Transmission | 24376 | Majestic-Milan - J1224 & J1329 GIA (Neblo) TOIF | Install a line entrance structure and switch for the generator to connect to position CQ at the Neblo (J1224&J1329) 345 kV station. | MI | GIP | [5 empty] | 2025-12-29 | 345
MTEP23 | East | METC | 24377 | Coldwater - Byers Rebuild (J1320) - Network Upgrade | Rebuild entire J1320 - Coldwater 138 kV line with OPGW. Replace existing 336 and 477 ACSR conductor with 954 ACSR. | MI | GIP | [5 empty] | 2024-12-23 | 138 |  | 7296394
MTEP23 | East | ITC Transmission | 24393 | MDOT I-375 Construction - Underground Cable Relocation | Relocate a portion of the Alfred-St. Antoine and Esset-St. Antoine 120 kV underground cables currently located in the Larned I-375 bridge to accommodate the reconstruction of I-375 in downtown Detroit as directed by the Michigan Department of Transportation (MDOT). | MI | Other | Other Local Needs |  |  |  |  | 2024-12-31 | 120 |  | 8200000
MTEP23 | East | METC | 24395 | Luce - Summerton Line Reconductor (J1379) - Network Upgrade | Reconductor the entire ~10.5 mile-long Luce – Summerton 138 kV line with OPGW. Replace the existing 336 ACSR conductor with new 795 ACSS conductor. Replace any structures as necessary. | MI | GIP | [5 empty] | 2025-11-26 | 138 |  | 9682800
MTEP23 | East | METC | 24396 | J1210 Generator Interconnection TOIF | Install required line entrance structures and 138 kV disconnect switch at the new Quarry station. | MI | GIP | [5 empty] | 2025-03-31 | 138
MTEP23 | East | Wolverine Power Supply Cooperative, Inc. | 24414 | WPSC Elephant Interconnection (Project 23865 Partial Alternative) | CE has requested a new 103 MW (expanding to 206 MW) Industrial interconnection near METC's Mecosta substation. To accommodate this request, METC would install a new, 3-row, 138 kV substation near the customer site, and loop the existing Chase-Mecosta 138 kV line approx. 1.5 miles into the new substation. A 138 kV, 54 MVAR cap bank would be installed at the new substation. METC would also rebuild the entire Chase-Mecosta 138 kV circuit (approx. 17.6 miles). Wolverine's portion of the project will be to will cut in the Hersey to White Cloud by building 4 miles of double circuit 138kV on new ROW. | MI | Other | Other Local Needs |  | Large Industrial |  | 103-206 | 2025-03-01 | 138 |  | 6000000 | 103MW expanding to 206MW industrial near Mecosta (Consumers Energy/METC)
MTEP23 | South | Cleco Power LLC | 24415 | Ragely Substation | Tap the existing 138 kV line between Nelson and Longville 11.3 miles from Longville. At this location build a new 138 kV Substation Turps. Build a new 6.1 mile 138 kV line from Turps to a new substation Ragley. This project will also add a 14 MVAR cap bank at Ragley. | LA | Other | Load Growth |  |  |  |  | 2024-07-17 | 138 |  | 40000000
MTEP23 | South | Cleco Power LLC | 24416 | Rosepine Substation | Build a new 230 kV substation Rosepine tapped into the existing Leesville to Cooper 138 kV line 11.5 miles from Leesville. Build a new 230 kV line 3.4 miles from Rosepine to Deridder. This substation and line will be energized at 138 kV. | LA | BRP | [5 empty] | 2027-07-15 | 138 |  | 35585000
MTEP23 | East | ITC Transmission | 24417 | J1350 Generator Interconnection Network Upgrades | Build a new 345 kV 3 Breaker ring substation and cut in the Milan - Lulu 345kV 345 kV line. System changes will require relay upgrades at Milan 345kV station. | MI | GIP | [5 empty] | 2025-05-16 | 345 |  | 13376550
MTEP23 | East | ITC Transmission | 24418 | J1350 Generator Interconnection TOIF | Install a line entrance structure and a switch for the generator to connect at position CI. | MI | GIP | [5 empty] | 2025-05-16 | 345
MTEP23 | East | METC | 24419 | J1320 Generator Interconnection Network Upgrades | Construct new Byers switching station. Install three 138 kV breakers rated at 40 kA and two new bus sections. Loop in the Batavia – Coldwater circuit to the new Byers station. Remove existing X and Z phase wave traps and tuners at Batavia and Coldwater. Install approximately 6 miles of fiber from Byers Switching Station to Batavia and approximately 2 miles of fiber from Byers Switching Station to Coldwater. | MI | GIP | [5 empty] | 2025-12-10 | 138 |  | 14607533
MTEP23 | East | METC | 24420 | Cobb - Peterson Tap Sag Remediation (J1375) - Network Upgrade | Remediate the sag on the 336 ACSR conductor on the Cobb - Peterson Tap 138 kV line section to meet or exceed a rating of 125 MVA Summer Emergency. | MI | GIP | [5 empty] | 2024-12-23 | 138 |  | 418800
MTEP23 | East | METC | 24433 | Vergennes - Marquette - J1255 GIA (Hawley) TOIF | Install WM14 line position and disconnect at the Hawley station to interconnect J1255 generation. | MI | GIP | [5 empty] | 2025-12-31 | 138
MTEP23 | East | METC | 24434 | J1203 Generator Interconnection TOIF | Install required entrance structures and 345 kV disconnect switch at METC Thetford Substation. | MI | GIP | [5 empty] | 2025-05-05 | 345
MTEP23 | East | METC | 24435 | J1226 Generator Interconnection TOIF | Install required entrance structures and 345 kV disconnect switch at Morocco station. | MI | GIP | [5 empty] | 2024-06-06 | 345
MTEP23 | East | METC | 24436 | J1375 Generator Interconnection TOIF | Install required line entrance structures and 138 kV disconnect at new Lamos station. | MI | GIP | [5 empty] | 2025-05-12 | 138
MTEP23 | East | METC | 24437 | Delhi-Thompkins #2 J1399 (Edgar) TOIF | Install a line entrance structure and a switch for the generator to connect at position BM14. | MI | GIP | [5 empty] | 2025-12-31 | 138
MTEP23 | East | METC | 24438 | J1401 Generator Interconnection Network Upgrades | Install one 138 kV breaker rated at 40 kA and associated disconnects. | MI | GIP | [5 empty] | 2024-04-05 | 138 |  | 1053802
MTEP23 | East | METC | 24439 | J1401 Generator Interconnection TOIF | Install a line entrance and 138 kV disconnect switch at Wagner Station. | MI | GIP | [5 empty] | 2024-04-05 | 138
MTEP23 | East | ITC Transmission | 24441 | J1331 Generator Interconnection TOIF | Install required entrance structures and 120 kV disconnect switch at Greenwood Substation. | MI | GIP | [5 empty] | 2025-02-28 | 120
MTEP23 | West | American Transmission Co. LLC | 24445 | J1374 Ebenezer SS Network Upgrades and Interconnection Facilities | Wind Turbine generating Facility located in Grant County, Wisconsin. | WI | GIP | [5 empty] | 2024-08-01 | 138 |  | 1577013
MTEP23 | West | American Transmission Co. LLC | 24446 | J1251 Summer Meadow Switching Station Network Upgrades and Interconnection Facilities | A 100 MW solar farm located in Marquette County, Michigan. | MI | GIP | [5 empty] | 2025-06-12 | 345 |  | 8002656
MTEP23 | West | American Transmission Co. LLC | 24447 | J1483 Hill Valley SS Network Upgrades and Interconnection Facilities | Wind farm in Iowa County, Wisconsin. | WI | GIP | [5 empty] | 2026-09-01 | 345 |  | 2252888
MTEP23 | East | METC | 24448 | Murphy-Styx - J1389 Generator Interconnection - Network Upgrades | Build a new 345 kV 3 Breaker ring substation (Palomino) cut in from the Murphy - Styx (J984) 345 kV line. | MI | GIP | [5 empty] | 2025-10-31 | 345 |  | 12375600
MTEP23 | West | ITC Midwest | 24449 | Nevada Area Load Interconnections | IPL has requested a new substation interconnection in the Ames/Nevada area for a new load in their Prairie View Industrial Center. As part of this request, ITC Midwest will be building a new 3 row 161 kV breaker and ½ substation with 4 line positions and 2 transformer positions initially, with the ability to add 3 additional rows in the future for additional transformer positions as well as additional line positions. The new Prairie View Industrial Center substation will be PD and the common facilities will be owned by IPL. ITC will build a new 161 kV line from Prairie View Industrial Center substation to the ITC Ames substation, approximately 5 miles in length, to support the load additions/growth in this area. The existing Ames 161 kV bus will be required to be rebuilt to a ring bus to accommodate the new 161 kV line position for the line to Prairie View Industrial Center substation. IPL has also requested to interconnect a new substation/load directly south of the existing Nevada Lincoln Highway Industrial Substation. ITC will be building a new 4 position ring bus substation (expandable to future 4 row breaker and ½) named “Teller” to serve this load. There is a possibility to connect this substation to Lincoln Highway Industrial in the future to convert that from 69 kV to 161 kV. ITC will also be building a new approximately 2.5 mile 161 kV line from the Prairie View Industrial Center substation to the Teller Substation, and a new approximately 8 mile 161 kV line from the Fernald substation to the Teller Substation. ITC will also need to add an additional 161 kV line terminal at the Fernald 161 kV substation by adding an additional 161 kV breaker to the existing ring bus. In addition, the Prairie View Industrial Center Substation will interconnect to the existing City of Ames 161 kV line that runs the Ames Plant and NE Ankeny substations, providing 4 161 kV lines into the Prairie View Industrial Center substation initially, with the ability to add a 2nd line to the City of Ames Plant substation in the future. | IA | Other | Load Growth | New transmission substations networked to existing 161 kV at Ames, NE Ankeny, Fernald; load interconnections in Ames/Nevada area | Area Load Growth |  |  | 2024-12-31 | 161 |  | 56519142.5 | ITCM $56.5M; major load interconnection
MTEP23 | East | METC | 24453 | Hawley-Peddler - New Circuit #1 and #2 (J1255, J1292) - Common Use Network Upgrade | Install two breakers at positions 8B7 and 8W8 at J1292, and two breakers at positions at positions 8W8 and 10B7. Install about 15 miles of 954 ACSR DCT in new Right of Way to connect J1292 Interconnection Station to J1255 Interconnection Station. | MI | GIP | [5 empty] | 2025-12-31 | 138 |  | 27716208
MTEP23 | East | METC | 24454 | Leoni - Lark 138 kV Sag Remediation (J1310, J1472) - Network Upgrade | Remediate the sag on the 477 ACSR conductor on the Leoni – Washtenaw Tap 138 kV segment to meet or exceed a summer emergency rating of 179 MVA. | MI | GIP | [5 empty] | 2024-04-05 | 138 |  | 660000
MTEP23 | East | METC | 24455 | Verona - Mud Lake #1 Rebuild (J1248, J1310, J1430) - Network Upgrade | Replace existing 336 ACSR conductor on the Verona – Mud Lake #1 138 kV line with 954 ACSR including one 48 count OPGW ~ 3.6 Miles. Any new 138kV towers should be expandable to double circuit in the future. | MI | GIP | [5 empty] | 2024-12-23 | 138 |  | 8770564
MTEP23 | East | METC | 24456 | Marshall - Blackstone (Stable) - J1248 GIA (Bearcat) TOIF | Stable - Install a line entrance structure and switch for the generator to connect at position WM14. | MI | GIP | [5 empty] | 2025-11-30 | 138
MTEP23 | West | Otter Tail Power Company | 24457 | OTP Bagley Jct. 115 kV Capacitor Addition | Expand the Bagley Jct. 115 kV switching station to allow for the installation of a single step 20 MVAR 115 kV capacitor bank. The project will consist of the addition of two 115 kV breakers, three disconnect switches, a single 20 MVAR 115 kV capacitor bank, and other associated equipment to allow for the installation of a 20 MVAR 115 kV capacitor bank. | MN | GIP | [5 empty] | 2024-07-31 | 115 |  | 1153145
MTEP23 | East | METC | 24459 | J1379 Generator Interconnection TOIF | Install an Entrance structure and 138 kV disconnect switch at the new switching station. | MI | GIP | [5 empty] | 2024-05-31 | 138
MTEP23 | South | East Texas Electric Cooperative Inc. | 24460 | Coldspring Load Addition | A member of ETEC is adding a total of 21.2 MW to the existing Coldspring substation to serve a new customer load. The load addition will be completed in two phases. Phase I - Serving 5MW of additional load via the existing distribution transformer. Phase II - Adding a new distribution transformer to serve 16.2 MW of additional load. | TX | Other | Load Growth |  |  |  | 2 | 2024-07-31 | 138 |  | 3740960
MTEP23 | West | ITC Midwest | 24464 | Eagle to Tharp 69kV Line Relocation | A 0.75 section of the Eagle - Tharp 69 kV line is required to be moved to a new permanent location by the Iowa DOT due to a project to rebuild the I-380 and Wright Bros Blvd interchange. Thirteen new wooden poles, three new steel poles, and new T2-477 ACSR cabling is to be constructed as shown in the sketched figures. PTS 1158 is to be retired and PTS 1114 is to have the jumpers remade to face towards Eagle. PTS 1114 will remain in this configuration until the switch is retired with the Kitty Hawk rebuild. | IA | Other | Other Local Needs |  |  |  |  | 2024-05-01 | 69 |  | 1618750
MTEP23 | West | American Transmission Co. LLC | 24465 | Walworth - Brick Church (Y-159), OPGW Addition & Partial Rebuild | OPGW Addition on the Walworth - Brick Church (Y-159) line and partial transmission line rebuild. | WI | Other | Other Local Needs |  |  |  |  | 2026-06-30 | 69 |  | 4600000
MTEP23 | East | ITC Transmission | 24466 | MDOT I-96 Construction - Cody - Nolan Structure Relocation | Relocate five structures on the Cody – Nolan 120 kV line that are in conflict with the reconstruction and rehabilitation project along US-23 at the I-96/Grand River intersection. | MI | Other | Other Local Needs |  |  |  |  | 2024-08-01 | 120 |  | 1250000
MTEP23 | West | American Transmission Co. LLC | 24473 | Rock River SS, DIC, Additional Transformer | Expanding Rock River 138kV Bus 3 to interconnect a distribution transformer | WI | Other | Load Growth |  |  |  |  | 2024-07-01 | 138 |  | 3000000
MTEP23 | West | American Transmission Co. LLC | 24475 | Tommy's Turnpike DIC, New Sub | ATC will construct an approximately 0.3 mile 115 kV double-circuit transmission line extension from the Whiting Ave – Okray 115kV line (B-106) to interconnect the proposed T-D substation. • ATC will construct a 115 kV loop-through straight bus with line switches, bus-tie switches, and space reserved for potential line and bus-tie breakers. • WPS to construct a new substation site, install two new 115/24.9 kV 33/38 MVA transformers with high side breaker protection for each and other supporting equipment. | WI | Other | Load Growth |  |  |  | 38 MVA | 2025-12-31 | 115 |  | 7700000
MTEP23 | East | METC | 24493 | Claremont - Cornell #2 - J1297 GIA (Hathon) TOIF | Install a line entrance structure and a switch for the generator to connect at position BM10. | MI | GIP | [5 empty] | 2026-01-31 | 138
MTEP23 | West | ITC Midwest | 24513 | Maquoketa (CIPCO) 161 kV Sub Rebuild | CIPCO has notified ITC that they will be rebuilding the 161 kV portion of their Maquoketa substation to a ring bus. ITC will need to relocate the Grand Mound – Maquoketa and Maquoketa – Sale 161 kV lines into new bus positions at Maquoketa to accommodate the new layout of the substation. T2-636 ACSR should be used for new conductor for the new line taps. | IA | Other | Reliability |  |  |  |  | 2024-05-30 | 161 |  | 2028750
MTEP23 | East | METC | 24514 | Murphy-Styx - J1389 Generator Interconnection - TOIF | Install a line entrance structure and a switch for the generator to connect at position RH31. | MI | GIP | [5 empty] | 2024-01-29 | 345
MTEP23 | Central | Northern Indiana Public Service Company | 24562 | J1333 -J1340 Network Upgrades | Greenfield 345kV double breaker double bus station named Hinshaw. | IN | GIP | [5 empty] | 2024-06-01 | 345 |  | 47288518
MTEP23 | West | American Transmission Co. LLC | 24575 | DPC Clearfield Jct Tap, New T-T | New T-T interconnection to Council Creek-Hilltop 69 kV (Y-74), and constructing a new 69 kV loop-through substation near New Lisbon Tap with three line breakers to replace an existing three-way GOAB. | WI | Other | Load Growth |  |  |  |  | 2026-06-01 | 69 |  | 11100000
MTEP23 | East | ITC Transmission | 24593 | GM Orion Plant Expansion | At Sunbird, expand the existing substation to include 3-120 kV line breakers, 1-120 kV section breaker, and create bus 103. Construct a 2nd Pontiac-Sunbird 120 kV line and install 2-120 kV pole top switches on the Colorado taps on the Pontiac-Sunbird #1 and Sunbird-Bloomfield 120 kV lines. At Pontiac, bypass the existing series reactor and install a line breaker on the new Pontiac-Sunbird #2 line position. Install OPGW between Pontiac and Sunbird. | MI | Other | Load Growth |  |  |  |  | 2025-05-31 | 120 |  | 25796000
MTEP23 | West | American Transmission Co. LLC | 24613 | J1214 J1326 Rockdale SS Network Upgrades and Interconnection Facilities | Solar development with energy storage in Dane County, Wisconsin. | WI | GIP | [5 empty] | 2025-06-01 | 345 |  | 4069937
MTEP23 | East | METC | 24673 | Project Hickory Load connection | METC will construct the new 138 kV, 3-row, breaker and a half Charge substation to be fed by looping the existing Highfield-Brooks Industrial 138 kV line approximately 0.2 miles into the new substation. | MI | Other | Other Local Needs |  |  |  |  | 2024-05-31 | 138 |  | 16623125
MTEP23 | Central | Ameren Services Company | 24695 | New Fauna 345 kV Sub for Flora Solar (J1679) | 125 MW solar generation project J1679. Interconnection at Fauna sub on Xenia - Mt Vernon West 345 kV Line 4591. | IL | GIP | [5 empty] | 2025-12-01 | 345 |  | 11000000
MTEP23 | Central | Ameren Services Company | 24696 | New Vanhorn 345 kV Substation for Wolf Creek Solar (J1352) | Construct the Interconnection Facilities at the J1352 Interconnection Switching Station, line cut-in and relay upgrades. Vanhorn sub on Montgomery-Spencer Creek 345 kV line. | MO | GIP | [5 empty] | 2025-06-01 | 345 |  | 11000000
MTEP23 | South | Entergy Arkansas | 24697 | Aurelle 115kV: POI for J1612 | A new point of interconnection for J1612 100 MW solar project. The interconnection customer will install the SANU. Network Upgrades at El Dorado 115kV and Sterlington 115kV will be installed by Entergy as well as the transmission line cut-in. New underground fiber will be installed between Strong and Huttig tap stations. | AR | GIP | [5 empty] | 2024-11-27 | 115 |  | 13031000
MTEP23 | Central | Ameren Services Company | 24718 | New Quotient 345 kV Substation for Casey Fork Solar(J1241) | Construct a new 345kV Quotient switching station in Jefferson County, IL to provide a Point of Interconnection for the Generating Facility. The new J1241 Interconnection Switching Station will split the existing Xenia – Mt Vernon West 345 kV transmission line | IL | GIP | [5 empty] | 2025-12-01 | 345 |  | 11000000
MTEP23 | West | ITC Midwest | 24740 | Commercial (JCE) 69 kV Substation | For ITC’s portion of the Commercial Substation ITC will install a new 69 kV substation with 2 69 kV line breakers, one distribution transformer position, and one mobile transformer position. All the ITC equipment will be capable of 600A or greater. | IL | Other | Load Growth |  |  |  |  | 2024-06-01 | 69 |  | 3801869
MTEP23 | West | American Transmission Co. LLC | 24758 | J1410 J1411 North Arlington Swt St MPFCA & Network Upgrades | J1410 is a solar facility located in Dane County, Wisconsin. J1411 is an energy storage facility co-located in Dane County with J1410. | WI | GIP | [5 empty] | 2026-06-03 | 345 |  | 21988404
MTEP23 | Central | Ameren Services Company | 24779 | New Hoot 138kV Substation (J1266) | Hoots J1266 Interconnection Switching Station will cut the existing Kinmundy – Salem West 138 kV transmission line | IL | GIP | [5 empty] | 2025-12-01 | 138 |  | 10500000
MTEP23 | Central | Ameren Services Company | 24780 | Fayetteville Bee Hollow Substation (J1311) | The Fayetteville Bee Hollow Substation will be rebuilt to a 4 position (6 position ultimate) 138kV ring bus to allow J1311 interconnection. | IL | GIP | [5 empty] | 2025-12-01 | 138 |  | 8000000
MTEP23 | Central | Ameren Services Company | 24781 | New Greenwave 138kV Substation (J1232) | The J1232 Generating Facility will interconnect at the Greenwave substation cutting the Mattoon West-Arland-1539 138 kV Transmission Line. | IL | GIP | [5 empty] | 2025-12-01 | 138 |  | 8000000
MTEP23 | West | American Transmission Co. LLC | 24782 | J1304 J1305 J1460 MPFCA Network Upgrades | Transmission owner will reconductor one of the two segments of the line UNIG52. | WI | GIP | [5 empty] | 2025-12-31 | 138 |  | 4930697
MTEP23 | West | American Transmission Co. LLC | 24783 | Hodag SS, DIC, Add Additional Transformer | Expand and reconfigure substation to a loop through straight bus configuration. | WI | Other | Load Growth |  |  |  |  | 2024-12-31 | 115 |  | 2700000
MTEP23 | West | American Transmission Co. LLC | 24784 | Ellisville SS, DIC, New Substation | ATC will construct approximately 0.7 miles of 138 kV double-circuit transmission line extension from line M-39 to interconnect the proposed T-D substation. • ATC will construct a 138 kV loop-through straight bus with two-line breakers and provisions for a future bus-tie breaker. | WI | Other | Load Growth |  |  |  |  | 2025-06-01 | 138 |  | 10200000
MTEP23 | West | American Transmission Co. LLC | 24785 | Pleasant Prairie 345 kV Capacitor Bank Addition | Install four 345 kV 75 Mvar capacitor banks at Pleasant Prairie substation | WI | Other | Reliability |  |  |  |  | 2025-06-30 | 345 |  | 7600000
MTEP23 | West | American Transmission Co. LLC | 24799 | J1377 Blitz SS Network Upgrades and Interconnection Facilities | Solar generating facility in Rock County, WI. | WI | GIP | [5 empty] | 2026-11-12 | 345 |  | 14574360
MTEP23 | West | American Transmission Co. LLC | 24801 | J1253 El Dorado SS Network Upgrades and Interconnection Facilities | Solar generating facility along with substation and network upgrades in Fond du Lac County, Wisconsin. | WI | GIP | [5 empty] | 2027-11-12 | 345 |  | 50461169
MTEP23 | West | American Transmission Co. LLC | 24802 | J1460 Sunrise SS Network Upgrades and Interconnection Facilities | Solar generating facility and substation upgrades in Rock County, WI. | WI | GIP | [5 empty] | 2025-12-27 | 138 |  | 4465266
MTEP23 | West | American Transmission Co. LLC | 24819 | Racine 345 kV Capacitor Bank Addition | Install two 345 kV 75 Mvar capacitor banks at Racine substation. | WI | Other | Reliability |  |  |  |  | 2025-06-30 | 345 |  | 8400000
MTEP23 | West | American Transmission Co. LLC | 24838 | J1316 Paris SS Network Upgrades | J1316 is an energy storage facility interconnected at the same location as J878, a solar facility located in Kenosha County, WI. | WI | GIP | [5 empty] | 2028-12-29 | 345 |  | 22432466
MTEP23 | South | Entergy | 24839 | J1671 230 kV Interconnection Project(Rocky Creek to Veteran) | Facilities required for the interconnection of J1671 on the Rocky Creek to Veteran 230 kV. | TX | GIP | [5 empty] | 2025-12-04 | 230 |  | 18847000
MTEP23 | Central | Ameren Services Company | 24840 | New Zeke 345kV J1263 Interconnection Switching Station | New 345¿kV Switching Station on Casey West – Kansas 345 kV for the Generating Facility J1263 | IL | GIP | [5 empty] | 2025-12-01 | 345 |  | 10000000
MTEP23 | West | American Transmission Co. LLC | 24841 | J1214 J1326 J1377 J1410 J1411 MPFCA Network Upgrades | Network upgrades to support new interconnections J1214 (solar), J1326 (storage), J1377 (solar), J1410 (solar), J1411 (storage). | WI | GIP | [5 empty] | 2025-05-30 | 138 |  | 1279961
MTEP23 | West | American Transmission Co. LLC | 24858 | J1253 J1410 J1411 MPFCA Network Upgrades | Network upgrades to support new interconnections J1253 (solar), J1410 (solar), and J1411 (energy storage). | WI | GIP | [5 empty] | 2025-12-30 | 138 |  | 55520
MTEP23 | Central | Ameren Services Company | 24859 | Casey West 345 kV- New Position for Union Center Solar(J1204) | A new 345 kV position will be constructed at Casey West Substation to serve as the Point of Interconnection for Union Center Solar, LLC under GIA J1204. The CSYW-NWTY-1 line position will also be moved from the southwest corner of the substation to the southeast corner to avoid line crossing with the IC. | IL | GIP | [5 empty] | 2025-12-01 | 345 |  | 1200000
MTEP23 | Central | Ameren Services Company | 24860 | Bullion 161 kV Add Breaker Position for Kelso 2 Solar (J1299) | This project will construct a new Point of Interconnection for the Interconnection Customer's Generating Facility, Kelso 2 Solar LLC, to the Buillion Switching Station. The 161 kV lead line from Kelso 2 Solar LLC will terminate into the fourth position. | MO | GIP | [5 empty] | 2025-12-01 | 161 |  | 1000000
MTEP23 | South | Entergy | 24861 | J1583 Interconnection on Evergreen to Donaldsonville 230 kV | Facilities required for the interconnection of J1583 on the Evergreen to Donaldsonville 230 kV. | LA | GIP | [5 empty] | 2025-06-01 | 230 |  | 5000000
MTEP23 | South | Entergy | 24862 | J1644 Generator Interconnection on Champagne to Plaisance 138 kV | Facilities required for the interconnection of J1644 on the Champagne to Plaisance 138 kV. | LA | GIP | [5 empty] | 2024-12-15 | 138 |  | 4329000
MTEP23 | Central | Ameren Services Company | 24878 | Ashley-IL 138 kV New Position for Ashley Solar (J1216) | This project will tap into the existing Ashley 138 kV 3-position ring bus to serve as the Point of Interconnection for the Interconnection Customer's Generating Facility, Ashley Solar, LLC. The existing ASHL-JORD-1536 138 kV transmission line will be raised to provide adequate space for the new interconnection line. The 138 kV lead line from Ashley Solar, LLC will terminate into the third position. | IL | GIP | [5 empty] | 2025-12-01 | 138 |  | 1000000
MTEP23 | South | Entergy Arkansas | 24879 | Prairie Creek 161kV: POI for J1816 | A new interconnection three breaker ring-bus substation will be constructed on the Fisher - Cherry Valley 161kV transmission line. Line protection and breaker control panels will be installed at Newport and Parkin 161kV stations. The existing wave trap will be removed from Pecan Street 161kV station. New underground fiber will be installed between Prairie Creek and Cherry Valley 161kV substation. | AR | GIP | [5 empty] | 2025-11-01 | 161 |  | 12604000
MTEP23 | South | Entergy Mississippi | 24880 | Cotton Blossom 230 kV: Solar Interconnection (J1747) | Interconnect a 50 MW solar generation facility to the Cotton Blossom 230 kV substation. | MS | GIP | [5 empty] | 2024-07-31 | 230 |  | 724000
MTEP23 | South | Entergy Arkansas | 24898 | Flat Lake 161kV J1562: Cut-in Switching Station | The interconnection customer will self build the switching station needed to interconnect J1562 200 MW solar project. The cut-in will connect the new POI station to the existing Blytheville I-55 and AECC Blytheville North 161kV line section. Entergy will install new line protection panel and breaker control panel at Blytheville I-55 161kV substation and AECC Blytheville North 161kV substation. Two existing breakers at Blytheville Elm St. 161kV will also be replace with new surge arresters, line protection and breaker control panels and a new RTU. New underground fiber will be installed between the new POI station to Blytheville I-55 and AECC Blytheville North substations. | AR | GIP | [5 empty] | 2025-01-31 | 161 |  | 5161000
MTEP23 | South | Entergy Mississippi | 24899 | Twinkletown 230 kV: Solar Interconnection (J1748) | Interconnect a 100 MW generation facility to the Twinkletown 230 kV substation. | MS | GIP | [5 empty] | 2024-07-31 | 230 |  | 672000
MTEP23 | Central | Ameren Services Company | 24900 | Ipava 138 kV New Position (J1383) | Interconnection Facilities shall consist of one 138 kV terminal in the Ipava substation to connect the J1383 leadline. | IL | GIP | [5 empty] | 2025-12-01 | 138 |  | 1000000
MTEP23 | Central | Ameren Services Company | 24901 | Morganfield 138 kV New Position (J1302) | Add 138 kV terminal in the Morganfield substation to connect the J1302 and J1096 leadline to the Morganfield substation | IL | GIP | [5 empty] | 2025-12-01 | 138 |  | 1000000
MTEP23 | West | Northern States Power (Xcel Energy) | 24902 | Brookings - Lyon, Hampton - Helena OPGW Replacement | This project will replace the aging OPGW on the Brookings - Lyon County and Hampton - Helena 345kV lines. This project will be performed in tandem with the installation of the Brookings - Lyon County and Hampton - Helena 2nd circuit installation project. | MN,SD | MVP | [5 empty] | 2025-09-01 | 345 |  | 4007320
MTEP23 | South | Entergy Arkansas | 24918 | Hamrick 161kV J1842: Cut-in Switching Station | The Hamrick 161kV switching station will be constructed for the 135 MW wind farm (J1842) per the terms of the executed GIA. The wind farm will be connected by a 4 mile 161kV gen-tie line to the new Hamrick 161kV SS that will be constructed by the Interconnection Customer. Entergy Arkansas will construct the the 161kV cut-in as well as relay settings updates at the remote end stations. New underground fiber will also be installed between Hamrick and Wynne South 161kV. | AR | GIP | [5 empty] | 2024-10-31 | 161 |  | 2073000
MTEP23 | South | Entergy | 24920 | Cole Road 138 kV New Customer Station | Entergy is proposing to construct a new 138 kV transmission station called Cole Road 138 kV which will serve a new industrial customer’s 10 MW of load near Cleveland, TX. Cole Road 138 kv station will be cut into the Jacinto to Splendora 138 kV line. | TX | Other | Load Growth |  |  |  | 10 | 2024-10-31 | 138 |  | 29600000
MTEP23 | West | MidAmerican Energy Company | 24923 | Sidney-Percival 69 kV Line Rebuild | Rebuild the Sidney-Percival 69 kV line and replace line structures. | IA | Other | Age and Condition |  |  |  |  | 2025-06-01 | 69 |  | 9100000
MTEP23 | South | Entergy Arkansas | 24938 | Driver - Hybar 230kV: New transmission line | Entergy Arkansas will build a new 2 mile 230kV radial transmission line from the Driver 230kV substation to a new customer build Hybar 230kV substation. A new circuit breaker and relay upgrades will be needed at Driver 230kV substation. Two 500kV transmission lines will be raised for the new 230kV line crossing. | AR | Other | Load Growth |  |  |  |  | 2025-05-01 | 230 |  | 10632090
MTEP23 | West | Montana-Dakota Utilities Company | 24978 | Tatanka Load Addition | MDU will be signing agreement to serve 100 MW of load at the Tatanka Wind Farm collector substation off the Tatanka South Substation. There will be no cost to MDU to serve the customer. | SD,ND | Other | Load Growth | MDU serving 100 MW of load at Tatanka Wind Farm collector substation off Tatanka South | Large Industrial |  | 100 | 2023-12-01 | 230 |  |  | Tatanka: 100MW load at wind farm collector sub (MDU). $0
MTEP23 | South | Entergy | 24984 | J1760 Generator Interconnection on Plum Grove to Colony 230 kV | Facilities required for the interconnection of J1760 on the Plum Grove to Colony 230 kV. | TX | GIP | [5 empty] | 2026-06-01 | 230 |  | 16300000
MTEP23 | South | Entergy | 24985 | J1827 Generator Interconnection Bastrop Tap 115 kV | Facilities required for the interconnection of J1827 at the Bastrop Tap 115 kV station. | LA | GIP | [5 empty] | 2026-04-01 | 115 |  | 18500000
MTEP23 | South | Entergy | 24986 | J1795 Generator Interconnection on Richard to Bayou Cove 138 kV(Ln 258) | Facilities required for the interconnection of J1795 on the Richard to Bayou Cove 138 kV Line 258. | LA | GIP | [5 empty] | 2025-12-04 | 138 |  | 17700000
MTEP23 | West | MidAmerican Energy Company | 24999 | Southland Expansion & Upgrades | Expand 345 kV bus at existing Southland Substation to serve new customer load. Construct new 345 kV line from Overland Trail to Pony Creek Substation, reroute the existing Pony Creek-Rolling Hills 345 kV line into Southland Substation and rebuild the existing CBEC-Pony Creek 345 kV line. | IA | Other | Load Growth | Expand 345 kV bus at Southland to serve new customer load; new 345 kV line from Overland Trail to Pony Creek | Large Industrial |  |  | 2027-06-03 | 345 |  | 58000000 | Southland Expansion: 345kV bus expansion for new customer (MEC IA). $58M
MTEP23 | East | METC | 25038 | Murphy - Orr Road #3 138 kV Line | Construct a 3rd 138 kV circuit from Murphy to Orr Rd utilizing 954 ACSR on the open side of the existing structures currently carrying the Orr Rd-Murphy #2 138 kV circuit. This scope will potentially add some structures at Murphy and Orr Road station ends to terminate the new 138 kV line. Install OPGW on the new circuit and terminate it at both ends. Install a new breaker at Murphy Pos. 4B7, and install a new breaker at Orr Road Pos. 6B7. | MI | Other | Other Local Needs |  |  |  |  | 2025-03-31 | 138 |  | 7600000
MTEP23 | West | ITC Midwest | 25060 | Grant Milford Interconnection | Rebuild approximately 4 miles of existing 34.5 kV line to 69 kV construction standards to interconnect new IPL Grant Milford substation and facilitate future area conversion to 69 kV operation as part of CIPCO's SW IA 34.5 to 69 kV conversion plans. | IA | Other | Reliability |  |  |  |  | 2025-06-30 | 69 |  | 3483750
MTEP23 | South | Entergy | 25083 | J1794 Generator Interconnection on Richard to Scott 138 kV | Facilities required for the interconnection of J1794 on the Richard to Scott 138 kV | LA | GIP | [5 empty] | 2025-05-06 | 138 |  | 12840000
MTEP23 | South | Entergy Mississippi | 25086 | Tinnin Road 230 kV: Solar Gen Interconnection (J1672) | Interconnect a 150 MW generation facility to the Tinnin Road 230 kV substation. | MS | GIP | [5 empty] | 2025-11-16 | 230 |  | 5529000
MTEP23 | South | City Water & Light - Jonesboro, Arkansas | 25094 | Commerce to Ringier 69 kV Relocation | Relocation of JCWL Commerce – Ringier 69kV line due to ARDOT project | AR | Other | Other Local Needs |  |  |  |  | 2023-09-30 | 69 |  | 315000
MTEP23 | South | Entergy | 25101 | J1564 Generator Interconnection on the Bogalusa to Talisheek 230 kV | Facilities required for the interconnection of J1564 on the Bogalusa to Talisheek 230 kV | LA | GIP | [5 empty] | 2025-12-22 | 230 |  | 18820000
MTEP23 | South | Entergy | 25102 | J1709 Generator Interconnection at Grimes 138 kV | Facilities required for the interconnection of J1709 at the Grimes 138 kV station. | TX | GIP | [5 empty] | 2025-02-01 | 138 |  | 7212000
MTEP23 | South | Entergy | 25122 | J1542 Generator Interconnection on Vacherie to Chackbay 230 kV | Facilities required for the interconnection of J1542 on the Vacherie to Chackbay 230 kV | LA | GIP | [5 empty] | 2026-06-01 | 230 |  | 19300000
MTEP23 | South | Entergy | 25140 | J1669 Generator Interconnection on Lake Charles Bulk to Henning 138 kV | Facilities required for the interconnection of J1669 on the Lake Charles Bulk to Henning 138 kV | LA | GIP | [5 empty] | 2025-12-04 | 138 |  | 16910000
MTEP23 | South | Entergy | 25143 | J1602 Generator Interconnection at Rilla 115 kV | Facilities required for the interconnection of J1602 at Rilla 115 kV. The J1602 battery will be interconnected behind the main step up transformer for J1239 (Rilla 115 kV POI) | LA | GIP | [5 empty] | 2024-10-25 | 115
MTEP23 | West | American Transmission Co. LLC | 25154 | CRP Substation Ethernet Migration (Phase 2) | The telecommunication companies will construct fiber infrastructure to the substation locations. This fiber will extend from the road right of way to a telecommunications handhole located outside of the fence. When a handhole does not exist outside of the fence, a new ATC owned handhole will be installed. • The telecommunication companies will install fiber from this handhole through existing conduit and into the control house. • The telecommunication companies will install a network interface device (NID) and any other needed associated equipment on the telecommunications board to terminate their fiber. • ATC will power the NID from at least one direct current (DC) circuit and will coordinate turn up of the new ethernet circuit with the telecommunication companies. • ATC will coordinate with AT&T for the decommissioning of the existing T1 service. • ATC will replace the substation router at 14 locations. Some of these locations will also require a cellular router and cell booster to be installed as the backup communications medium, replacing the existing plain old telephone service (POTS). • ATC will install Voice over Internet Protocol (VoIP) phones at ATC owned control houses with existing analog phones. | WI,MI | Other | Other Local Needs |  |  |  |  | 2024-06-30 | 0 |  | 5500000
MTEP23 | West | American Transmission Co. LLC | 25207 | Forsyth - Empire (Forsyth) 138 kV, Rerate | Rerate Line Forsyth conductor for the Forsyth to Empire section to keep up with the system demand. The thermal study identified 18 clearance issues needed to be fixed to bring the rating up to meet Operations/Planning's needs. | MI | Other | Reliability |  |  |  |  | 2024-10-20 | 138 |  | 5000000
MTEP23 | South | Entergy | 25242 | Amite South Reliability Project Phase 1 - alternative | Construct 500/230 kV Commodore station near the existing Derrick 230 kV Station o Cut in Derrick to Iberville and Richardson to Wise 230 kV lines. Cut in the Webre to Bayou Labutte 500 kV line o Install one 500-230 kV Autotransformer o Commodore 230 kV station will be a breaker and half station o Commodore 500 kV station will be a 4 breaker ring • Construct a new ~60 mile 230 kV line between Commodore and Waterford. • Construct a new ~85 mile 500 kV line between Commodore and Churchill. • Expand Waterford 500 kV into a three-breaker ring. Add additional bay at Waterford 230 kV to accommodate the new 230 kV line. • Construct a new 500 kV four-breaker ring at Churchill, to accommodate two 500 kV lines and two Autotransformers. Install two 500-230 kV Autotransformers. • Convert existing Waterford to Churchill 230 kV to 500 kV operation. | LA | Other | Reliability |  |  |  |  | 2028-07-01 | 500 |  | 1700000000
MTEP23 | West | Southern Minnesota Municipal Power Agency | 25252 | Fairmont, MN Area 69kV Transmission Expansion | Building of a new 69/12.5kV distribution substation “West Industrial Park” (WIP) west of Fairmont, construction of a new 69 kV SMMPA breaker station and construction two 69kV transmission lines, one from WIP to the SMMPA’s Fairmont Energy Station (FES) substation (approx. 2mi) and one from WIP which will tap Great River Energy’s 69 kV line between Rutland substation and the Fairmont 10th Street Substation (0.5mi). | MN | Other | Load Growth |  |  |  |  | 2026-03-01 | 69 |  | 8920000
MTEP23 | West | Otter Tail Power Company | 25256 | OTP Jamestown, ND Load Addition #2 | OTP has received a customer request to add an additional 10 MWs of load at an existing site that is being served from the Jamestown 345 kV substation. In order to serve this new load, the 115 kV bus at the Jamestown 345 kV substation will be expanded to allow for the addition of a new 115/41.6 kV transformer. The 41.6 kV side will serve the new load and be tied into the existing 41.6 kV transmission system to provide backup via a normally open breaker. | ND | Other | Load Growth |  |  |  |  | 2024-06-01 | 115 |  | 3250000
MTEP23 | West | American Transmission Co. LLC | 25262 | J1305 Norwegian Creek SS Network Upgrades and Interconnection Facilities | Solar generating facility in Green County, Wisconsin. | WI | GIP | [5 empty] | 2023-11-08 | 138 |  | 8132415

## MTEP24
MTEP Year | Planning Region | Utility/TO | Project ID | Project Name | Project Description | State | Project Type | Other Type | System Need / Rationale | Project Driver | Data Center Flag | Load (MW) | Expected ISD | Max kV | Min kV | Estimated Cost ($) | Report Notes
MTEP24 | West | MINNESOTA POWER INC. | 25141 | Arrowhead 115kV SPF Upgrade | Add redundancy or monitoring to the single point of failures to mitigate P5 contingences associated with the Arrowhead 115kV buses. | MN | BRP | [5 empty] | 2024-12-31 | 115 |  | 250000
MTEP24 | West | MINNESOTA POWER INC. | 25142 | Forbes 115kV SPF Upgrade | Add redundancy or monitoring to the single point of failures to mitigate P5 contingences associated with the Forbes 115kV buses. | MN | BRP | [5 empty] | 2024-12-31 | 115 |  | 250000
MTEP24 | West | ITC MIDWEST | 25200 | J1190 GIA NU Calamus East 161 kV Bus Expansion | A 161 kV straight bus expansion at the Calamus East station will be constructed for the interconnection of project J1190. | IA | GIP | [5 empty] | 2026-10-01 | 161 |  | 155146
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50113 | J1716 Eldorado SS Network Upgrades | J1716 is a solar facility located in Fond du Lac County, WI. | WI | GIP | [5 empty] | 2027-03-19 | 345 |  | 225000
MTEP24 | West | ITC MIDWEST | 25201 | J1325 GIA TOIF Magnolia 161 kV Terminal Addition | TOIF includes facilities and equipment dedicated to the Generating Facility including; dead-end, switch, relay panel, CCVTs, etc. TOIF costs estimates are funded by the customer and ITC costs will be $0 as it will be a CIAC project for ITCM. | MN | GIP | [5 empty] | 2025-06-30 | 161 |  | 417240
MTEP24 | West | ITC MIDWEST | 25182 | J1313 GIA TOIF Karma 161 kV Terminal Addition | The Karma 161 kV substation will be expanded to accommodate the J1313 terminal, including the addition of a new breaker position and switches. New equipment should be capable of 2000A. TOIF costs estimates are funded by the customer and ITC costs will be $0 as it will be a CIAC project for ITCM. | IA | GIP | [5 empty] | 2025-06-30 | 161 |  | 427809
MTEP24 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 50089 | Aetna Synchronous Condenser | Synchronous Condenser placed at Aetna 138kV substation. +360/-180 MVAR capabilities. | IN | Other | Local Reliability | Synchronous condenser for voltage support driven by EPR load growth | Load Growth (Voltage Support) |  |  | 2024-05-01 | 138 |  | 91000000 | Central region EPR $91M
MTEP24 | West | ITC MIDWEST | 25184 | J1365 GIA TOIF Traer 161 kV Terminal Addition | TOIF includes surge arrestors, switch, current transformers, and relay dedicated to J1365 radial line and generating facility. TOIF costs estimates are funded by the customer and ITC costs will be $0 as it will be a CIAC project for ITCM. | IA | GIP | [5 empty] | 2024-09-06 | 161 |  | 462831
MTEP24 | South | CITY WATER AND LIGHT PLANT OF JONESBORO ARKANSAS | 25544 | JCWL - Commerce to Ringier 69kV Rebuild | Rebuild the Commerce - Ringier 69kV line | AR | Other | Age and Condition |  |  |  |  | 2024-07-01 | 69 |  | 873580
MTEP24 | South | CLECO POWER LLC | 25312 | J1832 Plaisance Expansion | Expand Plaisance Substation to interconnect J1832 Solar | LA | GIP | [5 empty] | 2024-07-15 | 138 |  | 6512000
MTEP24 | West | ITC MIDWEST | 25202 | J1325 GIA NU Magnolia 161 kV Bus Expansion | Expand Magnolia 161 kV substation from a 4-terminal, 4 breaker, ring-bus substation to a 5 terminal ring bus substation. | MN | GIP | [5 empty] | 2025-06-30 | 161 |  | 486788
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25144 | Y52-3 Oakland City - Duke Oakland City Rebuild | Rebuild ~2.76 miles of 69kV line due to aging infrastructure and pole condition | IN | Other | Age and Condition |  |  |  |  | 2024-08-01 | 69 |  | 3882590
MTEP24 | Central | HOOSIER ENERGY | 25304 | HE_J1396_Ratts_3_Solar | Engineering labor is to be required to modify protection settings to comply with increased load flow | IN | GIP | [5 empty] | 2024-08-20 | 161 |  | 10000
MTEP24 | West | ITC MIDWEST | 25183 | J1313 GIA NU Karma 161 kV Ring Bus Expansion | The Facilities Study for J1313 identified Network Upgrades and TOIF necessary for the interconnection of project J1313 to ITCM’s Karma 161 kV station. Project J1313’s impact to the transmission system was evaluated as part of the DPP 2019 April West Area Study. | IA | GIP | [5 empty] | 2025-06-30 | 161 |  | 556081
MTEP24 | West | ITC MIDWEST | 25197 | J1734 GIA TOIF New Wever 161 kV Terminal | Perform TOIF upgrades for J1734 per the GIA. The J1734 TOIF upgrades will include dead-end, disconnect switch, arresters, PT’s, line relay panel, and associated equipment dedicated to the generating facility. TOIF costs estimates are funded by the customer and ITC costs will be $0 as it will be a CIAC project for ITCM. | IA | GIP | [5 empty] | 2024-06-01 | 161 |  | 562250
MTEP24 | West | ITC MIDWEST | 25221 | J1432 GIA TOIF New Bryant 345 kV Terminal | TOIF includes facilities and equipment at the Bryant 345 kV switching station dedicated to the 345 kV radial line and Generating Facility. TOIF costs estimates are funded by the customer and ITC costs will be $0 as it will be a CIAC project for ITCM. | IA | GIP | [5 empty] | 2028-09-01 | 345 |  | 716244
MTEP24 | Central | HOOSIER ENERGY | 25261 | HE_J1028_Ratts1_Solar | Transmission Owner Upgrades consist of filling and leveling the site for the proposed Apollo Substation and constructing on it the new 161kV switchyard in a ring bus arrangement with proposed dimensions of 250’ x 275’ for the fenced area. The station will have an initial build out of 3 positions along with accommodations for a fourth future position. The initial terminals shall connect to the IC’s facilities, Victory Substation, and Petersburg Substation. | IN | GIP | [5 empty] | 2024-09-06 | 161 |  | 11424620
MTEP24 | West | ITC MIDWEST | 25181 | J1190 GIA TOIF Calamus East 161 kV Terminal Addition | TOIF includes facilities including, 161 kV breaker, switches, dead-end, and equipment at Calamus East substation dedicated to the 161 kV radial line and Generating Facility. TOIF costs estimates are funded by the customer and ITC costs will be $0 as it will be a CIAC project for ITCM. | IA | GIP | [5 empty] | 2026-10-01 | 161 |  | 803119
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25148 | Posey Solar Gen Interconnection (J1308) | New interconnection substation for Posey Solar generation project J1308 | IN | GIP | [5 empty] | 2024-10-01 | 345 |  | 20000000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25145 | Lynnville 69kV OCB Replacement | Replace two 69kV oil breakers with gas breakers at Lynnville substation | IN | Other | Age and Condition |  |  |  |  | 2024-11-01 | 69 |  | 872319
MTEP24 | West | OTTER TAIL POWER COMPANY | 22487 | OTP Audubon and Erie 230/115 kV Transformer Tap Adjustments | Adjust Audubon 230/115 kV transformer #1, Audubon 230/115 kV transformer #2, and Erie 230/115 kV transformer taps. | MN | Other | Local Reliability |  |  |  |  | 2025-11-30 | 230 |  | 3000
MTEP24 | West | OTTER TAIL POWER COMPANY | 50009 | OTP Winger 41.6 kV Line Reroute | Reconductor and reroute small portion of 41.6 kV line between Winger 41.6 kV and Winger Town 41.6 kV. | MN | Other | Local Reliability |  |  |  |  | 2025-12-31 | 42 |  | 115000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25146 | Fairlawn 69kV Switch Replacement | Replacement of several 69kV switches at Fairlawn substation due to aging infrastructure. | IN | Other | Age and Condition |  |  |  |  | 2024-12-01 | 69 |  | 1000000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25357 | BYN-NRH Pilot Channel Replacement | Install modern leased Ethernet circuits and associated communication equipment for this protection system, point to point between substations. | MN | Other | Age and Condition |  |  |  |  | 2023-12-15 | 345 |  | 200000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25353 | Replace Southwest 138 kV #1 Breaker | Replacement of 1 138 kV breaker at Southwest. Breaker #1. | IN | Other | Age and Condition |  |  |  |  | 2024-12-05 | 138 |  | 900000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25356 | CNC-BUL-SHC Pilot Channel Replacement | Install modern leased Ethernet circuits and associated communication equipment for this protection system, point to point between substations. | MN | Other | Age and Condition |  |  |  |  | 2024-01-15 | 345 |  | 300000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25319 | Sheas Lake Pilot Channel Replacement | Replace secondary pilot communication circuit from SLL - WLM 345 kV. Install a modern Ethernet circuit and associated communication equipment for this protection system. | MN | Other | Age and Condition |  |  |  |  | 2024-04-01 | 345 |  | 300000
MTEP24 | East | ITC | 24693 | Milan - J799 Amended Generation Interconnection - TOIF | Milan- J799 TOIF - Install line at position HD | MI | GIP | [5 empty] | 2024-12-31 | 120
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25376 | Line 0876 Redwood Falls Tap Switch Replacement | Line 0876 Switch 278 replacement at SMMPA Redwood Falls tap. | MN | Other | Age and Condition |  |  |  |  | 2024-12-01 | 115 |  | 350000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25317 | Wakefield Protection Upgrade | Upgrade system protection equipment at Wakefield 115 kV substation. | MN | Other | Local Reliability |  |  |  |  | 2024-09-30 | 115 |  | 450000
MTEP24 | West | OTTER TAIL POWER COMPANY | 50008 | OTP Oklee Rebuild 41.6 kV Tap | Rebuild and relocate 41.6 kV line near Oklee 41.6 kV. | MN | Other | Local Reliability |  |  |  |  | 2025-12-31 | 42 |  | 450000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25377 | DPC North Wal Interconnection | Build 3 way switching structure on line W3421 between Rice Lake - Barron 69 kV to accommodate DPC North Wal interconnection. | WI | Other | Load Growth |  |  |  |  | 2024-12-01 | 69 |  | 500000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25368 | W3418 Insulator Replacement And Refurb | W3418 line refurb on 2.8 miles from structures 716-762. | WI | Other | Age and Condition |  |  |  |  | 2024-12-31 | 69 |  | 500000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25369 | W3410 Ellsworth Switch Replacement | Replace 3-way switch at Ellsworth substation tap with two 1-way switches. | WI | Other | Local Reliability |  |  |  |  | 2024-12-31 | 69 |  | 500000
MTEP24 | South | ENTERGY SERVICES, LLC. | 25413 | Retirement of Golden Meadow to Barataria 115 kV line | Retirement of Golden Meadow to Barataria 115 kV line. | LA | Other | Local Needs |  |  |  |  | 2024-12-31 | 115 |  | 1
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25302 | Hills 69 kV Breaker Replacement | Replace the 69 kV breaker 514 at Hills Substation with a breaker that has interrupting rating of 40 kA. | IA | Other | Local Reliability |  |  |  |  | 2025-12-01 | 69 |  | 500000
MTEP24 | East | ITC | 25365 | ITCT Line Relocation - 2024 | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI | Other | Local Needs |  |  |  |  | 2024-12-31 | 345 |  | 2500000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25439 | Sub G 69 kV Line Taps | Install two 69 kV line taps terminating at Sub G 69 kV line breakers. | IA | Other | Local Reliability |  |  |  |  | 2030-12-31 | 69 |  | 600000
MTEP24 | East | METC | 25278 | METC Line Relocation - 2024 | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI | Other | Local Reliability |  |  |  |  | 2024-12-31 | 345 |  | 2500000
MTEP24 | South | ENTERGY MISSISSIPPI, LLC. | 25214 | Virlilia 230 kV Substation | The Virlilia 230 kV breaker and a half substation will be fed out of the existing Catlett 230 kV substation. The existing Catlett substation will be reconfigured into a breaker and a half substation with two additional bays to connect to (2) 230 kV lines to the Virlilia 230 kV substation. A 108 MVAR capacitor bank will also be added to the new Virlilia 230 kV substation. Customer load will be fed out of (3) 150 MVA 230/34.5 kV transformers. | MS | Other | Load Growth | Virlilia 230 kV Substation; large load EPR | Large Load |  | 150 MVA | 2025-01-01 | 230 |  | 79500003 | EML EPR $80M
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25295 | 2023 Line Clearance Mitigations | Replace structures at five different faclities to mitigate clearance limitations. Facilities include Raptor-Red Rock, Wilmarth-Swan Lake, St Augusta-Wakefield, North Rochester-Prairie Island, and Monticello-Oakwood. | MN | Other | Local Reliability |  |  |  |  | 2023-09-30 | 345 |  | 625000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25380 | OTP Erie Junction Interconnection | Build two deadend structures to accommodate in-and-out Erie Junction interconnection (MTEP ID 15344). | MN | Other | Local Reliability |  |  |  |  | 2023-11-01 | 230 |  | 650000
MTEP24 | South | ENTERGY SERVICES, LLC. | 24959 | Kolbs to Port Acres 230 kV upgrade project | Upgrade station equipment at Port Acres and conductor to achieve an upgrade on the Kolbs to Port Acres Bulk 230 kV line. | TX | BRP | [5 empty] | 2025-02-01 | 230 |  | 17300000
MTEP24 | West | NORTHWESTERN WISCONSIN ELECTRIC CO. | 50147 | Frederic To Lewis - 69 KV - Clam Falls Drive Section | Upgrade Conductor and Structure from Crossarm 1/0 ACSR to Horizontal Post 477 ACSR. | WI | Other | Local Reliability |  |  |  |  | 2027-05-01 | 69 |  | 660000
MTEP24 | East | METC | 25227 | Dowling Junction-Knowles Sag Remediation (J1658) - Network Upgrade | Remediate Knowles-Dowling Junction sag limit to achieve a rating of at least 240 MVA SN and 266 MVA WN. | MI | GIP | [5 empty] | 2025-03-03 | 138 |  | 1098750
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25088 | Givens 69/12kV T1 Replacement | Replacement of transformer T1 at Givens substation due to age and condition | IN | Other | Age and Condition |  |  |  |  | 2025-04-01 | 69 |  | 3500000
MTEP24 | East | METC | 24538 | J1635 Generator Interconnection TOIF | Install required line entrance structures and 138 kV disconnect at the new Lukesport substation. | MI | GIP | [5 empty] | 2025-04-01 | 138
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25257 | W3419 Str 162 Switch Replacement | Replace damaged 3-way switch with new 3-way switch on steel pole. | WI | Other | Age and Condition |  |  |  |  | 2024-12-31 | 69 |  | 700000
MTEP24 | South | ENTERGY ARKANSAS, LLC | 50013 | Grand Prairie 115kV: New substation | Construct a new 115 kV substation with two 115/4.16 kV 33.3 MVA transformers to serve the planned motors at the pumping station. Cut into the Devalls Bluff – Brinkley East 115kV line and build ~.20 circuit mile (.40 total circuit mile) of “in and out” 115kV line. | AR | Other | Load Growth |  |  |  | 3 MVA | 2025-04-01 | 115 |  | 15626062
MTEP24 | East | METC | 24537 | J1635 Generator Interconnection Network Upgrades | Install new Lukesport 138 kV substation. Install three 138 kV breakers and associated disconnects rated at 40 kA and two new bus sections. Cut the Michigan Ave - Newton 138 kV circuit into the new Lukesport station. | MI | GIP | [5 empty] | 2025-04-03 | 138 |  | 9608322
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25383 | Replace South 138 kV Breakers | Replace 3 138 kV breakers at South. Breakers #1, #2, and #3. | IN | Other | Age and Condition |  |  |  |  | 2025-04-28 | 138 |  | 2700000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25384 | Replace East 138 kV Breakers | Replace 5 138 kV breakers at East. Breakers #1, #2, #4, #5, and #7. | IN | Other | Age and Condition |  |  |  |  | 2025-04-29 | 138 |  | 4500000
MTEP24 | South | ENTERGY ARKANSAS, LLC | 50034 | J1437 Nimbus Wind FCA | Facilities Construction Agreement for the upgrade of relays and protection schemes at Osage Creek, Berryville, Green Forest, Green Forest South, Harrison West and Harrison East station. | AR | GIP | [5 empty] | 2025-04-30 | 161 |  | 1869029
MTEP24 | East | METC | 24444 | Barton Lake-Batavia - J1550 Generator Interconnection (Dorrance) TOIF | Install a line entrance structure and a switch for the generator to connect at position BM14. | MI | GIP | [5 empty] | 2025-05-01 | 138
MTEP24 | South | ENTERGY ARKANSAS, LLC | 50035 | Doylestown 115kV: Cut in Switching Station (J1577 & J1607) | New three breaker ring bus switching station for J1577 (100 MW solar) and J1607 (25 MW battery) GIA projects on the Hardin West SS - Sheridan 115kV line section. | AR | GIP | [5 empty] | 2025-05-01 | 115 |  | 3797000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 50075 | Raun-Remsen 345 kV Structure Replacement | The project will replace some line structures on MidAmerican's Raun to Remsen 345 kV line. This project will increase the line rating of the Raun to Remsen 345 kV line. | IA | Other | Local Needs |  |  |  |  | 2025-06-01 | 345 |  | 700000
MTEP24 | South | CLECO POWER LLC | 50011 | WeeksIsland Sub | Tap the existing Ivanhoe to Bayou Warehouse 138 kV line with a new 3 breaker ring substation 2 miles form Ivanhoe to serve a new industrial load. | LA | Other | Local Reliability | New industrial load requiring substation at Weeks Island | New Industrial Load |  |  | 2025-05-16 | 138 |  | 21224064 | Labeled Local Reliability but desc says "serve a new industrial load". Tap Ivanhoe-Bayou Warehouse 138kV for industrial customer
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25355 | Replace Northwest 138 kV Breakers | Replace 4 138 kV breakers at Northwest. Breakers #1, #4, #21, and #22. | IN | Other | Age and Condition |  |  |  |  | 2025-05-21 | 138 |  | 3600000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25354 | Replace Parker 138 kV Breakers | Replace 3 138 kV breakers at Parker. Breakers #1, #2, and #3. | IN | Other | Age and Condition |  |  |  |  | 2025-05-21 | 138 |  | 2700000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25402 | Replace Petersburg 138 kV #4 Breaker | Replace 1 138 kV breaker at Petersburg. Breaker #4. | IN | Other | Age and Condition |  |  |  |  | 2025-05-28 | 138 |  | 900000
MTEP24 | East | METC | 24515 | J1553 Generator Interconnection TOIF | Install required entrance structures and 138 kV disconnect switch at the METC Bingham Substation. | MI | GIP | [5 empty] | 2025-05-30 | 138
MTEP24 | East | METC | 24535 | J1553 Generator Interconnection Network Upgrades | Extend White Bus and move capacitor to make room for a third row at Bingham. Add Row 4, install 2-138 kV breakers and associated disconnects rated at 40 kA. Re-terminate the Cornell circuit at position WM4. Complete row 8, install 2-138 kV breakers and associated disconnects rated at 40 kA. | MI | GIP | [5 empty] | 2025-05-30 | 138 |  | 6200531
MTEP24 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 25080 | J1323 J1392 Network Upgrades | Relocate one existing 138kV line, create new position on LaGrange ring bus for generating lead line, replace control enclosure | IN | GIP | [5 empty] | 2025-06-01 | 138 |  | 5431638
MTEP24 | Central | AMEREN ILLINOIS | 25153 | New Moyer 138 kV Ring Bus for One Earth Energy Interconnection | This project will interconnect the One Earth Energy 30 MW ethanol plant. It will construct a new 138 kV substation called Moyer and a new AIC 138/12 kV substation called Gibson City One Earth. | IL | Other | Load Growth |  | Ethanol Plant |  | 30 | 2025-06-01 | 138 |  | 16700000 | One Earth Energy 30MW ethanol plant interconnection (AmerenIL)
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25293 | 0725 Tracy Switching Station to 5535 Str 191 Rebuild | Rebuild 1 mile 69 kV with new structures, new OPGW shield wire, and new conductor. | MN | Other | Age and Condition |  |  |  |  | 2024-12-31 | 69 |  | 750000
MTEP24 | West | GREAT RIVER ENERGY | 50101 | Hodges Substation Tap | Install a 3-way manual load break 115 kV, 2000 A switch on GRE’s Walden – Morris 115 kV line (near structure 89) and construct about 2 spans of 115 kV line with 477 ACSR conductor to the high side of Agralite’s new Hodges area distribution substation. Install metering/telecom and a new EEE for the distribution substation. | MN | Other | Load Growth |  |  |  |  | 2025-07-31 | 115 |  | 750116
MTEP24 | Central | AMEREN MISSOURI | 25225 | Maurer Lake 161 Aging Infrastructure | Replace breaker H9 Bus Tie (G735) and associated switches (G734 and G736) Add disconnect switch and breaker to XFMR 1 and 2 | MO | Other | Local Reliability |  |  |  |  | 2025-06-01 | 161 |  | 4000000
MTEP24 | South | ENTERGY SERVICES, LLC. | 25465 | Paincourtville 115 kV Capacitor Bank Split | Split the current Paincourtville 115 kV 32.4 MVAR capacitor bank into two smaller banks, by reducing the size of the current bank and installing a second smaller bank, | LA | BRP | [5 empty] | 2025-06-01 | 115 |  | 4400000
MTEP24 | South | ENTERGY SERVICES, LLC. | 25480 | Port Hudson 230-138 kV AT4 & 5 SPOF | Ensure Port Hudson 230/138 kV AT4 and AT5 both have redundant high-speed protection. | LA | BRP | [5 empty] | 2025-06-01 | 230 |  | 4400000
MTEP24 | West | MINNESOTA POWER INC. | 20030 | LSPI Cap Bank Asset Renewal | Replace the problematic LSPI capacitor bank with capacitor cans that are the new standard size. | MN | Other | Age and Condition |  |  |  |  | 2024-12-31 | 115 |  | 800000
MTEP24 | West | OTTER TAIL POWER COMPANY | 50007 | OTP Omemee Rebuild 41.6 kV Line | Rebuild and relocate 41.6 kV line between Rugby 41.6 kV and Bottineau 41.6 kV. | ND | Other | Local Reliability |  |  |  |  | 2025-11-01 | 42 |  | 800000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25367 | New 138 kV Hawthorne Substation | New 138 kV 3 breaker, 2 40 MVA transformer straight-bus substation to serve customer load. Looped-in on 132-28 Prospect to Ford line. | IN | Other | Load Growth |  |  |  | 40 MVA | 2025-06-25 | 138 |  | 15000000
MTEP24 | West | OTTER TAIL POWER COMPANY | 50005 | OTP Donaldson 41.6 kV CB 215 Reconductor | Rebuild 41.6 kV line between Donaldson 41.6 kV and Drayton 41.6 kV. | MN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 42 |  | 800000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 50002 | Overstress Breaker Replacement | End of Life replacement and upgrade of breakers identified in MTEP23 Short-Circuit Analysis. | MN | Other | Age and Condition |  |  |  |  | 2026-05-01 | 115 |  | 800000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25467 | Substation P Iowa City Transformer Breakers | Add two 161 kV breakers at Substation P to separate the distribution transformers from the substation's line terminals | IA | Other | Local Reliability |  |  |  |  | 2025-12-01 | 161 |  | 900000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25370 | W3401 Insulator Replacement And Refurb | W3401 line refurb on 18.8 miles from Alma Center to Blair. | WI | Other | Age and Condition |  |  |  |  | 2024-12-31 | 69 |  | 1000000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25375 | W3415 EGA-DUR-ARK Insulator Replacement and Refurbishment | Line W3415 refurb and insulator replacement on 5.9 miles between Eau Galle - Durand and 5.5 miles between Durand - Arkansas. | WI | Other | Age and Condition |  |  |  |  | 2025-12-01 | 69 |  | 1000000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25273 | Bateman Substation Breaker Upgrade | Project to convert 69kV switch 4E442 to a circuit breaker and upgrade and bus relaying scheme at the Bateman substation. | WI | Other | Local Reliability |  |  |  |  | 2025-12-31 | 69 |  | 1000000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25401 | New 138-34.5 kV Northwest Transformer | New 138/34.5 kV 66.7 MVA transformer and 1 new 138 kV east bus tie breaker to create double breaker position at Northwest | IN | Other | Local Reliability |  |  |  |  | 2025-06-30 | 138 |  | 4000000
MTEP24 | South | CLECO POWER LLC | 50087 | J1673&J1759 Ft. Jessup Substation | Tap the future Marthaville to Belmont 230 kv line 6.8 miles from Marthaville for a new Ft. Jessup 230 kV substation. This substation will serve as the POI for J1673 and J1759 generators. | LA | GIP | [5 empty] | 2025-07-01 | 230 |  | 4070667
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25336 | Greensburg Washington St. 69kV Breaker upgrades | Replace (3) 69kV oil CBs with SF6 gas circuit breakers (GCBs) – 6937, 6964, 69119; replace relays on (3) 69kV lines; replace (12) 69kV switches. | IN | Other | Local Reliability |  |  |  |  | 2025-07-24 | 69 |  | 2141580
MTEP24 | West | MINNESOTA POWER INC. | 25311 | Stinson PST Retirement | Retire Stinson Phase Shifting Transformer (PST) due to age and increased maintenance costs. | WI | Other | Age and Condition |  |  |  |  | 2028-12-31 | 115 |  | 1000000
MTEP24 | West | ITC MIDWEST | 25251 | J1734 GIA NU Wever 161 kV Bus Expansion | ITC Midwest will add a 161 kV breaker to expand the Wever 161 kV bus to allow for the interconnection of J1734 and the new 161 kV gen-tie line. | IA | GIP | [5 empty] | 2025-07-31 | 161 |  | 1086141
MTEP24 | East | METC | 24440 | Van Tyle - J1603 NU - Install breaker 4B7 and switches 4M5 and 4B3 | Install breaker 4B7 and switches 4M5 and 4B3 | MI | GIP | [5 empty] | 2025-08-01 | 138 |  | 1122500
MTEP24 | East | METC | 24442 | Van Tyle-J1603 TOIF-Install position BM4 and switch 177 | Install BM4 line entrance structure and disconnect switch 177 for generator interconnection. | MI | GIP | [5 empty] | 2025-08-01 | 138
MTEP24 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 24939 | J1407 Network Upgrades | South Valparaiso substation 138kV yard will be expanded by one breaker to accommodate the Generating Facility lead line. Additionally, existing 13820 terminal pole 1008845 will be relocated | IN | GIP | [5 empty] | 2025-08-01 | 138 |  | 5401744
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25521 | J992 Appleseed Solar POI | J992 - 200MW AppleSeed Solar (NextERA) Gen Intercon - Expand Walton 230 kV ring bus and add line terminal | IN | GIP | [5 empty] | 2025-08-15 | 230 |  | 7327980
MTEP24 | South | CLECO POWER LLC | 25313 | J1599 Daspit Substation | Build a new Daspit Substation on the Hopkins and Morbihan 138 kV line to allow J1599 Solar Generator | LA | GIP | [5 empty] | 2025-09-01 | 138 |  | 16236000
MTEP24 | West | GREAT RIVER ENERGY | 25391 | Mud Lake to Riverton 230 kV Upgrade | The Riverton – Mud Lake “MR” 230 kV line is temperature rated at 189 degrees and is limited by seven spans. Make the necessary upgrades, six H-frame pole replacements, to get the Riverton – Mud Lake “MR” 230 kV line up to 212°F operating temperature and achieve a rating of 384.8/515.8 (summer/winter) MVA. | MN | Other | Local Reliability |  |  |  |  | 2027-06-01 | 230 |  | 1146876
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25335 | Add new Thorntown 69kV ckt and rebuild 6943 ckt | Rebuild 6943 line from Thorntown Substation to Lebanon Substation with 954ACSR@120C - approx. 10 miles; Rebuild the double circuit section of 69134/6943; upgrade line terminals at Thorntown and Lebanon Enterprise; Thorntown substation: Add a 69kV 2000 amp line terminal and line to existing radial line off of the 6943 serving the Boone County REMC Pike 69kV substation (and new proposed WVPA Eli Lilly load). | IN | Other | Load Growth |  |  |  |  | 2025-09-04 | 69 |  | 31200000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25385 | Replace Petersburg 345 kV Breakers | Replace 6 345 kV breakers at Petersburg. Breakers #3A, #3B, #3C, #4A, #4B, and #4C. | IN | Other | Age and Condition |  |  |  |  | 2025-09-11 | 138 |  | 5400000
MTEP24 | West | GREAT RIVER ENERGY | 25405 | Lakeville Area Projects | GRE will be adding a second radial circuit tap (double circuit) into Lakeville substation for the addition of a second transformer and switchgear to Lakeville substation. Dakota Electric Association (DEA) is responsible for the high side structures and associated transmission side substation equipment. | MN | Other | Local Reliability |  |  |  |  | 2025-09-30 | 115 |  | 1200000
MTEP24 | South | ENTERGY SERVICES, LLC. | 50043 | J1834 NRIS/ERIS Sabine to Neches L5 & L-172 upgrade to Double Bus Double Breaker | Add two additional 138 kV breakers at the Sabine 138 kV station to convert the Sabine to Neches lines to double bus double breaker configuration. | TX | GIP | [5 empty] | 2025-09-30 | 138 |  | 10000000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25542 | J1357 Williams Power POI | J1357 - 150MW Williams Power - battery storage: Madison 138 - add breaker (straight bus config) and line terminal | IN | GIP | [5 empty] | 2025-09-30 | 138 |  | 5680572
MTEP24 | East | METC | 25196 | Beecher-Dowling Junction Sag Remediation (J1550, J1635, J1658) - Network Upgrade | Remediate the Beecher-Dowling Junction sag limit to achieve a rating of at least 219 MVA SN and 249 MVA WN. | MI | GIP | [5 empty] | 2025-09-30 | 138 |  | 258750
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25464 | CBEC Upgrade Sync Check Relaying | Retire existing sync check relaying panel at CBEC and incorporate sync check into existing relays or replace relays where necessary | IA | Other | Local Reliability |  |  |  |  | 2025-12-01 | 345 |  | 1200000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25089 | New Harmony 69/12kV T2 and CB's Replacement | Replacement of transformer T2 and breakers at New Harmony substation due to age and condition | IN | Other | Age and Condition |  |  |  |  | 2025-10-01 | 69 |  | 5300000
MTEP24 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25416 | Lucedale 69kV Switching Station | In order to serve the member delivery points of North Lucedale and South Lucedale economically and reliably a new 69kV switching will be constructed at near Lucedale, MS. | MS | Other | Load Growth |  |  |  |  | 2025-10-01 | 69 |  | 2860000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25347 | WVPA Lebanon Industrial 69/12kV Sub | WVPA Lebanon Industrial 69kV Sub - Construct a new 69/12kV substation to serve a new Eli Lilly facility, the substation will have a high side 69kV ring bus | IN | Other | Load Growth |  | Pharmaceutical (Eli Lilly) |  |  | 2025-10-01 | 69 |  | 12215000 | WVPA Lebanon Industrial sub for new Eli Lilly facility
MTEP24 | South | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | 50099 | Lewisville West Capacity Increase | Add 2nd transformer at existing Lewisville West substation. New transformer will be 115/69 kV, 100 MVA. | AR | Other | Load Growth | Lewisville West Capacity Increase EPR | Load Growth |  | 100 MVA | 2025-10-01 | 115 |  | 4500000 | AECC EPR $5M
MTEP24 | Central | HOOSIER ENERGY | 25303 | HE_J1027_Ratts2_Solar | Network Upgrades include upgrades to bay 4 at Petersburg Substation in order to tie in the IC’s new generator lead line from the solar PV plant. Switches 29-463 and 29-461 will be replaced as well as all existing conductor. All existing structures and breaker 52-462 will be reused. New CTs, CCVTs, and arresters will be added on the line side of switch 29-463. | IN | GIP | [5 empty] | 2025-10-01 | 161 |  | 3636500
MTEP24 | West | DAIRYLAND POWER COOPERATIVE | 25505 | J1314/S1039 Generation Interconnection Upgrades | J1314/S1039 will require substation modifications at the existing Apple River 161 kV substation for the interconnection | WI | GIP | [5 empty] | 2025-06-30 | 161 |  | 1263371
MTEP24 | West | GREAT RIVER ENERGY | 25388 | Cleveland Breaker Replacement | Cleveland – replace breaker 4S100 and 4S99. Replace GE JVS-350 PTs and any other type PTs in poor condition (verify during scoping which PTs are this type, possibly replace all 5 depending on age/condition/type – Maximo data is incomplete). Add missing 69 kV breaker to complete topology. | MN | Other | Local Reliability |  |  |  |  | 2025-10-01 | 69 |  | 1311954
MTEP24 | West | GREAT RIVER ENERGY | 25373 | Salem Breaker Station | Expand the existing Salem transmission site to include line breakers for each of the three lines that tie into the site. Boy River, circuit to Deer River and Blind Lake circuit would have breakers. | MN | Other | Local Reliability |  |  |  |  | 2025-10-17 | 69 |  | 1342821
MTEP24 | West | GREAT RIVER ENERGY | 25453 | Medina Breaker Addition and Replacement | Replace 55WB2 and breaker addition | MN | Other | Age and Condition |  |  |  |  | 2026-11-30 | 115 |  | 1400052
MTEP24 | West | OTTER TAIL POWER COMPANY | 50006 | OTP Marvin - Corona Area 41.6 kV Rebuild | Rebuild 41.6 kV line between Wilmot 41.6 kV and Summit 41.6 kV in the Marvin/Corona 41.6 kV area. | SD | Other | Local Reliability |  |  |  |  | 2025-12-31 | 42 |  | 1500000
MTEP24 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 25021 | J1387 Network Upgrades | Network Upgrades work consists of: • installation of three (3) new class H1direct-embed wood poles, • 336 kcmil ‘Merlin’ ACSR conductor to interconnect the 6958 line into the new 69kV tap substation’s • two (2) 69kV 1200 ampere disconnect switches. Transmission Owner will also install direct transfer trip relay equipment at Transmission Owner’s Thayer substation on 6958 breaker to communicate with the new station. | IN | GIP | [5 empty] | 2025-10-16 | 69 |  | 1066894
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25090 | Northwest CB's Replacement | Replacement of breakers at Northwest substation due to age and condition | IN | Other | Age and Condition |  |  |  |  | 2025-10-17 | 138 |  | 5000000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 50068 | HE Taylorsville 69/12kV Sub | HE Taylorsville 69/12kV Sub: construct new 22MVA sub at the same location as existing HE Taylorsville sub; to be served radially off the DEI 69146 ckt.; load at HE Taylorsville will be transferred from Edinburgh sub 69/12kV bank #2 = 3MW+/- | IN | Other | Load Growth |  |  |  | 3 | 2025-10-17 | 69 |  | 900000
MTEP24 | West | ITC MIDWEST | 25204 | J1365 GIA NU Traer 161 kV Ring Bus Expansion | A new 161 kV, breaker, and ring-bus expansion at the station will be constructed for J1365. | IA | GIP | [5 empty] | 2024-07-26 | 161 |  | 1574200
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25463 | Glenwood to Rushville 69kV Line Rebuild | TDSIC 69kV Line Rebuild: Glenwood -(6920 / 5.72 mi.)- Rushville East -(69192 / 1.85 mi.)- Rushville; replace approx. 150 single poles; conductor size = 477ACSR45X7@120C; replace (2) line switches at Glenwood Jct; reroute 6920 around Glenwood area | IN | Other | Age and Condition |  |  |  |  | 2025-10-31 | 69 |  | 24685000
MTEP24 | East | METC | 25245 | Coldwater-Ash Road Junction Sag Remediation (J1550) - Network Upgrade | Remediate the Coldwater-Ash Road Junction sag limit to achieve a minimum rating of 200 MVA Summer Emergency. | MI | GIP | [5 empty] | 2025-10-31 | 138 |  | 335000
MTEP24 | West | MINNKOTA POWER COOPERATIVE, INC | 24413 | Richer-Littlefork 230 kV Line Rebuild | 230 kV transmission structure replacement from Richer to Littlefork. | MN | Other | Age and Condition |  |  |  |  | 2025-02-28 | 230 |  | 1590000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25411 | Second 69 kV Line into Rock Valley Town Substation | Construct a second 69 kV line into Rock Valley Town Substation and retire a section of existing Rock Valley Town Tap-NIPCO K218 69 kV line | IA | Other | Load Growth |  |  |  |  | 2027-12-01 | 69 |  | 1600000
MTEP24 | Central | HOOSIER ENERGY | 25280 | HE_J1354_Decatur_Battery | Decatur County 138kV Switching Station upgrades to accommodate interconnection of Decatur Battery Storage project J1354. Modifications in the switching station will include relocation of the capacitor bank to make available a terminal position for connection of the new transmission line from the battery storage facility. Upgrades also include CCVTs, CTs, Disconnect Switches, Arrestors, etc. | IN | GIP | [5 empty] | 2025-11-15 | 138 |  | 3248872
MTEP24 | East | ITC | 24461 | Grassmere - J1525 Gen Network Upgrade | Install breakers AT, BF, CT and CM and install switches AV, BD, CV, CR, CO, and CK. | MI | GIP | [5 empty] | 2025-11-17 | 345 |  | 7602430
MTEP24 | East | ITC | 24462 | Grassmere - J1525 TOIF - Install Position CQ and switch CQA | Install a CQ line entrance structure and disconnect switch CQA for generator interconnection. | MI | GIP | [5 empty] | 2025-11-17 | 345
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25466 | Maynard Substation: Replace Three 69 kV Breakers and Relaying | Replace oil breakers, bus differential relaying, and breaker failure relaying. | IA | Other | Age and Condition |  |  |  |  | 2029-12-31 | 69 |  | 1600000
MTEP24 | South | ENTERGY ARKANSAS, LLC | 25472 | 2025 EAL Asset Renewal Program | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2025 asset renewal plans have not yet been finalized. | AR | Other | Age and Condition |  |  |  |  | 2025-12-01 | 161 |  | 32893800
MTEP24 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25417 | Line 34 Rebuild | To ensure reliable service a complete rebuild of L34 (Lucedale – Rocky Creek 7.97 miles) is recommended. | MS | Other | Age and Condition |  |  |  |  | 2025-12-01 | 69 |  | 5000000
MTEP24 | West | GREAT RIVER ENERGY | 25421 | Sand Lake Area Projects | Add approximately .75 mile to the Sand Lake tap (LP Line) and add new metering to a new substation site. | MN | Other | Age and Condition |  |  |  |  | 2024-11-20 | 69 |  | 1630051
MTEP24 | Central | AMEREN ILLINOIS | 22951 | Upgrade Rantoul 138 kV substation | Reconfigure 138kV into ring bus | IL | Other | Age and Condition |  |  |  |  | 2025-12-01 | 138 |  | 7100000
MTEP24 | Central | AMEREN ILLINOIS | 25091 | Replace 345/138kV Transformer 2 at Norris City North | Replace the existing Transformer 2 at Norris City North with a new 345/138kV 700 MVA unit | IL | Other | Age and Condition |  |  |  |  | 2025-12-01 | 345 |  | 7000000
MTEP24 | Central | AMEREN ILLINOIS | 25193 | Turkey Hill - Transformer 1 Replacement | Replace Turkey Hill XFMR 1 with a new 345/138kV 700 MVA transformer. | IL | Other | Age and Condition |  |  |  |  | 2025-12-01 | 345 |  | 6700000
MTEP24 | Central | AMEREN ILLINOIS | 50148 | Havana-Puro 138 kV1422 MPFCA | Rebuild the 138 kV Havana-Puro 1422 transmission line with new wood H frame structures, steel structures, OPGW and 1200 A conductor. Affected J#s include: J1408, J1453, J1454 | MO | GIP | [5 empty] | 2025-12-01 | 138 |  | 13200000
MTEP24 | West | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | 25199 | Fairmont 10th St 69kV Substation Modernization | Current breakers were installed in 1985, and they have become unreliable and difficult to maintain with their age. Along with these breakers, the associated switches and relays will also be replaced with newer and more reliable equipment. The new equipment includes new PTs, arresters, and new solid-state relay panels. | MN | Other | Age and Condition |  |  |  |  | 2025-02-01 | 69000 |  | 1800000
MTEP24 | Central | AMEREN ILLINOIS | 25043 | Moose 138 kV Substation for Albion PV1 (J1422) | This project will install a new 138 kV line position to serve as the Point of Interconnection for Albion PV 1, LLC under GIA J1422, within the new 3-position ring bus named Moose. | IL | GIP | [5 empty] | 2025-12-01 | 138 |  | 8400000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25545 | J1390 Lowland Solar Park POI | J1390 - 150MW Lowland Solar Park - Oversite of Self-Build Switching Station by developer (3-CB ring); inserted in the 23004 Gallagher to Columbus ckt; includes relay upgrades on the remote ends, 23004 loop-through line work; and reroute of the 23005 around the new switching station | IN | GIP | [5 empty] | 2025-12-01 | 230 |  | 6843406
MTEP24 | Central | CITY OF HENDERSON, KY, UTILITY COMMISSION, DBA HENDERSON MUNICIPAL POWER AND LIGHT (BA) | 25499 | Reconductor HMPL Sub 2 to HMPL Sub 5 69kV line | Reconductor line from HMPL Sub 2 to HMPL Sub 5 69 kV line | KY | Other | Age and Condition |  |  |  |  | 2025-12-01 | 69 |  | 1036568
MTEP24 | West | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | 25260 | Loon Lake 69kV Substation Modernization | Current breakers were installed in 1985, and they have become unreliable and difficult to maintain with their age. Along with these breakers, the associated switches and relays will also be replaced with newer and more reliable equipment. The new equipment includes new PTs, arresters, and new solid-state relay panels. | MN | Other | Age and Condition |  |  |  |  | 2025-02-01 | 69000 |  | 1800000
MTEP24 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25540 | State Line 69kV Delivery Point | In order to serve the member delivery point, tap L32 (State Line - Leakesville) with a 69kV Goab and construct a new line to the delivery point. | MS | Other | Load Growth |  |  |  |  | 2025-12-01 | 69 |  | 725000
MTEP24 | South | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | 50164 | Woodberry Load Addition | AECC has received a request for a 26 MW load addition served out of the Summerville delivery point. This new load will require a 69kV substation to be built off of the 69kV Summerville system as well as load additions to existing substations served out of Summerville. Two (2) 15.3 MVAR capacitor banks will also be needed for voltage support during contingencies. | AR | Other | Load Growth | Woodberry Load Addition EPR | Load Growth |  | 26 | 2025-12-01 | 69 |  | 10200000 | AECC EPR $10M
MTEP24 | Central | AMEREN ILLINOIS | 23151 | Rebuild East Quincy-Hamilton-4 138 kV line | Rebuild the 30.5 mile East Quincy-Hamilton-4 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL | Other | Local Reliability |  |  |  |  | 2025-12-01 | 138 |  | 46000000
MTEP24 | Central | AMEREN ILLINOIS | 24738 | Rebuild Hull-Herleman-1682 138 kV Transmission Line | Rebuild the Hull-Herleman-1682 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL | Other | Local Reliability |  |  |  |  | 2025-12-01 | 138 |  | 24000000
MTEP24 | Central | AMEREN ILLINOIS | 24737 | Rebuild Woodhall-Hallock-1570 138 kV Transmission Line | Rebuild the Woodhall-Hallock-1570 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL | Other | Local Reliability |  |  |  |  | 2025-12-01 | 138 |  | 16000000
MTEP24 | Central | AMEREN MISSOURI | 25349 | Labadie-Montgomery 345kV Aging Infrastructure | Address aging infrastructure issues on the Labadie-Montgomery 345kV line. | MO | Other | Local Reliability |  |  |  |  | 2025-12-01 | 345 |  | 10500000
MTEP24 | South | ENTERGY ARKANSAS, LLC | 25481 | Arklahoma 115kV Bus Relay Improvement SPOF | Construct redundant high speed protection for the Arklahoma 115kV bus. All elements of the auto protection scheme should have high-speed redundancy including redundant DC supply such that loss of any component of the auto protection scheme would not result in delayed fault clearing. All single points of failure should be avoided, and the following should be accounted for: Independent and redundant communication for each relay. Dual station batteries with separate DC system feeding each relay or monitoring sufficient to FERC 754 guidelines. Independent CT and PT winding inputs for each relay. | AR | Other | Local Reliability |  |  |  |  | 2025-12-01 | 115 |  | 2525674
MTEP24 | South | ENTERGY ARKANSAS, LLC | 25485 | Champs 115kV: New Substation Phase 1 | Build a new 115kV operating and transfer bus substation with one 40 MVA 115/13.8kV transformer in Maumelle, AR. | AR | Other | Local Reliability |  |  |  |  | 2025-12-01 | 115 |  | 10804929
MTEP24 | Central | AMEREN ILLINOIS | 24717 | Rebuild Edwards-Keystone-1397 138 kV Transmission Line | Rebuild Edwards-Keystone-1397 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL | Other | Local Reliability |  |  |  |  | 2025-12-01 | 138 |  | 5500000
MTEP24 | Central | AMEREN TRANSMISSION COMPANY OF ILLINOIS | 25092 | Zachary 161 kV BAAH Addition | Add six breakers at Zachary 161 kV station to complete a breaker-and-a-half arrangement | MO | Other | Local Reliability |  |  |  |  | 2025-12-01 | 161 |  | 3000000
MTEP24 | South | ENTERGY ARKANSAS, LLC | 25487 | Frazier Pike 115kV: New Substation | Build a new 115kV operating and transfer bus substation with a single 50 MVA 115/13.8kV transformer that will include a 0.5 mile in and out 115kV transmission line in Little Rock, AR. | AR | Other | Local Reliability |  |  |  |  | 2025-12-01 | 115 |  | 18007302
MTEP24 | Central | AMEREN ILLINOIS | 24739 | Rebuild Greenback-Lanesville 138 kV Line | Rebuild the Greenback-Lanesville-1314 138 kV line from Str. 159-Lanesville Substation with conductors capable of carrying 2000 amps under Summer Emergency conditions at 2 OPGW's. | IL | Other | Local Reliability |  |  |  |  | 2025-12-01 | 138 |  | 2200000
MTEP24 | West | GREAT RIVER ENERGY | 25452 | Dickinson Breaker Replacement | Replace 62WB1, WB2 and WB4 and replace BPRO | MN | Other | Age and Condition |  |  |  |  | 2027-06-01 | 115 |  | 1845219
MTEP24 | Central | AMEREN TRANSMISSION COMPANY OF ILLINOIS | 25093 | Zachary 161 kV Terminal Addition | Add one 161 kV breaker and line terminal for Locust Creek (AECI) | MO | Other | Local Reliability |  |  |  |  | 2025-12-01 | 161 |  | 1500000
MTEP24 | West | ITC MIDWEST | 25306 | ITCM Burlington 4th Street Control Enclosure & 69 kV Tie Breaker Addition | IPL has notified ITC that they will be rebuilding their Burlington 4th Street sub and installing a 2nd 20/26/33 MVA transformer; as well as, replacing the existing transformer, T1, with a new one of the same size. As part of this, ITC will need to install a new bus tie breaker at the Burlington 4th Street sub. In addition, ITC will build a new control enclosure with all new relays and SCADA equipment. All new ITC owned equipment is to be rated minimum 1200 amps summer normal rating. | IA | Other | Load Growth |  |  |  | 33 MVA | 2026-12-31 | 69 |  | 1984333
MTEP24 | West | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | 25446 | Willmar System Upgrades | Willmar is upgrading SCADA, relays, RTUs, and replacing 69 kV poles due to age. | MN | Other | Age and Condition |  |  |  |  | 2025-12-05 | 230 |  | 2000000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 50020 | 0711 Redwing - Str 11 Rebuild | Rebuild 1 mile 69 kV with new structures, new OPGW shield wire, and new conductor. | MN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 2000000
MTEP24 | Central | AMEREN ILLINOIS | 24987 | Mason-IL 138 kV Upgrade for Glacier Sands Wind II (J1454) | MISO project J1454, a 40.90 MW Wind Generating Facility, will interconnect to the Ameren Illinois Transmission System. Project No. J1454 is an expansion of J1055 Generating Facility. Transmission Owner will modify the 138 kV bus at its existing Mason substation | IL | GIP | [5 empty] | 2025-12-01 | 138 |  | 100000
MTEP24 | Central | AMEREN MISSOURI | 25039 | Taum Sauk 138 kV Upgrade for 60MW Hydro (J1213) | MISO project J1213, will add 60 MW to the existing Hydro Energy Generating Facility, Transmission Owner will modify the 138 kV bus at its existing Taum Sauk 138 kV substation. | MO | GIP | [5 empty] | 2025-12-01 | 138 |  | 100000
MTEP24 | Central | BIG RIVERS ELECTRIC CORPORATION | 25081 | J1450 Webster County Switching Station for POI | Construction of a new switching station called Webster County to accommodate a POI per the executed GIA for project J1450. This will be constructed 4.23 miles from BREC's existing Hopkins County substation on the existing Hopkins-Reid EHV 161 kV line. OPGW will be ran for the length of the existing Hopkins-Reid EHV 161 kV line for remote end communications. Relaying will be upgraded at both Hopkins and Reid EHV. | KY | GIP | [5 empty] | 2025-12-01 | 161
MTEP24 | Central | BIG RIVERS ELECTRIC CORPORATION | 25120 | J1466 Reid EHV 161 kV Terminal Addition | Add a 161 kV terminal for POI for project J1466, which has an executed GIA. | KY | GIP | [5 empty] | 2025-12-01 | 161
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50109 | J1814 Nordic SS Network Upgrades and Interconnection Facilities | J1814 is a solar facility located in Dickinson County, MI. | MI | GIP | [5 empty] | 2028-09-10 | 138 |  | 2150000
MTEP24 | West | ITC MIDWEST | 25253 | ITCM Flint Ridge Control Enclosure & 69 kV Tie Breaker Addition | IPL has notified ITCM that they will be rebuilding their Flint Ridge sub and installing a 2nd 20/26/33 MVA transformer. This rebuild will also be replacing the existing transformer, T1, with a new one of the same size. As part of this, ITC will need to install a new bus tie breaker at the Flint Ridge sub. In addition, ITC will build a new control enclosure with all new relays and SCADA equipment. All new ITC owned equipment is to be rated minimum 1200 amps summer normal rating. | IA | Other | Load Growth |  |  |  | 33 MVA | 2026-12-31 | 69 |  | 2160171
MTEP24 | West | GREAT RIVER ENERGY | 23851 | Stanton Breaker Replacement | Replace Stanton oil breakers 31RB1, 2, 3, 4 & 6. | MN | Other | Age and Condition |  |  |  |  | 2026-11-05 | 230 |  | 2179821
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25294 | Reinforce Tracy Switching Station TR01 | Upgrade existing transformer at Tracy Switching Station to 14 MVA. Convert town of Tracy to 13.8 kV and retire Tracy (TRA) substation. | MN | Other | Local Reliability |  |  |  |  | 2025-10-15 | 69 |  | 2200000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25386 | Replace North 138 kV Breakers | Replace 2 138 kV breakers at North. Breakers #3 and #4. | IN | Other | Age and Condition |  |  |  |  | 2025-12-22 | 138 |  | 1800000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25389 | Replace Northeast 138 kV Breakers | Replace 2 138 kV breakers at Northeast. Breakers #1 and #3. | IN | Other | Age and Condition |  |  |  |  | 2025-12-22 | 138 |  | 1800000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25390 | Replace Brookwood 138 kV Breakers | Replace 2 138 kV breakers at Brookwood. Breakers #1 and #2. | IN | Other | Age and Condition |  |  |  |  | 2025-12-22 | 138 |  | 1800000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25387 | Replace Prospect 138 kV #2 Breaker | Replace 1 138 kV breaker at Prospect. Breaker #2. | IN | Other | Age and Condition |  |  |  |  | 2025-12-22 | 138 |  | 900000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25334 | Kokomo Webster St Ckt Brkr Replacements | Kokomo Webster St Ckt Brkr Replacements - 230kV: replace (2) oil CBs (23022-20 and 230B2-22) and their disconnect switches (motorize); replace all 230kV relays; install SCADA controlled line disconnect switches (23016, 23020 & 23022) and upgrade wave traps as needed; Upgrade RTU and DC power supply systems; 69kV: Replace (4) oil CBs (69173, 69174, 6912-1 and 69230-2) and their disconnect switches as needed; replace all 69kV relays | IN | Other | Local Reliability |  |  |  |  | 2025-12-22 | 230 |  | 6300000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25414 | Rebuild 138kV Line from Speed to Jeffersonville | (1) Rebuild entire 13898 ckt from Speed to Jeffersonville with 954ACSS@200C; (2) upgrade very short 13882 tie with LGE at Jeffersonville to 954ACSS@200C and have LGE add ATO switches at the junction just outside Jeffersonville sub; (3) rebuild 6955 ckt where double circuited with 13898 ckt; (4) upgrade line terminals and substation buses as needed | IN | BRP | [5 empty] | 2025-12-31 | 138 |  | 38300000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25447 | Forest & Vermont Breaker Replacements | Replace four (4) overdutied 69 kV breakers | IA | Other | Local Reliability |  |  |  |  | 2025-12-01 | 69 |  | 2400000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50091 | Milwaukee County, New DIC | ATC will tap 138 kV line 836 (Oak Creek-Oakview) to serve new interconnection request. | WI | Other | Load Growth | Milwaukee County New DIC expansion | Data Center/DIC Campus | Y |  | 2027-06-01 | 138 |  | 2600000 | ATC $2.6M
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50108 | J1573 Plover SS Network Upgrades and Interconnection Facilities | J1573 is a solar facility located in Portage County, WI. | WI | GIP | [5 empty] | 2028-09-10 | 115 |  | 2633000
MTEP24 | West | ITC MIDWEST | 25241 | ITCM Newton 8th St Control Enclosure, Relay, and SCADA Replacement | Replace the existing relaying and SCADA at Leon by ITC installing a new ITC owned control building. IPL owns and maintains this building. Separating the buildings by owner lines up with the current substation standards. | IA | Other | Age and Condition |  |  |  |  | 2026-12-31 | 161 |  | 2655119
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25431 | Dakota Dunes: Install 69 kV Capacitor Bank | Install a 69 kV, 14.7 MVAR capacitor bank at Dakota Dunes Substation | IA | Other | Local Reliability |  |  |  |  | 2026-06-01 | 69 |  | 2800000
MTEP24 | South | ENTERGY SERVICES, LLC. | 25484 | 2025 ETI Asset Renewal Program | This project is for the ETI Asset Renewal Program that will be executed in 2025. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2025 asset renewal plans have not yet been finalized | TX | Other | Age and Condition |  |  |  |  | 2025-12-31 | 500 |  | 38300000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25151 | Y67/Z78 Junction - Jasper South Rebuild | Replacement of poles from Y67/Z78 Junction to Jasper South (no conductor change) and several switches. | IN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 69 |  | 10000000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25152 | Z99 AB Brown - Wolf Road Rebuild | Replacement of poles along Z99 from AB Brown to Wolf Road (no conductor change) | IN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 138 |  | 8500000
MTEP24 | West | ITC MIDWEST | 25307 | ITCM State Center Rural 69 kV Interconnection | IPL will construct a new 69/24.9kV - 10/12.5MVA w/ LTC substation, State Center Rural. This new substation is due to the 69kV conversion of the Maxwell North to Timbercreek line. ITC will install two 69kV line breakers in both directions from the sub, and tap and reroute the Nevada North-Timber Creek line in and out of the new State Center Rural sub. | IA | Other | Load Growth |  |  |  | 5 MVA | 2026-12-15 | 69 |  | 2910514
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25150 | Y52-2 Mackey - Oakland City Rebuild | Replacement of poles along Y52-2 due to age and condition (conductor no changing) | IN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 69 |  | 8000000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25441 | Z91-2 Pigeon Creek - Heidelbach Rebuild | Rebuilding ~2 miles of 138kV line from 795 to 954 | IN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 138 |  | 5500000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25149 | County Line 69/12kV T1 Replacement | Replacement of transformer T1 at County Line substation due to age and condition | IN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 69 |  | 3000000
MTEP24 | South | ENTERGY SERVICES, LLC. | 25482 | 2025 ELL Asset Renewal Program | This project is for the ELL Asset Renewal Program that will be executed in 2025. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2025 asset renewal plans have not yet been finalized | LA | Other | Age and Condition |  |  |  |  | 2025-12-31 | 500 |  | 87900000
MTEP24 | South | ENTERGY MISSISSIPPI, LLC. | 25486 | 2025 EML Asset Renewal Program | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2025 asset renewal plans have not yet been finalized. | MS | Other | Age and Condition |  |  |  |  | 2025-12-31 | 500 |  | 47800000
MTEP24 | South | ENTERGY SERVICES, LLC. | 25483 | 2025 ENOL Asset Renewal Program | This project is for the ENOL Asset Renewal Program that will be executed in 2025. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2025 asset renewal plans have not yet been finalized | LA | Other | Age and Condition |  |  |  |  | 2025-12-31 | 230 |  | 9600000
MTEP24 | East | METC | 24559 | J1658 Generator Interconnection TOIF | Install required line entrance structure and 138 kV disconnect at new Cronk Station. | MI | GIP | [5 empty] | 2025-12-31 | 138
MTEP24 | East | METC | 24561 | J1614 Generator Interconnection TOIF | Install required line entrance structures and disconnect at the new Aphis station. | MI | GIP | [5 empty] | 2025-12-31 | 138
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25331 | WVPA Blacketor 69/12kV Sub | WVPA Blacketor 69kV Sub - Construct a new 69/12kV substation to serve load fed from an existing meter point | IN | Other | Load Growth |  |  |  |  | 2025-12-31 | 69 |  | 8753000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 50014 | West Grand Add 161 kV Line Breakers | Install two 161 kV line breakers and associated relaying at West Grand Substation. | IA | Other | Load Growth |  |  |  |  | 2025-06-30 | 161 |  | 3000000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25379 | Rebuild Wabasha Substation | Rebuild Wabasha substation at a nearby location due to flooding concerns. | MN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 3000000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50136 | Baraboo SS, DIC, Substation Relocation | The LDC is planning to relocate the Baraboo substation from its current location to a nearby site. To accommodate this ATC will install 2x new T-Line structures and replace one T-Line structure to reroute the Kirkwood-Dam Heights 69kV (Y-75) line. This will require roughly 0.04 miles of new conductor. Additionally, a new 3 way tap structure to the new substation will be required. A new ATC control house will be required to retain supervisory control of the tap switches. Lastly, ATC to retire 9x T-Line poles and the substation equipment at the current Baraboo location. | WI | Other | Load Growth | Baraboo SS DIC Substation Relocation | Data Center/DIC Campus | Y |  | 2027-06-01 | 69 |  | 3000000 | ATC $3M
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25425 | Metro East Substation 161 kV line breakers | Install 161 kV line breakers and relaying | IA | Other | Local Reliability |  |  |  |  | 2027-12-01 | 161 |  | 3000000
MTEP24 | East | METC | 25500 | METC Line Relocation - 2025 | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI | Other | Local Needs |  |  |  |  | 2025-12-31 | 345 |  | 2500000
MTEP24 | East | ITC | 25478 | ITCT Line Relocation - 2025 | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI | Other | Local Needs |  |  |  |  | 2025-12-31 | 345 |  | 2500000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25408 | Fort Branch 69kV Capacitor Bank | Install 69kV 15.6MVAR capacitor bank at Fort Branch | IN | Other | Local Reliability |  |  |  |  | 2025-12-31 | 69 |  | 3000000
MTEP24 | West | GREAT RIVER ENERGY | 25454 | East Chain Tie Line Projects | Construct a tie line between East Chain municipal and GRE’s FE-WB (East Chain to Wilbert) line. | MN | Other | Local Reliability |  |  |  |  | 2028-10-06 | 69 |  | 3000000
MTEP24 | West | ITC MIDWEST | 25213 | ITC Midwest SCADA Controlled Motor Operated Switch Addition Program 2025 | ITC Midwest will add SCADA controlled motor operated switches on 69 kV lines that do not have existing remote sectionalizing capability and do not have any planned rebuilds. These 69 kV lines will be utilized to add SCADA controlled motor operated switches as part of an existing planned project to increase sectionalizing capability on the 69 kV system. ITC Midwest plans to install SCADA controlled motor operators on 3-5 lines/year as part of this program until existing circuits are brought up to ITC Midwest sectionalizing guidelines requirements. | IA; IL; MN | Other | Local Needs |  |  |  |  | 2025-12-31 | 69 |  | 3125000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50107 | J1513 Clintonville Swt St Network Upgrades and Interconnection Facilities | J1513 is a solar facility in Waupaca County, WI. | WI | GIP | [5 empty] | 2028-09-10 | 138 |  | 3168000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50120 | J1615 Morgan SS Network Upgrades and Interconnection Facilities | J1615 is a solar facility located in Oconto County, WI. | WI | GIP | [5 empty] | 2028-09-10 | 138 |  | 3342000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25285 | 0891 West St Cloud - Crossroads Rebuild | Rebuild 4.1 miles 115 kV from West St. Cloud - Crossroads with new structures and new OPGW shield wire. | MN | Other | Age and Condition |  |  |  |  | 2025-12-15 | 115 |  | 3500000
MTEP24 | South | ENTERGY MISSISSIPPI, LLC. | 25229 | Costas 230 kV Substation | The Costas 230 kV breaker and a half substation will cut into the existing Lake Castle – North Park 230 kV transmission line. A 108 MVAR capacitor bank will also be added to the new Costas 230 kV substation. Customer load will be fed out of (3) 150 MVA 230/34.5 kV transformers. | MS | Other | Load Growth | Costas 230 kV Substation; large load EPR | Large Load |  | 150 MVA | 2026-01-01 | 230 |  | 44500002 | EML EPR $45M
MTEP24 | Central | AMEREN MISSOURI | 50057 | Vessel Bulk Sub - Add 2nd 138/34 kV Transformer | At Vessel Bulk Sub Install the second 84 MVA transformer | MO | Other | Load Growth |  |  |  | 84 MVA | 2026-01-01 | 138 |  | 4000000
MTEP24 | South | ENTERGY MISSISSIPPI, LLC. | 25438 | Pickens - South Canton 230 kV Line Rebuilds | Rebuild the Pickens – Canton – South Canton 230 kV line with new conductor and through–path rating no lower than 779 MVA. | MS | BRP | [5 empty] | 2026-01-01 | 230 |  | 55200001
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50032 | New Pike County Energy Storage 345kV (R1021 & R1022) | Generator Project R1021 Interconnection Customer shall install a 117.6 MVA battery storage system. Generator Project R1022 Interconnection Customer shall install a 117.6 MVA battery storage system. | IN | GIP | [5 empty] | 2026-01-15 | 345 |  | 3000000
MTEP24 | South | ENTERGY SERVICES, LLC. | 24958 | Sandling 230 kV Customer Load Addition Project | Entergy is proposing to construct a new 230 kV transmission station called Sandling 230 kV which will serve a new industrial customer’s load near Port Arthur, TX. Sandling 230 kV station will be cut into the Legend to Keith Lake 230 kV line and the Keith Lake to Port Acres Bulk 230 kV line. Two capacitor banks will also be installed in the new Sandling 230 kV station. | TX | Other | Load Growth | Sandling 230 kV Customer Load Addition; large industrial load | Large Industrial |  |  | 2026-01-30 | 230 |  | 114200000 | New industrial customer near Port Arthur TX. Sandling 230 kV. $114M
MTEP24 | East | METC | 25210 | Replace Moore Road WM33 Trainer (J1658) - Network Upgrade | Replace Moore Road WM33 477 ACSR 26/7 trainer with 1590 to raise rating to 209 MVA SN and 237 MVA SE. | MI | GIP | [5 empty] | 2026-01-30 | 138 |  | 27635
MTEP24 | East | METC | 24558 | J1658 Generator Interconnection Network Upgrades | Install new Cronk 138 kV Substation. Install three 138 kV breakers rated at 40 kA and two new bus sections. Cut the Coldwater - Moore 138 kV line to loop in the new station. Island at Ash Road will need to be mitigated. | MI | GIP | [5 empty] | 2026-02-02 | 138 |  | 19660970
MTEP24 | East | METC | 25194 | Cronk-Moore Road Rebuild & Station Equipment Upgrades (J1550, J1635, J1658) - Network Upgrade | Rebuild the Cronk - Moore Rd circuit utilizing conductor rated at least that of 1431 ACSR. Replace Moore Road conductor and equipment to achieve a rating at least that of 348 MVA SE. Any new towers should be 230 kV double circuit structures to be operated at 138 kV. Structures in spans entering the new Cronk station do not need to be 230 kV structures. | MI | GIP | [5 empty] | 2026-02-02 | 138 |  | 11323126
MTEP24 | Central | AMEREN MISSOURI | 50086 | Load addition at Montgomery 161 kV Substation | This project will facilitate the connection of a 250 MW datacenter load at Montgomery (161 kV) Substation with a new straight bus and terminal | MO | Other | Load Growth | Load addition at Montgomery 161 kV Substation; 250MW data center EPR | Data Center | Y | 250 | 2026-03-01 | 161 |  | 2500000 | 250 MW datacenter at Montgomery 161 kV Substation (Ameren Missouri)
MTEP24 | East | METC | 24560 | J1614 Generator Interconnection Network Upgrades | Install new Aphis substation. Install three 138 kV breakers and associated disconnects rated at 40 kA and two new bus sections. Cut the Cobb – Meyer line into the new Aphis station. Fiber will be needed to mitigate an island at White Road. | MI | GIP | [5 empty] | 2026-03-03 | 138 |  | 11805174
MTEP24 | West | MONTANA-DAKOTA UTILITIES CO. | 25301 | Leola load addition | MDU has new customer requesting service on our 41.6 kV system near our Leola substation of 50 MW. MDU will need to add 2-10 Mvar capacitors and add additional 41.6 kV breaker to the Leola substation. | SD | Other | Load Growth | Leola load addition EPR | Load Growth |  | 50 | 2024-09-01 | 115 |  | 3600000 | MDU EPR $4M
MTEP24 | East | METC | 24478 | Kenowa - J1527 Gen Network Upgrade | Add Row 35, install 2-345kV breakers and associated disconnects at positions 35H9, 35F7 with minimum 40kA interrupting capability. | MI | GIP | [5 empty] | 2026-04-01 | 345 |  | 5567500
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25504 | J1481 Emerald Green Solar POI | J1481 - 200MW Emerald Green Solar: Greentown 230 - Expand 230 kV sub by adding a new CB that will share the existing ring bus terminal of the 23022 line and add line terminal equipment | IN | GIP | [5 empty] | 2026-04-01 | 230 |  | 8535044
MTEP24 | South | ENTERGY ARKANSAS, LLC | 50040 | Morrilton East 161kV: POI for J1559 | A new point of interconnection at the existing Morrilton East 161kV substation for the J1559 200 MW ERIS solar project. | AR | GIP | [5 empty] | 2026-04-01 | 161 |  | 3175000
MTEP24 | East | ITC | 24553 | J1659 Generator Interconnection Network Upgrades | Install 120 kV breaker HG rated at 40 kA. | MI | GIP | [5 empty] | 2026-04-01 | 120 |  | 922579
MTEP24 | East | ITC | 24554 | J1659 Generator Interconnection TOIF | Install required line entrance structures and 120 kV disconnect at Dorset Substation. | MI | GIP | [5 empty] | 2026-04-01 | 120
MTEP24 | South | ENTERGY SERVICES, LLC. | 50039 | J1561 Generator Interconnection at Richard138 kV | Facilities required for the interconnection of J1561 at the Richard 138kV | LA | GIP | [5 empty] | 2026-04-01 | 138 |  | 8263000
MTEP24 | South | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | 50094 | Northstar | Interconnect Entergy's Monticello South to Wilmar transmission line east of Wilmar and construct a 115/13.2 kV, 20 MVA substation. | AR | Other | Load Growth | Northstar load growth EPR | Load Growth |  | 20 MVA | 2026-04-01 | 115 |  | 7000000 | AECC EPR $7M
MTEP24 | South | ENTERGY ARKANSAS, LLC | 50004 | J1670 Crooked Lake 2 GIA upgrades | This project is to install power quality metering panel and remove current transformers. Also, revenue meters, telecom equipment, and a digital disturbance recorder panel will be installed. | AR | GIP | [5 empty] | 2026-04-03 | 161 |  | 1296000
MTEP24 | East | METC | 24443 | Tallmadge-Argenta - J1663 Generator Interconnection (Gordon) - Network Upgrade | Build a new 345 kV 3 Breaker ring substation cut in from the Tallmadge-Argenta 345 kV line. System changes will require relay upgrades at Argenta and Tallmadge 345 kV stations. | MI | GIP | [5 empty] | 2026-05-01 | 345 |  | 14811052
MTEP24 | East | METC | 24479 | Gordon-J1663 TOIF-Install position RH29 and switch 177 | Install RH29 line entrance structure and disconnect switch 177 for generator interconnection. | MI | GIP | [5 empty] | 2026-05-01 | 345
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25309 | Substation Technology Package #2 - 2024 | The Substation Technology Package #2 (SSTP#2) program of work will set the stage for the future of the digital substation field worker by providing enhanced Business Capabilities over ATC’s substation fiber network infrastructure. The SSTP#2 – 2024 project scope will include the following technology enhancements: • The installation of Wireless Access Points and enhanced Cyber Security fortifications at ~75 ATC substations. • Wireless connectivity will provide field workers with secure access from the substation ATC’s corporate data centers. • Cyber Security fortifications will introduce substation communication equipment protections in the event of a rogue device breach by pro-actively monitoring data activity between the substation router and switch. | WI | Other | Local Needs |  |  |  |  | 2024-12-31 | 0 |  | 3600000
MTEP24 | East | ITC | 24533 | J1526 Generator Interconnection Network Upgrades | Install 345 kV breaker KT rated at 63 kA. | MI | GIP | [5 empty] | 2026-05-13 | 345 |  | 1364741
MTEP24 | East | ITC | 24534 | J1526 Generator Interconnection TOIF | Install required line entrance structure and 345 kV disconnect switch at the ITCT Greenwood Substation. | MI | GIP | [5 empty] | 2026-05-13 | 345
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25546 | J1388 Galea Springs SPV POI | J1388 - 150MW Galea Springs SPV - solar farm - construct new switching station (3-CB ring) in the radial Oakland City 13862 ckt. - includes Oakland City relay upgrades and rebuilding 6.75 miles of 138kV line from POI to Oakland City | IN | GIP | [5 empty] | 2026-06-01 | 138 |  | 52928159
MTEP24 | Central | AMEREN ILLINOIS | 22878 | Upgrade Cat Mapleton 138 kV substation | New ring bus across road with two lead lines back to Cat Mapleton. | IL | Other | Age and Condition |  |  |  |  | 2026-06-01 | 138 |  | 8700000
MTEP24 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25459 | Line 35 Rebuild | To ensure reliable service a complete rebuild of L35 (Lucedale – Benndale 11.37 miles) is recommended. | MS | Other | Age and Condition |  |  |  |  | 2026-06-01 | 69 |  | 7100000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25272 | MNN MOD Installation | Install new MOD transmission line switches at Monticello. Potential for new pole and substation fence expansion. | MN | Other | Local Reliability |  |  |  |  | 2025-06-13 | 345 |  | 3600000
MTEP24 | Central | AMEREN MISSOURI | 22950 | Upgrade Watson 161 kV substation | Add line breakers to Pos. V & W Remove HSGS' and Add CS/PCB on the XFMRs 1,2,3 | MO | Other | Age and Condition |  |  |  |  | 2026-06-01 | 138 |  | 6200000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25523 | J1348 Brouilletts Creek Solar POI | J1348 - 200MW Brouilletts Creek Solar: Provide construction oversite for new switching station constructed by the IPP; relaying upgrades at Cayuga CT and Sugar Creek (34513 ckt); Loop 34513 in and out of new substation | IN | GIP | [5 empty] | 2026-06-01 | 345 |  | 8372617
MTEP24 | Central | AMEREN ILLINOIS | 22969 | Upgrade Decatur East Main St. 138 kV substation | Add line breaker to the L1522 line. | IL | Other | Age and Condition |  |  |  |  | 2026-06-01 | 138 |  | 2250000
MTEP24 | West | ITC MIDWEST | 25211 | ITCM Customer Interconnects with short lead time 2026 | These projects are being done at the request of an interconnection customer to facilitate new load, to re-distribute existing load, to improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA | Other | Load Growth |  |  |  |  | 2026-12-31 | 345 |  | 3750000
MTEP24 | West | OTTER TAIL POWER COMPANY | 50012 | OTP Buffalo Area 41.6 kV Rebuild | Rebuild 41.6 kV line between Buffalo 41.6 kV and Colgate 41.6 kV | ND | Other | Age and Condition |  |  |  |  | 2028-12-31 | 42 |  | 3770000
MTEP24 | Central | AMEREN MISSOURI | 22949 | Rebuild Stoddard 161 kV substation | Rebuild Stoddard substation into a ring bus configuration, including replacement of aging/overstressed/broken equipment. | MO | Other | Local Reliability |  |  |  |  | 2026-06-01 | 161 |  | 15900000
MTEP24 | Central | AMEREN ILLINOIS | 24921 | New Steamboat 138 kV Ringbus for Babylon 138 kV Sub for PPI Connection | Prairie Power Incorporated (PPI) 138 kV delivery point substation to supply a new bulk distribution transformer at the PPI Ellisville tap on the Ameren Castro-Galesburg Monmouth Blvd-1427 138 kV line | IL | Other | Local Reliability |  |  |  |  | 2026-06-01 | 138 |  | 9700000
MTEP24 | Central | AMEREN MISSOURI | 22880 | Zion 161 kV Substation Add High Side Interrupter | Add high side interrupting device on 161/69 kV transformer #1 | IL | Other | Local Reliability |  |  |  |  | 2026-06-01 | 161 |  | 2000000
MTEP24 | South | ENTERGY SERVICES, LLC. | 25436 | Bobville 230-138 kV Station | Cut a new 230 kV station called Bobville into the Castle to Ponderosa 230 kV line. Install a 230-138 kV Autotransformer. Cut Bobville 138 kV station into the Dobbin to Spring Branch 138 kV line. Bobville 230 kV and 138 kV stations will both be three breaker ring. Upgrade the short section between the Dobbin and Bobville 138 kV stations. | TX | BRP | [5 empty] | 2026-06-01 | 230 |  | 48600001
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25160 | Weston - Morrison Ave 115kV (Z-52), Reconductor | Reconfigure Weston - Sherman Street (O-41) line terminal to new position on West bus and relocate the Weston - Morrison Ave (Z-52) line terminal to the vacated position. Z-52 to be reconductored from Weston to Morrison Ave. Install upgraded communication equipment at remote ends. | WI | Other | Local Reliability |  |  |  |  | 2026-06-01 | 115 |  | 3800000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 24980 | Pioneer SS Breaker Relay and Remote Ends Asset Renewal | At Pioneer SS: Replace 3 breakers and remove free standing CTs and replace relaying. Install arrestors as required for the new breakers. Replace CCVT on line F-58. Replace GPS clock. Replace three Bus 1 potential transformers and one bus station power transformer. Replace two disconnect switches. At Stiles SS: Replace relaying on line 64442. | WI | Other | Age and Condition |  |  |  |  | 2027-12-31 | 138 |  | 3800000
MTEP24 | South | ENTERGY SERVICES, LLC. | 50048 | MPFCA J1644, J1686, J1832: Upgrade of Champagne – East Opelousas – Colton 138 kV line | Upgrade of of Champagne – East Opelousas – Colton 138 kV line. | LA | GIP | [5 empty] | 2026-06-09 | 138 |  | 9105556
MTEP24 | West | MIDAMERICAN ENERGY CO. | 50031 | Maffitt Lake Add 161 kV Breakers | Install four 161 kV breakers and associated equipment at Maffitt Lake Substation. | IA | Other | Load Growth |  |  |  |  | 2025-06-01 | 161 |  | 4000000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25525 | Kokomo Project Fusion Phase 2 - 230/69kV Sub | Kokomo Fusion Phase 2 (StarPlus Energy) - 155MW/51MVAR load addition; relocate 23022, 69172, and 69174 lines away from Phase 2 facilities; add (1) 150MVA 230/69kV transformer; add (2) 230CBs; add (4) 60MVA 69/34kV transformers | IN | Other | Load Growth |  | Battery Mfg (StarPlus) |  | 155 | 2026-06-30 | 230 |  | 14000000 | StarPlus Energy battery mfg Phase 2: 155MW in Kokomo IN
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25324 | Downing Substation | Install new distribution substation in the Downing area. | WI | Other | Local Reliability |  |  |  |  | 2025-10-15 | 69 |  | 4000000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50137 | Line ILKY31 and 6912 Grounding Improvement | Test all of 138kV and 69kV Line ILKD31/6912 double circuit structures with 3-point ground test method (356) structures). Install additional grounding on an estimated and assumed 190 each of the steel structures to meet ATC Construction Specifications. Retest and install additional 4-150 ft runs of counterpoise system grounding with Ground Enhancing. Counterpoise will likely need to be installed after initial ground rod installation and retesting between structures 106635 and 106765 (Boring B-20 to B-53) due to bedrock located less than 10 feet from the surface. Replace broken ground connection on approximately 24 structures per ATC specification as required. | MI | Other | Age and Condition |  |  |  |  | 2025-12-01 | 138 |  | 4000000
MTEP24 | Central | AMEREN ILLINOIS | 25041 | Virden 138 kV Substation for Virden Wind (J1408) | This project will install a new 138 kV line position to serve as the Point of Interconnection for Virden Wind, LLC under GIA J1408, within the new 3-position ring bus named Virden. | IL | GIP | [5 empty] | 2026-07-01 | 138 |  | 8000000
MTEP24 | East | ITC | 24450 | J1516 Generator Interconnection Network Upgrades | Install 120 kV breaker HF and associated disconnects rated at 40 kA. | MI | GIP | [5 empty] | 2026-08-03 | 120 |  | 912475
MTEP24 | East | ITC | 24451 | J1516 Generator Interconnection TOIF | Install required line entrance structure and 120 kV disconnect switch at the ITCT Fitz Substation. | MI | GIP | [5 empty] | 2026-08-03 | 120
MTEP24 | East | METC | 50038 | Project Phoenix-Husky Substation | Install line tap on the Murphy-Orr Rd 1 138 kV line for the temp load. Expand Orr Rd station and constructs a new Murphy to Orr Rd 345 kV line and 345/138 kV transformer at Orr Road to support CE’s transformers and METC’s new transformer at Orr Rd. | MI | Other | Local Needs | Project Phoenix-Husky Substation; large new load | Large Load |  |  | 2026-08-19 | 345 |  | 50252000 | METC EPR $50M
MTEP24 | South | CLECO POWER LLC | 50067 | J1686 Generator Interconnection on Coughlin - Plaisance 138 kV | J1686 Generator Interconnection of 100 MW solar facility on the Coughlin -Plaisance 138 kV line section. | LA | GIP | [5 empty] | 2026-09-01 | 138 |  | 18175765
MTEP24 | South | ENTERGY ARKANSAS, LLC | 50090 | Wheatley 500kV: New POI J1710 J1819 J1820 J1821 | A new 500kV point of interconnection for GIA projects J1710, J1819, J1820, and J1821. This is for 300 MW of solar and 100 MW of Battery. The project will include a new 500kV interconnection substation that will be cut in on the KEO - Heth 500kV line. | AR | GIP | [5 empty] | 2026-09-13 | 500 |  | 32354000
MTEP24 | South | ENTERGY ARKANSAS, LLC | 50093 | Galet 500/230kV New Substation | Construct a new 500/230kV substation to serve a new customer on the West Memphis - Heth 500kV line. The substation will include two 1200 MVA autotransformers and a four 500kV breaker ring bus new 230kV lines extending to the customer 230kV station. | AR | Other | Load Growth | Galet 500/230 kV New Substation for load growth | Load Growth |  | 1200 MVA | 2026-09-30 | 500 |  | 142000000 | Galet 500/230kV: 2x1200 MVA autotransformers, new customer (EAL AR). $142M
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50095 | Upgrade Stout CT - CT 4 and 5 Relaying | Upgrading the protection packages for generating units CT 4 and 5 and GSUs at Stout CT substation. | IN | Other | Local Reliability |  |  |  |  | 2026-09-30 | 138 |  | 300000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50096 | Upgrade Stout CT - CT Bus Relaying | Upgrading the protection packages for the bus section at Stout CT substation. | IN | Other | Local Reliability |  |  |  |  | 2026-09-30 | 138 |  | 150000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25322 | 0890 Granite City - Crossroads Rebuild | Rebuild 3.7 miles 115 kV line from Granite City - Crossroads with new structures and new OPGW shield wire. | MN | Other | Age and Condition |  |  |  |  | 2025-12-15 | 115 |  | 4000000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25289 | 0821 Highbridge - Miriam Park Refurb | Rebuild 3.3 miles 115 kV with new structures and new OPGW shield wire. | MN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 115 |  | 4000000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25434 | J1218/J1229 Network Upgrades at Sub 92 | Expand Substation 92 to interconnect generators J1218 and J1229 | IA | GIP | [5 empty] | 2027-06-30 | 345 |  | 4000000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25543 | J1381 Locomotive Solar POI | J1381 - 200MW Locomotive Solar: Greentown 230 - Expand 230 kV ring bus and add line terminal equipment | IN | GIP | [5 empty] | 2026-10-01 | 230 |  | 6666686
MTEP24 | South | ENTERGY ARKANSAS, LLC | 50059 | Kinder 161kV: New POI J1558 | New 161kV switching station for the J1558 200 MW solar interconnection on the Moreland - St. Vincent 161kV line. | AR | GIP | [5 empty] | 2026-10-01 | 161 |  | 14012000
MTEP24 | West | GREAT RIVER ENERGY | 25358 | Burnsville Area Projects | Replace and relocate EEE (all new panels/relays/etc.). Soil correction at new EEE site, northwest fence line expansion, replacement of 5M197, addition of breakers with new 115 kV ring bus configuration on north end of substation. This ring bus configuration will prepare site for Pilot Knob to Burnsville line conversion to 115 kV in the future. | MN | Other | Local Needs |  |  |  |  | 2028-05-31 | 115 |  | 4000000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25296 | Install Lawrence LAW TR02 | Install second 115/34.5 kV transformer with LTC at Lawrence substation. | SD | Other | Local Reliability |  |  |  |  | 2025-06-15 | 115 |  | 4158000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 50061 | CAPX Fargo-TC OPWG Replacement | Replacement of the existing OPGW on the Fargo line with. In conjunction with the LRTP 2 project the spans from MNN-ALS will also be replaced. | MN; ND | Other | Age and Condition |  |  |  |  | 2026-12-15 | 345 |  | 4280000
MTEP24 | West | ITC MIDWEST | 25188 | ITCM Boone South 69 kV Substation Interconnection | Once ITC has converted the Grand Junction to Doud line from 34.5kV to 69kV through the work in ITCMW_16_60, IPL will retire its current Boone South substation and transfer its load to a new IPL Boone South station at a site ~0.7 miles away. IPL is requesting ITC to install a double bus with a two transformer template. IPL will initially install one 69/26.1kV 20/26/33 MVA transformer. ITC will install two line breakers and a bus tie breaker at the new site. ITC will also retire the tap to the old Boone South sub as well as retire pole top switches 2055 and 2057. | IA | Other | Load Growth |  |  |  | 33 MVA | 2025-12-01 | 69 |  | 4363663
MTEP24 | West | ITC MIDWEST | 25346 | ITCM Walcott 80 Substation Interconnection | IPL has notified ITC that they will be constructing a new Walcott 80 Substation which will replace their existing Walcott and Walcott North substations. The new substations will initially connect at 34.5 kV and then be converted to 69 kV as part of the Fulton – Dixon 69 kV conversion. IPL has requested ITC install two 69 kV busses with two line breakers and a bus tie breaker. New line taps for Walcott 80 substation to be constructed with T2-4/0 ACSR conductor. While operating at 34.5 kV, one new breaker looking toward Calamus 3350 should be operated as the new normal open point, with PTS 3372 becoming normally closed to allow the Walcott 80 load to be switched between the two 34.5 kV sources. Existing taps to Walcott and Walcott North to be retired under separate future EI Sketches prior to 69 kV conversion. | IA | Other | Local Needs |  |  |  |  | 2029-12-30 | 69 |  | 4475472
MTEP24 | South | ENTERGY SERVICES, LLC. | 50065 | J1576 Generator Interconnection on the Adams Creek - Angie 230 kV | Facilities required for the interconnection of J1576 on the Adams Creek - Angie 230 kV. | LA | GIP | [5 empty] | 2026-11-15 | 230 |  | 19725228
MTEP24 | West | GREAT RIVER ENERGY | 25469 | Silver Lake Transformer Replacement | Replace existing 230/41.6 kV transformer with XXX MVA and replace associated breakers | MN | Other | Age and Condition |  |  |  |  | 2027-12-31 | 230 |  | 4646984
MTEP24 | Central | AMEREN MISSOURI | 22886 | Reconfigure Berkeley 138 kV substation | Age and condition maintenance: Replace Breakers: BERK-138 Pos. F; BERK-138 BT 1-2; BERK-138 BT 2-3 Add high side interrupting devices. Add line BRKs to Pos. D & J. | MO | Other | Age and Condition |  |  |  |  | 2026-12-01 | 138 |  | 39200000
MTEP24 | Central | AMEREN ILLINOIS | 25042 | Supernova 345 kV Substation for Perry County Solar (J1306) | This project will install a new 345 kV line position to serve as the Point of Interconnection for Perry County under GIA J1306, within the new 3-position ring bus named Supernova. | IL | GIP | [5 empty] | 2026-12-01 | 345 |  | 11000000
MTEP24 | Central | AMEREN ILLINOIS | 50044 | Hull-Marion-7324 Rebuild | Rebuild the 7 mile Hull-Marion-1690 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL | Other | Age and Condition |  |  |  |  | 2026-12-01 | 138 |  | 5500000
MTEP24 | Central | AMEREN ILLINOIS | 24034 | Coffeen N. XFMR 2 Replacement | Replace Existing XFMR 2 at Coffeen North Substation with a new 345/138kV 700 MVA unit. | IL | Other | Load Growth |  |  |  | 700 MVA | 2026-12-01 | 345 |  | 6000000
MTEP24 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25501 | County Line 115kV Delivery Point | In order to serve the member delivery point, tap the Olive Oil Loop line with a 115kV Goab and construct a new line to the new delivery point. | MS | Other | Load Growth |  |  |  |  | 2026-12-01 | 115 |  | 2160000
MTEP24 | West | GREAT RIVER ENERGY | 25471 | St. Clair Tap Rebuild | BE-SC line - St. Clair 69-kV tap rebuild (4.5 miles) | MN | Other | Age and Condition |  |  |  |  | 2027-12-30 | 69 |  | 4728756
MTEP24 | Central | AMEREN MISSOURI | 25243 | Rockwood 138kV Aging Infrastructure and Line Breaker Addition | At Rockwood 138/34.5 kV substation, install three 138 kV line breakers on the Rockwood-Big River-1 line position H2, Gray-Rockwood-3 position H6, Gray-Rockwood-4 position H10 having a 2000 A continuous capability. | MO | Other | Local Reliability |  |  |  |  | 2026-12-01 | 138 |  | 3500000
MTEP24 | South | ENTERGY ARKANSAS, LLC | 50197 | West Memphis 500/161kV Auto Replacement MPFCA | The existing 500/161kV autotransformer at West Memphis EHV will be replaced with a 600MVA rated autotransformer. Also, the 161kV breaker B2600 will also be replaced. All new relay panels will be installed. | AR | GIP | [5 empty] | 2026-12-05 | 500 |  | 25506000
MTEP24 | South | CLECO POWER LLC | 25283 | Dolet Solar Replacement R1004 | Upgrade Dolet Substation for replacement generation interconnection for R1004 | LA | GIP | [5 empty] | 2026-12-15 | 345 |  | 19687305
MTEP24 | West | ITC MIDWEST | 25205 | ITCM Meservey 69 kV Tap Rebuild | Rebuild the 6.9 mile Meservey Tap 69 kV line. New line should be rebuilt with T2-4/0 ACSR conductor. | IA | Other | Age and Condition |  |  |  |  | 2027-12-31 | 69 |  | 4766250
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50102 | University – Whitewater 138 kV (UNIG51), Partial Reconductor & OPGW | • Reconductor 3.54 miles of UNIG51 (University-Whitewater 138-kV line), increasing UNIG51’s ratings. This increase allows continuous operation of University generation at full capability after the University – Mukwonago 138-kV line contingency, prepares the corridor for future needs, and enhances operational flexibility in the area. • Install OPGW (24-strand retrofit) in the roughly 6.3 miles of UNIG51, contingent upon no structure replacements needed. OPGW addition completes the communication circuit and create a self-healing optical ring between University and Whitewater substations, leveraging both pre-existing fiber and the future OPGW. • Replace the two bus-side disconnect switches at University SS on both Line UNIG51 and Line UNIG52 • Project to be done in parallel with MTEP ID 24782 J1304 J1305 J1460 MPFCA Network Upgrades, which optimizes ATC’s expenditures and local generation outages. | WI | Other | Local Reliability |  |  |  |  | 2025-12-31 | 138 |  | 4825000
MTEP24 | West | ITC MIDWEST | 25308 | ITCM Leon Rodeo 69 kV Substation Interconnection | IPL will construct a new 69/26.2kV substation, Leon Rodeo, west of the town of Leon and north of the existing Leon substation. For the ITC owned portion of Leon Rodeo, ITC will build a 69kV substation with two single boxes, two 69 kV line breakers, and a 69 kV bus tie breaker. ITC will also take the cap bank from the J2 bus of the Leon sub and relocate it to the Grand River bus section of the new Leon Rodeo substation. ITC will also build the line taps to connect Leon Rodeo to the Grand River-Leon and Leon-Saling circuits. Once the Leon Rodeo sub is put in-service, the existing Leon substation will be retired. | IA | Other | Load Growth |  |  |  |  | 2028-12-31 | 69 |  | 4860742
MTEP24 | West | MONTANA-DAKOTA UTILITIES CO. | 25475 | Merricourt Reactor | Adding a 50 MVar reactor at Merricourt to support high voltages on the 230 kV when wind and load are low. | ND | BRP | [5 empty] | 2026-12-31 | 230 |  | 5000000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25378 | Gaylord Substation Rebuild | Rebuild Gaylord substation at a new location, converting 4.16kV feeders to 13.8kV. | MN | Other | Age and Condition |  |  |  |  | 2026-10-15 | 69 |  | 5100000
MTEP24 | Central | AMEREN ILLINOIS | 25279 | Replace Pole and Insulator Program - MTEP24 | Miscellaneous replacements requested by maintenance. Missouri and Illinois. | IL; MO | Other | Age and Condition |  |  |  |  | 2026-12-31 | 345 |  | 20000000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25403 | Newtonville T3, T2 and CB's Replacement | Replacing 161/138kV T3 transformer, 138/69kV T2 transformers, and several circuit breakers. Breaker replacements result in 138/69kV T1 transformers rating to increase. | IN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 161 |  | 18500000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 23951 | Line Clearance Mitigation Program 2025 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2025. | MI; WI | Other | Local Reliability |  |  |  |  | 2027-06-30 | 345 |  | 5400000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25442 | Z91-1 NW - Pigeon Creek Rebuild | Rebuilding ~3 miles of 138kV line from 795 to 954 | IN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 138 |  | 11000000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25340 | Albany Second Transformer | Rebuild and relocate NSP's facilities on the west side of the Albany substation yard and install a second 69/12.5 kV transformer. | MN | Other | Local Reliability |  |  |  |  | 2025-10-15 | 69 |  | 5500000
MTEP24 | West | ITC MIDWEST | 25206 | ITCM Lime Creek 161/69 kV Transformer Replacement | Replace the existing two 161/69 kV transformers T1 and T2 at Lime Creek with a new single 150 MVA 161/69 kV transformer with LTC. The new transformer will be installed at the current T2 location. T1 and its associated equipment will be retired. The existing high and low side breakers associated with T2 will be reused for the new transformer. | IA | Other | Age and Condition |  |  |  |  | 2026-12-31 | 161 |  | 5690194
MTEP24 | West | GREAT RIVER ENERGY | 25422 | Airport Substation Breaker Addition | The Anoka County Highway Department is planning to expand Highway 65 and Great River Energy’s Highway 65 Switching Station is in the way and needs to be relocated. The switching station will be relocated just outside Connexus’ Airport Substation. This project will relocate the Highway 65 Switch to Connexus’ Airport substation by: 1. Building a breaker station at Connexus’ Airport substation 2. Rebuild the “CR” line from structures #158 (Highway 65 Switch) – #145 (CE Airport) to double circuit 69 kV – Will be a MN/DOT project | MN | Other | Local Reliability |  |  |  |  | 2026-06-30 | 69 |  | 5692565
MTEP24 | East | METC | 24458 | Kenowa - J1527 TOIF - Install position FH35 and switch 177 | Install FH35 line entrance structure and disconnect switch 177 for generator interconnection. | MI | GIP | [5 empty] | 2026-12-31 | 345
MTEP24 | East | METC | 24516 | J1571 Generator Interconnection Network Upgrades | Install new Rouget 138 kV station. Install three 138 kV breakers rated at 40 kA and two new bus sections. Cut the Beecher - Pixley (Beecher - Morocco #1) 138 kV circuit into the new Rouget station. | MI | GIP | [5 empty] | 2026-12-31 | 138 |  | 8574899
MTEP24 | Central | AMEREN ILLINOIS | 25362 | Replace Breakers and Relays Program - MTEP24 | Miscellaneous breaker and relay replacements requested by maintenance. Missouri and Illinois. | IL; MO | Other | Age and Condition |  |  |  |  | 2026-12-31 | 345 |  | 5000000
MTEP24 | West | GREAT RIVER ENERGY | 25381 | Long Siding - Princeton Area Projects | Rebuild OL line segment 1, BM line segment 3, and SS-2887 (Long Siding tap switch) | MN | Other | Local Reliability |  |  |  |  | 2027-12-19 | 69 |  | 5728758
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25393 | Chrisney 69/12kV T1 Replacement | Replacement of 69/12kV transformer at Chrisney substation | IN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 4000000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25397 | Tepe Park 138/15kV Transformer Addition | Adding 138/13.09kV 20MVA transformer and 15kV breakers | IN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 138 |  | 4000000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25444 | Y74 Azteca - VIP Pole Replacement | Replacing ~1 mile of poles for 69kV line from Azteca to VIP | IN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 4000000
MTEP24 | East | METC | 24536 | J1571 Generator Interconnection TOIF | Install required line entrance structures and 138 kV disconnect switch at the new Rouget station. | MI | GIP | [5 empty] | 2026-12-31 | 138
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25407 | Angel Mounds CB and Switch Replacement | Replacing several 138kV circuit breakers and switches | IN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 138 |  | 3000000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25395 | Oakland City 69/15kV Xformer and CB Replacement | Replacing 69/15kV 5MVA transformer and several 69kV circuit breakers | IN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 2700000
MTEP24 | East | METC | 24557 | J1586 Generator Interconnection TOIF | Install required line entrance structures and 345 kV disconnect switch at the new Oxby station. | MI | GIP | [5 empty] | 2026-12-31 | 345
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25404 | Winslow 69kV CB Replacement | Replacing 2 69kV circuit breakers at Winslow substation | IN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 1500000
MTEP24 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 50174 | New Customer X 138kV Substation | 200MW load is being looped into circuit 13853 Roxana to StatelineB circuit.(NIPSCO-CE) | IN | Other | Load Growth | New Customer X 138kV Substation; new large customer EPR | Large Load |  | 200 | 2026-12-31 | 138 |  | 12000000 | 200MW Customer X on Roxana-StatelineB circuit (NIPSCO)
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25297 | Blue Heron Second Transformer | Install new 69/13.8 kV transformer with LTC at Blue Heron substation. Substation equipment at Blue Heron and Rich Spring will be reinforced to increase flow capacity on their feeders. | MN | Other | Local Reliability |  |  |  |  | 2025-10-15 | 69 |  | 5800000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25190 | Badger SS Control House, Breaker, and Relay Asset Renewal | Asset Renewal of control house and contents, one circuit breaker, and replacement of various other relay panels to meet ATC standards. | WI | Other | Age and Condition |  |  |  |  | 2026-06-01 | 138 |  | 5900000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25333 | Westfield 156th St 69/12kV Sub | Westfield 156th St 69/12kV Sub (new sub) - Loop 69142 line through Sub; transfer 69155 wire to 5 new poles | IN | Other | Load Growth |  |  |  |  | 2026-12-31 | 69 |  | 3442000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25286 | 0754 Buffalo - Maple Lake Rebuild | Rebuild 8.2 miles 69 kV from Buffalo - Maple Lake with new structures, new OPGW shield wire, and new conductor. | MN | Other | Age and Condition |  |  |  |  | 2025-12-15 | 69 |  | 6000000
MTEP24 | East | WOLVERINE POWER SUPPLY COOPERATIVE, INC | 21786 | Vestaburg 69kV Relocation | The Vestaburg 69 kV Transmission Station was built in the late 1950s and is due for a major upgrade, including new ground grid and switches. To consolidate the transmission station, the transmission line terminations will be relocated across the road to the 138/69 kV transmission yard after expanding the 69 kV bus in the planned expansion area. As a part of this project the Vestaburg Distribution station will be moved from the Altona-Vestaburg line to the North Shade-Vestaburg line. The old Vestaburg 69 kV Transmission Station will be decommissioned. | MI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 7500000
MTEP24 | East | METC | 25327 | METC Asset Replacement Program - 2026 | Replace aging and outdated equipment at a pace that will ensure each type of equipment is replaced near its projected end of life. | MI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 345 |  | 53960000
MTEP24 | East | ITC | 25366 | ITCTransmission Asset Replacement Program - 2026 | Replace aging and outdated equipment at a pace that will ensure each type of equipment is replaced near its projected end of life. | MI | Other | Age and Condition |  |  |  |  | 2026-12-31 | 345 |  | 60700000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25287 | W3402 Loyal - Spokesville Rebuild | Rebuild 8 miles 69 kV with new structures, new OPGW shield wire, and new conductor. | WI | Other | Age and Condition |  |  |  |  | 2025-12-31 | 69 |  | 6000000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25288 | 0774 Goodview - Str 444 Rebuild | Rebuild 3 miles 69 kV with new structures, new OPGW shield wire, and new conductor. | MN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 69 |  | 6000000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 50029 | SE Soteria Add 161 kV Breakers | Install six 161 kV breakers and associated equipment at SE Soteria Substation. | IA | Other | Load Growth |  |  |  |  | 2026-06-01 | 161 |  | 6000000
MTEP24 | South | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | 24694 | Coop Office Breaker Addition | AECC will be adding a sectionalizing breaker on Woodruff Electric's Coop Office to Colt 69kV line. | AR | Other | Local Reliability |  |  |  |  | 2026-12-31 | 69 |  | 2500000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 50030 | Johnson Creek Add 161 kV Breakers | Install six 161 kV breakers and associated equipment at Johnson Creek Substation. | IA | Other | Load Growth |  |  |  |  | 2026-06-01 | 161 |  | 6000000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25162 | Milwaukee Leased Dark Fiber Retirement Plan | Installation of 8+ miles of ATC Owned Underground (UG) Fiber to replace leased UG Fiber with Midwest Fiber Networks in Milwaukee Metro Area. | WI | Other | Local Needs |  |  |  |  | 2027-12-31 | 0 |  | 6000000
MTEP24 | East | ITC | 24574 | J1664 Generator Interconnection Network Upgrades | Expand Carrigan Substation and extend Bus 102 to start the J row. Install one 120 kV breaker and two disconnect switches rated at 40 kA. | MI | GIP | [5 empty] | 2027-01-01 | 120 |  | 1969214
MTEP24 | East | ITC | 25082 | J1664 Generator Interconnection TOIF | Install required line entrance structures and 120 kV disconnect switch at Carrigan Substation. | MI | GIP | [5 empty] | 2027-01-01 | 120
MTEP24 | East | METC | 24556 | J1586 Generator Interconnection Network Upgrades | Install new Oxby 345 kV station. Install three 345 kV breakers and associated disconnects rated at 50 kA and two new bus sections. Cut the Argenta - Tompkins 345 kV circuit into the new Oxby station. | MI | GIP | [5 empty] | 2027-01-21 | 345 |  | 14487583
MTEP24 | East | METC | 25209 | Battle Creek-Oneida and Argenta-Tompkins Line Upgrades (J1586) - Network Upgrade | Install Row 31 by installing 3-345 kV breakers and associated disconnect. Install breakers 29R8 and 33F7 and associated disconnects. Cut the Battle Creek-Oneida 345 kV circuit into Oxby station using a conductor rated at least that of 2-1431 ACSR. Remediate the sag on the Oxby-Oneida 345 kV line to achieve a rating of at least 1327 MVA SN and 1327 MVA SE. Reconductor the Oxby-Tompkins 345 kV line with OPGW using 2-1431 ACSR conductor. | MI | GIP | [5 empty] | 2027-02-01 | 345 |  | 16178613
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25526 | Terre Haute Project Tonic Water | Terre Haute Project Tonic Water new load: 130MW/43MVARs; located north of the Vigo Co. Industrial Park in the 13821 ckt; new 138kV line loop to be 954ACSS@200C; 138kV sub to be 7 breakers in a breaker and 1/2 layout; (2) dedicated customer-owned 138kV outlet lines to their load; (2) 36MVAR-138kV capacitors | IN | Other | Load Growth |  | Large Industrial |  | 130 | 2027-03-01 | 138 |  | 35777500 | Project Tonic Water: 130MW north of Vigo Co Industrial Park, Terre Haute
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25165 | Glory Road - Oak St. 69 kV (GLNY41), Partial Rebuild | Rebuild and install OPGW on approximately 0.7 miles of line GLNY41 from Glory Rd SS towards Oak St SS. | WI | Other | Age and Condition |  |  |  |  | 2028-06-01 | 69 |  | 6000000
MTEP24 | West | MINNKOTA POWER COOPERATIVE, INC | 24394 | Maple River-Buffalo River 69 kV Line Rebuild | Rebuild of 69 kV line from Maple River to Buffalo River. | MN; ND | Other | Age and Condition |  |  |  |  | 2024-12-31 | 69 |  | 6050000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 24922 | Forest Junction SS and Remote End Relay Asset Renewal | Scope of work combines work at Forest Junction with remote end work at Kaukauna Central, Lake Park, Melissa, and Tecumseh Rd. | WI | Other | Age and Condition |  |  |  |  | 2027-12-01 | 345 |  | 6480000
MTEP24 | South | ENTERGY SERVICES, LLC. | 25352 | J1833 Generator Interconnection | Interconnection of gas generator (J1833) at Leeville 115kV | LA | GIP | [5 empty] | 2027-04-01 | 115 |  | 17825000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25424 | NE 6th St Substation and 161 kV line taps | Construct a new 161-13 kV substation and 161 kV taps | IA | Other | Load Growth |  |  |  |  | 2027-06-01 | 161 |  | 6500000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25460 | Southridge Substation and 161 kV line taps | Construct a new 161-13 kV substation and 161 kV taps | IA | Other | Load Growth |  |  |  |  | 2027-06-01 | 161 |  | 6500000
MTEP24 | South | ENTERGY MISSISSIPPI, LLC. | 25215 | Andes 500/230 kV Substation | The Andes 500 kV four breaker ring bus station will cut into the existing Lakeover – McAdams 500 kV transmission line. Two 720 MVA autotransfomers (2 x 3 single phase 240 MVA autotransformers + 2 single phase spares) will connect the 500 kV ring bus to the 230 kV breaker and a half station. A 108 MVAR capacitor bank will also be added to the new 230 kV substation. Customer load will be fed out of (6) 150 MVA 230/34.5 kV transformers. | MS | Other | Load Growth | Andes 500/230 kV Substation; large load EPR | Large Load |  | 720 MVA | 2027-06-01 | 500 |  | 158000005 | EML EPR $158M
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50026 | Kaukauna Central Tap - Melissa 138 kV (971K11), Rerate | Rerate line 971K11 to keep up with system demand. The thermal study identified issues that need to be fixed to bring the rating up to meet Operations and Planning needs. | WI | Other | Local Reliability |  |  |  |  | 2025-05-01 | 138 |  | 7000000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25163 | Freeman - Presque Isle (X-118), OPGW Addition | Installation of 7.5 miles of OPGW to provide an alternate fiber path establishing two diverse fiber routes connecting into ATC larger OPGW Network Infrastructure. | MI | Other | Local Needs |  |  |  |  | 2026-12-31 | 138 |  | 7000000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25437 | Substation 85: Convert to Ring Bus | Install 161 kV circuit breakers and bus work to convert Substation 85 to a ring bus configuration | IA | Other | Local Reliability |  |  |  |  | 2027-12-31 | 161 |  | 7000000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50017 | West Middleton - Str 36 69 kV (6967/6963), Rebuild Green Poles (CAC/CCA/SX) Replacements | Rebuild 2 miles of double circuit 6967/6963 from structure 36 to West Middleton. Install new structures, conductor, shield wire. | WI | Other | Age and Condition |  |  |  |  | 2026-10-01 | 69 |  | 7200000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50112 | J1781 Hill Valley SS Network Upgrades and Interconnection Facilities | J1781 is a wind facility in Iowa and Lafayette County, WI. | WI | GIP | [5 empty] | 2030-03-10 | 345 |  | 7219000
MTEP24 | East | METC | 21968 | Delaney 138 kV Station Rebuild | The new Delaney 138 kV station will be rebuilt as a compressed four breaker ring bus configuration. Install new control house. Install (3) 138 kV, 3000 A breakers with at least 40 kA interrupting. The summer emergency rating of all new equipment should be no less than 644 MVA/2693 amps. | MI | Other | Age and Condition |  |  |  |  | 2027-06-01 | 138 |  | 8632000
MTEP24 | South | ENTERGY SERVICES, LLC. | 25455 | Amite South/DSG Reactive Support Project | •Addition of reactive support in the form of capacitor banks at 3 substations. ·Gypsy 230 kV – 2 x 81.4 MVAR ·Peters Road 230 kV – 1 x 81.4 MVAR ·Munster 230 kV – 1 x 81.4 MVAR | LA | Other | Local Needs |  |  |  |  | 2027-06-01 | 230 |  | 21100000
MTEP24 | East | METC | 25522 | Oakland 138 kV Station Rebuild | The new Oakland 138 kV station will be rebuilt as a compressed four breaker ring bus configuration. Replace 50MVAR w/2x 25 MVAR cap banks on separate buses with new synchronous breakers. | MI | Other | Age and Condition |  |  |  |  | 2027-06-01 | 138 |  | 8294000
MTEP24 | East | ITC | 24998 | Pontiac 345 kV Station - Extend Buses and Add A Row | Extend bus 303 and construct a fifth breaker and a half row for terminating Transformer 301 and Transformer 303 into breaker and a half positions. All breakers should be 3000 A, 63 kA breakers. Fitz-Pontiac 345kV line termination will be moved from position BQ to position AQ. Transformer 301 will be terminated at Pos AI. Transformer 303 will be terminated at Pos BQ. Remove breakers from Row E, replacing disconnect switches, and upgrade replaying as necessary to accommodate new configuration. | MI | Other | Local Needs |  |  |  |  | 2027-06-01 | 345 |  | 8274000
MTEP24 | South | ENTERGY SERVICES, LLC. | 25457 | PCI 69 kV Breaker Upgrades | Replace PCI 69 kV Breakers 8220, 8225 and 8230 with 40kA breakers. | LA | Other | Local Reliability |  |  |  |  | 2027-06-01 | 69 |  | 2730000
MTEP24 | South | ENTERGY SERVICES, LLC. | 25470 | Sunrise 230 kV New Station | Cut a new 230 kV station named Sunrise on the Wells to Labbe 230 kV line. Install distribution facilities to serve load currently served from the existing Sunset 69 kV station. | LA | BRP | [5 empty] | 2027-06-01 | 230 |  | 39600000
MTEP24 | South | ENTERGY SERVICES, LLC. | 25468 | Southline to Jacinto 138 kV New Line | Construct a new ~6 mile 138 kV line between Jacinto and Southline 138 kV stations. | TX | BRP | [5 empty] | 2027-06-01 | 138 |  | 40700000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25258 | Prior TR02 And Feeder | Install second 115/13.8 kV transformer and associated equipment. | MN | Other | Local Reliability |  |  |  |  | 2026-06-15 | 115 |  | 7280000
MTEP24 | East | ITC | 25223 | Lulu - Construct 345 kV Station - Multiple Generator Interconnect Network Upgrade | Construct the Lulu 345 kV switchyard. Cut in the Lemoyne-Maple and Milan-Monroe-Morocco lines into the new station. | MI | GIP | [5 empty] | 2027-06-11 | 345 |  | 29916928
MTEP24 | East | METC | 25244 | Morocco - Replace RH34 Relaying - Multiple Generator Network Upgrade | Construct the Lulu 345 kV switchyard. Cut in the Lemoyne-Maple and Milan-Monroe-Morocco lines into the new station. | MI | GIP | [5 empty] | 2027-06-11 | 345 |  | 319323
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25104 | 2nd St. Tap - 30th Ave. 69 kV (N-14), Partial Rebuild | Rebuild and install OPGW on approximately 1.5 miles of N-14 from Structure 145364 to 30th Ave. | MI | Other | Age and Condition |  |  |  |  | 2027-11-01 | 69 |  | 7500000
MTEP24 | West | MINNKOTA POWER COOPERATIVE, INC | 24375 | Center-Maple River 345 kV Foundation Restoration | Replacement of aging structures and concrete foundations on the Center - Maple River 345 line. | ND | Other | Age and Condition |  |  |  |  | 2028-12-31 | 345 |  | 7550000
MTEP24 | West | GREAT RIVER ENERGY | 25445 | Prairie Woods to Sunburg Rebuild | Rebuild Sunburg to Prairie Woods Switch 69 kV line. | MN | Other | Age and Condition |  |  |  |  | 2027-12-31 | 69 |  | 7649388
MTEP24 | West | ITC MIDWEST | 25321 | Winnebago City Substation Interconnection | BENCO/GRE has notified ITC that they will be retiring the existing Winnebago Local substation and replacing it with a new Winnebago City substation which will consolidate all the BENCO load onto one substation. As part of this, ITC will be retiring the transmission portion of the Winnebago Local substation and constructing the transmission portion of the new Winnebago City substation. ITC will construct a new 4 line terminal bus with one BENCO transformer position, with provisions to accommodate a 2nd BENCO transformer and future bus tie breaker. | MN | Other | Local Needs |  |  |  |  | 2025-10-31 | 69 |  | 7915596
MTEP24 | East | ITC | 24463 | Greenwood-Rapson#1 - J1557 Generator Interconnection (Cribbins) - Network Upgrade | Build a new 345 kV 3 breaker ring substation cut in from the Greenwood – Rapson #1 345kV line. | MI | GIP | [5 empty] | 2027-07-01 | 345 |  | 13994489
MTEP24 | East | ITC | 24494 | Cribbins-J1557 TOIF- Install position CQ and switch CQA | Install CQ line entrance structure and disconnect switch CQA for generator interconnection. | MI | GIP | [5 empty] | 2027-07-01 | 345
MTEP24 | South | ENTERGY SERVICES, LLC. | 24960 | Legend to Sandling 230 kV Circuit 2 Project | Construct a new ~7.6 mile 230 kV Legend to Sandling Ckt 2. | TX | BRP | [5 empty] | 2027-07-31 | 230 |  | 77320000
MTEP24 | West | OTTER TAIL POWER COMPANY | 16289 | Bemidji 115/12.5 kV Substation | New Bemidji 115/12.5 kV Substation design with express feeders and source transfer, one transformer 37MVA. This is a multi-year project. In the event that a new transformer will not fit in the original substation, the 115 kV line will be tapped just outside the substation. | MN | Other | Load Growth |  |  |  | 37 MVA | 2025-12-31 | 115 |  | 8000000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 24842 | Atlantic – Osceola 69kV (Laurium2), Re-insulate | Replace crossarms at ~140 structures with new insulators, replace select structures, obtain rights for gaps along existing corridor, and complete vegetation management activities. | MI | Other | Age and Condition |  |  |  |  | 2025-12-31 | 69 |  | 8100000
MTEP24 | East | METC | 50151 | Sphinx 138 kV Station | METC to build a new station as a 138 kV four-row breaker-and-a-half configuration to serve 255 MVA new load. Rebuild 2.5 mile of Gaines – Plaster Creek to DCT 1431 ACSS and install OPGW. Gaines 138 kV station rows 7 and 11 will be expanded. | MI | Other | Load Growth | Sphinx 138 kV Station; new load station | Load Growth |  | 255 MVA | 2027-09-01 | 138 |  | 32810000 | METC EPR $33M
MTEP24 | East | METC | 24477 | Gaines - Thompson Road 138kV - J1292 GIA (Peddler) TOIF | Connect generator at position BM6 as TOIF. | MI | GIP | [5 empty] | 2027-09-29 | 138
MTEP24 | West | OTTER TAIL POWER COMPANY | 10001 | OTP Voltaire 115 kV Substation | Tap Xcel's 115 kV line between GRE McHenry and Magic City and build a new 115/41.6 kV substation in the Voltaire area. Install three 115 kV breakers and three 41.6 kV breakers. Install one 56 MVA 115/41.6 kV transformer. | ND | Other | Local Needs |  |  |  |  | 2026-12-31 | 115 |  | 8100000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25164 | Menominee - 30th Ave. 69 kV (Y-199), Rebuild | Rebuild and install OPGW on approximately 1.3 miles of line Y-199 from Menominee SS to 30th Ave. SS. | MI | Other | Age and Condition |  |  |  |  | 2028-06-01 | 69 |  | 8400000
MTEP24 | West | OTTER TAIL POWER COMPANY | 9997 | OTP Rolette 230 kV Substation | Tap Xcel's 230 kV line between Rugby and Peace Garden and install 230/115/69 kV Transformer - Install three 230 kV breakers and two 69 kV breakers, and install one 230/115/69 kV Transformer (140 MVA) leaving the 115 kV winding disconnected. | ND | Other | Local Needs |  |  |  |  | 2026-12-31 | 230 |  | 8700000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50041 | West Junction SS 138 kV Sectionalizing | • Add a 138 kV bus with two-line breakers and a bus tie breaker and associated facilities at West Junction substation to provide for the required sectionalizing facilities, • Retirement of the West Junction Tap to Bluemound portion of 138 kV line 5066 and associated facilities in coordination with the Milwaukee Area 230 kV conversion to 345 kV Project, • Modification of the protection scheme and implement required networking protection. | WI | Other | Local Reliability |  |  |  |  | 2026-12-31 | 138 |  | 8700000
MTEP24 | Central | AMEREN ILLINOIS | 50045 | Austin Transformer 3 Replacement | Replace transformer 3 at Austin Substation which is AIC owned. | IL | Other | Age and Condition |  |  |  |  | 2027-12-01 | 345 |  | 6800000
MTEP24 | Central | AMEREN ILLINOIS | 22872 | Upgrade Macomb NE 138 kV substation | Add line breaker on the Macomb West line | IL | Other | Age and Condition |  |  |  |  | 2027-12-01 | 138 |  | 1800000
MTEP24 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25489 | North Lucedale 69kV Delivery Point | In order to serve the member delivery points economically and reliably, L34 (Lucedale – Rocky Creek) will be tapped with a 69kV Goab and a new 2.6-mile radial line will be constructed from the Goab to the member delivery point. | MS | Other | Load Growth |  |  |  |  | 2027-12-01 | 69 |  | 6399100
MTEP24 | West | GREAT RIVER ENERGY | 25547 | Blind Lake Breaker Addition | Remove switch 58NSM4 and replace with a circuit breaker. Replace existing breakers B1 and B2. | MN | Other | Local Reliability |  |  |  |  | 2027-12-30 | 69 |  | 8777667
MTEP24 | Central | AMEREN MISSOURI | 25276 | Conway 138kV Add Breakers and Aging Infrastructure | Add interrupting devices on XFMRs 1,2,3,4 Add Line BKRs to MASN-WLDW-1&2, CNWY-TYSN-3&4 Aging infrastructure replacements | MO | Other | Local Reliability |  |  |  |  | 2027-12-01 | 138 |  | 17500000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25000 | Lakefront SW YD – Revere Dr 69 kV (D-104), Partial Rebuild | Rebuild and install OPGW on approximately 1.84 miles of D-104 form Lakefront to Revere Dr. | WI | Other | Age and Condition |  |  |  |  | 2028-10-01 | 69 |  | 9000000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25342 | Missouri Creek Substation | Rebuild Eau Galle distribution substation as new Missouri Creek substation and convert existing Eau Galle distribution to 23.9kV. | WI | Other | Age and Condition |  |  |  |  | 2029-06-01 | 69 |  | 9000000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50036 | J1304 Big Hill Park SS Network Upgrades and Interconnection Facilities | Solar farm in Rock County, Wisconsin. | WI | GIP | [5 empty] | 2023-07-31 | 138 |  | 9112672
MTEP24 | South | ENTERGY SERVICES, LLC. | 25430 | Fairview to Madisonville 230 kV Upgrades | Upgrade Fairview to Madisonville 230 kV circuit to at least 2000 Amps. This includes conductor on this 0.2 mile facility. | LA | BRP | [5 empty] | 2027-12-01 | 230 |  | 700000
MTEP24 | South | ENTERGY SERVICES, LLC. | 25410 | Winshire 69 kV Capacitor Banks | Install two 11 MVAR capacitor banks at the Winshire 69 kV station. | TX | BRP | [5 empty] | 2027-12-01 | 69 |  | 7000000
MTEP24 | West | GREAT RIVER ENERGY | 25338 | Victor to Woodland Rebuild Projects | Rebuild about 14.4 miles of 69 kV line from Victor to the DX line. | MN | Other | Local Reliability |  |  |  |  | 2027-12-01 | 69 |  | 9303114
MTEP24 | South | ENTERGY MISSISSIPPI, LLC. | 50160 | J1672 Network Upgrades: Gerald Andrus 230kV Auto | Install a second 230/115 kV 392 MVA Autotransformer. The second autotransformer bank install will also require installing new protection panels per current Entergy standards. Installation of a double bus double breaker bay scheme at the 230 kV yard and a transfer bus configuration bay scheme on the 115 kV yard will be required. This project will also require the removal of the existing oil circuit breaker J7202 and installation of a new 115 kV bus tie breaker. | MS | GIP | [5 empty] | 2027-12-15 | 230 |  | 19750000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50110 | J1751 Young St SS Network Upgrades and Interconnection Facilities | J1751 is a solar facility in Wood County, WI. | WI | GIP | [5 empty] | 2028-09-10 | 138 |  | 9703000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25506 | Inver Grove – Inver Hills 115 kV Rebuild to Double Circuit 115 kV | Rebuild 2.2 miles 115 kV line 5507 to double circuit from Inver Grove - Inver Hills. Expand Inver Hills substation. Add 1 breaker at Umore substation. | MN | Other | Age and Condition |  |  |  |  | 2025-12-31 | 115 |  | 10000000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25270 | 0760 Redwing - Lake City - Str 217 Rebuild | Rebuild 18 miles 69 kV with new structures, new OPGW shield wire, and new conductor. | MN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 69 |  | 10000000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25443 | Z84-1 Culley - Dubois Rebuild | Replacing ~ 33 miles of poles for the 138kV line from Culley to Dubois | IN | Other | Age and Condition |  |  |  |  | 2027-12-31 | 138 |  | 47500000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25348 | Saratoga – 7 Mile Creek 138 kV, Construct New Line | Interim configuration: • Construct a new Saratoga – 7 Mile Creek (X-New) 138-kV line, double-circuiting it with existing Saratoga – ACEC Grant (Y-301) 69-kV line. • At 7 Mile Creek SS, relocate existing 7 Mile Creek – Sand Lake (X-11) 138-kV line to connect the new line at existing X-11’s terminal. In addition, construct a new section of approx. 0.05 miles on X-11 for its interconnection to bus 4, eliminating the need for 138-kV crossings. Finally, install new 138 kV substation equipment (breaker and switch) at 7 Mile Creek to complete its 4-position ring bus. • At Saratoga SS, install one 138-kV line circuit breaker with manual line and bus-side disconnect switches for the new line. In addition, install a new 138-kV bus-tie breaker and replace Saratoga – Badger West (X-43) 138-kV line jumpers, and buses 1 and 2 jumpers, to allow higher ratings on existing facilities. Finally, reroute X-159 line preventing it from being above the new line’s terminal. Final configuration: • After Northern Adams County Area Network Improvement Project is placed in service in 2027, retire Saratoga 138/69-kV T33 transformer and re-terminate the new line with this vacated position. This will prevent the new line passing over its existing box structure. | WI | Other | Local Reliability |  |  |  |  | 2027-12-31 | 138 |  | 10300000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50042 | Substation Technology Package #2 - 2025 | The Substation Technology Package #2 (SSTP#2) program of work will set the stage for the future of the digital substation field worker by providing enhanced Business Capabilities over ATC’s substation fiber network infrastructure. The SSTP#2 – 2025 project scope will include the following technology enhancements: • Installation of Wireless Access Points (AP) at various ATC substations • Installation of Cyber Security fortifications for Rogue Device detection at various ATC substations • Convert select Telecom equipment to DC power at various ATC substations | WI | Other | Local Needs |  |  |  |  | 2025-12-31 | 0 |  | 10500000
MTEP24 | West | ITC MIDWEST | 25247 | ITCM Abbott - Marshalltown 161 kV Rebuild | ITC will rebuild the Pheonix/SD and Rail portions of Abbott – Marshalltown 161kV circuit with T2-Grosbeak. | IA | Other | Age and Condition |  |  |  |  | 2028-12-31 | 161 |  | 10762500
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25220 | Cuba City South, DIC, Sub Expansion | • ATC will construct 0.63 miles of new 69 kV line. • ATC will rebuild 1.12 miles of the existing Cuba City South Tap as a new double circuit 69 kV line to provide a loop-through connection to the Cuba City South Substation. • ATC will construct a loop-through, straight bus substation with two 69 kV line breakers. • Cuba City will install a 69/12.47 kV transformer at Cuba City South. | WI | Other | Load Growth | Cuba City South DIC Sub Expansion | Data Center/DIC Campus | Y |  | 2027-12-31 | 69 |  | 11000000 | ATC $11M
MTEP24 | Central | PRAIRIE POWER, INC. | 25450 | Rebuild Breiner-Spring Lake Jct. 69 kV Line | Rebuild Breiner-Spring Lake Jct. 69 kV Line | IL | Other | Age and Condition |  |  |  |  | 2027-12-31 | 69 |  | 5500000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25226 | Union Townline, DIC, Sub Expansion | • ATC will construct an approximately 0.08 mile 69 kV transmission line extension from the Bass Creek-Sheepskin 69 kV line (Y-158) to the Union Townline substation for a networked substation feed. • ATC will construct a 69 kV loop-through straight bus with line breakers, associated switches, and space reserved for a potential bus-tie breaker. • Evansville Water & Light (WPPI) to install a second 69/12.47 kV transformer with high side circuit switcher protection and necessary low side bus equipment. | WI | Other | Load Growth | Union Townline DIC Sub Expansion | Data Center/DIC Campus | Y |  | 2026-11-01 | 69 |  | 11600000 | ATC $11.6M
MTEP24 | West | MINNESOTA POWER INC. | 21767 | 13 Line Rebuild | Rebuild Portage Lake - Riverton ("13 Line") 115 kV Line. The project will also add shield wire and OPGW for operations and relay improvements. | MN | Other | Age and Condition |  |  |  |  | 2027-03-31 | 115 |  | 12000000
MTEP24 | East | METC | 25230 | Manning #2 345-138 kV Transformer Replacement | Replace the Manning #2 345/138 kV transformer with at least 650 MVA (2718 Amps) summer emergency rated transformer. Also install a new high side 3000 Amps disconnect switch. | MI | Other | Age and Condition |  |  |  |  | 2027-12-31 | 345 |  | 7060000
MTEP24 | East | ITC | 25208 | Brownstown #304 345-120 kV Transformer Replacement | Replace the Brownstown #304 transformer with a standard 345/120 kV, 560MVA (approx. 715MVA Summer-Emergency rated) transformer. | MI | Other | Age and Condition |  |  |  |  | 2027-12-31 | 345 |  | 6572000
MTEP24 | East | ITC | 25218 | Sterling #201 230-120 kV Transformer Replacement | Replace the Sterling #201 230/120 kV transformer with a transformer of at least 728 MVA (3503 Amps) summer emergency rating. Install a breaker and associated equipment on the high side of the transformer. | MI | Other | Age and Condition |  |  |  |  | 2027-12-31 | 230 |  | 7950000
MTEP24 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 25290 | Sprott 69/12kV Substation | Construct New Sprott 69/12 kV Substation to serve new load and relieve nearby delivery points | MO | Other | Load Growth |  |  |  |  | 2027-12-31 | 69 |  | 1200000
MTEP24 | East | METC | 25277 | METC Customer Interconnections - 2027 | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in service date within the year 2027 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million a separate project will be submitted for approval. | MI | Other | Load Growth |  |  |  |  | 2027-12-31 | 345 |  | 2500000
MTEP24 | West | GREAT RIVER ENERGY | 25337 | Meadowbrook to Side Lake Area Projects | Rebuild Meadowbrook to Side Lake line, replace Meadowbrook and Side Lake switches. | MN | Other | Age and Condition |  |  |  |  | 2027-12-01 | 69 |  | 12124891
MTEP24 | East | ITC | 25364 | ITCT Customer Interconnections - 2027 | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in-service date within the year 2027 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million a separate project will be submitted for approval. | MI | Other | Load Growth |  |  |  |  | 2027-12-31 | 345 |  | 2500000
MTEP24 | Central | HOOSIER ENERGY | 25560 | Centerton-Wilbur New 69kV Line and Upgrades | Construct a new 5.8 mile 69kV line between Hoosier's Wilbur station and DEI's Centerton station. Upgrade approximately 18 miles of 69kV line around the Mooresville, IN area, including the following branches: 07Wilbur-07Nelson, 07Nelson-07WilburJct, 07WilburJct-07Moores, 07WilburJct-07HartLake, 07HartLake-08MoorJct, 07Moores-08ToytJct. | IN | Other | Local Reliability |  |  |  |  | 2027-12-31 | 69 |  | 34650000
MTEP24 | Central | PRAIRIE POWER, INC. | 23374 | New Babylon 138/69 kV Substation and Lines | 1) New 138 kV line to interconnect Babylon substation to a new Ameren Steamboat ring bus 2) New Babylon 138/69 kV substation 3) New Babylon-Canton 69 kV line 4) New Babylon-Ellisville/Smithfield double-circuit line | IL | Other | Local Reliability |  |  |  |  | 2027-12-31 | 138 |  | 18320000
MTEP24 | Central | PRAIRIE POWER, INC. | 23373 | New Industry-Ipava 69 kV Line | 1) New Industry-Table Grove 69 kV line 2) New Table Grove-Ipava 69 kV line | IL | Other | Local Reliability |  |  |  |  | 2027-12-31 | 69 |  | 15700000
MTEP24 | West | GREAT RIVER ENERGY | 25423 | Fox Lake Area Upgrades | Rebuild FE-FD line, the Fox Lake switching station, and the Dunnell switch. | MN | Other | Age and Condition |  |  |  |  | 2027-09-30 | 69 |  | 12469907
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25429 | Liberty Substation 161-69 kV Expansion and Associated Lines | Construct second 69 kV line into Terra Substation, expand Liberty Substation to install a 161-69 kV, 125 MVA transformer and 69 kV bs and rebuild the existing Neal North-Terra 69 kV line. | IA | Other | Local Reliability |  |  |  |  | 2027-12-01 | 161 |  | 12500000
MTEP24 | West | MONTANA-DAKOTA UTILITIES CO. | 50152 | Ellendale load 3 addition | MDU has a third load request at Ellendale, ND for an additional 125 MW. MDU will serve this load from the Ellendale Data Center Substation that is being built as part of MTEP project 50037. An additional 230 kV line will be added that will run from the Ellendale Substation to the Ellendale Data Center Substation. An additional 230/34.5 transformer, 230 kV breakers and 34.5 kV breakers will be added at the Ellendale Data Center Substation. | ND | Other | Load Growth | Ellendale load 3 addition; 125MW data center EPR | Data Center | Y | 125 | 2025-09-01 | 230 |  | 12575738 | 3rd data center load at Ellendale ND, 125 MW. Served from Ellendale Data Center Sub (MTEP 50037)
MTEP24 | West | ITC MIDWEST | 25222 | J1432 GIA NU New Bryant 345 kV Switch Station | A new Bryant 345 kV, 3 breaker, ring-bus switching station will be constructed for the interconnection of project J1432. The Salem to Rock Creek 345 kV line will be opened and 2 dead-end structures will be installed to allow the line to be looped through the Bryant 345 kV switching station and dual fiber will be needed to Rock Creek from the new substation.¿ And upgrades required to install fiber at Rock Creek. | IA | GIP | [5 empty] | 2028-09-01 | 345 |  | 12787112
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25300 | Nobles County Third Transformer | Add third 345/115 kV transformer with tertiary reactor at Nobles County. | MN | BRP | [5 empty] | 2028-05-01 | 345 |  | 13250000
MTEP24 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25520 | South Lucedale 69kV Delivery Point | In order to serve the member delivery point economically and reliably, a new 2.7-mile radial line will be constructed from the Lucedale 69kV Switching Station to the member delivery. | MS | Other | Load Growth |  |  |  |  | 2028-03-01 | 69 |  | 6477100
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25448 | Browns Woods Substation and 161 kV lines | Construct a new 161-13 kV substation and 161 kV lines and retire 63rd & Park Substation and 69 kV lines | IA | Other | Load Growth |  |  |  |  | 2026-12-01 | 161 |  | 13400000
MTEP24 | West | GREAT RIVER ENERGY | 25374 | Blackberry Area Rebuild Projects | Rebuild 69 kV lines in Blackberry area along with switch replacements. | MN | Other | Local Reliability |  |  |  |  | 2027-12-10 | 69 |  | 14260525
MTEP24 | Central | HOOSIER ENERGY | 25350 | New Waynesville 345kV Station | A new transmission station South of Walesboro, IN will be built to support load growth and reliability in the Walesboro Area. The station will be a 345 kV to 69 kV station. The station will feature a 345 kV ring bus design with 4 breakers and two 345 kV :69 kV transformers. The project also includes new 69kV lines from the Waynesville Transmission Station to Ogilville, Walesboro Industrial Park, and Woodside. The existing 2-mile Ogilville tap line will be rebuilt to support the new 69kV transmission loop. | IN | Other | Local Reliability | New Waynesville 345kV Station for load growth and reliability | Load Growth + Reliability |  |  | 2028-05-31 | 345 |  | 58160000 | Labeled Local Reliability but desc says "support load growth and reliability in the Walesboro Area"
MTEP24 | East | ITC | 50060 | Bismarck - Macomb 120 kV Line | Construct a new 120 kV line (~6.7 miles) from Bismarck to Macomb. Approximately 3.9 miles of this new circuit will be using new 954 ACSR conductor, 2.7 miles of which will be strung on the vacant side of existing Lenox - Stephens 120 kV structures and the other 1.2 miles will be on new ROW. The remaining section from the west-to-east crossover point toward Macomb (2.8 miles) will utilize existing 795 ACSR conductor through undoing 6-wire on the Macomb - Stephens 120 kV circuit. This new 120 kV line will require installations of a new 120 kV breaker at Bismarck and Macomb stations. | MI | BRP | [5 empty] | 2028-06-01 | 120 |  | 11160000
MTEP24 | East | METC | 20017 | Rebuild Alma (Cheesman) - Regal #1 138 kV | ITC is to rebuild approximately 1.34 miles of the Alma (Cheesman) – Regal #1 138kV with 954 ACSR 138kV double circuit standards with OPGW and upgrade terminal station equipment at Regal. | MI | BRP | [5 empty] | 2028-06-01 | 138 |  | 18031000
MTEP24 | East | METC | 15831 | Alma - Regal #2 138 kV Rebuild | Rebuild ~3.8 miles of the ~5.8 mile-long Alma – Regal 2 138 kV line to 138 kV double circuit standards construction by replacing the existing assets (all structures and 336 ACSR conductor) with new structures that are designed for 954 ACSR conductor and install this conductor along with OPGW. Relocate CE's 46kV circuit to the under-build and leave the vacant 138 kV side of the new structures for future transmission use. | MI | BRP | [5 empty] | 2028-06-01 | 138 |  | 11311000
MTEP24 | East | METC | 22015 | Blackstone – Leoni #1 and #2 138 kV Rebuild | Rebuild approximately 4.2 miles of circuits #1 and #2 from Blackstone 138 kV to Leoni 138 kV to 954 ACSR conductor using 138 kV double- circuit structures. Install OPGW. Upgrade station equipment at Blackstone to at least 431 MVA (1804 Amps) summer emergency rating. The Blackstone – Leoni #2 138 kV circuit currently shares towers with both the Blackstone – Leoni #1 and #3 138 kV circuits. This project moves the Blackstone – Leoni #2 138 kV circuit entirely on to the Blackstone – Leoni #1 138 kV double-circuit structures. | MI | BRP | [5 empty] | 2028-06-01 | 138 |  | 9840000
MTEP24 | East | METC | 22018 | Blackstone – Leoni #3 138 kV Rebuild | The proposed solution is to rebuild approximately 4.2 miles of the Blackstone – Leoni #3 138 kV line using 954 ACSR on double circuit structures constructed at 138kV Standards, with future double circuit on the northeast side of the towers. Install OPGW along the entire length from Blackstone to Leoni. | MI | BRP | [5 empty] | 2028-06-01 | 138 |  | 8405000
MTEP24 | East | METC | 25217 | Blendon 138 KV Capacitor | Install (1) 33.33 MVAR capacitor bank with associated 138kV, 40 kA synchronous breakers and disconnect switch at the Blendon 138kV substation. The proposed capacitor will be connected to bus 40 and Transformer 1 will be moved to Bus 50. Relocate the existing Blendon-Campbell 138kV line termination from bus 30 to the bus 60. Also, Relocate the existing Blendon-Fairview 138kV line termination from bus 60 to the section 30 bus. | MI | BRP | [5 empty] | 2028-06-01 | 138 |  | 4260000
MTEP24 | East | METC | 20034 | Sag Remediate Higgins - Mio Dam 138 kV | The proposed solution is to remediate sag limit on the 266.8 ACSR on the Higgins – Mio Dam 138kV line up to the conductor’s limit. | MI | BRP | [5 empty] | 2028-06-01 | 138 |  | 2800000
MTEP24 | East | METC | 20119 | Sag Remediate Claremont - Cornell #2 138 kV | METC is to raise the sag limit on the 477 ACSR to 257F and 795 ACSR to 178F on the Bell Road – Cornell section of the Claremont - Cornell #2 138 kV Line | MI | BRP | [5 empty] | 2028-06-01 | 138 |  | 1263000
MTEP24 | East | METC | 14344 | Airport - Hillman Tap 138 kV Sag Remediation | Remediate the sag limit on ~17.0 miles of 266 ACSR conductor of the ~21.3 mile-long Airport - Hillman Tap 138 kV section of the Airport - Mio 138 kV line to at least the planned target summer normal/summer emergency rating of 133 MVA/556 Amps. | MI | BRP | [5 empty] | 2028-06-01 | 138 |  | 1061250
MTEP24 | East | METC | 18072 | Sag Remediation Hubbard Lake – Spruce Road 138 kV | Remediate the sag on the Hubbard Lake – Spruce Road section of the Alpena – Iosco 138kV line to at least 124 MVA for summer emergency rating. | MI | BRP | [5 empty] | 2028-06-01 | 138 |  | 700000
MTEP24 | East | METC | 25216 | Gaines - Caledonia Jct. 138 kV Sag Remediation | Remediate sag on the 795 ACSS up to 153 MVA (summer ratings) on the Gaines – Caledon J. section of the Thompson Road – Gaines 138 kV circuit. | MI | BRP | [5 empty] | 2028-06-01 | 138 |  | 520000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25325 | 0986 K Frame Replacement | Replace wood K-frame and H-frame structures with new steel H-frame structures on 345 kV line 0986. | MN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 345 |  | 15000000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25341 | 0987 K Frame Replacement | Replace wood K-frame and H-frame structures with new steel H-frame structures on 345 kV line 0987. | MN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 345 |  | 15000000
MTEP24 | East | METC | 50121 | Iosco - Karn 138 kV Relocation (#50064 Alternative) | Utilizing the existing vacant side of the Twining – Whittemore and Shale - Twining to string East Tawas - Quarry and Quarry - Karn 138 kV circuits on these double-circuit structures with 954 ACSR and also install OPGW. Construct ~1.5 mile from Cottage Grove to a new location a new ROW. Replace station equipment East Tawas and Cottage Grove substations. CE to tap their existing Santiago and Seven Mile stations to the new conductor on Quarry – Cottage Grove 138 kV line. ITC’s Asset Management Department identified this line for rebuild due to the age and condition of the line. Rebuilding approximately 46 miles of the Iosco-Karn 138kV line would reduce equipment failures, unplanned outages and repair costs. Ultimately, increasing reliability of the system and bringing the line up to the current line design standards. Additionally, rebuilding this circuit with 954 ACSR conductor will increase system capacity to support the increasing load and renewable generator interconnections around the Arenac, Bay, and Iosco counties. | MI | Other | Age and Condition |  |  |  |  | 2028-06-01 | 138 |  | 45060000
MTEP24 | South | ENTERGY SERVICES, LLC. | 13905 | Burnside 230-115 kV Autotransformer | 1) Construct a 3 breaker 230 kV ring bus at Burnside, Minimum of 2000 Amp equipment. 2) Cut in and out the Conway to Panama 230 kV line. 3) Install 230-115 kV Autotransformer 4) Install 115 kV low side breaker at Burnside. | LA | BRP | [5 empty] | 2028-06-01 | 230 |  | 34260000
MTEP24 | East | METC | 25195 | MCV 345-138 kV Transformer Addition | Install six 345 kV breakers to convert the 345 kV side to ring-bus. Expand MCV 138 kV buses, replace 10 existing breakers, and install 3 additional breakers to the west as depicted in the diagram to accommodate the 3rd XFMR at MCV. Install a new 345/138 kV transformer and terminated it at the newly created 345 & 138 kV positions. | MI | Other | Local Reliability |  |  |  |  | 2028-06-01 | 345 |  | 36750000
MTEP24 | East | METC | 25198 | Port Calcite 138 kV Station Rebuild | Rebuild Port Calcite into a four (4) position ring bus configuration that can be converted to Breaker and a half in the future. The new substation is located to the Northwest of existing station. | MI | Other | Local Reliability |  |  |  |  | 2028-06-01 | 138 |  | 9811000
MTEP24 | South | LAFAYETTE UTILITIES SYSTEM | 50139 | J1818 Generator Interconnection at Moss 69kV Station | Interconnection Facilities required for the interconnection of J1818 at Moss 69 kV Station | LA | GIP | [5 empty] | 2028-06-30 | 69 |  | 993000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25461 | Johnson Creek - Maffitt Lake 161 kV line | Construct a new 161 kV line | IA | Other | Load Growth |  |  |  |  | 2027-08-01 | 161 |  | 15300000
MTEP24 | West | MONTANA-DAKOTA UTILITIES CO. | 50037 | Ellendale load 2 addition | MDU has an additional load request at Ellendale, ND for a total demand of 225 MW. MDU will serve the customer from its Ellendale 345 substation from the 230 kV. A 230 kV line will run to a new sub where a 230/34.5 transformer will be added along with the 34.5 kV breakers. | ND | Other | Load Growth | Ellendale load 2 addition; 225MW data center EPR | Data Center | Y | 225 | 2024-09-01 | 230 |  | 16776939 | 2nd data center load at Ellendale ND, 225 MW total. New Data Center Sub with 230 kV line from 345 kV sub
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25449 | Norwoodville Substation and 69 kV lines | Construct a new 69 kV switching substation and lines | IA | Other | Local Reliability |  |  |  |  | 2027-12-31 | 69 |  | 16900000
MTEP24 | West | MONTANA-DAKOTA UTILITIES CO. | 25503 | MDU Network and Interconnection Upgrades - J1040 | A 250 MW wind project (J1040) is interconnecting at MDU's Wishek 230 kV substation as part of DPP 2018 study cycle. The project has been assigned the following network and interconnection upgrades. Wishek substation - terminal equipment to interconnect project (PCB, Disconnects, bus work) Mandan-Napoleon 230 kV line - terminal equipment (Re-tap CTs Mandan and jumpers at Napoleon) Wishek-Merricourt 230 kV line - reconductor and pole replacement Merricourt Substation - Add another breaker and re-terminate one of the 230 kV lines Ellendale Substation - 115 kV terminal equipment for line to Aberdeen | ND | GIP | [5 empty] | 2026-10-01 | 230 |  | 18115000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 22911 | Load Interconnection Program 2025 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2025. | MI; WI | Other | Load Growth |  |  |  |  | 2027-06-30 | 345 |  | 19000000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25428 | New Shenandoah Substation and 69 kV lines | Construct a new 69-13 kV substation and 69 kV lines | IA | Other | Load Growth |  |  |  |  | 2027-12-31 | 69 |  | 19100000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25433 | J1270 POI New 345 kV Interconnection Substation and 345 kV Line Taps | Construct new 345 kV POI substation and 345 kV line taps for J1270 wind farm | IA | GIP | [5 empty] | 2025-09-18 | 345 |  | 19500000
MTEP24 | West | DAIRYLAND POWER COOPERATIVE | 25498 | J898 Generation Interconnection Network Upgrades | J898 will require a 4-breaker, 161 kV ring bus for a POI | MN | GIP | [5 empty] | 2027-09-01 | 161 |  | 19574516
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50111 | J1773 Edmund Swt St Network Upgrades and Interconnection Facilities | J1773 is a wind facility in Lafayette County, WI. | WI | GIP | [5 empty] | 2030-03-10 | 345 |  | 19693000
MTEP24 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25419 | Hermanville 115kV Delivery Point | In order to serve the member delivery point, tap Utica Loop line with a 115kV Goab and construct a new line to the delivery point. | MS | Other | Load Growth |  |  |  |  | 2028-11-01 | 115 |  | 700000
MTEP24 | West | GREAT RIVER ENERGY | 25456 | Spring Creek Upgrade Projects | Spring Creek - transformer replacement and upgrade | MN | Other | Age and Condition |  |  |  |  | 2029-12-31 | 161 |  | 19992124
MTEP24 | South | ENTERGY SERVICES, LLC. | 25432 | Cypress to Legend 500 kV line | Construct a new ~35 mile 500 kV line between Cypress and Legend 500 kV stations. Expand the Cypress and Legend stations to accommodate the new facilities. Build a 500 kV station at Legend, and install a 500-230 kV Autotransformer. Upgrade Kolbs 69 kV breakers 2870 and 209. | TX | BRP |  | Cypress to Legend 500 kV line; selected because superior performance under future load growth; P3 overloads | Load Growth (BRP) |  |  | 2028-12-01 | 500 |  | 405900001 | ETI BRP $406M; load growth drove selection over alternatives
MTEP24 | South | ENTERGY SERVICES, LLC. | 25435 | Serpent to Tupper 69 kV Upgrade | Upgrade 69 kV bus at Tupper. | LA | BRP | [5 empty] | 2028-12-01 | 69 |  | 1200000
MTEP24 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 25284 | Rebuild Salem Bulk to Seminary 69kV Line T10 | Rebuild 29.54 miles of 69kV between Salem Bulk and Seminary. Voltage issue fix from Long Range Study. | MO | Other | Age and Condition |  |  |  |  | 2028-12-31 | 69 |  | 60000000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25458 | Gibson 345kV Ckt Brkr Upgrades | Gibson 345 CB upgrades - TPL-001 short ckt overduty - replace (18) 345kV-63kA interrupting rated CBs with 80kA; replace breaker disconnect switches and upgrade bus conductor as needed. ALTERNATIVE: add neutral to ground fault current limiting reactors on Gibson Units 1 and 2 GSUs (6 ohms) currently under consideration. | IN | BRP | [5 empty] | 2028-12-31 | 345 |  | 27000000
MTEP24 | West | ITC MIDWEST | 25345 | ITCM Cleveland to Sheas Lake Rebuild | ITC will rebuild approximately 10 miles of the Cleveland to Sheas Lake 69 kV line. The line will be rebuilt to 115 kV or 161 kV Standards with T2-477 ACSR and OPGW. | MN | Other | Age and Condition |  |  |  |  | 2029-12-30 | 69 |  | 22306250
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25268 | Replace 345-138 kV Petersburg East & West Autos | Replacement of the Petersburg 345/138 kV 300 MVA autotransformers with 500 MVA autotransformers. Project scope includes adding redundant relaying to each autotransformer. | IN | BRP | [5 empty] | 2028-12-31 | 345 |  | 12000000
MTEP24 | East | WOLVERINE POWER SUPPLY COOPERATIVE, INC | 50098 | Hagensville Junction Interconnection | Interconnect Wolverine's Hagensville Junction with METC's Rockport to Port Calcite line. | MI | BRP | [5 empty] | 2028-12-31 | 138 |  | 17550000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50184 | Elm Road Generation POI Relocation Project | Driven by WEC’s Generating Facility Modification Request to relocate Elm Road generation POIs, this project will expand Elm Road 345 kV substation breaker and a half configuration with three new rungs and six new 345kV breakers. | WI | GIP | [5 empty] | 2026-06-30 | 345 |  | 22600000
MTEP24 | West | GREAT RIVER ENERGY | 25399 | Congestion Mitigation Projects | The facilities included in this project are being upgraded to achieve higher ratings to mitigate market congestion caused by these facilities. | MN | Other | Local Reliability |  |  |  |  | 2028-02-01 | 230 |  | 23452560
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25440 | Vigo Coal 69/12kV Xformer and CB Replacement | Replacing 69/12kV transformer and circuit breakers | IN | Other | Age and Condition |  |  |  |  | 2028-12-31 | 69 |  | 6000000
MTEP24 | West | MINNESOTA POWER INC. | 23706 | 158 Line Rebuild | Rebuild Portage Lake - Cromwell ("158 Line") 115 kV Line. The project will also add shield wire and OPGW for operations and relay improvements. | MN | Other | Age and Condition |  |  |  |  | 2027-03-31 | 115 |  | 25000000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25147 | Mead Johnson 69/12kV Transformer Replacement | Replacement of a 69/12kV distribution transformer and several breakers due to age and to support local load growth | IN | Other | Age and Condition | Mead Johnson transformer replacement driven by load growth and age | Load Growth + Age |  |  | 2028-12-31 | 69 |  | 3800000 | Labeled Age&Condition but desc adds "and to support local load growth"
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25359 | Louis Allis Switch Replacement | Replacing several switches and distribution breakers | IN | Other | Age and Condition |  |  |  |  | 2028-12-31 | 69 |  | 2300000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25394 | Midway 69/2.4kV Transformer Replacement | Replacing several 69/2.4kV transformers and switches | IN | Other | Age and Condition |  |  |  |  | 2028-12-31 | 69 |  | 2000000
MTEP24 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 25406 | Santa Claus Switch Replacement | Replacing several 69kV switches | IN | Other | Age and Condition |  |  |  |  | 2028-12-31 | 69 |  | 1500000
MTEP24 | Central | DUKE ENERGY INDIANA, LLC | 25332 | WVPA Pike 69kV Line Rebuild | WVPA Pike 69kV Line Rebuild - Rebuild 69kV line feeding Pike substation | IN | Other | Load Growth |  |  |  |  | 2028-12-31 | 69 |  | 15000000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25507 | Umore Park 115 kV Substation | New 115kV load serving substation with in-and-out tap to existing Rosemount - Empire 115 kV line 0822. Build 6 miles new double circuit 115 kV line from Umore Park - Inver Grove. | MN | Other | Load Growth |  |  |  |  | 2025-12-31 | 115 |  | 35000000
MTEP24 | West | GREAT RIVER ENERGY | 25396 | Otsego Area Rebuilds | Rebuild EMX to Maple Lake line. | MN | Other | Age and Condition |  |  |  |  | 2029-02-28 | 69 |  | 40078416
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 22798 | Small Capital Project and Asset Renewal Program 2025 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2025. | MI; WI | Other | Age and Condition |  |  |  |  | 2027-06-30 | 345 |  | 45000000
MTEP24 | East | WOLVERINE POWER SUPPLY COOPERATIVE, INC | 25191 | Leroy to South Boardman DC Line Rebuild | Rebuild and upgrade 43 miles of 69 kV line from Cadillac to South Boardman to 138 kV using Wolverine’s construction standards. Line to be built with double circuit steel structures. | MI | Other | Local Reliability |  |  |  |  | 2028-12-31 | 138 |  | 52100000
MTEP24 | West | NORTHERN STATES POWER COMPANY | 25323 | St Croix Valley Upgrades | "New 115kV transmission line from the proposed Junction Mill substation in River Falls to a new South Hudson substation to Willow River Build a new South Hudson substation. Replace the two 70 MVA TR’s at Willow River. Add bus and breaker at Willow River to accommodate the new 115kV transmission line" | WI | Other | Local Reliability |  |  |  |  | 2029-09-30 | 115 |  | 45000000
MTEP24 | East | ITC | 25228 | DBGEN 41 120 kV Station Rebuild | Rebuild the 120 kV DBGEN 41 station to five rows of breaker and a half station due to age/condition. | MI | Other | Age and Condition |  |  |  |  | 2029-03-31 | 120 |  | 64200000
MTEP24 | East | ITC | 25363 | ITCT SPOF Blanket | Blanket for projects to address locations where single point of failure (SPOF) are identified that cause system issues. | MI | BRP | [5 empty] | 2029-06-01 | 345 |  | 12100000
MTEP24 | West | MIDAMERICAN ENERGY CO. | 25412 | Line Rebuilds Blanket 2025 - 2027 | Blanket project to rebuild 69 kV, 161 kV and 345 kV lines due to condition and to improve reliability and operational flexibility. | IA | Other | Age and Condition |  |  |  |  | 2029-12-01 | 345 |  | 45000000
MTEP24 | East | METC | 25275 | METC SPOF Blanket | Blanket for projects to address locations where single point of failure (SPOF) are identified that cause system issues. | MI | BRP | [5 empty] | 2029-06-01 | 345 |  | 19500000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 25372 | New 345-138 kV Monrovia Substation | New 2-bay 345/138 kV breaker-and-a-half substation. Looped-in on the 345-01 Petersburg-Thompson line. 1 300/400/500 MVA 345/138 kV autotransformer. 1 40 MVA 138 kV to serve load. | IN | Other | Load Growth |  |  |  | 500 MVA | 2029-06-30 | 345 |  | 35348000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 24778 | Grant County, DIC, New Substation | New load interconnection request in SW Wisconsin. Project scope includes construction of a new 69-kV transmission line to network Hillman – Miners (Y-130) 69-kV line with a new 69-kV substation near the customer site. | WI | Other | Load Growth | Grant County DIC New Substation for Data Innovation Campus | Data Center/DIC Campus | Y |  | 2028-01-01 | 69 |  | 50100000 | Grant County DIC: new load interconnection in SW Wisconsin. $50M
MTEP24 | West | ITC MIDWEST | 25212 | ITC Midwest Asset Replacement Program 2026 | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA; IL; MN | Other | Age and Condition |  |  |  |  | 2026-12-31 | 345 |  | 52625000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 24555 | New - Waverly - 138 kV Substation | New 138 kV, one 13.5 MVA transformer, three-breaker ring bus substation to serve customer load | IN | Other | Load Growth |  |  |  | 5 MVA | 2029-12-01 | 138 |  | 6000000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 24983 | Hilltop – Council Creek 69 kV (Y-74), Rebuild & OPGW | Rebuild and install OPGW on approximately 29 miles of 69 kV line Y-74 from Hilltop Substation to Council Creek Substation and rebuild ~0.5 miles of Camp Douglas Tap. | WI | Other | Age and Condition |  |  |  |  | 2026-10-31 | 69 |  | 56000000
MTEP24 | West | MINNESOTA POWER INC. | 3856 | HVDC 900MW Transmission Line Upgrades | Upgrade the capacity of the existing Square Butte – Arrowhead HVDC transmission line from 550 MW to 900 MW, generally by replacing existing structures with taller structures and reconductoring a short segment of line. | MN; ND | TDSP | [5 empty] | 2028-12-31 | 250 |  | 58000000
MTEP24 | West | ITC MIDWEST | 50106 | Big Cedar Interconnection | ITC Midwest will construct the new Big Cedar 345 kV Switching Station which will connect to the existing ITC Midwest Beverly - Morgan Valley 345 kV line and add a 2nd Beverly – Big Cedar 345 kV line on existing structures. The new switching station will be constructed in a breaker and ½ configuration and provide service/connections to multiple customer owned transformers/substations. | IA | Other | Load Growth | Big Cedar Interconnection - large new load in Cedar Rapids IA area | Large Industrial |  |  | 2026-03-31 | 345 |  | 63743317 | Big Cedar Load Expansion Phase 2: new 345kV switching station + 2nd 345kV line (ITCM). $64M
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 21900 | Mullet River Area Reliability Project | Retire existing Mullet River and North Mullet River substations, retire Y-50 between North Mullet River substation and tap to new substation. Design and construct a new 138 kV / 69 kV switching station at a green field location, proposed site to be located south of County Road PP at the intersection of South Road. Tie X-97 and X-57 together near existing Mullet River substation using the south circuit on X-57. Tie X-89and X-57 together near the existing Mullet River substation using the north circuit on X-57. Reroute 8241, LYNG11, X-57, X-89, X-97, and Y-50 into new substation, including any OPGW fiber. Rebuild X-57 which currently is single circuit bifurcated as double circuit from existing Mullet River to location of taps to new site to accommodate extending X-89 and X-97 from existing Mullet River to new substation. | WI | BRP | [5 empty] | 2028-11-01 | 138 |  | 64600000
MTEP24 | Central | PRAIRIE POWER, INC. | 25318 | Upgrade Winchester 138/69 kV Transformer | Upgrade Winchester 138/69 kV Transformer with 140 MVA unit | IL | Other | Age and Condition |  |  |  |  | 2029-12-31 | 138 |  | 3500000
MTEP24 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 24274 | New - 138 kV Maloney-Reservoir Loop | A new 138 kV loop with two substations to serve growing customer load including a rebuild of one existing 138 kV line. | IN | Other | Load Growth |  | Load Growth |  |  | 2029-12-31 | 138 |  | 71400000 | Maloney-Reservoir Loop: 138kV loop with 2 new subs for growing customer load (IPL IN). $71.4M
MTEP24 | Central | PRAIRIE POWER, INC. | 25315 | New Forest City-St. David 69 kV Line | 1) New Forest City-Breeds 69 kV Line 2) New Breeds-Sky Rocket 69 kV Line 3) New Sky Rocket-St David 69 kV Line | IL | Other | Local Reliability |  |  |  |  | 2029-12-31 | 69 |  | 20130000
MTEP24 | Central | PRAIRIE POWER, INC. | 25316 | New Plymouth-Macomb 69 kV Line | 1) New Plymouth Breaker Station 2) New Plymouth-Colmar 69 kV Line 3) New Colmar-Fandon 69 kV Line 4) New Fandon-Colchester 69 kV Line 5) New Colchester-Macomb 69 kV Line | IL | Other | Local Reliability |  |  |  |  | 2029-12-31 | 69 |  | 19065000
MTEP24 | Central | PRAIRIE POWER, INC. | 23426 | New Rushville-Ipava 69 kV Line | 1) New Rushville-Astoria 69 kV line 2) New Astoria-Ipava 69 kV line | IL | Other | Local Reliability |  |  |  |  | 2029-12-31 | 69 |  | 16185000
MTEP24 | Central | PRAIRIE POWER, INC. | 23375 | Replace Babylon 138/69 kV XFMR | Replace the 56 MVA Delta-Wye Babylon 138/69 kV transformer with an 84 MVA Wye-Wye transformer. | IL | Other | Local Reliability |  |  |  |  | 2029-12-31 | 138 |  | 2600000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 23910 | Eden – Rock Branch 69kV (Y-106), Rebuild & OPGW | Rebuild of line Y-106 from Eden SS to Rock Branch SS. Full rebuild of line with enhanced 69 kV structures and OPGW. This project relieves economic congestion and serves as an asset renewal project. | WI | Other | Age and Condition |  |  |  |  | 2030-12-31 | 69 |  | 67900000
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 25299 | Racine County, DIC, Nimbus Substation | A new 138/24.9 kV breaker-and-a-half substation named Nimbus and 4 short 138 kV transmission lines (less than 1.0 mile) from the existing Mount Pleasant Substation to the new Nimbus Substation. New bus positions at the Mount Pleasant Substation will need to be added to connect the new transmission lines. | WI | Other | Load Growth | Racine County Data Innovation Campus Nimbus Substation; EPR | Data Center/DIC Campus | Y |  | 2025-04-01 | 138 |  | 89000000 | Racine County Nimbus: new 138/24.9kV BAAH sub (ATC WI). $89M. Precursor to DIC campus
MTEP24 | West | AMERICAN TRANSMISSION COMPANY | 50138 | Dodge County, DIC, New Substation | Construct one new 138 kV interconnection substation named Manhattan near the city of Beaver Dam. Also, expand and upgrade the exiting North Randolph 138 kV bus to support additional circuits to Manhattan. Rebuild the existing N Randolph – N Beaver Dam 138 kV line (X-47) forming a new North Randolph - Manhattan 138 kV line and construct a new double circuit 138 kV transmission line between North Randolph and Manhattan substations. | WI | Other | Load Growth | Dodge County DIC New Substation for Data Innovation Campus | Data Center/DIC Campus | Y |  | 2027-06-01 | 138 |  | 161000000 | Dodge County Manhattan: new 138kV sub near Beaver Dam (ATC WI). $161M
MTEP24 | West | MINNESOTA POWER INC. | 4295 | HVDC Modernization Project | Replace the existing Center (Square Butte) and Arrowhead high voltage direct current (HVDC) converter stations and associated assets with modern equipment. To modernize the terminals of the existing Square Butte HVDC Line and implement the latest VSC HVDC technology, new buildings and electrical infrastructure need to be constructed on a new site near the existing HVDC terminals. In Minnesota, to connect the new HVDC terminal to the existing AC system, the Project would require the construction of a new St. Louis County 345 kV/230 kV substation located less than one mile west of the current Arrowhead Substation. The new HVDC terminal would be connected to the St. Louis County Substation by less than one mile of 345 kV transmission line and the new St. Louis County Substation would be connected to the existing Arrowhead Substation by two parallel 230 kV transmission lines less than one mile in length. Additionally, a short portion of the existing ±250 kV HVDC Line in Minnesota will need to be reconfigured to terminate at the new HVDC terminal. Similar modifications will take place near the existing Center HVDC terminal in North Dakota. | MN; ND | TDSP | [5 empty] | 2028-12-31 | 345 |  | 800000000

## MTEP25
MTEP Year | Planning Region | Utility/TO | Project ID | Project Name | Project Description | State | Project Type | Other Type | System Need / Rationale | Project Driver | Data Center Flag | Load (MW) | Expected ISD | Max kV | Min kV | Estimated Cost ($) | Report Notes
MTEP25 | Central | AMEREN ILLINOIS | 25018 | New Moonshine Solar Bootleg 138 kV switching station (J1382) | The J1382 150MW Solar Interconnection Switching Station will split the existing Hutsonville-Neoga South-1 138 kV. | IL | GIP |  | Generator interconnection |  |  |  | 2025-12-01 | 138 |  | 8000000
MTEP25 | Central | AMEREN ILLINOIS | 50077 | New Aster 138 kV interconnection (J1777) | The Great Plains Solar (J1777) Generating Facility will interconnect with the Transmission System via a 138 kV leadline running from the Interconnection Customer's collector substation to the Transmission Owner's Aster Substation in Perry County, IL. IF POS | IL | GIP |  | Generator Interconnection |  |  |  | 2026-06-01 | 138 |  | 800000
MTEP25 | Central | AMEREN ILLINOIS | 50084 | New Ramsey East 138 kV Connection (J1714) | Install a new 138 kV line position to serve as the Point of Interconnection for Saluki Solar, LLC within the Ramsey East Substation. IF POS | IL | GIP |  | Generator Interconnection |  |  |  | 2026-12-01 | 138 |  | 800000
MTEP25 | Central | AMEREN ILLINOIS | 50118 | Upgrade Powerton-Tazewell 345 kV line (AE1-163) | This transmission project will consist of all network upgrades required to relieve the overloaded Powerton-Tazewell 345 kV transmission line caused by PJM project AE1-163. | IL | GIP |  | External Generator Interconnection - Relieve the overload caused by PJM project AE1-163 |  |  |  | 2025-12-01 | 345 |  | 1500000
MTEP25 | Central | AMEREN ILLINOIS | 50119 | New Moro-Cottage Hills 138 kV Line (C1908 MPFCA) | These Common Use Upgrades consist of equipment for all the substation and transmission line upgrades to support New Moro-Cottage Hills MPFCA. Add 138 kV position at Moro, expand Cottage Hills to a 4 pos., 6 ult. ring bus. Add second circuit between Moro and Cottage Hills on existing ROW utilizing DC structures. Rebuild Moro to Laclede N Tap, Cottage Hills to Laclede S tap and Laclede S tap to Mississippi tap. | IL | GIP |  | Generation Interconnections |  |  |  | 2028-06-30 | 138 |  | 38550000
MTEP25 | Central | AMEREN ILLINOIS | 50189 | Rebuild Latham-Docket-1409 138 kV line (C1903 MPFCA) | Rebuild 5 miles of the existing 138 kV Latham-Docket-1409 with OPGW and 1600 A conductor. | IL | GIP |  | Generator Interconnection for solar/wind project. |  |  |  | 2027-12-01 | 138 |  | 4000000
MTEP25 | Central | AMEREN ILLINOIS | 50504 | Upgrade Dupo Ferry 138 kV breakers | Dupo Ferry 138kV Breakers Upgrade - Replace 4 overstressed 138kV circuit breakers, existing interrupting capability 40kA, with 50kA new breakers 3000A minimum continuous | IL | GIP |  | Replacement project-GIP |  |  |  | 2026-12-01 | 138 |  | 2500000
MTEP25 | Central | AMEREN ILLINOIS | 22788 | Rebuild Prest-Tibbs 138 kV line (1558) | Repair issues found during inspections on the Prest-Tibbs 138 kV Line (1558) | IL | Other | Local Reliability | Maintain the reliability of the Transmission system |  |  |  | 2025-12-01 | 138 |  | 23000000
MTEP25 | Central | AMEREN ILLINOIS | 22907 | Upgrade Tuscola West 138 kV substation | Install ring bus at Tuscola West 138 kV Substation after addressing aging infrastructure | IL | Other | Age and Condition | Inspection items were found to be in poor condition necessitating the need to address before failure or before current issues persist. |  |  |  | 2026-12-01 | 138 |  | 5800000
MTEP25 | Central | AMEREN ILLINOIS | 22908 | Rebuild Joppa - Marion South 161kV line | Rebuild the Joppa-Marion South-1 161 kV line on direct-embed steel H-Frame structures with conductor capable of carry 2000 amps at Summer Emergency conditions. | IL | Other | Age and Condition | Existing ACAR conductor will be 60 years old and at the end of its expected life. Steel towers are showing signs of rust and will need O&M $$$ for painting to extend their service life. Shield wire attachment hardware does not have commercially available spares. |  |  |  | 2030-12-01 | 161 |  | 46500000
MTEP25 | Central | AMEREN ILLINOIS | 25269 | Replace West Frankfort East 345/138 kV transformer 1 | At West Frankfort East substation replace the existing 560 MVA 345/138 kV Transformer 1 with a new 345/138 kV 700 MVA transformer. Replace 138 kV breaker 1520 and 345 kV circuit switcher C3550. Also replace limiting bus conductor on the 138 kV Transformer 1 branch. | IL | Other | Age and Condition | Age and condition |  |  |  | 2026-12-01 | 345 |  | 10600000
MTEP25 | Central | AMEREN ILLINOIS | 25328 | Upgrade Charleston NE 138kV line | Add line breakers and address aging infrastructure items on Charleston NE 138 kV Line | IL | Other | Age and Condition | Aging infrastructure and increased operability. |  |  |  | 2026-06-01 | 138 |  | 4019794
MTEP25 | Central | AMEREN ILLINOIS | 50140 | Upgrade Fargo 138 kV Line Position for Lucky | New 138kV breaker required on Fargo 138kV Bus breaker and a half scheme, and new circuit switcher on the high side of the substation. AIC to construct a new 138kV/13.2kV distribution substation near the Fargo bulk supply substation | MO | Other | Local Needs | Increased load |  |  |  | 2029-12-01 | 345 |  | 2000000
MTEP25 | Central | AMEREN ILLINOIS | 50175 | Upgrade Taylorville South 138 kV Substation | This project will reconfigure Taylorville South 138 kV substation in a 4 position ring bus configuration. Replace circuit breakers 1511, 1512 and 1514. Replace associated switches 1511B, 1511L, 1512B, 1512L, 1514B, and 1514L. Install one new 138 kV circuit breaker and two associated breaker disconnect switches. Remove shield wire over substation and install lightning masts and finials. | IL | Other | Local Reliability |  |  |  |  | 2026-12-01 | 138 |  | 5200000
MTEP25 | Central | AMEREN ILLINOIS | 50185 | Replace Marion South 161/138 kV transformer | Replace XFMR 1 at Marion South with a new 161/138kV 300 MVA unit | IL | Other | Age and Condition | Age and Condition for transformer unit replacement. |  |  |  | 2026-12-01 | 161 |  | 3600000
MTEP25 | Central | AMEREN ILLINOIS | 50190 | New Peru-Princeton 138 kV line | Rebuild the existing Princeton substation as a 4-position 138 kV substation in a ring bus configuration with two additional positions available for future expansion. Construct a new 4-position 138 kV substation in a ring bus configuration with two additional positions available for future expansion. Construct a new 23-mile 138 kV Transmission line from Ameren's Princeton substation to the new substation near the City of Peru. | IL | Other | Load Growth | Rebuild Princeton sub, new 4-position 138kV sub near Peru, new 23mi 138kV line; submitted through EPR | Large Load (EPR) |  |  | 2029-06-01 | 138 |  | 90000000 | AMIL EPR $90M
MTEP25 | Central | AMEREN ILLINOIS | 50198 | New Wieland Metals 138 kV Load Addition | Construct a new 138 kV substation, four position ultimate in a ring bus arrangement, 3000 Amps minimum continuous capability. The substation will be located approximately 1 mile east from the existing Wood River 138 kV substation. Split the existing Granite City 23rd Street-Wood River-1452 138 kV line and route into the new substation. Provide two positions at the new ring bus for the connection of Wieland Metals (Falls) | IL | Other | Load Growth | New Wieland Metals 138 kV Load Addition | Large Industrial (Wieland Metals) |  |  | 2026-12-01 | 138 |  | 10700000 | AMIL EPR $10.7M
MTEP25 | Central | AMEREN ILLINOIS | 50230 | New Harco South-Carrier Mills 161 kV line | Rebuild the Harco South substation to install a new transformer and a new line to the South. Install a 161/138kV transformer at Harco South. Build a 161kV line from Ameren's Harco South substation to SIPC's Carrier Mills substation. | IL | Other | Local Reliability | SIPCo requested connection to address reliability needs. Included within SCITE project. |  |  |  | 2029-12-31 | 161 |  | 30000000
MTEP25 | Central | AMEREN ILLINOIS | 50257 | Reconfigure Steeleville 138 kV Substation to Ring Bus | Reconfigure Steeleville 138 kV as a five-position switching station, in a ring bus arrangement, with one additional position for future expansion with continuous capability of 3000 A. Install a new 40 Mvar 138 kV capacitor bank in one of the initial ring bus positions. | IL | Other | Age and Condition | Age and Condition |  |  |  | 2026-12-01 | 138 |  | 6001746
MTEP25 | Central | AMEREN ILLINOIS | 50282 | New Radbourn 345 kV and Leghorn 345 kV Shunt Reactors | Install (1) 50 Mvar shunt reactor, (1) 345 kV circuit breaker, and (1) motor-operated disconnect switch at Radbourn 345 kV substation. Install (1) 50 Mvar shunt reactor, (1) 345 kV circuit breaker, and (1) motor-operated disconnect switch at Leghorn 345 kV substation. | IL | Other | Load Growth | System Growth |  |  |  | 2026-12-01 | 345 |  | 4800000
MTEP25 | Central | AMEREN ILLINOIS | 50288 | Replace Marblehead North 161/138 kV transformer | Replace Existing XFMR at Marblehead North with the onsite spare 161/138kV 300 MVA unit. | IL | Other | Age and Condition | Age and Condition |  |  |  | 2027-12-01 | 161 |  | 1500000
MTEP25 | Central | AMEREN ILLINOIS | 50299 | New Wakefield 138 kV switching station | Construct a three (3) position 138 kV substation in a ring bus configuration, with one (1) additional position available for future expansion, all with a 3000 A minimum continuous capability. Route the existing South Bloomington-Tabor-1445 138 kV line in and out of the new Wakefield substation. | IL | Other | Load Growth | System Growth |  |  |  | 2027-12-01 | 138 |  | 10700000
MTEP25 | Central | AMEREN ILLINOIS | 9740 | Reconductor Grand Tower-Campbell Hill 138 kV line | Reconductor Grand Tower-Campbell Hill 138 kV Line to 2000 A summer emergency capability | IL | Other | Age and Condition | Age and condition |  |  |  | 2029-12-01 | 138 |  | 34900000
MTEP25 | Central | AMEREN MISSOURI | 23530 | New Spencer Creek generation interconnection MPFCA (J956/J1026) | Expand 345kV bus at Spencer Creek Substation to connect J956 and J1026 | MO | GIP |  | Connecting the generator in the MISO Interconnection queue as required. Allows for the generator to inject power into the MISO. |  |  |  | 2024-05-03 | 345 |  | 4600000
MTEP25 | Central | AMEREN MISSOURI | 50154 | Grain Belt Express AECI Facilities Construction Agreement (GI-083) | The network upgrades outlined in the affected system study for AECI GI-083 are being performed to accommodate the interconnection with GrainBelt Express HVDC interconnection (GBX) at McCredie substation. This is required per Ameren's contractual obligation with GBX and in compliance with FERC Order 888, Promoting Wholesale Competition Through Open Access Non-discriminatory Transmission Services by Public Utilities. | MO | GIP |  | Generator Interconnection |  |  |  | 2027-12-01 | 345 |  | 70460000
MTEP25 | Central | AMEREN MISSOURI | 50186 | Grain Belt Express HVDC Network Upgrades (H104-H105) | This transmission project includes all the network upgrades that are required to support generation interconnection projects H104 and H105. | MO | GIP |  | MHVDC interconnection |  |  |  | 2030-12-01 | 345 |  | 171000000
MTEP25 | Central | AMEREN MISSOURI | 50220 | Rebuild McCredie-Overton 345 kV Line (MPFCA) | Rebuild 35.5 miles of the 345 kV McCredie-Overton transmission line, including a river crossing | MO | GIP |  | MISO's MHVDC System Impact Study identified that the connection of projects J1488 and J1490 will cause constraints on the transmission system that must be mitigated before the projects are placed in-service. |  |  |  | 2031-06-01 | 345 |  | 63115000
MTEP25 | Central | AMEREN MISSOURI | 50221 | Rebuild Overton-McBaine Tap 161 kV Line (MPFCA) | Rebuild the existing Loy Martin – Overton 161 kV transmission line from the McBaine Tap to Overton. | MO | GIP |  | MISO's MHVDC System Impact Study identified that the connection of projects J1488 and J1490 will cause constraints on the transmission system that must be mitigated before the projects are placed in-service |  |  |  | 2030-12-01 | 161 |  | 9552000
MTEP25 | Central | AMEREN MISSOURI | 50222 | Rebuild Overton-Sedalia East 161 kV Line (MPFCA) | Rebuild 10 miles of existing Overton – Sedalia East 161 kV | MO | GIP |  | MISO's MHVDC System Impact Study identified that the connection of projects J1488 and J1490 will cause constraints on the transmission system that must be mitigated before the projects are placed in-service. |  |  |  | 2030-12-01 | 161 |  | 9710000
MTEP25 | Central | AMEREN MISSOURI | 22874 | Upgrade Ashley 161 kV substation | Install high side interrupting devices on XFMRs 1, 2, & 3 Install line breakers on Cahokia and Hall Street | MO | Other | Age and Condition | Remove shield wire and install lightning masts prevents unnecessary outages and future expenditures to repair or replace at that later date. High side interrupting devices prevent a XFMR zone fault from taking out the XFMR. |  |  |  | 2027-12-01 | 138 |  | 4100000
MTEP25 | Central | AMEREN MISSOURI | 22881 | Upgrade Belleau 138 kV substation | Expand Belleau by adding 2 positions for O'Fallon so they don't tap the lines. (i.e. (2)new 138kV Line positions for 138kV Feeds to O'Fallon) | MO | Other | Local Reliability | Reducing line taps will prevent additional elements from experiencing issues during maintenance or unplanned outages. |  |  |  | 2027-06-01 | 138 |  | 3000000
MTEP25 | Central | AMEREN MISSOURI | 23046 | Upgrade Montgomery 345/161 kV Substation | Address aging infrastructure items and expand 161 kV bus | MO | Other | Local Reliability | breaker on or after bus 2 at MTGY will prevent outages and maintenance from taking transmission connections to WARR out of service temporarily. |  |  |  | 2026-06-01 | 345 |  | 17000000
MTEP25 | Central | AMEREN MISSOURI | 25040 | Replace Tyson 345/138 kV transformer 3 | Replace Tyson XFMR 3 with a new 345/138kV 700 MVA unit. | MO | Other | Age and Condition | Age and condition |  |  |  | 2027-12-01 | 345 |  | 8500000
MTEP25 | Central | AMEREN MISSOURI | 25496 | New Blanchette 138 kV Ring Bus | Install a 4 position ring bus at Blanchette 138kV Substation. In addition, fiber will be installed to Kisker with some line re-routing. | MO | Other | Local Reliability | Increased reliability |  |  |  | 2027-06-01 | 138 |  | 7000000
MTEP25 | Central | AMEREN MISSOURI | 25497 | Reconfigure Overton 161kV Substation | Rebuild the existing Overton 161kV straight bus as a breaker-and-a-half (BAAH) station. | MO | Other | Local Reliability | Increased reliability. Overton is getting a new 161kV 67MVAR Capacitor Bank and a 2nd 345/161kV transformer. |  |  |  | 2027-12-01 | 161 |  | 46000000
MTEP25 | Central | AMEREN MISSOURI | 50100 | Rebuild Baumgartner 138 kV Substation | This project will replace aging infrastructure at Baumgartner 138 kV substation | MO | Other | Age and Condition | Aging infrastructure |  |  |  | 2028-06-01 | 138 |  | 6300000
MTEP25 | Central | AMEREN MISSOURI | 50226 | New Vulcan 138/34 kV Substation | Build a new 138-34.5 kV bulk substation on property adjacent to the MSD Lemay Pump. (fka Germania) | MO | Other | Load Growth | Load growth |  |  |  | 2027-06-01 | 138 |  | 12000000
MTEP25 | Central | AMEREN MISSOURI | 50227 | Upgrade California 161 kV Terminal | Add a line breaker on the AECI terminal and a new terminal for Apache Flats. New terminal contains a breaker and two switches and houses the line to Apache Flats. BARN-CALF-1 will be rebuilt into a double circuit from California to structure 197A which eliminates the tap to Apache Flats. | MO | Other | Local Reliability | Increased reliability |  |  |  | 2028-06-01 | 161 |  | 22600000
MTEP25 | Central | AMEREN MISSOURI | 50256 | New Tibbe 138/34.5 kV Substation | Tibbe 138/34.5 kV Substation - Utilize 9.6 miles of existing 34.5 kV line in the Saddle Creek-73 feeder, at 138 kV. In addition, construct 6.1 miles of new 138 kV line to establish the Gray Summit-Prairie Dell and Franklin-Prairie Dell 138 kV lines. Establish a new 138 kV ring bus at the Tibbe 138-34.5 kV Substation. (fka Prairie Dell) | MO | Other | Load Growth | Load growth |  |  |  | 2029-12-01 | 138 |  | 33000000
MTEP25 | Central | AMEREN MISSOURI | 50259 | Rebuild Fletcher-Pilot Knob-2 161 kV line | The project consists of replacing 8 wood H-frame with steel H-frame structures to increase system reliability. Replace structure 84 down guy due to age and condition. | MO | Other | Local Reliability | Local Reliability |  |  |  | 2026-06-01 | 161 |  | 1400000
MTEP25 | Central | AMEREN MISSOURI | 50403 | Relocate Dardenne 161/138 kV Substation | The existing Dardenne Substation has the majority of its equipment that needs to be replaced due to reliability and condition based issues rendering it costly and unreliable. In addition, the existing configuration does not meet the needs for Operations or Planning. Therefore, all equipment will be re installed at Belleau substation and retired from Dardenne Substation. | MO | Other | Age and Condition | Age and condition |  |  |  | 2027-12-01 | 161 |  | 3600000
MTEP25 | Central | AMEREN MISSOURI | 50531 | New AECI Load Addition at Ameren Fredericktown 138 kV | Description of the load: At full capacity, it is expected that the customer will consume up to 75 MW. Overview of Ameren Fredericktown: In the Fall of 2025, Ameren will expand its 138kV ring bus at Ameren-Fredericktown. This substation is located about 3 miles from the customer load. | MO | Other | Load Growth | New AECI Load Addition at Ameren Fredericktown 138 kV | Load Growth (EPR) |  | 75 | 2026-12-01 | 161 |  | 1200000 | AMMO EPR
MTEP25 | Central | AMEREN MISSOURI | 50615 | New Central 138 kV Substation Load Addition | Add a 138 kV position at Central substation for a new load. | MO | Other | Load Growth | New Central 138 kV Substation Load Addition | Load Growth (EPR) |  |  | 2026-12-01 | 138 |  | 1000000 | AMMO EPR
MTEP25 | Central | AMEREN MISSOURI | 50616 | New Rootbeer 345 kV Substation Load Addition | To serve the load proposed, Ameren will add a position at Rootbeer substation. | MO | Other | Load Growth | New Rootbeer 345 kV Substation Load Addition | Load Growth (EPR) |  |  | 2026-12-01 | 345 |  | 2000000 | AMMO EPR
MTEP25 | Central | AMEREN MISSOURI | 50617 | New 345 kV Lumberjack substation for Load Connection | Construct a new 345 kV substation called Lumberjack 8 position ultimate BAAH bus arrangement for the connection of Load Addition at New Florence, MO | MO | Other | Load Growth | New 345 kV Lumberjack Substation for Load Connection | Load Growth (EPR) |  |  | 2027-12-01 | 345 |  | 38500000 | AMMO EPR $38.5M
MTEP25 | Central | AMEREN MISSOURI | 50696 | New Huster-McClay 138 kV line tap for Hayford load | Temporary line tap on Huster-McClay 138 kV for new customer load | MO | Other | Load Growth | Customer request |  |  |  | 2027-06-01 | 138 |  | 500000
MTEP25 | Central | AMEREN TRANSMISSION COMPANY OF ILLINOIS | 50631 | Missouri Multi-Entity New Transmission (MoMENT) Project (Primary) | New 40 mile 345 kV line from Loose Creek to Barnett. New 345/161 kV substation at Barnett. New 38 mile 345 and 161 kV double circuit line from Overton to Barnett. New 65 mile double circuit 345 kV line from Barnett to Clinton. New Clinton substation. New 50 mile double circuit 345 kV line from Clinton to LaCygne. | MO | Other | Local Reliability | This program is the result of a joint effort between ATXI, AECI and Evergy to identify a portfolio of projects which would increase reliability to all customers across the Central and Western Missouri region. Benefits include Increased transfer capability between regions and increased reliability to multiple substations. Future benefits include potential interconnection points for generators and load customers. | Reliability (Multi-Entity) |  |  | 2030-12-01 | 345 |  | 604000001 | MoMENT: multi-entity 345kV reliability project across Central/West MO. $604M
MTEP25 | Central | AMEREN TRANSMISSION COMPANY OF ILLINOIS | 50636 | New Diamond Core Load Addition (RECC Territory) at Mogul 345 kV substation | This new load will connect to MOGL-DBDS-4566 345 kV line that feeds (J1464) Double Black Diamond Solar and will be separately metered. RECC will install, own, and operate the metering at the data center. | IL; MO | Other | Load Growth | Diamond Core Load Addition at Mogul 345 kV substation; EPR load growth | Data Center | Y |  | 2027-12-01 | 138 |  |  | Diamond Core data center at Mogul 345 kV, RECC territory. Connected to solar line, separately metered
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 24919 | Mill Road – Granville Project | - Construct new 345/138 kV Mill Road SS, with one 500 MVA 345/138 kV transformer, - Loop in Granville – Arcadian 345 kV line and Cypress – Arcadian 345 kV line to new Mill Road 345 SS, Rebuild Mill Road SS – Granville SS section as 345 kV double circuit, - Loop in Germantown – Bark River 138 kV line and west portion of the Tamarack – Sussex 138 kV line into new Mill Road 138 kV SS, install series reactor in line to Sussex. - Construct new Mill Road SS – Tamarack SS – Butler SS 138 kV line, - Butler SS 138 kV reconfiguration, and install series reactor between Butler bus 1 and bus 2, - Granville SS 345 kV ring bus expansion, Replace 345/138 kV transformer T3. | WI | BRP |  | Reliability. Address MTEP and TYA reliability P6 (N-1-1) issues, future sensitivities identify N-1 issues. Significant market congestion has been an issue for many years and is expected to become more severe with load interconnections and generation related changes, Portions of the existing 138 kV facilities are within the Asset Life Cycle Program window to replace, Portions of the corridor (line 3453, 3443 and 5041) are required to be rebuilt due to Generator Interconnection queue study limitations. | Data Center/DIC Campus (BRP) | Y |  | 2027-10-01 | 345 |  | 423705000 | ATC BRP; Racine DIC CAP $424M
MTEP25 | West | ITC MIDWEST | 50157 | Big Cedar Load Expansion | Interstate Power and Light Company (IPL) has requested to interconnect two new loads to the transmission system the Cedar Rapids, Iowa area. ITC Midwest is proposing to serve the new load from the Big Cedar Switching Station which requires expansion to serve the two new loads. In addition to expanding the Big Cedar Switching Station, ITC Midwest will be installing reactive compensation at the Big Cedar Switching Station to support this load addition. ITC Midwest will also add a 2nd Big Cedar – Morgan Valley 345 kV line on the existing structures of the Big Cedar – Morgan Valley 345 kV line and construct a new Beverly – Hills 345 kV line to support the load addition. The LRTP Tranche 1 Marshalltown (Twinkle) - Morgan Valley 345 kV line is required to support the first phase of the load addition, and the LRTP Tranche 1 Beverly – Sub 92 345 kV line is required to support the second phase of the load addition. | IA | Other | Load Growth | In order to reliably serve the two new requested loads, upgrades on the ITC Midwest transmission system are required. These upgrades include expansion of the Big Cedar Switching Station, an additional 345 kV line/source into the Cedar Rapids area, and reactive power compensation at Big Cedar to support system contingent voltages. In addition to the upgrades included here the Morgan Valley - Twinkle (Marshalltown) Tranche 1 LRTP project and Beverly - Sub 92 Tranche 1 LRTP project are also required to ensure system reliability with these load additions. | Large Industrial (EPR) |  |  | 2028-09-30 | 345 |  | 380549625 | Big Cedar Load Expansion: two new loads in Cedar Rapids area, 345kV upgrade. $381M. EPR
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50167 | Racine County, DIC, Jupiter Substation | Install a new 345/138 kV breaker-and-a half substation with 4 –500 MVA 345/138 kV transformers, +/- 350 Mvar STATCOM, 138 kV capacitor banks, 4 – 345 kV line terminal. | WI | Other | Load Growth | Racine County DIC Jupiter Substation; part of Racine DIC CAP | Data Center/DIC Campus | Y | 500 MVA | 2027-01-01 | 345 |  | 295000000 | Racine County Jupiter Sub: 4x500MVA 345/138kV transformers, STATCOM. Part of Data Innovation Campus
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50543 | Racine County, DIC, Cosmos Substation | Install a new 345/138 kV breaker-and-a half substation with 4 –500 MVA 345/138 kV transformers, 138 kV capacitor banks, and 4 – 345 kV line terminals, and 1 – 138 kV line terminals with a series reactor. | WI | Other | Load Growth | Racine County DIC Cosmos Substation; DIC campus project | Data Center/DIC Campus | Y | 500 MVA | 2028-04-01 | 345 |  | 195000000 | Racine County Cosmos Sub: 4x500MVA 345/138kV transformers. Part of DIC cluster ~$850M+
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50489 | Split Rock - Chanarambie 345kV line JTIQ | Tap JTIQ line Lyon Co-Lakefield, route into Chanarambie. Add (2) 345/115kV transformers at Chanarambie. Add (1) 345kV/115kV transformer at Renner. New 345kV line Split Rock -Renner-Chanarambie. Upgrade 115kV line Split Rock-Pipestone-Chanarambie. | MN; SD | Other | Local Needs | Southern MN has stability concerns and congestion. Supports load serving in Sioux Falls. Relieves generation deliverability issues identified in MTEP24. |  |  |  | 2033-06-30 | 345 |  | 165000000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50168 | Racine County Western Feed Transmission Line Project | Construct two new 345 kV double circuit lines from the existing Arcadian – Pleasant Prairie (PLPL81)/Arcadian – Paris (W-30) 345 kV double circuit line to loop in and out of the Jupiter and Mount Pleasant. Construct a new Jupiter – Mount Pleasant 345 kV line. | WI | Other | Load Growth | Racine County Western Feed Transmission Line; part of Racine DIC CAP | Data Center/DIC Campus | Y |  | 2027-01-01 | 345 |  | 124000000 | Racine County Western Feed: two new 345kV double circuit lines for DIC campus
MTEP25 | West | GREAT RIVER ENERGY | 50481 | LG - 2 | Install new facilities to meet load growth in the area. | MN | Other | Load Growth | Load growth in area exceeds capacity of existing substations and requires installation of new load serving distribution substations in the area. | Large Load |  |  | 2030-12-31 | 345 |  | 120000000 | GRE LG-2: $120M for load growth exceeding capacity in MN area
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50166 | Racine County, DIC, Mount Pleasant Substation Expansion | Install a new 500 MVA, 345/138 kV transformer, +/- 350 Mvar STATCOM, 138 kV capacitor banks, and associated 345 kV and 138 kV substation facilities. | WI | Other | Load Growth | Racine County DIC Mount Pleasant Substation Expansion; part of Racine DIC CAP | Data Center/DIC Campus | Y | 500 MVA | 2027-01-01 | 345 |  | 117000000 | Racine County Mt Pleasant expansion: 500MVA 345/138kV transformer, STATCOM for DIC campus
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50711 | Brookings County - Lyon County 345kV Davit Arm Replacement | Age and Condition replacement of Davit Arms on Brookings County - Lyon County, Lyon County - Helena, Hampton - Helena 345kV lines. Project is categorized as MVP because it replaces assets associated with previously approved MTEP11 MVP #1203 - Candidate MVP Portfolio 1 - Brookings, SD - SE Twin Cities 345 kV. | MN; SD | MVP |  | Age and Condition rebuild of Davit Arms on Brookings County - Lyon County, Lyon County - Helena, Hampton - Helena 345kV lines |  |  |  | 2030-09-30 | 345 |  | 91900000
MTEP25 | West | MINNESOTA POWER INC. | 50218 | Riverton STATCOM | Placing a +/- 300 MVAR STATOM at the Riverton 230 kV Substation | MN | BRP |  | Providing dynamic voltage support with moving baseload generation to economic dispatch |  |  |  | 2028-03-31 | 230 |  | 70000000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50165 | Racine County, DIC, Stratus Substation | A new 138/24.9 kV breaker-and-a-half substation named Stratus, 138 kV capacitor banks, and construct short transmission lines to cut into the Mount Pleasant-Nimbus 138 kV lines (X-171, X-172) and loop in and out of the Stratus Substation. | WI | Other | Load Growth | Racine County DIC Stratus Substation; part of Racine County Area 2&3 DIC EPR CAP | Data Center/DIC Campus | Y |  | 2027-01-01 | 138 |  | 68500000 | Racine County Stratus Sub: new 138/24.9kV BAAH sub for DIC campus
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50329 | Substation 91 Expansion | Expand Substation 91 by converting the 345 kV yard to a ring bus configuration and by installing a second 345-161 kV transformer. | IA | BRP |  | NERC TPL-001-5 Corrective Action Plan for thermal and voltage violations identified in the MTEP24 study for Category P6 N-1-1 contingencies. |  |  |  | 2028-12-31 | 345 |  | 66000000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 25161 | Sun Prairie Area Reliability Project | The Sun Prairie Area Reliability Project provides additional sources in the Sun Prairie Area to prevent thermal overloads due to multiple contingencies. Sun Prairie Area Reliability Project scope is as it follows: • Loop through Sun Prairie – Kegonsa (Y-81) 69-kV line in Reiner Road SS, constructing a 2-mile double circuited 69-kV line. In addition, install a new 138/69-kV transformer at Reiner Road SS. Finally, install new equipment due to asset renewal needs. • Loop through DeForest – Sun Prairie (Y-137) 69-kV line in Yahara River SS, constructing a 1.1-mile double circuited 69-kV line. In addition, install a new 138/69-kV transformer at Yahara River SS. Finally, install new equipment due to asset renewal needs. • Jumper replacements in Sun Prairie SS and additional modifications due to asset renewal needs. | WI | BRP |  | Reliability |  |  |  | 2029-06-30 | 138 |  | 61450000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50445 | Sioux Falls 115kV Conversion | Rebuild lines 0730 and 0729 Lawrence - South Sioux Falls, West Sioux Falls - South Sioux Falls, South Sioux Falls - Lincoln to 115kV. Convert remaining 69kV substations to 115kV. | SD | Other | Load Growth | conversion of the 69kV system from West Sioux Falls-Lincoln-Lawrence to 115kV addresses voltage concerns and overloading associated with future load growth. Line 0730 is at end of life. | Area Load Growth |  |  | 2029-06-01 | 115 |  | 60000000 | Sioux Falls 115kV conversion: voltage concerns from future load growth + end-of-life line
MTEP25 | West | ITC MIDWEST | 50380 | ITC Midwest Asset Management blanket | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA; IL; MN | Other | Age and Condition | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance have increased potential for misoperations and higher maintenance costs associated with their ongoing use. |  |  |  | 2027-12-31 | 345 |  | 53875000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 23841 | Pine – Skanawan Tap – Eastom 115kV (I-9), OPGW Addition & Partial Rebuild | Install ~21 Miles of OPGW fiber on T-Line (I-9) between the Pine substation and the Eastom substation. | WI | Other | Local Needs | Other Local Needs - Communication |  |  |  | 2031-05-31 | 115 |  | 47000000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 25185 | Small Capital Project and Asset Renewal Program 2026 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2026. | MI; WI | Other | Age and Condition | Asset Renewal – Program |  |  |  | 2028-06-30 | 345 |  | 45000000
MTEP25 | West | ITC MIDWEST | 50213 | Rock Creek 345 kV Substation Expansion and Rock Creek - Quad Cities #2 345 kV line | ITC will be expanding the Rock Creek 345 kV substation to accommodate two additional 345 kV lines. ITC will be installing the 2nd Quad Cities to Rock Creek 345 kV circuit and increasing the rating on the existing circuit. The substation will be expanded to a Breaker and a Half configuration. All new substation equipment will be capable of 3000 Amps or greater. | IA; IL | Other | Local Reliability | The Rock Creek substation will require expansion in order to build additional circuits for increased reliability in the area as well as create room to serve additional future load. Due to increased loading on the Quad Cities - Rock Creek 345 kV line, a 2nd 3000 amp nominal Quad Cities - Rock Creek 345 kV line will be installed on existing spare position and the existing Quad Cities - Rock Creek 345 kV line will have its rating increased to 3000 amps nominal. |  |  |  | 2028-12-31 | 345 |  | 44412329
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 25314 | Pittsville Area Reliability Project | • ATC will construct ~9.6 miles of single circuit 138 kV transmission line to interconnect the proposed distribution substation. • ATC will construct a 138 kV loop-through straight bus with three line breakers to accommodate tapping X-42 and terminating the new line. | WI | Other | Local Reliability | Reliability |  |  |  | 2028-12-31 | 138 |  | 35900000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50529 | Appleton Area Reliability Project | 1) Construct new 138kV line between City Limits – Northside 2) Rebuild a 138kV line section of 50632 (From STR132131 - City Limits), 3) Rebuild a 138kV line section of 43025 (From STR132131 - Northside), 4) Rebuild two 138kV line sections of 971K11 (Melissa - Meadows Tap and Meadows Tap - Kaukauna Central Tap). | WI | BRP |  | BRP |  |  |  | 2029-05-01 | 138 |  | 35700000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50398 | Install Inver Hills TRs and Feeders | Expand the Inver Hills substation and install two new distribution transformers and feeders to take over the existing Rich Valley loads | MN | Other | Local Reliability | Rich Valley substation is currently under loss of load risk due to single bank configuration. This project would add transfer the load from RIch Valley to Inver HIlls and add the capacity to support the additional load. |  |  |  | 2028-12-15 | 115 |  | 35100000
MTEP25 | West | MONTANA-DAKOTA UTILITIES CO. | 50260 | Hettinger-Elgin rebuild to 115 kV | Rebuilding a 69 kV line to 115 kV from Hettinger, ND to Elgin, ND approximately 46.2 miles. Adding a new 115 kV bay at Hettinger and building a new substation at Elgin 115/69/41.6 kV. | ND | Other | Age and Condition | Age and Condition of the existing 69 kV line. |  |  |  | 2029-12-31 | 230 |  | 32100000
MTEP25 | West | GREAT RIVER ENERGY | 50482 | LG - 3 | Install new facilities to meet load growth in the area. | MN | Other | Load Growth | Load growth in area exceeds capacity of existing substations and requires installation of new load serving distribution substations in the area. | Large Load |  |  | 2026-12-31 | 115 |  | 25000000 | GRE $25M
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50440 | West Maple Grove Substation | Build new Substation in Northwest Maple Grove to accommodate load growth | MN | Other | Load Growth | New substation needed in the NW Maple Grove area due to substantial load growth in area | Area Load Growth |  |  | 2028-09-01 | 115 |  | 25000000 | Xcel/NSP $25M
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50225 | North Lake Geneva – Elkhorn 138 kV (X-55), Rebuild | Rebuild X-55 North Lake Geneva - Elkhorn 138 kV line per ATC T-Line design standards to achieve minimum 1342 Amps (321 MVA) normal and 1822 Amps (436 MVA) emergency ratings for all seasons. | WI | Other | Local Reliability | Reliability |  |  |  | 2026-08-15 | 138 |  | 23900000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50508 | J1629 Welsh Prairie SS Network Upgrades and Interconnection Facilities | J1629 is a 200 MW solar facility in Columbia County, WI. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2030-09-10 | 345 |  | 21461000
MTEP25 | West | GREAT RIVER ENERGY | 50264 | Soderville Area Projects | Rebuild SP line. Soderville Substation to #152. Line length is approx. 10 miles | MN | Other | Age and Condition | The line is in the 1950’s vintage and is targeted to be replaced due to age and condition. |  |  |  | 2031-03-31 | 69 |  | 21269000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50336 | Substation Equipment Replacement Blanket | Replace substation equipment because of condition and/or to improve reliability | IA | Other | Age and Condition | Condition and Reliability Improvement |  |  |  | 2028-12-31 | 345 |  | 21000000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50500 | Byron - Pleasant Valley 161kV Line Upgrade | Upgrade Byron - Pleasant Valley 161kV line | MN | Other | Local Needs | Line is frequently congested and is limiter in MTEP24 Appendix D6 Generator Deliverability and is identified as needed underbuild for LRTP Tranche 2.2. |  |  |  | 2029-06-01 | 161 |  | 20000000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50514 | J1502 Emerson Rd SS Network Upgrades and Interconnection Facilities | J1502 is a 225 MW solar facility in Juneau County, WI. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2028-06-30 | 345 |  | 19847000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 25187 | Load Interconnection Program 2026 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2026. | MI; WI | Other | Load Growth | Load Interconnection – Program |  |  |  | 2028-06-30 | 345 |  | 19000000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50506 | J1706 North Monroe SS Network Upgrades and Interconnection Facilities | J1706 is a 100 MW solar facility in Green County, WI. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2029-06-11 | 138 |  | 18266000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50233 | Birnamwood Area Reliability Project | Build a greenfield 69 kV switching station near the location of the Birnamwood tap. The station will be a 6-position straight bus with three breakered line terminals, one for the line segment to Deer Trail, one for the segment to Whitcomb, and one for the radial line to Birnamwood. One position for an 8 MVAR cap bank, provisions for a bus tie breaker and two future positions. | WI | Other | Local Reliability | Reliability |  |  |  | 2028-12-31 | 69 |  | 17500000
MTEP25 | West | GREAT RIVER ENERGY | 50419 | Bena Area Projects | Rebuild BE line from SS2505 to Bena Substation. Line length is approx. 15 miles. Enbridge plans to remove Line 3 which is located roughly 15ft north of GRE’s BE line between Bena Sub and Str 158 near the Mississippi River crossing (approx 12mi). The corridor where the pipeline and transmission line are located is very crowded, swampy and includes a LCP distribution line which is located about 12ft north of the BE line between the Enbridge Pipeline and BE line. The GRE line and LCP line are tied together with crossarms on many structures and there are side guys which extend under the pipeline in many locations. LCP plans to remove their distribution and relocate. | MN | Other | Age and Condition | The line is to be replaced due to age and poor condition. |  |  |  | 2029-11-29 | 69 |  | 17450679
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50673 | Portage - Columbia 138 kV (X-13/X-20), Reconductor | This project resolves thermal overloads under single contingency conditions on either the X-13 or X-20 lines between Portage and Columbia. | WI | BRP |  | Reliability |  |  |  | 2027-06-30 | 138 |  | 17296600
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50497 | MidAmerican Upgrades for MTEP 50157 Big Cedar Load Expansion | Network upgrades on MidAmerican Energy's transmission system identified during the MISO Expedited Project Review study for MTEP 50157 Big Cedar Load Expansion | IA | BRP |  | MISO MTEP 50157 Big Cedar Load Expansion Expedited Project Review study identified network upgrades to meet NERC TPL-001-5 compliance | Large Industrial (BRP) |  |  | 2028-12-31 | 345 |  | 16700000 | MEC BRP $17M; Big Cedar CAP
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50545 | J1752 Shady Dr SS Network Upgrades and Interconnection Facilities | J1752 is a 148.1 MW solar facility in Portage County, WI. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2029-04-04 | 138 |  | 16455000
MTEP25 | West | ITC MIDWEST | 50211 | Hayward - County Line - Ellendale 69 kV Rebuild | Rebuild the 13.34 miles between Hayward and County Line and 5.71 miles between County Line and Ellendale. The line will be rebuilt with T2-477 ACSR conductor and OPGW for communications path between Ellendale – County Line – Hayward. | IA | BRP |  | The 13.34 mile section between Hayward and County Line and 5.71 mile section between County Line and Ellendale overload for P0, P11, P12, P23, and P7 events |  |  |  | 2028-12-30 | 69 |  | 16015755
MTEP25 | West | GREAT RIVER ENERGY | 50284 | Cormorant to Pelican Rapids Rebuild Projects | Rebuild all sections of the LR-PC line. | MN | Other | Age and Condition | The line has a composite reliability grade of F, due for replacement due to age/condition and the area would benefit from additional capacity. |  |  |  | 2030-11-29 | 115 |  | 15121921
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50459 | Install Stewart TR2 | Install new distribution transformer to meet load growth in area | MN | Other | Load Growth | Load growth in area is exceeding capability of existing transformer at substation |  |  |  | 2027-12-31 | 69 |  | 15000000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50507 | J1508 Galvin Ave SS Network Upgrades and Interconnection Facilities | J1508 is a 98.9 MW wind facility in Marathon County, WI. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2029-03-13 | 115 |  | 14094000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50456 | Fort Ridgely 69kV Rebuild | Upgrade 69 kV lines Fort Ridgley-GRE Schilling Tap, Lafayette-GRE Lafayette, GRE Schilling Tap-GRE Lafayette Tap, and Winthrop-Lafayette | MN | Other | Local Reliability | Line overloads on these lines were observed in the MTEP24 Appendix D6 generator deliverability study. These lines are also at end of life. |  |  |  | 2029-01-01 | 69 |  | 14000000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50194 | J1532 POI New 69 kV Interconnection Substation and 69 kV Line Taps | Construct new 69 kV POI substation and 69 kV line taps for J1532 solar farm. | IA | GIP |  | J1532 network upgrades from DPP 2020 |  |  |  | 2027-09-01 | 69 |  | 13900000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50192 | J1529 POI New 69 kV Interconnection Substation and 69 kV Line Taps | J1529 POI New 69 kV Interconnection Substation and 69 kV Line Taps | IA | GIP |  | J1529 network upgrades from DPP 2020 |  |  |  | 2027-09-01 | 69 |  | 13800000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50193 | J1530 POI New 69 kV Interconnection Substation and 69 kV Line Taps | Construct new 69 kV POI substation and 69 kV line taps for J1530 solar farm. | IA | GIP |  | J1530 network upgrades from DPP 2020 |  |  |  | 2027-09-01 | 69 |  | 13800000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50417 | Rebuild 0735 St Bonifacius to Mound | Rebuild line 0735 from St. Bonifacious to Mound and add OPGW | MN | Other | Age and Condition | The existing structures are at end of life and have numerous defects. OPGW installation on the line will likely replace more than 50% of existing structures triggering a complete rebuild. Significant load growth is forecasted in the area and increased capacity is needed. | Load Growth + Age |  |  | 2026-12-31 | 69 |  | 13157400
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50161 | Empire Mine – Huron 138 kV (X-119), OPGW Addition | ~10.4 Miles of OPGW Installation - This project will align with the 446 T-Line Reinsulate Project between the National and Presque Isle substations as well as the ~7.5 Miles of OPGW Installation on X-118 (MTEP24) will provide an alternate fiber path establishing two diverse OPGW fiber routes providing high-speed fiber communications connecting into ATC larger OPGW Network Infrastructure. | MI | Other | Local Needs | Communication |  |  |  | 2027-12-31 | 138 |  | 13000000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50424 | Maple Street Substation | Install new distribution substation to meet load growth in area | SD | Other | Load Growth | Load growth in area is exceeding capability of existing distribution substations in area |  |  |  | 2027-06-01 | 115 |  | 13000000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50421 | Rebuild 0737 Gleason Lake to Mound | Rebuild line 0737 from Gleason Lake to Mound and add OPGW | MN | Other | Age and Condition | The existing structures are at end of life and have numerous defects. OPGW installation on the line will likely replace more than 50% of existing structures triggering a complete rebuild. Significant load growth is forecasted in the area and increased capacity is needed. | Load Growth + Age |  |  | 2028-03-15 | 69 |  | 12996320
MTEP25 | West | GREAT RIVER ENERGY | 50266 | Green Lake Area Projects | Rebuild SH line. SS306 to Green Lake Sub to Hawick Sub. Line length is approx. 13.7 miles | MN | Other | Age and Condition | The line is in the 1950’s vintage and is targeted to be replaced due to age and condition. |  |  |  | 2030-04-30 | 69 |  | 12790000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50720 | Fargo-St. Cloud-Monticello 345kV Davit Arm Replacement | Replace select steel davit arms on the Fargo-St. Cloud-Monticello 345 kV Transmission line. | MN | Other | Age and Condition | Age and Condition replacement of steel davit arms on Fargo-St. Cloud-Monticello 345 kV Transmission line. |  |  |  | 2030-09-30 | 345 |  | 12500000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50461 | Line 0868 Le Sauk - Fischer Hills - St Stephens Rebuild | Rebuild 0868 from Le Sauk to Fisher Hills to St. Stephens | MN | Other | Age and Condition | Line is frequently binding and is at end of life |  |  |  | 2029-01-01 | 115 |  | 12231418
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50428 | Replace Cass County TR1 | Upgrade transformer to support load growth | ND | Other | Load Growth | Load growth in area is exceeding capability of existing transformer |  |  |  | 2028-06-01 | 115 |  | 12200000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50530 | J1750 Grace Lake SS Network Upgrades and Interconnection Facilities | J1750 is a 153 MW solar facility in Marquette County, MI. | MI | GIP |  | Generation Interconnection Project |  |  |  | 2029-03-13 | 138 |  | 12110000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50334 | Eagle Grove-Goldfield 69 kV Interconnection and Clarion-Latimer 69 kV Line Rebuild | Install two line switches on a steel pole and rebuild the Clarion-Latimer 69 kV line sections. | IA | Other | Load Growth | Serve load |  |  |  | 2028-06-01 | 69 |  | 12000000
MTEP25 | West | GREAT RIVER ENERGY | 50263 | Rush City Area Projects | Rebuild CP line. CPX Line to the CPT Line. Line length is approx. 11 miles. Rebuild RLT Line. Line length is approx. 0.1 miles Rebuild CPT Line. SS2984 to SS2555. Line length is approx. 1.5 miles | MN | Other | Age and Condition | The lines are in the 1950’s vintage and targeted to be replaced due to age and condition. |  |  |  | 2029-08-31 | 69 |  | 11751000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50162 | Substation Technology Package #2 – 2026 | High level scope is to install Wi-Fi AP’s & Rogue Detection at various substations and remove Inverter equipment at various substations to complete the Wireless connectivity and Cyber Security fortifications. | WI | Other | Local Needs | Communication |  |  |  | 2026-12-31 | 0 |  | 11700000
MTEP25 | West | GREAT RIVER ENERGY | 50418 | Denham - Kettle River Rebuild | Rebuild the existing Kettle River to Denham (DK line) 69 kV. | MN | Other | Age and Condition | The transmission line has had conductor failures over the last few years. A recent failure caused a grass fire. The line was planned to be rebuilt due to age/condition starting in 2027 and due to the current maintenance issues the project should start as soon as possible. |  |  |  | 2026-12-31 | 69 |  | 11442911
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 24924 | Straits SS Power Transformer Asset Renewal | Power Transformer Asset Renewal at Straits SS. | MI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2027-12-01 | 138 |  | 11200000
MTEP25 | West | Central Minnesota Municipal Power Agency | 50261 | Blue Earth - North Transmission Substation Add 84/140 MVA transformer | North Transmission Substation Add 2nd 161/69 Transformer 45-60-75 MVA. | MN | Other | Load Growth | Load growth is driving this need. |  |  | 75 MVA | 2026-12-31 | 161 |  | 11200000
MTEP25 | West | GREAT RIVER ENERGY | 50473 | Pennock Area Projects | Construct a new 69 kV line from the Pennock distribution substation to a new breaker station at the point of interconnection of the GRE owned WS 69 kV line and the WMUC 69 kV line (St. Johns breaker station). Retire BR line west of AG-RK to Granite Falls. | MN | Other | Local Reliability | Pennock currently has redundant service from both Willmar and Granite Falls. The Pennock to Granite Falls line is 34 miles long and is due for rebuild due to its age and condition. This line serves no other substations and rather than rebuild and maintain it, it is proposed to create a new loop back to the Willmar area to provide redundancy to Pennock and operational flexibility to the Willmar area to pick up 115 kV and 230kV sources around Willmar. The new St. Jons breaker station will be owned by Willmar municipal and will provide resiliency to both Municipal and GRE member owner loads. |  |  |  | 2029-12-31 | 69 |  | 11000000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50331 | Substation 39 Replace 345-161 kV Transformer 9T1 | At Substation 39, replace the existing 345-161 kV, 500 MVA Transformer 9T1 with a new 560 MVA transformer. | IL | BRP |  | NERC TPL-001-5 Corrective Action Plan for thermal violations identified in the MTEP24 study for Category P6 N-1-1 contingencies. |  |  |  | 2029-06-01 | 345 |  | 10500000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50534 | J1824 Academy SS Network Upgrades and Interconnection Facilities | J1824 is a 67 MW solar facility located in Columbia County, WI. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2029-12-08 | 138 |  | 10244000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50455 | Prairie Reactor | Install new reactor and substation upgrades to accommodate new reactor at Prairie. | MN; ND | BRP |  | Remediates observed high voltages under FAC-011 required monitoring |  |  |  | 2029-01-01 | 230 |  | 10000000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50458 | Install Avon Area Substation | Install new distribution substation to meet load growth in area | MN | Other | Load Growth | Load growth in area is exceeding capability of existing substations |  |  |  | 2027-12-31 | 69 |  | 10000000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50173 | Ellinwood SS Power Transformer Asset Renewal | Ellinwood SS T1 Power Transformer Asset Renewal | WI | Other | Age and Condition | Asset Renewal |  |  |  | 2028-12-01 | 138 |  | 9900000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50535 | J1732 Wolfram Rd SS Network Upgrades and Interconnection Facilities | J1732 is a 98.4 MW solar facility in Columbia County, WI. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2029-03-13 | 138 |  | 9894000
MTEP25 | West | GREAT RIVER ENERGY | 50427 | Winthrop to Bell rebuild projects | Rebuild Winthrop to Bell line, about 12 miles. | MN | Other | Age and Condition | The line has an F grade for reliability and is a 1959s vintage which is being targeted for replacement. |  |  |  | 2028-08-31 | 69 |  | 9868407
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50172 | Arpin SS Power Transformer Asset Renewal | Arpin SS T21 Power Transformer Asset Renewal | WI | Other | Age and Condition | Asset Renewal |  |  |  | 2028-12-01 | 345 |  | 9800000
MTEP25 | West | MINNESOTA POWER INC. | 25267 | 180 Line Rebuild | Rebuild 115kV 180 Line (Hibbing -Maturi) with 636 ACSR. | MN | BRP |  | 180 Line rebuild project is needed for its age and condition as well as to increase capacity to mitigate P6 overloads. |  |  |  | 2028-12-31 | 115 |  | 9750000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50200 | PLPL81 and W-30 345 kV Line, Uprate | Uprate low rated segments of the Arcadian to Pleasant Prairie 345 kV line (PLPL81) and the Arcadian to Paris 345 kV line (W-30). The line ratings of both segments PLPL81 and W-30 will become insufficient in the near future as the transmission system will need to accommodate new loads and generation sources. | WI | Other | Local Reliability | PLPL81 and W-30 345 kV Line Uprate; new load | Load Growth |  |  | 2027-01-31 | 345 |  | 9500000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 25203 | Highland – Hill Valley 138 kV, Construct New Line | Create a new Highland - Hill Valley 138 kV line by: - Converting 6.25 miles of the existing Highland - Eden 69 kV line Y-207 to 138 kV. Along the 69 kV corridor, new easements will be required. - Construct 0.2 miles of new 138 kV into Highland SS. - Construct 1 mile of new 138 kV into Hill Valley SS. - Add one new ring bus position at Highland SS. - Add one new ring bus position at Hill Valley SS. - Retire and remove 0.2 miles of Y-207 into Eden SS and Highland SS. - Retire and remove two breakers, one at Eden SS and one at Highland SS. | WI | Other | Local Reliability | Reliability |  |  |  | 2026-09-03 | 138 |  | 9500000
MTEP25 | West | GREAT RIVER ENERGY | 50243 | Merton Area Projects | Rebuild SW-OM line. SS2755 to Merton Substation. Line length is approx. 6.5 miles. Planning has requested line be rebuilt to 161kV. | MN | Other | Age and Condition | The line is in the 1950’s vintage and is targeted to be replaced due to age and condition. |  |  |  | 2030-09-30 | 69 |  | 9273000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50145 | Beloit Area DIC, New Substation | - WPL will construct a new substation with two new 138/12.47 kV, 20/33 MVA transformers. - WPL will install a high side circuit breaker for transformer protection and low side bus. - ATC will install two 138kV feeds from the line section between BOC Gas Tap and Tripp Road (X-111) to the new Beloit LNG substation to support the new loop through configuration. - ATC will remove a section of the conductor from X-111. - ATC will install a new loop through configuration at the New Beloit LNG substation with space provision for a future bus tie breaker. - ATC will construct a 138 kV loop through bus at the new Beloit LNG substation and install two 138 kV line circuit breakers with associated line and bus side disconnect switches. - ATC will install two bus-tie disconnect switches and allow space provision for a future bus-tie breaker. | WI | Other | Load Growth | Load Interconnection |  |  | 33 MVA | 2027-06-30 | 138 |  | 9000000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50176 | Audubon 230 kV Load Addition and Line upgrades | Entergy is proposing to construct new 230 kV facilities at the planned Audubon 230 kV station to serve new load near Geismar, LA. There will be two ~2.8 mile new 230 kV lines from Audubon to the customer station. Also part of this addition are small partial upgrade of the Willow Glen to Point Pleasant 230 kV line and station equipment upgrades on the Willow Glen to Wise 230 kv line. | LA | Other | Load Growth | Entergy has received a request from a customer to add new load in the Geismar, LA area. Upgrades, including this facility, have been identified as needed due to the load growth. |  |  |  | 2026-01-01 | 230 |  | 5900000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50350 | Babel to Webre 500 kV New Line | Construct a new ~145-mile 500 kV line from Babel to Webre 500 kV line. | LA | BRP |  | Loss of the 500 kV path between Hartburg and Webre along with generation in South Louisiana overloads multiple facilities during high west to east or east to west transfers across the southern portion of Entergy’s system. This project also increases the load serving capability for the Amite South region of the Entergy service territory which is critical to maintaining reliability while accommodating expected load growth. The project will also increase operational flexibility and enhance resiliency by creating a geographically diverse EHV transmission path which is especially important during extreme weather events. | Reliability (BRP) |  |  | 2030-06-01 | 500 |  | 1066000000 | BRP: Babel-Webre 500kV new line ($1.066B). Loss of 500kV path thermal overloads in South LA
MTEP25 | Central | BIG RIVERS ELECTRIC CORPORATION | 2037-12-22 00:00:00 | New BREC Bon Harbor-OMU Sub ‘M’ 69 kV Interconnection | To be included in MTEP24, the creation of a 69 kV interconnection between BREC and OMU. | KY | Other | Local Reliability | A plan has been developed to construct a 69 kV tie between BREC’s Bon Harbor site and OMU’s Substation M. The construction is expected to be completed and in-service on December 1st, 2026. This project is part of OMU’s plan to establish connection to BREC’s system to obtain a path to join MISO as a member and expand MISO’s footprint. In adding this interconnection two 69 kV line section between BREC’s Daviess substation and the interconnection point of Bon Harbor are being upgraded. One section, Rome Jct.-West Owensboro was already scheduled and approved in a previous MTEP study (project ID 3435). |  |  |  | 2026-12-01 | 69 |  | 7500000
MTEP25 | Central | BIG RIVERS ELECTRIC CORPORATION | 50577 | Henderson County Capacitor Bank | Henderson County Capacitor Bank Addition | KY | Other | Local Reliability | Local reliability voltage support |  |  |  | 2027-12-01 | 69 |  | 1500000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 25240 | Line Clearance Mitigation Program 2026 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2026. | MI; WI | Other | Local Reliability | Reliability – Line Clearance Program |  |  |  | 2028-06-30 | 345 |  | 9000000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50324 | 88th Street Substation bus expansion and 161-13 kV transformer installation | Expand 88th St Substation steel to ring bus and add a third 161-13 kV transformer | IA | Other | Load Growth | Serve load |  |  |  | 2027-12-31 | 161 |  | 9000000
MTEP25 | West | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | 50483 | St. John's Lake Breaker Station | Construct a new 69 kV breaker station near Willmar and rebuild the 69 kV line from the WMU tap to this breaker station to a double circuit line. | MN | Other | Local Reliability | Improve Load Serving Reliability. This is paired with 3 other projects from the Willmar Area Study. |  |  |  | 2029-12-30 | 69 |  | 9000000
MTEP25 | West | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | 50484 | Priam Second Transformer | This project adds a second 115/69 kV transformer at the Priam substation near Willmar and expands the substation buses. | MN | Other | Local Reliability | Improve Load Serving Reliability. This is paired with 3 other projects from the Willmar Area Study |  |  |  | 2029-12-30 | 115 |  | 9000000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50433 | Install Pine Island Island Area Substation | Install new distribution substation to meet load growth in area | MN | Other | Load Growth | Load growth in area is exceeding capability of existing substations |  |  |  | 2026-12-30 | 69 |  | 8900000
MTEP25 | West | ITC MIDWEST | 50204 | Clinton Rail and Air Park 161 kV Interconnection | IPL has requested a new substation interconnection in the Clinton area for a new load in the Clinton Rail and Air Park. To facilitate the request ITC Midwest will be building a new 161 kV 2 row 4 position breaker and ½ substation with 2 line positions and 2 transformer positions. The new substation will be expandable to 4 rows. All new 161 kV equipment will be capable of 2000A or greater. The new substation will be a PD substation and the common facilities and substation naming will be owned by IPL. | IA | Other | Load Growth | Customer requested interconnection for a new distribution source. |  |  |  | 2026-06-01 | 161 |  | 8760389
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50134 | Huiskamp - Division Street Tap 69 kV (Y-132), Rebuild | Rebuild and install OPGW on approximately 2.7 miles of Y-132 from Huiskamp SS to Division Street Tap switch structure, in addition rebuild 0.2 miles of the Division Street Tap to Division Street SS and install OPGW from Waunakee to Huiskamp SS. | WI | Other | Age and Condition | Asset Renewal |  |  |  | 2028-11-30 | 69 |  | 8500000
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50201 | Rebuild Slugger to LGE Trimble 34530 Ckt. 345kV Line | 34530 Rebuild - Slugger to LGE Trimble to (2)954ACSS@200C (DEI-owned portion only) | IN | BRP |  | MTEP24 confirmed - thermal OL of 111% (249541 08SLUGGERTMP 345 324114 7TRIMBLE CO 345 1) for "P7:345:LGEE:TRIMBLE DBL CKT TOWER1" identified; 10 yr summer peak model only so 6/1/2030 is the earliest MTEP required IS date |  |  |  | 2031-06-01 | 345 |  | 42964000
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50279 | Replace Staunton 230/138kV Xfmr Bk1 and 2 | Staunton sub: (alternative project submittal to replace MTEP #22227) upgrade 230/138kV Banks 1 and 2 to 250MVA nameplate | IN | BRP |  | Past MTEP P6 OL of Staunton Bk1 or Bk2 flo 13861 Dresser to Staunton line coupled with the loss of one of the Staunton 230/138 banks - somewhat exacerbated by Bolton 345/230 project. Interim operating mitigation: open circuit breaker 13801 at Cloverdale (open branch 249708,249731,1). |  |  |  | 2026-12-31 | 230 |  | 18800000
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50718 | Rebuild Cayuga to Nucor 345 kV line | Line rebuild (~32.3mi) to bundled 954ACSS conductor or 4000A equivalent. | IN | BRP |  | This project is driven by recent EPR submission of Project LEAP load, and future adjacent loads. | Data Center (BRP) | Y |  | 2029-06-01 | 345 |  | 95529061 | BRP: Rebuild Cayuga-Nucor 345kV driven by LEAP data center EPR submission
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50719 | Rebuild Nucor to Wolf Creek 345 kV line | Line rebuild (~14mi) to bundled 954ACSS conductor or 4000A equivalent. | IN | BRP |  | This project is driven by recent EPR submission of Project LEAP load, and future adjacent loads. | Data Center (BRP) | Y |  | 2029-06-01 | 345 |  | 49000000 | BRP driven by LEAP data center EPR. Rebuild Nucor to Wolf Creek 345kV
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50725 | Rebuild Kokomo HP to Tipton West to Cammack Rd Jct 230kV | Rebuild two separate 230kV lines to mitigate overloads due to EPR study. ~11.8mi of 23008 line from Tipton to Cammack Rd Jct to bundled 954ACSS conductor or 4000A equivalent and ~14.4mi of 23032 line from Kokomo Highland Park to Tipton West to bundled 954ACSS conductor or 4000A equivalent. | IN | BRP |  | This project is driven by recent EPR submission of Project LEAP load, and future adjacent loads. | Data Center (BRP) | Y |  | 2029-06-01 | 230 |  | 65500000 | BRP: Rebuild Kokomo-Tipton-Cammack 230kV driven by LEAP data center EPR
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50370 | Replace New London to Kokomo Highland Park 230kV Line | New London to Kokomo Highland Park 230kV - 23009 ckt. - Replace/Upgrade structures (7.5 miles) to get 100C operation of existing 900ACSR54X7@80C conductor | IN | GIP |  | J1378/J1482 (network upgrade) |  |  |  | 2027-02-12 | 230 |  | 1976000
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50374 | Upgrade Dresser 345kV Line | Dresser 345kV Line Upgrades: 34520 (to Fairbanks) and 34538 (to Sugar Crk) ckts. - replace structures to achieve line ratings of 100°C | IN | GIP |  | Network upgrades associated with J1027, J1028, & J1189 |  |  |  | 2027-07-01 | 345 |  | 11600000
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50280 | New Neuron - Lafayette 27MW load | Project Neuron (fka Mars) - Lafayette new load 27MWs - 13806 line very near Tipmont Co Farm | IN | Other | Load Growth | New Neuron - Lafayette; industrial load addition 27 MW | Large Industrial |  | 27 | 2028-12-31 | 138 |  | 24970000 | Project Neuron: 27MW new customer in Lafayette (DEI)
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50285 | New HE Shadow Lake 138/12kV Sub | New HE Shadow Lake 138/12kV distribution substation for Clark Co REMC to be inserted in the 13898 Speed – Jeffersonville 138kV line between River Ridge Central and Stoney Point Jct.; looped through with ATO; loop in/out with 954ACSS/TW20x7@200C conductor | IN | Other | Load Growth | HE - transfer load and distribution load growth |  |  |  | 2026-06-01 | 138 |  | 2974000
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50289 | New Wabash Industrial 69/12kV Sub | Wabash Industrial 69/12kV new sub to serve new 20+MW customer in the 69132 ckt - near Chippewa; includes 14.4MVAR capacitor | IN | Other | Load Growth | new large customer load | Large Industrial |  | 20+ | 2026-10-16 | 69 |  | 2968000 | Wabash Industrial: 20+MW customer near Chippewa (DEI)
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50341 | Replace 34507 Gibson-Petersburg 345 kV Line | 34507 Gibson-Petersburg Line Improvements - replace 16 aluminum Kaiser A, B, or C towers with 3 pole dead end structures at 2.5 mile intervals | IN | Other | Age and Condition | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with the Indiana Utility Regulatory Commission. |  |  |  | 2027-05-21 | 345 |  | 15207000
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50342 | Rebuild Greencastle Industrial Jct. to WVPA Vandalia 69kV Line | 6996 Greencastle Industrial Jct. to WVPA Vandalia Rebuild - 0.74 miles with 477ACSR/VR2@120C; Greencastle Industrial Jct. upgrade to ATO / SCADA control | IN | Other | Local Reliability | The dominate contingency is the loss of the 34541 Line between Amo (249240) and Qualitech Steel (249518). This triggers automated opening of the Amo bank to avoid overloading of this non-BES bank and extensive overloads on the 69kV system. This results in Greencastle Industrial Jct. (250469) to Vandalia (251002) and Vandalia (251002) to Filmore (250442) to load to 96.4% and 82.3% respectively. This is based on a MISO24 2009 SUM case. The loss of the Amo bank also results in contingency emerging loading issues but to a lesser extent. | Emerging Load |  |  | 2026-06-01 | 69 |  | 1984000
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50343 | Terre Haure Water St. 138kV Ring Bus | Terre Haure Water St. 138kV sub - construct 3-breaker 138kV ring bus | IN | Other | Local Reliability | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with the Indiana Utility Regulatory Commission. |  |  |  | 2026-12-10 | 138 |  | 16520000
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50345 | New WVPA Richland 69kV ring bus | WVPA Richland 69kV ring bus: install 3 - CB ring at existing sub; rebuild 0.9 mile WVPA Richland to Rochester Tap 6968 with 954ACSR | IN | Other | Local Reliability | This a WVPA-requested project. The new ring bus addresses sustained 6968 ckt. outages from line exposure (38 miles) and NIPSCO's interconnection with their field line fault inspection protocol. |  |  |  | 2026-11-11 | 69 |  | 11736000
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50347 | Replace Frankfort 230/69 Bk1 | Frankfort 230/69 Bk1: Replace 84MVA 230/69kV Transformer with new 150MVA transformer; replace 23069-1 ckt. switcher; replace substation RTU | IN | Other | Age and Condition | Asset Management-Reliability Programs: age and condition |  |  |  | 2026-07-31 | 230 |  | 6329000
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50349 | Crane Naval Base load expansion | Crane South Substation: expand 138kV bus into (4) CB Ring; Install 100MVA 138/69kV Transformer Bank 2; Add (2) 69kV breakers to the existing ring; construct new 69kV line to Crane Naval Base NW; reconductor 69193 line from Crane South to Crane Naval Base | IN | Other | Load Growth | Crane Naval Base Load Expansion; federal military facility | Federal/Military |  | 100 MVA | 2027-03-08 | 138 |  | 28966000 | Crane Naval Base load expansion with new 138/69kV transformer and 69kV line
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50351 | Rebuild Arcadia N to Arcadia 69kV Line | Arcadia N to Arcadia 69kV Rebuild - 2.5 miles of 69kV line 69180 from Arcadia north sub to Arcadia sub | IN | Other | Age and Condition | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with the Indiana Utility Regulatory Commission. |  |  |  | 2027-01-19 | 69 |  | 5500000
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50369 | Rebuild Huntington Goblesville Jct to United Jct 69kV Line | Huntington Goblesville Jct to United Jct 69kV rebuild: 6.45 miles of line 6923 ckt. | IN | Other | Age and Condition | The assets being addressed in this project fall under one or more of the system programs as outlined in TDSIC Plan filed with the Indiana Utility Regulatory Commission. |  |  |  | 2026-12-11 | 69 |  | 9238000
MTEP25 | Central | DUKE ENERGY INDIANA, LLC | 50376 | Rebuild HE Bethany to Charlestown Jct 69kV Line | 6955 ckt. Rebuild HE Bethany to Charlestown Jct - 954 ACSR at 120C | IN | Other | Load Growth | Project Driver: Multiple future proposed Indiana economic development projects such as The Cheesecake Factory, Sazerac in Charlestown, and Canadian Solar that are distribution-fed and interconnected to the 69kV system at River Ridge. 69kV contingency of most concern is the 250363 08CLRKSV to 250593 08INDARS id=1 outage, limiting River Ridge North to a very low future additional capacity of 7.7MW. | Multiple Industrial |  | 7 | 2026-06-01 | 69 |  | 3305000 | Cheesecake Factory, Sazerac, Canadian Solar in Charlestown IN driving 69kV rebuild
MTEP25 | South | ENTERGY SERVICES, LLC. | 50357 | Harelson-Jones Creek Tap 69kV Upgrades | Upgrade Harelson – Jones Creek Tap 69 kV line (~2.5 miles) and line bay riser | LA | BRP |  | Entergy’s Planning Guidelines and Criteria. P2.1 for the loss of Lockhart – Coly 69kV line overload Harelson – Jones Creek Tap 69 kV line. |  |  |  | 2027-06-01 | 69 |  | 14700000
MTEP25 | South | ENTERGY MISSISSIPPI, LLC. | 50367 | 2026 EML Asset Renewal Program | This project is for the EML Asset Renewal Program that will be executed in 2026 | MS | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc. |  |  |  | 2026-12-31 | 500 |  | 68400000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50196 | Admiral 138 kV New Substation and Transmission Line | The Admiral 138 kV station will be designed as a 138kV six breaker ring bus. The substation will include six (6) breakers, one (1) Cap Bank, two (2) 67MVA power transformers, and two (2) main/feeder breakers. Construction and installation of a new line from Moril substation to Admiral will also be part of the permanent scope of work, along with the installation of a new 138kV breaker at Moril. | LA | Other | Load Growth | Entergy received a request from a customer adding new load near New Iberia, LA. Entergy is proposing to construct a new 138 kV substation name Admiral that will be cut in on the existing Kirk to Moril 138 kV line to serve the new load. |  |  | 67 MVA | 2025-09-01 | 138 |  | 54400001
MTEP25 | South | ENTERGY MISSISSIPPI, LLC. | 50368 | McAdams 500 kV Bus SPOF | All 500kV line panels at McAdams need to have primary 1 relays on a separate DC panel than primary 2/backup relays. • The breakers for these lines must have trip coil #1 and trip coil #2 fed from separate DC panels. • The DC panels must be fed from separate battery sets and the DC panels cannot be wired in series or in parallel to one another. | MS | BRP |  | NERC TPL-001-5 and Entergy Local Planning Guidelines and Criteria for P5 contingency involving the failure of a non-redundant component of the protection system on the McAdams-Wolf Creek 500kV, McAdams-Lakeover 500kV, or McAdams-Attala 500kV lines followed by a single line to ground fault one of the lines result in Attala and Hinds generation going unstable |  |  |  | 2026-06-01 | 500 |  | 4100000
MTEP25 | South | ENTERGY SERVICES, LLC. | 25436 | Bobville Area Menu Phases 1 through 7 | Phase 1 is relay improvement at Grimes 345 and 138 kV stations needed by 2025 Summer. Phase 2 adds the first 25.1 MVAR capacitor bank at Dobbin 138 kV substation needed by 2026 Summer. Phase 3 adds the second 25.1 MVAR capacitor bank at Dobbin needed by 2029 Summer. Phase 4 rebuilds the existing Fish Creek - Deer Lake 138 kV line needed by 2031 Summer. Phase 5 rebuilds the existing Dobbin - Tubular 138 kV line needed by 2031 Summer. Phase 6 rebuilds the existing Deer Lake - Spring Branch 138 kV line needed by 2034 Summer. Phase 7 rebuilds the existing Dobbin - Spring Branch line needed by 2034 Winter. | TX | BRP |  | NERC TPL-001-5 Reliability Standards and Entergy's Planning Guidelines and Criteria. Drivers: (1) A P5 at Grimes overloads Fish Creek to Deer Lake to Spring Branch. Mitigated by Phase 1. (2) The P2-1 contingency of the Ponderosa to Fish Creek 138 kV line section results in low voltage at Fish Creek, Dobbin, Spring Branch, and Deer Lake 138 kV. Mitigated by Phase 2 and 3. (3) The P2-3 contingency of a Grimes 345 kV breaker results in a thermal overload of the Deer Lake to Fish Creek and Dobbin to Spring Branch 138 kV line sections. Mitigated by Phase 4 and 7. (4) The P2-1 contingency of the Ponderosa to Fish Creek 138 kV line section results in a thermal overload on the Tubular to Dobbin and Deer Lake to Spring Branch 138 kV line sections. Mitigated by Phase 5 and 6. |  |  |  | 2034-12-31 | 345 |  | 138000000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50352 | Amelia to Poly 69 kV Upgrades | Upgrade station equipment and line sections on Amelia - Poly 69 kV through path. | TX | BRP |  | The P1.2 contingency of Amelia-Elizabeth 69 kV line causes a thermal overload on Amelia-Poly 69 kV line. |  |  |  | 2029-12-31 | 69 |  | 3700000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50354 | Mid County to Stonegate 138 kV Rebuild | Rebuild Mid County-Stonegate 138 kV line | TX | BRP |  | The P7 contingency of Carroll Street Park-South Beaumont 138 kV lines causes thermal overloads on Mid County-Stonegate 138 kV and Dupont-Nitro 69 kV line. |  |  |  | 2027-12-17 | 138 |  | 6540000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50199 | Rhodair 230 kV New Substation and Transmission Lines | Entergy is proposing to construct new 230 kV transmission lines sourced from the existing Garden 230 kV station to serve new load at the new Rhodair 230 kV station near Port Arthur, TX. The Garden to Rhodair 230 kV circuits 1 and 2 are a combined ~4.5 miles long. | TX | Other | Load Growth | Entergy has received requests from customers adding new load in the Port Arthur, TX area. Upgrades, including this facility, have been identified as needed due to the load growth. | Large Industrial (EPR) |  |  | 2025-08-26 | 230 |  | 85000000 | ETI EPR $85M
MTEP25 | South | ENTERGY SERVICES, LLC. | 50353 | 2026 ENOL Asset Renewal Program | This project is for the ENOL Asset Renewal Program that will be executed in 2026 | LA | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | 2026-12-31 | 230 |  | 3200000
MTEP25 | South | ENTERGY MISSISSIPPI, LLC. | 50600 | Oak Bend 230 kV station | The Oak Bend 230 kV breaker and a half substation will be fed out of a new Baxter Wilson 230 kV substation. The existing Baxter Wilson 500 kV substation will expanded to include a new Baxter Wilson 230 kV substation fed from 2-500/230 kV Auto Transformers. Two bays to connect to (2) 3-mile 230 kV lines to the Oak Bend 230 kV substation. Customer load will be fed out of (3) 150 MVA 230/34.5 kV transformers. | MS | Other | Load Growth | Entergy received a request from a customer adding new load in Warren County, MS. Upgrades, including this facility, have been identified as needed due to the load growth. | Large Load |  | 150 MVA | 2029-12-01 | 500 |  | 150000002 | Oak Bend 230kV: $150M for new customer in Warren County MS
MTEP25 | South | ENTERGY SERVICES, LLC. | 50355 | 2026 ELL Asset Renewal Program | This project is for the ENLL Asset Renewal Program that will be executed in 2026 | LA | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | 2026-12-31 | 500 |  | 83300000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50528 | Benoit 230 kV Station | Entergy is proposing to construct a new 230 kV station named Benoit to serve a new customer cut into the existing Mud Lake to Big Lake 230 kV line south of Lake Charles, LA. The Benoit 230 kV station will be a 5 bay breaker and a half substation, including two 64.8 MVAR capacitor banks. | LA | Other | Load Growth | Entergy received a request from a customer adding new load south of Lake Charles, LA. Upgrades, including this facility, have been identified as needed due to the load growth. The project is being submitted after the September 2024 cutoff for inclusion into MTEP25. | Load Growth |  |  | 2027-07-01 | 230 |  | 51800001 | ELL $51.8M
MTEP25 | South | ENTERGY SERVICES, LLC. | 50361 | Willow Glen 138 kV Bus SPOF | Install a new battery bank at Willow Glen 138 kV station. The primary 1 relay needs to be on a separate DC panel than primary 2/backup relay. The breakers for the AT must have trip coil #1 and trip coil #2 fed from separate DC panels and the DC panels must be fed from separate battery sets. The DC panels cannot be wired in series or in parallel to one another. | LA | BRP |  | NERC TPL-001 Reliability Standards and Entergy’s Planning Guidelines. A P5 non-redundant bus differential relay failure of both Willow Glen 138 kV busses causes Conway-Ellem and Conway-Zephyr 138 kV lines to exceed their thermal ratings. |  |  |  | 2026-06-01 | 138 |  | 4000000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50539 | Cargas 500 kV and Smalling 500-230 kV stations | Entergy is proposing to construct two new 500/230 kV stations to serve a new customer cut into the existing Perryville (Cargas) to Baxter Wilson 500 kV line in Holly Ridge, LA. Cargas 500 kV station will be cut into the Perryville to Sterlington 500 kV lines 1 and 2 and Perryville to Baxter Wilson 500 kV line. Smalling 500/230 kV station will be cut into the Cargas to Baxter Wilson 500 kV line. Two additional 27 mile 500 kV lines from Smalling to Cargas. The Smalling 230 kV station will be a breaker and a half substation, including four 1,500 MVA 500/230 kV autotransformers and eight 230 kV lines going to six 230 kV stations which will feed the new load. Upgrade Sterlington 500 kV Line trap on the El Dorado line, due to the loss of Grand Gulf Generation overloading the Sterlington to El Dorado 500 kV line. | LA | Other | Load Growth | Entergy received request from customer adding new load in Holly Ridge LA. Two new 500/230kV stations, 27mi new 500kV, four 1500MVA 500/230kV autotransformers, eight 230kV lines | Large Load (EPR) |  | 500 MVA | 2026-12-01 | 500 |  | 1210000001 | Cargas/Smalling 500-230kV: $1.21B for new customer in Holly Ridge LA
MTEP25 | South | ENTERGY MISSISSIPPI, LLC. | 50601 | Andes 230 kV Expansion | Expansion of the 230 kV Andes substation to include 3 additional bays, 9 breakers to allow for customer load addition and reactive resource installation. | MS | Other | Load Growth | Entergy received a request from a customer adding new load in Madison County, MS. Upgrades, including this facility, have been identified as needed due to the load growth. | Large Load |  |  | 2028-04-01 | 230 |  | 40000000 | EML $40M
MTEP25 | South | ENTERGY SERVICES, LLC. | 50546 | Bluepoint 230 kV New Substation and line Cut-ins | Entergy is proposing to construct a new 230 kV four breaker ring bus station named Bluepoint to serve a new customer cut into the new Commodore to Waterford 230 kV line (~10.4 miles in and out) near Donaldsonville, LA. The Bluepoint 230 kV station will also include (2) 150MVA transformers, (4) 3000A breakers. | LA | Other | Load Growth | Entergy received a request from a customer adding new load near Donaldsonville, LA. Upgrades, including this facility, have been identified as needed due to the load growth. | Load Growth |  | 150 MVA | 2027-08-01 | 230 |  | 59600000 | ELL $59.6M
MTEP25 | South | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | 50191 | Beebe North 115kV SS - Nelson 115kV SS | AECC will construct a new Beebe North 115kV switching station on EAI's Beebe to Garner 115kV transmission line. This new switching station will tap the Beebe to Garner line approximately 2 miles north of EAI's Beebe station. AECC will also construct a new, approximately 7-mile long, 115kV transmission line from the new Beebe North 115kV SS to a new Sylvania 115kV substation. Additionally, AECC will construct another new, approximately 7-mile long, 115kV transmission line from the new Sylvania station to a new Nelson 115kV switching station. The new Nelson 115 kV SS will tie into the Member Coop's existing 115kV system. | AR | BRP |  | This project is needed to support voltage and improve the reliability of the Member Coop's system caused by normal load growth in the area. | Area Load Growth (BRP) |  |  | 2028-09-01 | 115 |  | 37000000 | BRP driven by normal load growth. System Need: "support voltage and improve reliability caused by normal load growth"
MTEP25 | South | ENTERGY ARKANSAS, LLC | 50384 | Hot Springs 500kV SPOF | All 500kV line panels at Hot Springs EHV will have primary 1 relays on a separate DC panel than primary 2/backup relays. The breakers for these lines will have trip coil #1 and trip coil #2 fed from separate DC panels. The DC panels will be fed from separate battery sets. | AR | BRP |  | The Hot Spring, Magnet Cove, Remmel, Carpenter, Blakely, and Degray Dam generation go unstable for a SLG fault on Hot Springs-Etta 500kV or Hot Springs-Magnet Cove 500kV lines with non-redundant protection system component failure. |  |  |  | 2026-12-01 | 500 |  | 500000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50209 | South China 138 kV New Substation | South China 138 kV station will be interconnected on the Cheek - Petry Woods 138 kV line. | TX | Other | Load Growth | Entergy has received a request from a customer adding new load in the China, TX area. |  |  |  | 2025-05-12 | 138 |  | 5800000
MTEP25 | South | ENTERGY ARKANSAS, LLC | 50385 | El Dorado Donan - El Dorado Monsanto 115 kV: Rebuild Line | Rebuild the ~3.1 mile line segment along with any other station equipment to achieve a 1300 A flow-through rating. | AR | BRP |  | The Donan - Monsanto transmission line overloads for the loss of J1612 generation & El Dorado EHV – El Dorado E 115kV line. [NERC TPL-001 P3] |  |  |  | 2027-06-30 | 115 |  | 7900000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50608 | Riparian 115 kV Station | Entergy is proposing to construct a new 115 kV station named Riparian to serve a new customer cut into the existing Alliance to Happy Jack 115 kV line in Point Celeste, LA. | LA | Other | Load Growth | Entergy received a request from a customer adding new load in Point Celeste, LA. This facility was identified as needed due to the load growth. | Load Growth (EPR) |  |  | 2026-12-30 | 115 |  | 38200000 | ELL EPR $38.2M
MTEP25 | South | ENTERGY SERVICES, LLC. | 50356 | Port Acres Bulk to Legend 230 kV Rebuild | Cut Port Acres Bulk to Sandling 230 kV line in and out of Legend. Rebuild both Port Acres Bulk to Legend 230 kV lines. | TX | BRP |  | Multiple N-1 contingencies overload the Port Acres Bulk - Sandling and Port Acres Bulk - Legend 230 kV lines. The driving contingencies are: P1.1 loss of OCAPS, P2.3 breaker failure at Sabine 230 kV substation, P2.3 breaker failure at Cypress 500 kV substation, P7 loss of Sabine - VFW Park and Sabine - Gulfway 230 kV lines, and P7 loss of Sabine - Gulfway and VFW Park - Gulfway 230 kV lines. |  |  |  | 2028-06-01 | 230 |  | 21900001
MTEP25 | South | ENTERGY ARKANSAS, LLC | 50386 | Hilltop - Saint Joe 161kV: Rebuild Line | Rebuild Hilltop – St Joe along with any other station equipment to achieve a 1300 A through path rating. | AR | BRP |  | Compliance with NERC Reliability Standard TPL-001, R2.7. Increased reliability by updating aging infrastructure and increased line capacity for improved transmission system performance. |  |  |  | 2027-06-30 | 161 |  | 12384021
MTEP25 | South | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | 50594 | Helena Harbor Load Addition | A member cooperative has a new customer that will be adding a 250MW load. A new 230kV station (Helena Harbor) will be constructed and served on a new, approximately 6-mile radial off Entergy's existing Ritchie 230kV station. Entergy will add a new 230kV position at their Ritchie station to accommodate this new 230kV radial. | AR | Other | Load Growth | A member cooperative has a new customer that will be adding a 250MW load. A new 230kV station (Helena Harbor) will be constructed and served on a new, approximately 6-mile radial off Entergy's existing Ritchie 230kV station. Entergy will add a new 230kV position at their Ritchie station to accommodate this new 230kV radial. | Load Growth (EPR) |  | 250 | 2026-12-01 | 230 |  | 18200000 | Helena Harbor: 250MW customer via new 230kV station 6mi radial (AECC AR)
MTEP25 | South | ENTERGY ARKANSAS, LLC | 50383 | 2026 EAL Asset Renewal Program | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2026 asset renewal plans have not yet been finalized. | AR | Other | Age and Condition |  |  |  |  | 2026-12-30 | 161 |  | 16475000
MTEP25 | South | ENTERGY ARKANSAS, LLC | 50441 | Wrightsville 115kV: Build two 115kV lines | Build two 3.5 mile new radial 115kV transmission lines from Wrightsville 115kV substation to a new customer station to serve new load. | AR | Other | Load Growth |  |  |  |  | 2027-02-26 | 115 |  | 17800000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50362 | Richard 500/138 kV Bus SPOF | All 138kV line panels need to have primary 1 relays on a separate DC panel than primary 2/backup relays. The DC panels must be fed from separate battery sets. The existing auto relays need to be investigated to ensure sufficient contacts for the trip coils to be redundant. Existing auto relays will need to be replaced if there are no sufficient contacts. | LA | BRP |  | NERC TPL-001-5 and Entergy Local Planning Guidelines and Criteria. P5 Fault on the Richard 138 kV bus with delayed clearing overloads Scott to Bonin 138kV line. |  |  |  | 2028-06-01 | 500 |  | 8700000
MTEP25 | South | ENTERGY ARKANSAS, LLC | 50387 | Saint Joe - Everton Road 161kV: Rebuild Line | Rebuild St Joe – Everton Rd along with any other station equipment to achieve a 1300 A through path rating. | AR | BRP |  | The St Joe – Everton Rd transmission line overloads for the bus failure at Table Rock 161 kV. [NERC TPL-001 P2.2] |  |  |  | 2029-12-30 | 161 |  | 29720000
MTEP25 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25502 | Line 4B Rebuild | A complete rebuild of Line 4B and line extension to the existing Decatur Substation (Lake – Decatur 69kV) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Lake and Decatur. | MS | Other | Age and Condition | Line 4B (Lake - Decatur 69kV) was constructed in 1970 and is reaching the end of its useful life and needs to be rebuilt. The existing Decatur GOAB joins Line 4B, Line 5, and Line 4A being located approximately 0.5 mi from the Decatur Substation. Line 4B is to be extended to the existing Decatur Substation to a new GOAB installed as part of Line 5 Rebuild to significantly decrease the radial tap length. |  |  |  | 2027-03-01 | 69 |  | 10430000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50363 | Little Prairie – Mud Lake Low Voltage Project | Install 223.90 MVAR reactive support (2-SVCs) at Little Prairie 230 kV station | LA | BRP |  | NERC TPL-001 Reliability Standards and Entergy’s Planning Guidelines. P6 contingency for the loss of Little Prairie – Big Lake 230 kV line and Little Prairie – Carlyss 230 kV line causes low voltage violations at Little Prairie and Mud Lake 230 kV stations. |  |  |  | 2031-10-31 | 230 |  | 54300000
MTEP25 | South | ENTERGY ARKANSAS, LLC | 50388 | Everton Road - Harrison East 161kV: Rebuild Line | Rebuild Everton Rd – Harrison East along with any other station equipment to achieve a 1300 A through path rating. | AR | BRP |  | Compliance with NERC Reliability Standard TPL-001, R2.7. Increased reliability by updating aging infrastructure and increased line capacity for improved transmission system performance. |  |  |  | 2028-06-30 | 161 |  | 20140000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50358 | Dupont Beamont to Nitro 69 kV Station Upgrades | Upgrade station equipment at Dupont Beaumont 69 kV substation. | TX | BRP |  | The P7 contingency of Carroll Street Park-South Beaumont 138 kV lines causes thermal overloads on Mid County-Stonegate 138 kV and Dupont-Nitro 69 kV line. |  |  |  | 2029-12-01 | 69 |  | 250000
MTEP25 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 25541 | Line 5 Rebuild | A complete rebuild of Line 5 and line extension to the existing Decatur Substation (Newton – Decatur 69kV) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Newton and Decatur. | MS | Other | Age and Condition | Line 5 (Newton - Decatur 69kV) was constructed in 1970 and is reaching the end of its useful life and needs to be rebuilt. The existing Decatur GOAB joins Line 4B, Line 5, and Line 4A being located approximately 0.5 mi from the Decatur Substation. Line 5 is to be extended along new ROW adjacent to the existing Line 4A ROW corridor to the existing Decatur Substation where a new GOAB is to be installed to significantly decrease the radial tap length. |  |  |  | 2026-04-01 | 69 |  | 6100000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50671 | RiverPlex 500-230 kV Station | Entergy is proposing to construct a new 500-230 kV station named RiverPlex to serve a new customer cut into the new Commodore to Churchill 500 kV line and the Commodore to Blue Point, Blue Point to Waterford, and Donaldsonville to Evergreen 230 kV lines near Donaldsonville, LA. Two new 230 kV lines will be constructed between RiverPlex 230 kV and the new Mulberry Road 230 kV station which will serve the new load. One new 230 kV line will be constructed between Blue Point and Mulberry Road 230 kV stations. The RiverPlex 500 kV station will be configured as a ring bus, while the RiverPlex 230 kV station will be configured as a breaker and a half bus. Two 500-230 kV 1200 MVA autotransformers will also be installed at the station. The new station has a target ISD in August 2028. | LA | Other | Load Growth | Entergy received a request from a customer adding new load near Donaldsonville, LA. Upgrades, including this facility, have been identified as needed due to the load growth. | Large Load (EPR) |  | 1200 MVA | 2028-08-30 | 500 |  | 284000000 | RiverPlex 500-230kV: $284M for new customer near Donaldsonville LA
MTEP25 | South | ENTERGY SERVICES, LLC. | 50586 | 2026 ETI Asset Renewal Program | This project is for the ETI Asset Renewal Program that will be executed in 2026 | TX | Other | Age and Condition | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  |  |  | 2026-12-31 | 500 |  | 34400000
MTEP25 | South | ENTERGY ARKANSAS, LLC | 50581 | Fort Mountain 161kV: Build New Substation | Build 1 mile of in and out cut-in transmission line to a new 161 kV substation called Fort Mountain on the Berryville - Green Forest 161kV line section in Berryville, AR. Entergy will construct and operate the high-side through bus of the station only. | AR | Other | Load Growth | This project is needed to connect a new block load customer. |  |  |  | 2026-03-31 | 161 |  | 5727876
MTEP25 | South | ENTERGY MISSISSIPPI, LLC. | 50602 | Green Acres 500/230 kV New Substation | Construct a new 500/230 kV Green Acres Substation to serve a new customer. Green Acres 500 kV substation will be 4 bay breaker and a half substation. 500 kV will be cut in on Lakeover – Ray Braswell 500 kV and Lakeover - McAdams 500 kV lines. The Green Acres 230 kV station will be a 6 breaker ring expandable breaker and half scheme, including two 1200 MVA 500/230 kV autotransformers and 6 breakers with 5 nodes. 3-1 mile 230 lines supplying the new 230 kV County Line substation to support customer load. Construct County Line 230 kV substation breaker and a half station with 8 bays to support customer load and reactive resources | MS | Other | Load Growth | Entergy received a request from a customer adding new load in Madison County, MS. Upgrades, including this facility, have been identified as needed due to the load growth. | Large Load |  | 1200 MVA | 2029-12-01 | 500 |  | 312000002 | Green Acres 500/230kV: $312M for new customer in Madison County MS
MTEP25 | South | ENTERGY SERVICES, LLC. | 50364 | Waterford 500/230 kV AT Upgrade | Upgrade Waterford 230 kV jumper (~0.26 miles, located inside 230 kV station) to 1200 MVA min. | LA | BRP |  | NERC TPL-001 Reliability Standards and Entergy’s Planning Guidelines. P2.3 Breaker failure of Frisco 230 kV station breaker S4300 overloads the Waterford 230 kV low side jumper to switchyard . |  |  |  | 2030-06-01 | 230 |  | 310000
MTEP25 | South | ENTERGY SERVICES, LLC. | 50359 | Bryan to Runny 138 kV New Line and Substation | Build a new 138 kV switching station between College Station and Grimes 138 kV substations called Runny. Build a new 138 kV line from Bryan to Runny. | TX | BRP |  | The P2.3 breaker failure at College Station 138kV substation causes a thermal overload on the Rivtrin-Walker 138 kV line. The P1.2 loss of Bryan-College Station 138 kV line causes a thermal overload on the Rivtrin-Walker and Walker– Cincinnati 138 kV line. The P2.3 breaker failure at Bryan 138 kV substation causes a thermal overload on the Rivtrin-Walker and Walker– Cincinnati 138 kV line.The N-1-1 contingency resulting in the loss of the College Station to Bryan and Rivtrin to Gibbs 138 kV lines will result in NCLL. |  |  |  | 2031-05-01 | 138 |  | 99400001
MTEP25 | South | ENTERGY SERVICES, LLC. | 50675 | Cove Ridge 138 kV Station | Entergy is proposing to construct a new 138 kV station named Cove Ridge to serve a new customer cut into the existing Hollywood-Orange 138 kV line near Vinton, LA. The Cove Ridge 138 kV station will be equipped with two breakers and a Capacitor Bank. | LA | Other | Load Growth | Entergy received a request from a customer adding new load near Vinton, LA. This facility was identified as needed due to the load growth. | Load Growth (EPR) |  |  | 2027-12-01 | 138 |  | 24100000 | ELL EPR $24.1M
MTEP25 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 50391 | Line 74B Rebuild | A complete rebuild of Line 74B (Colonial Collins – Colonial Kola 69kV) is recommended at 161kV insulation with more reliable structural designs and OPGW. This project will increase reliability of the transmission system and provide an OPGW communication link between Colonial Collins and Colonial Kola. | MS | Other | Age and Condition | Line 74B (Colonial Collins - Colonial Kola 69kV) was constructed in 1975 and is reaching the end of its useful life and is in need of being rebuilt in order to maintain reliability. |  |  |  | 2027-01-01 | 69 |  | 900000
MTEP25 | South | ENTERGY ARKANSAS, LLC | 50496 | MPFCA Replace Sherwood 115kV Breakers | The 1200 A, 17.5 kA oil circuit breakers B0350 and B0397 will be replaced with new 3000 A gas circuit breakers. Disconnect switch B0392 will be replaced and two new replay panels for power transformers #1 and #2. | AR | GIP |  | This project is needed due to inadequate short circuit capability. This project has an executed MPFCA. |  |  |  | 2026-10-31 | 115 |  | 2132000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50437 | Horseshoe Lake Substation | Build new Horseshoe Lake Substation to transfer load from Richmond Substation | MN | Other | Local Reliability | The 69 kV line that Richmond substation is on has high throughflow issues due to the parallel configuration with the 115 kV line. The line serves multiple Xcel and GRE substations along with high exposure there is high risk of outage and impact. Building new substation and connecting to new line removes some exposure. |  |  |  | 2027-01-01 | 69 |  | 8500000
MTEP25 | West | GREAT RIVER ENERGY | 50273 | Heartland Lakes Area Projects | 1. Build a new, ~5.0-mile 115 kV tap line from IM-HSX line to the new Heartland Lakes distribution substation. 2. Add High side structure, breaker, switch, and relaying at the Hubbard substation 3. Utilize 477 ACSR conductor. | MN | Other | Local Needs | Member Requested Distribution Substation |  |  |  | 2029-10-01 | 115 |  | 8485501
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50702 | Elm Road HVB Breaker and Relay Asset Renewal | Replacement of (5) 345kV HVB SF6 breakers and jumpers with new SF6 gas breakers at Elm Road. | WI | Other | Age and Condition | Asset Renewal - Breakers |  |  |  | 2029-12-01 | 345 |  | 8400000
MTEP25 | West | MINNESOTA POWER INC. | 50395 | Transmission Line Pole Replacement 2025 | Replacing red-tag transmission line poles. | MN | Other | Age and Condition | Age and Condition |  |  |  | 2025-12-31 | 230 |  | 8250000
MTEP25 | West | GREAT RIVER ENERGY | 50265 | Victor Area Projects | Rebuild DS line. DSX Line to SS377. Line length is approx. 9.25 miles | MN | Other | Age and Condition | The line is in the 1950’s vintage and is targeted to be replaced due to age and condition. |  |  |  | 2029-12-12 | 69 |  | 8093000
MTEP25 | West | OTTER TAIL POWER COMPANY | 50521 | OTP Donaldson South J1575 Interconnection | Interconnection customer J1575 will be interconnecting 70 MWs onto the Donaldson to Warsaw 115 kV transmission line. | MN; ND | GIP |  | Interconnection facilities required to accommodate interconnection customer J1575. |  |  |  | 2028-08-03 | 115 |  | 8060297
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50443 | Monroe County Breaker and Transformer EOL Replacement | Replace 4 breakers and TR01 and TR02 at Monroe county | MN; WI | Other | Age and Condition | Breakers are at end of life and are experiencing gas leaks, causing reliability concerns. Transformers are at end of life, causing reliability concerns |  |  |  | 2028-12-01 | 161 |  | 8000000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50460 | Prairie Island TR10 Replacement | Replace end of life Prairie Island TR10 | MN | Other | Age and Condition | Transformer has reached end-of-replacement life and starting to show increasing signs of internal degradation |  |  |  | 2031-12-01 | 345 |  | 7990300
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50126 | Coyne Street SS Relay, Breaker and House Asset Renewal | At Coyne Street SS, asset renewal of four 115 kV oil circuit breakers, six 115 kV disconnect switches, and 1 control house with all panels and components. | WI | Other | Age and Condition | Asset Renewal |  |  |  | 2028-12-01 | 115 |  | 7950000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50436 | rebuild W3449 Marshland to Mississippi River | rebuild W3449 Marshland to Mississippi River | WI | Other | Age and Condition | The existing structures are at end of life and have numerous defects. |  |  |  | 2027-12-15 | 69 |  | 7800000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50588 | Forest Junction – Branch River 345 kV (W-15), Line Uprate | Uprate W-15 Forest Junction – Branch River 345 kV line per ATC T-Line design standards to achieve minimum 1918 Amps (1146 MVA) normal and 2490 Amps (1488 MVA) emergency ratings for all seasons. | WI | BRP |  | BRP |  |  |  | 2029-01-01 | 345 |  | 7754000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50518 | J1773 J1781 MPFCA Network Upgrades | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. J1773 is seeking interconnection service for 300 MW and J1781 is seeking interconnection service for 300 MW. Network upgrades will consist of Hill Valley – Eden 138kV (X-127) reconductor project and Eden – Highland 138 kV (X-147) rebuild project. | WI | GIP |  | Generation Interconnection Project (MPFCA) |  |  |  | 2027-10-10 | 138 |  | 7623089
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50429 | West Byron TR 2 | Install new distribution transformer to meet load growth in area | MN | Other | Load Growth | Load growth in area is exceeding capability of existing transformer at substation |  |  |  | 2026-10-15 | 69 |  | 7535000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50195 | Carroll County-Carroll South 69 kV Line Rebuild for DPP 2020 | Rebuild and reconductor the line to increase line rating. | IA | GIP |  | DPP 2020 West identified network upgrade |  |  |  | 2027-12-01 | 69 |  | 7500000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50449 | Roughrider Substation | Install new distribution substation to meet load growth in area | ND | Other | Load Growth | Load growth in area is exceeding capability of existing transformer at substation |  |  |  | 2029-10-15 | 115 |  | 7500000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50457 | Install Montrose TR2 | Install new distribution transformer to meet load growth in area | MN | Other | Load Growth | Load growth in area is exceeding capability of existing transformer at substation |  |  |  | 2026-12-31 | 69 |  | 7450000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50426 | Thunder Substation | Install new distribution substation to meet load growth in area | ND | Other | Load Growth | Load growth in area is exceeding capability of existing distribution substations in area |  |  |  | 2027-10-15 | 115 |  | 7300000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50547 | East Beloit SS, DIC, Sub Rebuild | In support of a distribution substation relocation/rebuild, ATC will extend COR-BEG 138kV (X-41) line approximately 0.15 mile (double circuit transmission) to the new East Beloit substation and install 2 sets of bus-tie disconnect switches. ATC will retire COR-ESB 69kV (Y-140) line (Approx. 0.5 miles) and the existing East Beloit SS location and install 2 line circuit breakers and 2 line disconnects at Dickinson SS. | WI | Other | Load Growth | Load Interconnection |  |  |  | 2028-12-30 | 138 |  | 7200000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50124 | Portage SS Relay and Breaker Asset Renewal | Asset Renewal of the Portage SS control house, all assets within the control house, and 5 oil circuit breakers. | WI | Other | Age and Condition | Asset Renewal |  |  |  | 2028-12-01 | 138 |  | 7100000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50532 | Stiles - Sherwood 138 kV (L-142), Partial Rebuild | Replace select ~50 wood poles across the line that were originally treated with Chromated Copper Arsenate (CCA). The initial assumption is to transfer existing wires. CCA treatment visually makes the poles look ‘green’ in the field and is a known bad performer on our footprint and in the industry. These poles are more brittle, decayed, dry out faster and susceptible to mechanical failure. | WI | Other | Age and Condition | Asset Renewal - Transmission Line |  |  |  | 2028-12-31 | 138 |  | 7000000
MTEP25 | West | GREAT RIVER ENERGY | 50242 | New Sweden Area Projects | Rebuild BE-NST line from SS2831 to New Sweden Substation. Line length is approx. 7.4 miles. | MN | Other | Age and Condition | The line is to be replaced due to age and poor condition. |  |  |  | 2030-02-28 | 69 |  | 6996498
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50435 | Install East Mankato Area Substation | Install new distribution substation in East Mankato to meet load growth in area | MN | Other | Load Growth | Load growth in area is exceeding capability of existing substations in the East Mankato area. |  |  |  | 2027-12-31 | 115 |  | 6700000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50434 | Replace Meire Grove TR1 | Upgrade transformer 1 at Meire Grove to support load growth | MN | Other | Load Growth | Load growth in area is exceeding capability of existing transformer |  |  |  | 2027-05-03 | 69 |  | 6200000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 24925 | Range Line Dist (WE) - Range Line Switchyard 138 kV (61452), Replace Underground Cable | Replace underground cable from Range Line Dist (WE) to Range Line Switchyard. | WI | Other | Age and Condition | Asset Renewal - Transmission Line |  |  |  | 2028-06-01 | 138 |  | 6000000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50127 | Finger Road SS Relays and Remote Ends Asset Renewal | Asset Renewal of the Finger Road SS control house and all assets within the control house. Project also includes the remote end asset renewal of 3 relay panels and the RTU panel at Danz Avenue. | WI | Other | Age and Condition | Asset Renewal |  |  |  | 2028-12-01 | 69 |  | 5801000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50125 | Rock River SS and Remote Ends Asset Renewal | Asset Renewal of several relay panels, disconnect switches, and two battery banks at Rock River SS. Project also includes asset renewals of several relay panels, RTU panel, disconnect switches, and battery bank at Town Line Road SS. | WI | Other | Age and Condition | Asset Renewal |  |  |  | 2028-12-01 | 138 |  | 5614000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 21922 | Sigel - Vesper 69 kV (Y-108/Y-107), Partial Rebuild | This project is to partially rebuild portions of Y-107 and Y-108 near Sigel and Vesper substations. Each circuit has ~1.5 miles of rebuild work that is needed. This work is intended to cover remaining scope of work that is not on potential LRTP Tranche 1 scope of work in this area. | WI | Other | Age and Condition | Asset Renewal - Transmission Line |  |  |  | 2030-12-31 | 69 |  | 5500000
MTEP25 | Central | HOOSIER ENERGY | 50490 | Merom Station 345kV Expansion and New 345kV line | Expand Merom 345kV station with additional 345kV position for new line. Extend a new 1.5-mile 345KV line to new customer substation. | IN | Other | Load Growth | To serve a new customer load southeast of Merom station. | Large Industrial |  |  | 2030-12-01 | 345 |  | 14000000 | Merom 345kV expansion for new customer SE of Merom (HE)
MTEP25 | Central | HOOSIER ENERGY | 50491 | New Ellettsville 345kV Station | Construct new 345kV transmission station ring-bus along existing Worthington-Bloomington 345kV transmission line. | IN | Other | Load Growth | To serve a new customer load that has requested 345kV service | Large Industrial |  |  | 2035-01-01 | 345 |  | 20000000 | Ellettsville 345kV for new customer requesting 345kV service (HE)
MTEP25 | Central | HOOSIER ENERGY | 50492 | Expand Wheeler Creek 138 kV Station | Expand Wheeler Creek Transmission Station to accept the 138 feeds from SIPC Hamilton and Ameren Kays. One 138 kV Breaker will be required as well as conversion to a ring bus. This is being planned in conjunction with other projects from Ameren and SIPC as part of coordinated portfolio of projects called "South Central Illinois Transmission Expansion". | IN | Other | Local Reliability | The project will support the SCITE portfolio of projects. This project will substantially increase reliability to the Wheeler Creek Substation. The station is currently served by one radial line tap. In the future, the station will be looped into the 138 kV system. |  |  |  | 2029-12-01 | 138 |  | 4700000
MTEP25 | Central | HOOSIER ENERGY | 50493 | Rebuild Ashland Tap - Cisne Junction 69 kV Line | The 5.7 mile 69 kV line from Ashland Tap - Cisne Junction will be rebuilt with poles replaced, an upgraded conductor, and a new switch at Ashland Junction. | IL | Other | Local Reliability | System need is to improve reliability. The upgraded conductor and new switch will allow greater operational flexibility and improve maintainability of the line. The existing line is limited to 13 MVA which severely limits the ability of the line to be used in response to contingency events or accommodate load growth. The lack of a switch at Ashland Junction prevents the line from being deenergized for maintenance which makes maintenance difficult. The project will remedy these issues. | Load Growth |  |  | 2028-12-01 | 69 |  | 9500000
MTEP25 | Central | HOOSIER ENERGY | 50599 | New Merom 345 kV Substation Load Addition | Extend a new 345kV line from Merom Transmission Station, approximately 1-mile, to a new data center. The data center has a total estimated load of 620 MW at 95% PF (653 MVA, 204 MVAR). | IN | Other | Load Growth | A new data center customer has plans to construct a 620 MW facility within Hoosier Energy’s service territory, approximately 1-mile from Hoosier Energy’s Merom Transmission Station. The is planning an in-service date of July 2026. The full ramp-up to 620 MW load is planned for service by July 2027. | Data Center | Y | 620 | 2026-07-01 | 345 |  | 12790684 | 620 MW data center at Merom, 1 mi from Merom Transmission Station. 653 MVA at 95% PF. Full load by 7/2027
MTEP25 | Central | HOOSIER ENERGY | 50614 | New Marble Hill 345 kV Station and Load | Construct a new 345kV ring-bus station on the 08TRIMBL (249532) – 7GHENT (324105) transmission line, approximately 4 line-miles from LGEE’s Trimble County Generator Station. New customer will construct substation adjacent to ring-bus station. The station will serve a new data center with a total estimated load of 310 MW at 95% PF (344 MVA, 150 MVAR). | IN | Other | Load Growth | A new data center customer has plans to construct a 310 MW facility within Hoosier Energy’s service territory, adjacent to the 345kV Trimble-Ghent transmission line. The customer is planning an in-service date of Q4 2027. The full 310 MW load is planned for service by Q1 2029. | Data Center | Y | 310 | 2027-10-01 | 345 |  | 20500000 | 310 MW data center near Trimble County on Trimble-Ghent 345kV. Full load by Q1 2029 (Hoosier Energy)
MTEP25 | Central | HOOSIER ENERGY | 50698 | New Scotland 345/69kV Substation | Construct a new 345kV ring-bus with 345/69kV transformation on the 16PETE (254529) – 16W_BLOOMGTN (254526) transmission line, approximately 35 line-miles from IPL’s Petersburg station and 19 line-miles from DEI’s planned 16W_Bloomington station. Extend a 69kV line from the new station to serve a new 20 MW customer. Bring the Hoosier Scotland-Bloomfield 69kV transmission line into the new 69kV station. Open 69kV branch 248537- 248538. | IN | Other | Load Growth | By late 2029, Hoosier Energy is projecting 20 MW of load growth in the Scotland, IN area. The existing 69kV transmission infrastructure cannot serve the additional load due to thermal and voltage constraints. | Data Center (supporting) | Y | 20 | 2029-12-01 | 345 |  | 38000000 | New Scotland 345/69kV Sub for 20MW load growth projection in Scotland IN area (HE)
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50216 | Upgrade Petersburg 138 kV Breakers - 3 Breakers | Upgrade existing 138 kV Petersburg breakers 6, 7, & 9 from 40 kA to 63 kA. | IN | BRP |  | MISO MTEP24 TPL-001-5 R2.3 annual assessment demonstrated exceedances of the existing breaker interrupting capabilities up to 104.9%. Project submitted as Corrective Action Plan pursuant to TPL-001-5 R2.8. |  |  |  | 2031-12-01 | 138 |  | 739000
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50217 | Upgrade Stout South Breakers - 12 Breakers 138 kV | Upgrade Stout South 138 kV breakers 1A, 2A, 2C, 3A, 3B, 3C, 4A, 4C, 5A, 5B, 5C, and 5D from 63 kA to 80 kA. | IN | BRP |  | MISO MTEP24 TPL-001-5 R2.3 annual assessment demonstrated exceedances of the existing breaker interrupting capabilities up to 104.3%. Project submitted as Corrective Action Plan pursuant to TPL-001-5 R2.8. |  |  |  | 2031-12-01 | 138 |  | 3050000
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50306 | Rebuild Southwest-Stout CT_132-02_138 kV Line | Rebuild existing 138 kV 132-02 Southwest-Stout CT line to new Summer rating of 2000A (478 MVA). New conductor and towers, with review of necessary terminal equipment to be replaced. | IN | BRP |  | MISO MTEP24 TPL-001-5 R3 annual assessment demonstrated 20 unique N-1-1 events resulting in thermal overloads >120% and up to 142.28%. Project submitted as Corrective Action Plan pursuant to TPL-001-5 R2.7. |  |  |  | 2029-12-31 | 138 |  | 9300000
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50307 | Rebuild Southwest-Northwest 132-04 138 kV Line | Rebuild existing 138 kV 132-04 Southwest-Northwest line to new Summer rating of 2000A (478 MVA). New conductor and towers, with review of necessary terminal equipment to be replaced. | IN | BRP |  | MISO MTEP24 TPL-001-5 R3 annual assessment demonstrated 12 unique N-1-1 events resulting in thermal overloads >120% and up to 127.42%. Project submitted as Corrective Action Plan pursuant to TPL-001-5 R2.7. |  |  |  | 2029-12-31 | 138 |  | 15200000
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50311 | Rebuild Stout North-Sanitation Belmont-Southwest_132-01_&_132-74_138 kV Lines | Rebuild existing 138 kV 132-01 Stout North-Sanitation Belmont line to new Summer rating of 2000A (478 MVA). New conductor and towers. Conversion of Stout North terminal from line breaker configuration to double breaker due to P23 and P42 planning events. Rebuild existing 138 kV 132-74 Sanitation Belmont-Southwest line to new Summer rating of 2000A (478 MVA). New conductor and towers, with review of necessary terminal equipment to be replaced. | IN | BRP |  | MISO MTEP24 TPL-001-5 R3 annual assessment demonstrated 5 P23 and 5 P42 planning events resulting in thermal overloads of the 132-02 line up to 142.49%. MISO MTEP24 TPL-001-5 R3 annual assessment demonstrated 16 unique N-1-1 events resulting in thermal overloads >120% and up to 131.21%. Project submitted as Corrective Action Plan pursuant to TPL-001-5 R2.7. |  |  |  | 2033-12-01 | 138 |  | 14990000
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50312 | Rebuild Southwest-Lilly South 132-10 138 kV Line | Rebuild existing 138 kV 132-10 Southwest-Lilly South line to new Summer rating of 2000A (478 MVA). New conductor and towers, with review of necessary terminal equipment to be replaced. | IN | BRP |  | MISO MTEP24 TPL-001-5 R3 annual assessment demonstrated 3 unique N-1-1 events resulting in thermal overloads >120% and up to 121.3%. Project submitted as Corrective Action Plan pursuant to TPL-001-5 R2.7. |  |  |  | 2033-12-01 | 138 |  | 7070000
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50313 | Rebuild Lilly South-Center 132-61 138 kV Line | Rebuild existing 138 kV 132-61 Lilly South-Center line to new Summer rating of 2000A (478 MVA). New conductor and towers, with review of necessary terminal equipment to be replaced. | IN | BRP |  | MISO MTEP24 TPL-001-5 R3 annual assessment demonstrated 5 unique N-1-1 events resulting in thermal overloads >120% and up to 131.44%. Project submitted as Corrective Action Plan pursuant to TPL-001-5 R2.7. |  |  |  | 2033-12-01 | 138 |  | 2900000
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50314 | Rebuild Georgetown-North 132-86 138 kV Line | Rebuild existing 138 kV 132-86 Georgetown-North line to new Summer rating of 1600A (382 MVA). New conductor and towers, with review of necessary terminal equipment to be replaced. | IN | BRP |  | MISO MTEP24 TPL-001-5 R3 annual assessment demonstrated 4 P23 and 2 P42 planning events resulting in thermal overloads of the 132-86 line up to 107.39%. Project submitted as Corrective Action Plan pursuant to TPL-001-5 R2.7. |  |  |  | 2029-12-31 | 138 |  | 12760000
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50315 | New Ralstone 138 kV Substation Eagle Valley Reinforcement | New 138 kV Ralston substation looped in on 132-23 Eagle Valley-Sanitation Southport line. Add new 138 kV line terminal at Camby substation to re-energize nearby 138 kV idle line and connect into Ralston substation. | IN | BRP |  | The [IPL] Heartland Crossing Tap – [IPL] Mooresville 138 kV, [IPL] Heartland Crossing Tap – [IPL] Eagle Valley 138 kV and [IPL] Bridgeport – [IPL] Rockville 138 kV lines become overloaded to one hundred eight (108%) percent in a year 2029 for a NERC defined category Spare equipment and P6 contingency events. The project is intended to resolve the thermal issues in the winter seasons starting from its ISD. |  |  |  | 2031-03-01 | 138 |  | 24000000
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50722 | New Pond Creek 345 : 138 kV Substation | New 345 : 138 kV substation in Pike County, Indiana to address thermal overloads at Petersburg substation | IN | BRP |  | New 345 : 138 kV substation in Pike County, Indiana to address thermal overloads at Petersburg substation | Data Center (BRP) | Y |  | 2029-06-01 | 345 |  | 40000000 | IPL BRP; LEAP 2 CAP $40M; Pike County IN
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50723 | Uprate IPL Petersburg to Cato 138 kV Equipment | Replace IPL leads and wave trap | IN | BRP |  | EPR BRP Mitigation for LEAP Phase 2 | Data Center (BRP) | Y |  | 2028-12-31 | 138 |  | 4000000 | IPL BRP; LEAP CAP $4M
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50727 | Replace Thompson 345/138/13.75 MVA Autotransformer at Thompson Substation | Replace 275 MVA, 345 : 138 kV Autotransformer with 500 MVA, 345 : 138 kV Autotransformer. | IN | BRP |  | EPR BRP TPL-001 Required, N-1-1 of P1-2 Thompson-Rockville transmission line and P1-3 of Stout autotransformer | Data Center (BRP) | Y |  | 2029-12-31 | 345 |  | 15000000 | IPL BRP; LEAP CAP $15M
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50731 | IPL Adoption of Seasonal Ratings - BRP | Indianapolis Power & Light is changing its Facility Rating Methodology to adopt seasonal ratings. This project covers all Facilities changes classified as BRPs. | IN | BRP |  | FERC 881 / local reliability. |  |  |  | 2029-12-31 | 345
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50502 | New Brownsburg East 138 kV Substation | In conjunction with MTEP 24274's phase 1. New 138 kV WVPA Brownsburg East substation with 2 138 kV feeds from Maloney Road. | IN | Other | Load Growth | Load-serving / load growth project |  |  |  | 2025-12-31 | 138 |  | 8600000
MTEP25 | Central | INDIANAPOLIS POWER & LIGHT COMPANY | 50503 | New Pleasant Acres Substation Feed 2 138 kV line | Second 138 kV feed and 1 22.4 MVA transformer for Pleasant Acres substation. In conjunction with MTEP 24293. Project required to match MOD submission. | IN | Other | Load Growth | Load-serving / load growth project |  |  | 4 MVA | 2025-12-31 | 138 |  | 2000000
MTEP25 | East | METC | 20020 | Rebuild Gaylord - Mio Dam 138kV line | Rebuild the Gaylord – Mio Dam 138kV line with 954 ACSR overhead conductor capable of double circuit 230kV. OPGW will be installed on the rebuild. Terminal equipment at Gaylord and Mio Dam substations will need to be upgraded. | MI | Other | Age and Condition | The Mio-Gaylord 138kV circuit consists of steel poles and wood poles, installed in the 1950s, with an average age of 70 years, nearing the end of their service life. Over the past 15 years, the circuit has experienced multiple outages, primarily due to storm conditions and high winds. Currently, there are open exceptions, including broken or damaged cross arms, wood pole rot, PTS ground resistance issues, and damaged insulators. Additionally, many poles are flagged for replacement due to resistograph failure, rot, and woodpecker damage. Given the circuit's outage and maintenance history, along with the significant issues identified, METC recommends a full rebuild. Portions of the line is also located in a moderate-high wildfire risk area. |  |  |  | 2029-12-31 | 138 |  | 87254000
MTEP25 | East | METC | 50203 | Rebuild and Relocate Alma 138 kV substation | Rebuild the 138 kV Alma station to three rows of breaker and a half station capable of three additional rows of BAH expansion. Install eight (8) 138 kV, 3000 A breakers with at least 40 kA interrupting capability. Install new control house and 25 MVAR capacitor. Reterminate all lines into the new station. Decommission and remove all equipment at the Alma 138 kV site. | MI | Other | Local Needs | METC received a formal notification of a CE planned project to replace the existing Alma 138/46 kV bulk power substation and expand to include an additional distribution transformer. Consumers Energy is proposing to rebuild Alma substation approximately 0.6 miles south of the existing substation location. Existing Alma 138 kV station has no potential future expansion capability and has multiple pieces of aging substation equipment already slated for replacement. Relocation with CE offers solutions to both issues. |  |  |  | 2029-12-31 | 138 |  | 15190000
MTEP25 | East | METC | 15993 | New [METC] Keystone 138 kV STATCOM | The proposed solution is to add +100/0 Mvar STATCOM and 4*25 Mvar MSC (Mechanical Switch Capacitor) at [METC] Keystone 138 kV 1. to provide the needed slow/fast reactive power supports to the bus voltages in [METC] Keystone 138 kV region 2. To reduce the lower flows on the [METC] Keystone 345/138 kV transformers. | MI | BRP |  | MISO identified the need for fast reactive supporting device at [METC] Keystone in the MTEP24 dynamics (D5) study. |  |  |  | 2031-06-01 | 138 |  | 62191000
MTEP25 | East | ITC | 50212 | Avery - New DTE Interconnection | DTE interconnection for 120 kV service in Detroit City. Cut the Frisbie – Waterman 120 kV line about 2 miles from Frisbie 120 kV to loop in the new ITCT’s Avery Substation. ITC will build a new Avery 120 kV station as a five (5) breaker ring bus configuration. DTE will install capacitor banks connected to 13.2 kV side, two 120/13.2 kV transformers with breakers for high side protection. | MI | Other | Load Growth | Accommodate a new interconnection request from DTE to provide capacity for load growth in Detroit city, MI. |  |  |  | 2027-09-30 | 120 |  | 15755000
MTEP25 | East | METC | 50229 | New Oneida - Tallman 138 kV circuit | Build new Oneida – Tallman 138 kV circuit utilizing 1431 ACSR and double circuit structures capable of OPGW. Use 9.5 miles METC existing easement and obtaining new 0.5 miles ROW to connect this corridor to Tallman. Install two one-way 3000A PTS at Tallman. Install new 138 kV breaker capable of 40 kA interrupting and complete an existing row at Oneida 138 kV station. Install new 138 kV three breaker ring bus station at Looking Glass. | MI | Other | Local Needs | The Bingham 138 kV substation only has two sources supporting a weak area of the 46 kV system. This restricts the ability to maintain the lines and station equipment at Bingham. Additionally, the Bingham – Looking Glass circuit is 25 miles long which feeds a similar area on the 46kV system. Outages on this circuit for any extended period are a concern for Consumers Energy and its customers. Running a circuit from Oneida to Tallman would not only support the immediate area but also provide relief for West – East flows during outages in this area. With the outage restrictions on the Bingham-Looking Glass line, it is not possible to rebuild the Bingham-Looking Glass line with typical construction methods. The Oneida-Tallman line would mitigate the outage constraints allowing for future maintenance to be completed without abnormal construction methods or undue impacts to the operations of the area. |  |  |  | 2029-12-31 | 138 |  | 29630000
MTEP25 | East | ITC | 50246 | Replace Caniff #303AB PST Transformer | Replace the Caniff #303(AB) PST Transformer with at least 736 MVA (3543 Amps) summer emergency rated transformer. Phase-shift angle of +/-15°. Install a breaker and associated equipment on the high side of the transformer. | MI | Other | Age and Condition | The Caniff #303(AB) PST Transformer is reaching end of life and has been identified for replacement due to age and condition. |  |  |  | 2028-12-31 | 345 |  | 30000000
MTEP25 | East | METC | 50251 | Rebuild Batavia - Dorrance #1 & #2 138 kV lines | Rebuild sections of the Batavia – Byers and Batavia – Kinderhook jct. circuits between Structure 124D100 to Batavia (~4.1mi) with 954 ACSR conductor and OPGW | MI | Other | Age and Condition | The Batavia-Coldwater 138kV circuit consists of (17) steel poles and (80) wood poles installed in the 70’s and have an average age of (45) years, which are nearing their end of life. |  |  |  | 2029-12-31 | 138 |  | 10555000
MTEP25 | East | WOLVERINE POWER SUPPLY COOPERATIVE, INC | 50337 | Rebuild Tower - Black Lake 69 kV line to 138 kV capability | Rebuild and upgrade 4.5 miles of 69 kV line to 138 kV standard with steel poles, 336 ACSR conductor, and OPGW. | MI | Other | Age and Condition | Condition Based - Replace aging infrastructure.P50337 • Built from 1972, age of 57 years • 5 condemned, 38 damaged poles • 84% of poles in need of replacement |  |  |  | 2029-12-31 | 69 |  | 4500000
MTEP25 | East | METC | 50317 | New Hagensville Junction Interconnection (METC) | Wolverine has requested to further integrate their Northeast Transmission System with METC’s around the Hagensville Tap location. To accommodate this request, METC proposes adding an additional row (row 6) on the parcel where future generators J1914 and J2875 will be located to terminate Wolverine’s 138kV lines. METC will install 5 new 138kV, 40kA breakers and associated switches. | MI | Other | Load Growth |  |  |  |  | 2028-12-31 | 138 |  | 5010000
MTEP25 | East | ITC | 50253 | Oliver - New DTE Interconnection | DTE interconnection request for transmission service tapped Cosmo – W-BA-C_TP section of the Bad Axe - Wyatt 120 kV line, approximately 12 miles West of W-BA-C_TP tap. DTE will install a single distribution transformer and associated high-side protection. | MI | Other | Local Reliability | Accommodate a new interconnection request from DTE to mitigate reliability issues that were observed on the DTE's system and provide thermal and voltage support across the entire thumb area which is DTE service territory. |  |  |  | 2027-12-01 | 120 |  | 5605500
MTEP25 | East | METC | 50377 | Rebuild Blackstone 138 kV Station | Construct a new 138 kV station (tentatively called Lansing Ave) as 6-breaker ring bus configuration. All new 138 kV breakers should be standard 3000 A 50 kA breakers. All new equipment at the new station must be rated 450 MVA for summer emergency. Cut the Blackstone – Stable and Tompkins - Blackstone #2 138 kV lines into the new station. Tie existing Blackman - Blackstone #1 and Blackstone - Leoni #1 138 kV lines to form Blackman - Leoni 138 kV Line. Completely remove all the sag on this new Blackman – Leoni 138 kV line (on the formerly Blackman – Blackstone section). Construct new 138 kV lines (~0.37 miles each) from the new substation to CONS Blackstone 46 kV TRF #1 and TRF#2 using 954 ACSR conductor. Also, decommission all 138 kV equipment's from Blackstone 138 kV Sub. | MI | Other | Age and Condition | The equipment at Blackstone substation is reaching end of life and need to be replaced. |  |  |  | 2030-06-01 | 138 |  | 17000000
MTEP25 | West | ITC MIDWEST | 50239 | MPFCA J1503 & J1504 - Network Upgrades - Huntley 345 kV Bus | To interconnect projects J1503 and J1504 to the ITC Midwest (“ITCM”) system at the Interconnection Customers’ requested point of interconnection, the Huntley 345 kV bus will need to be converted to a breaker and ½ to allow for the new 345 kV shared gen-tie terminal. The Interconnection Customers, MISO, and ITCM entered into a Multi-Party Facilities Construction Agreement (“MPFCA”). Network Upgrades and Transmission Owner Interconnection Facilities (“TOIF”) are expected to be constructed at the Huntley Substation for projects J1503 and J1504, each a 150 MW solar generating facility (300 MW total), under a Multi-Party Facilities Construction Agreement (“MPFCA”) as a condition of the project’s Interconnection Service. | MN | GIP |  | The Facilities Study for J1503 and J1504 identified Network Upgrades and TOIF necessary for the interconnection of projects J1503 and J1504 to ITCM’s Huntley 345 kV Substation. Projects J1503 and J1504 will share a new 345 kV gen-tie line out of the Huntley 345 kV bus to a Customer Owner collector substation. Both projects J1503 and J1504 are the same customer. The impact to the transmission system was evaluated as part of the DPP 2020 West Area Study. |  |  |  | 2027-10-31 | 345 |  | 5489562
MTEP25 | West | ITC MIDWEST | 50207 | Spirit Lake Anchor 69 kV Interconnection | IPL is to build a new 69/25 kV substation to be named Sprit Lake Anchor. ITCMW is to build the 69 kV portion of the substation. This substation will be located nearby the existing Spirit Lake South substation and is intended to take the load from the Spirit Lake South, Orleans, and Spirit Lake West substations. The new substation will support two IPL owned 69/25 kV 33/50 MVA transformers and one ITC owned capacitor bank rated at 13.2 Mvar(rated)/11.225 Mvar(effective). | IA | Other | Load Growth | Spirit Lake Anchor will consolidate and take on the load supported by numerous other substations in the area. ITCMW will build the 69 kV portion of this station and build the tap to ITCMW transmission. |  |  | 50 MVA | 2028-12-31 | 69 |  | 5398911
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50724 | North Appleton - Werner West (NAPL31) 345 kV, Rerate | Rerate NAPL31 to resolve 10 spans with ground issues to the existing SELD rating. | WI | Other | Local Reliability | Reliability - Line Clearance |  |  |  | 2026-12-26 | 345 |  | 5300000
MTEP25 | West | GREAT RIVER ENERGY | 50420 | Lakefield Area Projects | Expansion of the 345kV Gen tie bus at the Lakefield substation to accommodate the Three Waters Wind (340MW) Wind Farm. Installation of new 345kV breakers on the existing generator and installation of the GRE controlled EEE, 1500’ of 345kV Transmission to the interconnect 161kV/345kV step up substation | MN | GIP |  | Additional 345kV interconnection required to connect the Three Waters wind farm |  |  |  | 2027-08-24 | 345 |  | 5217392
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50519 | Reactor Relocation from North Madison SS to J1502 POI SS | Relocate the 80 Mvar reactor from North Madison SS to J1502 POI SS to regulate voltage when J1502 is unavailable. | WI | Other | Local Reliability | Reliability |  |  |  | 2028-06-30 | 345 |  | 5165000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50262 | Chaffee Creek SS Breaker Asset Renewal | Asset renewal replacement of oil circuit breakers at Chaffee Creek SS. In addition, replace the aging capacitor bank and internal components of the control house. | WI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2028-12-01 | 69 |  | 5155000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50128 | Eden SS Relay and House Asset Renewal | Asset Renewal of the Eden SS control house and all assets within the control house. | WI | Other | Age and Condition | Asset Renewal |  |  |  | 2028-12-01 | 138 |  | 5081000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50450 | Upgrade end of life Wilmarth TR7 and TR8 | Upgrade end of life Wilmarth TR7 and TR8 | MN | Other | Age and Condition | Transformers have reached end-of-replacement life and starting to show increasing signs of internal degradation |  |  |  | 2028-12-31 | 115 |  | 5000000
MTEP25 | West | GREAT RIVER ENERGY | 50237 | Butternut Area Projects | Rebuild BE-BUT line. SS145 to the Butternut Substation. Line length is approx. 4.5 miles | MN | Other | Age and Condition | The line has poor reliability, has been identified by the field to be in poor condition and is a 1950’s vintage which is being targeted for replacement. |  |  |  | 2029-12-21 | 69 |  | 4947000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50548 | Juneau Industrial SS, DIC, Transformer Addition | In support of a distribution transformer addition, ATC will rebuild Juneau Industrial and will install 1 bus-side load break disconnect switch, 1 bus side air break 2 bus-tie disconnect switches. | WI | Other | Load Growth | Load Interconnection |  |  |  | 2027-06-01 | 69 |  | 4800000
MTEP25 | West | Central Minnesota Municipal Power Agency | 50269 | Blue Earth Northeast Add 2nd Transformer 20-37.3 MVA | Northeast Add 2nd Transformer 20-37.3 MVA | MN | Other | Load Growth | Load growth |  |  | 3 MVA | 2026-05-31 | 69 |  | 4800000
MTEP25 | West | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | 50464 | Erie Road Substation Rebuild | Rebuild the Erie Road substation in Marshall with new 115 kV breakers and other equipment. | MN | Other | Age and Condition | Age and condition |  |  |  | 2029-01-01 | 115 |  | 4500000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50670 | Werner SS Relay and Remote Asset Renewal | Asset renewal of Werner control house and 138kV relay asset renewal at Werner, Werner West and White Lake SS. Install an additional breaker and eliminate two S&C Mark VI circuit switchers when replacing cap bank relaying at Werner. | WI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2026-12-01 | 138 |  | 4450000
MTEP25 | West | ITC MIDWEST | 50205 | Belmond Diesel to Hancock 69 kV Line Reroute | Erosion around the existing Belmond Diesel to Handcock line is proving troublesome. Rebuild is not an option due to the close proximity of the river and the railroad. The Belmond Diesel to Handcock line is to be Re-routed to a different river crossing location. The potential re-route would call for 0.44 miles of double circuit with Corn Belt Power Co-op, 1.8 miles along US Highway 69, and 0.54 miles along 168th St. All new line is to use T2-4/0 ACSR conductor. | IA | Other | Age and Condition | Eroding ground around the poles of the Belmond Diesel to Hancock line is causing structural concern of the line, so the line needs to be re-routed to a better area. |  |  |  | 2028-12-31 | 69 |  | 4097500
MTEP25 | West | ITC MIDWEST | 50244 | J1520 Generator Interconnection - Network Upgrades | To interconnect project J1520 to the ITC Midwest (“ITCM”) system at the Interconnection Customer’s requested point of interconnection, the Bluebill 345 kV bus will need to be converted to a breaker and ½ to allow for the new 345 kV terminal. The Interconnection Customer, MISO, and ITCM entered into Generator Interconnection Agreement (“GIA”). Network Upgrades and Transmission Owner Interconnection Facilities (“TOIF”) are expected to be constructed at the Bluebill Substation for project J1520, a 135 MW solar generating facility, under a Generator Interconnection Agreement (“GIA”) as a condition of the project’s Interconnection Service. | IA | GIP |  | The Facilities Study for J1520 identified Network Upgrades and TOIF necessary for the interconnection of the project to ITCM’s Bluebill 345 kV Switch Station. Project J1520 and the impact to the transmission system was evaluated as part of the DPP 2020 West Area Study. |  |  |  | 2027-10-31 | 345 |  | 4048730
MTEP25 | West | ITC MIDWEST | 50206 | Rock Creek T2 Replacement | The existing Rock Creek T2 transformer is at the end of its useful life and in need of replacement. T2 will be replaced with a new 150 MVA 161/69 kV transformer with LTC, and the existing motor operated switch will be removed and replaced with a new high side breaker and disconnect. | IA | Other | Age and Condition | The T2 transformer at the Rock Creek substation is at the end of its useful life and needs to be replaced to maintain operation at Rock Creek. |  |  |  | 2027-12-31 | 69 |  | 4044728
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 24982 | Range Line Dist (WE) - Range Line Switchyard 138 kV (61441), Replace Underground Cable | Replace underground cable from Range Line Dist (WE) to Range Line Switchyard. | WI | Other | Age and Condition | Asset Renewal - Transmission Line |  |  |  | 2028-06-01 | 138 |  | 4000000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50255 | Huiskamp - Ruskin 69 kV (6937), OPGW Addition | Install ~1.75 miles of ATC standard (DNO-10455) 48 strand OPGW fiber optic cable from structure #232 on T-Line (6937) into the Ruskin substation to complete the connection from Huiskamp. | WI | Other | Local Needs | Communication |  |  |  | 2026-12-31 | 69 |  | 4000000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50254 | Remsen Township 345 kV Substation Expansion for J1590 | Add one new 345 kV line terminal at Remsen Township substation for J1590 wind farm generator tie line. | IA | GIP |  | J1590 network upgrades from DPP 2020 |  |  |  | 2026-09-15 | 345 |  | 4000000
MTEP25 | East | ITC | 50468 | ITCT Customer Interconnections - 2028 | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in-service date within the year 2028 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million, a separate project will be submitted for approval. | MI | Other | Load Growth | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. These projects are strictly in response to customer interconnection requests. They are not being proposed to address any specific ITCT system reliability concerns. |  |  |  | 2028-12-31 | 345 |  | 2500000
MTEP25 | East | WOLVERINE POWER SUPPLY COOPERATIVE, INC | 50338 | Rebuild Lincoln Junction - Lincoln 69 kV line to 138 kV capability | Rebuild and upgrade 5 miles of 69 kV line to 138 kV standard with steel poles, 336 ACSR conductor, and OPGW. | MI | Other | Age and Condition | Condition Based - Replace aging infrastructure. • Condition Based - Replace aging infrastructure. • 3 condemned, 10 damaged poles • 12% of poles in need of replacement |  |  |  | 2029-12-31 | 69 |  | 5000000
MTEP25 | East | METC | 50447 | New [CONS] Baker Interconnection | METC to install two 138 kV, 63kA breakers at Weeds Lake to terminate Consumers Energy's new Baker connection at position “BM8” and construct approximately 36.5 miles of new 138 kV line on double-circuit structures (leave vacant side for future use) using 954 ACSR conductor. | MI | Other | Local Needs | Consumers Energy requested to connect their new Baker 138/46kV substation to METC’s Weeds Lake 138 kV station. |  |  |  | 2030-06-01 | 138 |  | 108810000
MTEP25 | East | METC | 50366 | Upgrade Mud Lake - Verona #1 138 kV line | Upgrade ~0.67 mile of 954 ACSR to 1431 ACSR on the Mud Lake – Verona 138 kV line No. 1. Also, upgrade the 2-4/0 Cu stranded bus at position “588” and switch 585 to at least 450 MVA for summer emergency rating. | MI | BRP |  | MISO's MTEP24 generator deliverability study shows the Mud Lake - Verona 138 kV line No. 1 overloaded for an N-1 contingency. |  |  |  | 2030-06-01 | 138 |  | 1590000
MTEP25 | East | ITC | 50476 | ITCT Line Relocation - 2026 | Relocate portion(s) of ITCT transmission lines located in public right of way at the government entities’ mandate. | MI | Other | Local Needs | These line relocation projects are being done at the request of government entities due to road construction or expansion where the ITCT transmission lines are impacted. |  |  |  | 2026-12-31 | 345 |  | 2500000
MTEP25 | East | METC | 50463 | Rebuild [CONS] Blackstone 46 kV Station | Consumers Energy notified METC, LLC of a planned project to rebuild the HVD portion of the Blackstone Street 138/46 kV bulk power substation. CONS will replace the two existing 60/80/100 MVA, 138/46 kV three-winding transformers with two new 60/80/100 MVA autotransformers. The new transformers will have an impedance of approximately 7.2% on a 60 MVA base. METC to install a new 138 kV, 40 kA breaker with disconnects at “188” position and re-name existing CONS “199” breaker as “288” after conveyed to METC. Also, METC to build two new radial 138 kV single-circuit lines using 954 ACSR conductor with OPGW from Blackstone to CONS TRF #1 terminating at "188" position and Blackstone to CONS TRF #2 terminating at "288" position. | MI | Other | Local Needs | CONS notified METC that they are rebuilding and relocation their 46 kV substation just south of the existing site. |  |  |  | 2028-10-01 | 138 |  | 3295000
MTEP25 | East | WOLVERINE POWER SUPPLY COOPERATIVE, INC | 50339 | Rebuild Bass Lake - Wolf Lake 69 kV line to 138 kV capability | Rebuild and upgrade 11 miles of 69 kV line to 138 kV standard with steel poles, 336ACSR conductor, and OPGW. | MI | Other | Age and Condition | Condition Based - Replace aging infrastructure. • Built from 1981, age of 43 years • 3 condemned, 94 damaged poles • 66% of poles in need of replacement |  |  |  | 2029-12-31 | 69 |  | 11000000
MTEP25 | East | WOLVERINE POWER SUPPLY COOPERATIVE, INC | 50401 | Rebuild East Jordan Junction - Barnard 69 kV line to 138 kV capability | Rebuild and upgrade 24 miles of 69 kV line to 138 kV standard with steel poles, 795ACSS conductor, and OPGW. | MI | Other | Age and Condition | Condition Based - Replace aging infrastructure. • Built from 1953 to 1978, age of 76 to 51 years • 36 condemned, 69 damaged poles • 36% of poles in need of replacement |  |  |  | 2029-12-31 | 69 |  | 26000000
MTEP25 | East | METC | 50466 | METC Customer Interconnections - 2028 | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in-service date within the year 2028 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million, a separate project will be submitted for approval. | MI | Other | Load Growth | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. These projects are strictly in response to customer interconnection requests. They are not being proposed to address any specific METC system reliability concerns. |  |  |  | 2028-12-31 | 345 |  | 2500000
MTEP25 | East | ITC | 50477 | ITCT Line Relocation - 2027 | Relocate portion(s) of ITCT transmission lines located in public right of way at the government entities’ mandate. | MI | Other | Local Needs | These line relocation projects are being done at the request of government entities due to road construction or expansion where the ITCT transmission lines are impacted. |  |  |  | 2027-12-31 | 345 |  | 2500000
MTEP25 | East | ITC | 50479 | ITCT Asset Replacement Program - 2027 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. | MI | Other | Age and Condition | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. |  |  |  | 2027-12-31 | 345 |  | 59750000
MTEP25 | East | ITC | 50597 | DTE New Hudson Interconnection | DTE interconnection for 120kV service in Lion Township. Cut in New Hudson (formerly Walbridge) 120kV station on the Cody – Proud 120kV line about 0.15 mile from Tamarack 120kV Tap. ITC will construct New Hudson as a new 4-breaker ring bus configuration, 120 kV station and allow enough space for future breaker and a half station configuration once DTE’s future positions are needed. Also cut in Cody – Proud 120 kV line about 0.15 mile from Tamarack 120 kV Tap into New Hudson 120 kV station. We want to reserve 4 additional rows for future connections. Install two 120/13.2 kV transformers with circuit switchers for high side protection. DTE want to build a substation with at least five connection points to 120 kV. DTE will want three connection points for a general-purpose substation and at least two extra positions if industrial substation(s) are needed. | MI | Other | Load Growth |  |  |  |  | 2028-03-31 | 120 |  | 12163500
MTEP25 | East | METC | 50474 | METC Line Relocation - 2026 | Relocate portion(s) of METC's transmission lines located in public right of way at the government entities’ mandate. | MI | Other | Local Needs | These line relocation projects are being done at the request of government entities due to road construction or expansion where the METC transmission lines are impacted. |  |  |  | 2026-12-31 | 345 |  | 2500000
MTEP25 | East | METC | 50475 | METC Line Relocation - 2027 | Relocate portion(s) of METC transmission lines located in public right of way at the government entities’ mandate. | MI | Other | Local Needs | These line relocation projects are being done at the request of government entities due to road construction or expansion where the METC transmission lines are impacted. |  |  |  | 2027-12-31 | 345 |  | 2500000
MTEP25 | East | METC | 50478 | METC Asset Replacement Program - 2027 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. | MI | Other | Age and Condition | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. |  |  |  | 2027-12-31 | 345 |  | 53875000
MTEP25 | West | MINNESOTA POWER INC. | 50393 | Iron Range 500kV Reactor Addition | Adding a third 500kV line reactor to help mitigate overheating concerns with one unit out for maintenance. | MN | Other | Local Reliability | Voltage support |  |  |  | 2030-12-31 | 500 |  | 4000000
MTEP25 | West | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | 50501 | Byron - Pleasant Valley 161kV Terminal Upgrade | Upgrade of terminal equipment of Byron - Pleasant Valley 161kV line to match joint facility owners. Upgrading outdated breakers and relays. | MN | BRP |  | 3000A Terminal upgrades due to overloads presented in MTEP24 Appendix D6 Generator Deliverability Models. Updating outdated breakers and relays to increase reliability. |  |  |  | 2027-12-01 | 345 |  | 3800000
MTEP25 | West | ITC MIDWEST | 50236 | J1444 Generator Interconnection - Network Upgrade | System Concern To interconnect projects J1444 to the ITC Midwest (“ITCM”) system at the Interconnection Customer’s requested point of interconnection, the DAEC 345 kV bus will need to be converted to a breaker and ½ to allow for the new 345 kV terminal. The Interconnection Customer, MISO, and ITCM entered into Generator Interconnection Agreement (“GIA”). Network Upgrades and Transmission Owner Interconnection Facilities (“TOIF”) are expected to be constructed at the DAEC Substation for project J1444, a 200 MW solar generating facility, under a Generator Interconnection Agreement (“GIA”) as a condition of the project’s Interconnection Service. | IA | GIP |  | The Facilities Study for J1444 identified Network Upgrades and TOIF necessary for the interconnection of the project to ITCM’s DAEC 345 kV Substation. Project J1444 and the impact to the transmission system was evaluated as part of the DPP 2019 West Area Study. |  |  |  | 2025-09-01 | 345 |  | 3777724
MTEP25 | West | ITC MIDWEST | 50379 | ITC Midwest Load interconnection blanket | Projects of significant size (greater than $1 Million) will be reported individually. Since these projects are being done at the request of interconnection customers and do not address any specific ITCM reliability concerns, only one alternative was identified for each project. Unless any reliability concerns on the ITCM system are identified, the identified alternative typically matches the one requested by the customer to accommodate the customer’s site location or desired level of service/reliability. Only those projects as determined by ITC as having no significant impact on the transmission system are included. | IA; IL; MN | Other | Load Growth | These projects are being done at the request of an interconnection customer to facilitate new load, to re-distribute existing load, to improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. These projects are strictly in response to customer interconnection requests and are not being proposed to address any specific ITCM system reliability concerns. |  |  |  | 2027-12-31 | 345 |  | 3750000
MTEP25 | West | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | 50498 | Byron - Cascade Creek Line Relocation | Relocation of 1.2miles of 161kV transmission lines due to MnDOT developing a new interchange on intersection of Hwy 14 & Hwy 44. MnDOT requests the project be completed by Spring 2025. | MN | Other | Local Needs | Relocation of 1.2miles of 161kV transmission line that runs from Byron - Cascade Creek. |  |  |  | 2026-12-31 | 161 |  | 3627000
MTEP25 | West | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | 50153 | Owatonna 161kV Cap Bank Addition | Addition of a 47MVAr cap bank to the existing West Owatonna Substation. | MN | BRP |  | Low voltage under various contingencies. |  |  |  | 2027-01-01 | 161 |  | 3500000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50223 | Whitewater – Sugar Creek 138 kV (WHIG53), Flow Control Device | The Whitewater – Sugar Creek (WHIG53) 138 kV, flow control device is needed to control power flow on WHIG52 and 6541 supporting load additions in south-east Wisconsin. The project will install three single-phase 20-ohm series reactors at the Sugar Creek terminal of WHIG53. | WI | Other | Load Growth | Load Growth |  |  |  | 2027-01-01 | 138 |  | 3358000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50612 | Terrace Ave Riser SS 69kV Pumping Plant Upgrade | Modernize the technology for the HPFF (high-pressure fluid-filled) pressurizing system, install physical security, install expanded metal fence, and make modifications to existing building to address corrosion issues at Terrace Ave Riser SS. | WI | Other | Age and Condition | Asset Renewal - Substation |  |  |  | 2027-12-01 | 69 |  | 3200000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50549 | Wilson St SS, DIC, Transformer Addition | To support a new distribution substation and associated station retirements, ATC will loop through the existing WAN-WANT 69kV (Y-306) line for new Wilson St SS. ATC will install 2 line disconnect switches and 2 bus-tie disconnect switches. ATC to retire portion of WAN-WANT 69kV (Y-306) line to Waupun Westside (WAW), Waupun Southside (WSS) and Comtech (COMH). | WI | Other | Load Growth | Load Interconnection |  |  |  | 2028-12-31 | 69 |  | 3200000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50613 | Central SS, DIC, New Substation | Construct a new substation with one new 69/12.47 kV, 3.75/5.25 MVA transformer with high-side switch. Install 3-way MOD with supervisory control near Y-71 structure 99. Route approx. 0.5 miles of new 69kV line to new SS location. | WI | Other | Load Growth | Load Interconnection |  |  | 25 MVA | 2026-04-01 | 69 |  | 3200000
MTEP25 | West | ITC MIDWEST | 50378 | ITC Midwest SCADA Controlled Motor Operated Switch Addition blanket | ITC Midwest will add SCADA controlled motor operated switches on 69 kV lines that do not have existing remote sectionalizing capability and do not have any planned rebuilds. These 69 kV lines will be used to add SCADA controlled motor operated switches as part of an existing planned project to increase sectionalizing capability on the 69 kV system. ITC Midwest plans to install SCADA controlled motor operators on 3-5 lines/year as part of this program until existing circuits are brought up to ITC Midwest sectionalizing guidelines requirements. | IA; IL; MN | Other | Local Reliability | These projects are being done to help reduce outage duration time for customers by improving line sectionalizing ability and will bring the ITCM system to be in line with its current sectionalizing guidelines. Individual projects will add SCADA controlled motor operated switches on ITCM 69 kV lines which currently are not up to ITCM’s sectionalizing guideline requirements. These lines do not have existing remote sectionalizing capability and generally exceed the number of taps and/or the MW-miles in the ITCM sectionalizing guidelines and will have SCADA controlled motor operated switches added to them. |  |  |  | 2026-12-31 | 345 |  | 3125000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50550 | North Monroe Breaker and SCADA Asset Renewal | Replace 138kV Capacitor cans and update bank specifications and equipment as appropriate. ATC Planning to confirm the required MVAR capacity and switching device required. Replace relay panels and Station Manager RTU. Install to current ATC standards including Dual bus differential relays on the 69kV and 138kV busses. Replace 69kV Siemens model SP breaker in Position 719-S. Replace three Turner Electric disconnects and one ITE model HPL disconnect. Replace S&C circuit switcher in Position 207-S. Replace station power transformer connected to 69kV bus. | WI | Other | Age and Condition | Asset Renewal |  |  |  | 2028-12-01 | 138 |  | 3105000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50622 | Substation High Voltage Protection (HVP) Equipment Removal | The objective of ATC’s Substation (HVP) Equipment Removal project is to enhance safety within and outside the control house by decommissioning the remaining High Voltage Protection (HVP) telecommunications equipment from (~269) ATC substations. The legacy HVP (copper cable) equipment is no longer in use due to the migration to fiber optic technology upgrades within ATC’s substation environment. | WI | Other | Local Needs | Communication |  |  |  | 2027-11-30 | 0 |  | 3000000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50642 | Substation Technology Package #3 - 2026 | Installation of Edge computing hardware at multiple substation locations. Scope includes edge compute interoperability with physical security cameras, rogue detection sensors and asset monitor devices. | WI | Other | Local Needs | Communication |  |  |  | 2026-12-31 | 0 |  | 3000000
MTEP25 | West | MINNESOTA POWER INC. | 50149 | Arrowhead 230kV SPF Upgrade | Add redundancy or monitoring to the single point of failures to mitigate P5 contingencies associated with the Arrowhead 230kV buses. | MN | BRP |  | MTEP24 results show multiple thermal and voltage violations in the Duluth area caused by multiple NERC defined P5 contingencies. |  |  |  | 2028-12-31 | 230 |  | 3000000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50453 | Prairie Island Breaker Addition | Replace motor operated disconnects 8H10 and 8H12 with breakers | MN | Other | Local Reliability | Remediates reliability concerns with MOD failure |  |  |  | 2028-12-01 | 345 |  | 3000000
MTEP25 | West | DAIRYLAND POWER COOPERATIVE | 50272 | Genoa Dist Tap-Ringe Tap N470 Rebuild | Rebuild 7.88 miles of 69 kV transmission between Genoa Dist. and Ringe on DPC's N470 line & retire legacy switch. | MN | Other | Age and Condition | The transmission needs rebuild due to age and condition. |  |  |  | 2026-06-02 | 69 |  | 2959357
MTEP25 | West | ITC MIDWEST | 50210 | Keokuk West Relay Replacement and 69 kV Tie Breaker Addition | IPL has notified ITC that due to aging equipment and to support their future conversion in the area, they will be doing a complete rebuild of the Keokuk West substation. As part of this, ITC will build a new, separate control enclosure and replace all of its existing relays and install a new bus tie breaker. | IA | Other | Age and Condition | ITCMW will be replacing all of its relay equipment at Keokuk West due to its ageing condition. |  |  |  | 2027-12-31 | 69 |  | 2958416
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 24474 | Winnebago County, New DIC | WPS is proposing to construct a new T-D substation with two new 69/12.47 kV transformers with circuit breakers. ATC will construct a 69 kV loop-through straight bus with two line switches with load breaks. ATC will also install two manual bus-tie switches and make provisions for a future bus-tie breaker. ATC will loop through the new substation from the Sunset Point – Oshkosh 69 kV (E-5) line on the line section between Sunset Point and Bowen St. | WI | Other | Load Growth | Load Interconnection |  |  |  | 2026-10-01 | 69 |  | 2900000
MTEP25 | West | Central Minnesota Municipal Power Agency | 50275 | Blue Earth West Sub Transformer Upgrade | Add 2nd 10-14 MVA | MN | Other | Load Growth | Load growth. |  |  | 14 MVA | 2029-05-31 | 69 |  | 2900000
MTEP25 | West | GREAT RIVER ENERGY | 50394 | Riverton Asset Renewal | GRE plans to upgrade equipment and relocated assets ahead of MP Riverton rebuild scheduled for in-service by 2030. The project includes pull all GRE assets out of MP control house that is planned for demo by 2030 into new GRE control house. GRE will also be upgrading physical assets in our yard including the 25WB1 oil breaker, relaying, the Westinghouse 3-phase 115kV PT with 3 single phase CCVTs on 115kV bus, GE PT’s, and bus modifications. | MN | Other | Age and Condition | - Value added project to systematically replace all remaining electromechanical relays. GE-T60 being replaced due to continuous technician callouts as a result of failed relay power supplies. Safety concerns with Westinghouse APT style 3-phase PTs. G.E. Superbute JVS-350 bus PT’s have a history of failing at this age. Replacing oil breakers with limited parts is a system reliability improvement and eliminates the need for oil containment. - Due to this site being a CIP medium impact site, along with the fact that MP plans to rebuild Riverton by 2030 and replace the existing control house with two new controls houses in new locations at Riverton (see snippet), the project team has determined that it would be best if GRE could pull all of our assets from the existing control house into a new GRE control house located somewhere near the GRE side of the Riverton yard. GRE plan is get our relocation of assets and equipment replacement done prior to MP Riverton rebuild, so as to be out of their way prior to their work starting. |  |  |  | 2026-05-29 | 115 |  | 2610398
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50319 | West Des Moines 69 kV Breaker Replacement | Replace 69 kV breaker DAE601 at West Des Moines Substation. Rebuild and reconfigure West Des Moines 69 kV lines to 37th & Rock Island and 73rd & Buffalo substations. | IA | Other | Local Reliability | A circuit breaker with a higher fault current interrupting capability will be needed. |  |  |  | 2026-12-01 | 69 |  | 2550000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50598 | Progress SS, DIC, Substation Rebuild | ATC will install a 138 kV loop through substation on the Aviation - Ellinwood 138 kV (X-50) line with line switches to support a distribution substation rebuild. | WI | Other | Load Growth | Load Interconnection |  |  |  | 2027-06-30 | 138 |  | 2500000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50146 | BOC Gasses Tap – Town Line Road 138 kV (X-111), Rebuild | Rebuild BOC Gasses Tap – Town Line Rd (X-111) 138-kV line to achieve target rating. | WI | Other | Local Reliability | Reliability |  |  |  | 2027-01-01 | 138 |  | 2427000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50442 | Rebuild 5400 Richmond to Rich Springs Tap | rebuild 2.6 miles of 69kV Line 5400 from Richmond to Rich Springs Tap | MN | Other | Age and Condition | Replace end of life poles and install shield wire to improve performance and reliability of the line |  |  |  | 2028-12-29 | 69 |  | 2404191
MTEP25 | West | Central Minnesota Municipal Power Agency | 50268 | Blue Earth Rice Street Transformer Replacement | Rice Street Transformer Upgrade to 12/20 MVA | MN | Other | Load Growth | Load growth |  |  | 20 MVA | 2026-05-31 | 69 |  | 2400000
MTEP25 | West | GREAT RIVER ENERGY | 50267 | Johnsville Double End | GRE to convert the existing Johnsville substation to an in-and-out substation. GRE will need to build a short 69 kV transmission line tap and add/alter metering/telecom for the 2nd transformer. 2000-amp motor operated FLB switches should be used. | MN | Other | Local Reliability | Connexus Energy is adding a second bay at Johnsville and has requested GRE to accommodate the transmission. |  |  |  | 2029-12-31 | 69 |  | 2362908
MTEP25 | West | GREAT RIVER ENERGY | 50587 | Darnen Substation | Tap the Great River Energy (GRE) owned 'AG-MB' 115 kV line between Morris and Walden to serve a new distribution substation with an 'in-and-out' configuration. | MN | Other | Load Growth | Agralite Electric Cooperative requires a new distribution substation to serve power to a new dairy processing plant. Agralite requested transmission service from GRE to serve this new load. In addition to the new industrial load some existing load will be reallocated to this substation from other nearby Agralite substations to better serve their members. Due to the size of the new interconnected load and the potential for multiple distribution transformers served in a double-ended configuration, the transmission line will be configured in-and-out with the transmission path going into the distribution substation and back out, thereby providing redundant service from Morris or Walden. |  |  |  | 2026-09-15 | 115 |  | 2362888
MTEP25 | West | GREAT RIVER ENERGY | 50274 | Iona Area Projects | The Iona 115 kV Conversion Project involves building a 0.5-mile 115 kV tap line to interconnect the existing Todd-Wadena Electric Cooperative (TWEC) Iona substation to the 47 Line via a 3-way, 2000-amp, full load break 115 kV switch. Utilize 477 ACSR conductor. | MN | Other | Local Reliability | The purpose for this project is to increase the reliability to the Iona delivery point. The Eagle Galley 517F circuit performance over the last 5 years scores an “F” based on GRE’s reliability metrics. A score of “D” or “F” is our trigger to mitigate the poor performance. The 115 kV 47 Line, however, performs very well. |  |  |  | 2027-12-31 | 115 |  | 2315747
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50422 | Coon Creek Breaker ELR | Replace 3 345kV and 2 115kV breakers at Coon Creek that are at end of life | MN | Other | Local Reliability | Breakers are at end of life and are experiencing gas leaks, causing reliability concerns |  |  |  | 2025-12-01 | 345 |  | 2250000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50332 | Division-Eastside 69 kV Line Rebuild & Terminal Upgrades | Rebuild and reconductor the line to increase line rating. | IA | Other | Local Reliability | Mitigates thermal issues following N-1-1 69 kV contingencies at maintenance load levels |  |  |  | 2027-06-01 | 69 |  | 2200000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 25186 | Communications Reliability Program 2026 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2026. | MI; WI | Other | Local Needs | Other Local Needs - Communication |  |  |  | 2028-06-30 | 345 |  | 2100000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50495 | J1745 Fitzgerald SS Network Upgrades and Interconnection Facilities | J1745 is a 100 MW solar farm in Winnebago County, Wisconsin. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2029-06-11 | 138 |  | 2021000
MTEP25 | West | GREAT RIVER ENERGY | 50472 | Hawick Breaker Station | Convert the Hawick switching station to a breaker station by installing three breakers at the existing site. | MN | BRP |  | As part of a Willmar area study, a breaker station at Hawick was seen to eliminate existing N-1-1 (or N-2 with system adjustments allowed) thermal overloads in the area and provide margin for load growth. This project will be done in conjunction with other Willmar Municipal projects in the area identified as part of the same study | Area Load Growth (BRP) |  |  | 2026-09-30 | 69 |  | 2000000 | Part of Willmar area study, driven by load growth thermal overloads
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50335 | Johnson Creek Add 161 kV Breakers | Install two 161 kV breakers and associated equipment at Johnson Creek Substation. | IA | Other | Load Growth | Serve growing customer load in the area. |  |  |  | 2027-08-01 | 161 |  | 2000000
MTEP25 | West | MINNESOTA POWER INC. | 25264 | Ridgeview Transformer Addition | Add 115/34.5 kV transformer to existing Ridgeview Substation. This project includes adding one breaker to the existing Ring Bus for the transformer addition. | MN | Other | Local Needs | Redundancy and load-serving capability in downtown Duluth distribution system. |  |  |  | 2027-12-31 | 115 |  | 2000000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50430 | Souris Upgrades | Install new bus tie breaker and upgrade limiting equipment at Souris substation | ND | Other | Local Reliability | Increases limiting rating and prevents loss of TR1 and TR2 on loss of 115kV bus |  |  |  | 2028-05-31 | 115 |  | 2000000
MTEP25 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 50390 | New Dune Acres 138 kV Breaker additions | Add Breakers to existing lines where feasible to complete double breaker double bus design. | IN | BRP |  | MTEP24 studies show thermal violations for common breaker at the Dune Acres 138kV substation. Substation has 2 buses with several incoming lines on single breaker vs double. Adding breakers will eliminate multiple outages for single breaker failure. |  |  |  | 2029-05-31 | 138 |  | 3000000
MTEP25 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 50163 | New J1358 IC Facilities Interconnection 138 kV | Interconnection Facilities to Connect J1358 to NIPSCO's Luchtman Rd to Shoreline 138kV line | IN | GIP |  | Generator Interconnection |  |  |  | 2028-05-31 | 138 |  | 23396985
MTEP25 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 50170 | New J1355 IC Facilities Interconnection 138 kV | Interconnection Facilites to connect J1355 to NIPSCO's Stillwell 138kV substation | IN | GIP |  | J1355 IC |  |  |  | 2028-06-01 | 138 |  | 4235626
MTEP25 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 50171 | Schahfer 345kV substation Redundancy | RM Schahfer station’s relay protection requires full redundancy. Both the northwest and northeast 345kV buses at RM Schahfer currently have only one system of protection. To meet the requirements triggered by this interconnection, both buses will require additional bus protection relays. The protection and control schemes require new relaying that will include two bus differential relay panels and the addition of battery monitoring. Major Items  Two (2) bus differential relay panels  Battery monitoring system | IN | GIP |  | J1355 Network upgrade |  |  |  | 2026-07-30 | 345 |  | 512947
MTEP25 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 50538 | J1386 IC Facilities | Construct Transmission Owner’s Interconnection Facilities at Transmission Owner’s Green Acres Substation consisting of one monopole, H frame pull off structure, metering equipment, conductor, and fiber optics. | IN | GIP |  | J1386 IC Facilities |  |  |  | 2028-05-31 | 138 |  | 8123620
MTEP25 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 50104 | Upgrade PJM project b3775.8 St. John to Crete 345 kV | Upgrade the existing terminal substation conductor at St. John on the existing St. John to Crete 345kV line. | IN | Other | Local Reliability | Part of PJM multi-driver project |  |  |  | 2026-06-01 | 345 |  | 1150000
MTEP25 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 50105 | Reconfigure PJM project b3775.9. Green Acres 345kV substation | Project will reconfigure the existing St. John and Green Acres 345kV connections creating a Green Acres to University Park 345kV line and St. John to Olive 345kV line | IN | Other | Local Reliability | PJM multi-driver project |  |  |  | 2026-06-01 | 345 |  | 2150000
MTEP25 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 50389 | New Leesburg 345/138kV Transformer addition | Add a 2nd Leesburg 345/138kV Transformer | IN | Other | Local Reliability | Past system studies (MTEP22) have shown need for project for a common breaker failure at Leesburg 138kV substation. Operating conditions involving the existing Transformer has been an increasing concern in this area. |  |  |  | 2027-12-31 | 345 |  | 8000000
MTEP25 | Central | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | 50488 | Upgrade Dumont to Stillwell 138 kV line (PJM Project B3775.11) | NIPSCO will replace conductor drops at its Stillwell station on the Dumont-Stillwell 345 kV line with (2) 1590 ASCR conductor. NIPSCO will also replace the existing A phase wave trap with a 4000A wave trap. These upgrades are necessary to increase station terminal ratings above line conductor rating. | IN | Other | Local Reliability | PJM MDW1 |  |  |  | 2026-12-01 | 345 |  | 601914
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50438 | Line 0955 Relocation | Relocate 2 structures on line 0955 Alexandria to Bison 345kV | ND | Other | Local Needs | Relocation request from Army Corps of Engineers to eliminate clearance violation for new flood diversion project. |  |  |  | 2025-04-30 | 345 |  | 1897429
MTEP25 | West | ITC MIDWEST | 50231 | J1359 Generator Interconnection - TOIF - PCI 69kV Terminal & Line | The 69 kV straight bus at PCI will be extended to accommodate an additional position for the J1359 project. The Interconnection Customer, Alliant Energy, has proposed connection of a 95 MW combustion turbine generating facility to the PCI 69 kV bus. TOIF cost to include the new breaker, switches, relay panel and any new associated equipment. An approximately 0.75 mile 69 kV line from PCI to the generating facility will need to be constructed using a standard 1200A tier conductor (T2-477 ACSR or equivalent). | IA | GIP |  | Generator interconnection |  |  |  | 2026-02-27 | 69 |  | 1845014
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50511 | J1746 Columbia SS Network Upgrades and Interconnection Facilities | J1746 is a 150 MW solar facility in Columbia County, WI. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2029-06-11 | 138 |  | 1845000
MTEP25 | West | MINNESOTA POWER INC. | 50365 | Shannon Capacitor Bank Replacement | Replacing the two 230 kV and one 115 kV capacitor banks at the Shannon Substation. | MN | Other | Age and Condition | Age and Condition |  |  |  | 2026-12-31 | 230 |  | 1750000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50624 | Substation 74: Relocate 161 kV Capacitor Bank from Substation A | Relocate the existing 161 kV, 50.4 MVAR capacitor bank from Substation A to Substation 74. | IA | BRP |  | Address low voltage violations identified in the MTEP24 steady state analysis for NERC TPL-001 Category P6 N-1-1 contingencies. |  |  |  | 2026-06-01 | 161 |  | 1600000
MTEP25 | West | MINNESOTA POWER INC. | 50402 | Boswell 115/23kV Transformer Addition | Expansion of the 115kV bus with an additional breaker to accommodate a new 115/23kV transformer for load serving. | MN | Other | Local Needs | Updating load serving capability. |  |  |  | 2026-12-31 | 115 |  | 1550000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50328 | Neal North: Replace 161-69 kV Transformer Relaying & 69 kV Breaker Replacement | Replace 161 kV transformer relaying and 69 kV breaker at Neal North Substation | IA | Other | Age and Condition | Replace due to condition |  |  |  | 2029-12-01 | 161 |  | 1500000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50452 | Peace Garden Reactor | Install new reactor at Peace Garden | ND | BRP |  | Remediates observed high voltages under FAC-011 required monitoring |  |  |  | 2027-12-01 | 230 |  | 1500000
MTEP25 | West | GREAT RIVER ENERGY | 50425 | Fischer Substation Rebuild | DEA plans to update their 115-kV Fisher in/out distribution substation (both east and west) on the same property to replace the aged substation equipment. GRE will need to move the meter and telecom equipment as part of this work. | MN | Other | Age and Condition | Member need and aging infrastructure replacements. GRE asset renewals at this sub while DEA has substation out of service for rebuild. |  |  |  | 2025-12-08 | 115 |  | 1476377
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50517 | S1018 7 Mile Creek SS Network Upgrades | S1018 is a 75 MW Surplus project in Wood County, WI. The S1018 project consists of the installation of 75 MW battery storage at the J986 collector station. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2026-08-03 | 138 |  | 1475000
MTEP25 | West | GREAT RIVER ENERGY | 50305 | Blue Earth Substation Rebuild Projects | BENCO plans to rebuild their 69kV Blue Earth distribution substation on an adjacent property to replace the aged substation as well as increase transformer size to 7.5 MVA bottom 10.5 MVA top end rating . GRE will need to relocate line and install a new building, meter, and telecom equipment. GRE planning has requested the high side be an in-and-out. | MN | Other | Local Needs | Member need. |  |  |  | 2027-10-29 | 69 |  | 1443735
MTEP25 | West | DAIRYLAND POWER COOPERATIVE | 50270 | J1808 Generation Interconnection Network Upgrades. | J1808 is a 148 MW net solar facility interconnecting at DPC's Barron 161 kV substation. This interconnection will require POI facilities as well as a Barron 161 kV ring bus expansion and disconnect switch. | WI | GIP |  | J1808 is a 148 MW net solar facility interconnecting at DPC's Barron 161 kV substation. |  |  |  | 2027-07-02 | 161 |  | 1438367
MTEP25 | West | OTTER TAIL POWER COMPANY | 50485 | OTP Eden - Grenville 41.6 kV Rebuild | Rebuild 41.6 kV line between Eden 41.6 kV and Grenville 41.6 kV. | SD | Other | Age and Condition | Reliability Improvement; Aging Asset replacement |  |  |  | 2029-12-31 | 42 |  | 1400000
MTEP25 | West | GREAT RIVER ENERGY | 50416 | Pine City Breaker Replacement | • Replace breaker 4NB2 o New breaker slab, unless determined usable o New 795 AAC Jumpers • Replace breaker 4NB3 o New breaker slab, unless determined usable o New 795 AAC Jumpers • Replace 69kV bus PTs, Grasston line PT and Rush City/Rock Lake line CCVT o Remove 69kV PT Fuses • Replace line arresters with new 48kV MCOV Surge Arresters on Grasston and Bear Creek/Hinckley Lines • Replace 69kV bus relaying with SEL-487E pri/sec panel • Replace the #3 311B panel with 2 line 311C panel • Remove NS3 bypass switch • Update Station Service System o Install new 50kVA SSVT (Pri.) o Install new 200A ATS o Install new 200A Safety Switch (Pri.) o Install new 200A Safety Switch (Emer.) o ECE to replace existing 10kVA Aux Xfmr with 50kVA Aux Xfmr • Update line naming/3 letter mnemonics • Review grounding | MN | Other | Age and Condition | • McGraw oil breakers with OA-3 mechanism known to have high maintenance cost and slow first trip issues. These McGraw breakers have none to minimal replacement parts available. Last oil breaker at Pine City. • Poor PT/CCVT condition • Bus relay used as back up line for all 69kV lines and no backup bus relay. Also, BRPO relay has had multiple failures on GRE system causing outages. |  |  |  | 2027-12-31 | 69 |  | 1364747
MTEP25 | West | DAIRYLAND POWER COOPERATIVE | 50271 | Rock Dell-Pleasant Valley N469 Rebuild | Rebuild 2.0 miles of 69 kV transmission between Rock Dell and Pleasant Valley on DPC's N469 line & retire legacy switches. | MN | Other | Age and Condition | The transmission needs rebuild due to age and condition. |  |  |  | 2028-03-01 | 69 |  | 1227000
MTEP25 | West | GREAT RIVER ENERGY | 50415 | Grand Lake Area Projects | Relocate and reterminate 69 kV transmission line into the new Grand Lake high side. | MN | Other | Local Needs | LCP is rebuilding the Grand Lake substation and has requested GRE to reconnect the transmission line. |  |  |  | 2025-10-31 | 69 |  | 1200259
MTEP25 | West | OTTER TAIL POWER COMPANY | 50470 | OTP Cyrus - Farwell 41.6 kV Rebuild | Rebuild 41.6 kV line between Cyrus 41.6 kV and Farwell 41.6 kV. | MN | Other | Age and Condition | Reliability Improvement; Aging Asset replacement. |  |  |  | 2025-12-31 | 42 |  | 1130000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50544 | MPFCA Rockdale SS Network Upgrade | Each individual Interconnection Customer is responsible for a proportionate percentage share of the CUU estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. Constrained facilities are those CUU facilities that are being upgraded in Section 1.2. J1502 is seeking interconnection service for 225 MW, J1629 is seeking interconnection service for 200 MW, J1706 is seeking interconnection service for 100 MW, J1732 is seeking interconnection service for 98.4 MW, J1746 is seeking interconnection service for 150 MW, J1773 is seeking interconnection service for 300 MW, J1779 is seeking interconnection service for200 MW, J1781 is seeking interconnection service for 300 MW, J1824 is seeking interconnection service for 67 MW. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2027-10-10 | 138 |  | 1120000
MTEP25 | West | ITC MIDWEST | 50240 | J1520 Generator Interconnection - TOIF | To interconnect project J1520 to the ITC Midwest (“ITCM”) system at the Interconnection Customer’s requested point of interconnection, the Bluebill 345 kV bus will need to be converted to a breaker and ½ to allow for the new 345 kV terminal. The Interconnection Customer, MISO, and ITCM entered into Generator Interconnection Agreement (“GIA”). Network Upgrades and Transmission Owner Interconnection Facilities (“TOIF”) are expected to be constructed at the Bluebill Switch Station for project J1520, a 135 MW solar generating facility, under a Generator Interconnection Agreement (“GIA”) as a condition of the project’s Interconnection Service. | IA | GIP |  | The Facilities Study for J1520 identified Network Upgrades and TOIF necessary for the interconnection of the project to ITCM’s Bluebill 345 kV Switch Station. Project J1520 and the impact to the transmission system was evaluated as part of the DPP 2020 West Area Study. |  |  |  | 2027-10-31 | 345 |  | 1101322
MTEP25 | West | ITC MIDWEST | 50238 | MPFCA J1503 & J1504 - TOIF - Huntley 345 kV Terminal | The MISO interconnection projects J1503 & J1504 has proposed the connection of two 150 MW solar powered generating facilities to the Huntley 345 kV bus. This section is for the TOIF portion only including: 345 kV dead end structure, 345 kV switch, PTs, relay panel for the gen-tie line, and lightning arrestors dedicated to the interconnection customer’s 345 kV gen-tie line. The IC, MISO, and ITCM executed GIAs for J1503 & J1504, but all construction will be done under the MPFCA J1503 J1504 for the expansion of the Huntley 345 kV sub to accommodate a new 345 kV line terminal. The cost of the project will be split 50/50 between J1503 & J1504, but both projects are owned by the same customer. | MN | GIP |  | Generator Interconnection |  |  |  | 2027-10-31 | 345 |  | 1083794
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50454 | Line 0730 Souris - West Sioux Falls Rebuild | Replace steel poles on line 0730 Souris - West Sioux Falls | ND; SD | Other | Age and Condition | Poles are in degraded condition and at risk of failure |  |  |  | 2025-09-01 | 69 |  | 1000000
MTEP25 | West | OTTER TAIL POWER COMPANY | 50486 | OTP Casselton Town New 115 kV Delivery | New 115 kV delivery to uprate Casselton town from 41.6 kV to 115 kV. | ND | Other | Local Reliability | Improve reliability by introducing new higher voltage delivery. |  |  |  | 2026-12-31 | 115 |  | 1000000
MTEP25 | West | GREAT RIVER ENERGY | 50304 | Slayton Area Projects | Nobles is planning on relocating Slayton/Nobles substation out of town. Currently, Nobles is planning an energization date of fall of 2025. This will require GRE to tap into the new substation, retap in Xcel’s line from the new Slayton substation and retire the tap line (etc) from the old Slayton substation. | MN | Other | Local Needs | Member need. |  |  |  | 2025-12-31 | 69 |  | 873200
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50512 | J1778 Paris SS Network Upgrades | J1778 is a 100 MW solar facility in Kenosha County, WI. Per the J1778 GIA, there are no TOIFs associated with this project. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2027-11-09 | 138 |  | 811000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50533 | S1016 Lone Rock SS Network Upgrades | S1016 is a 25 MW Surplus project Richland County, WI. The S1016 project consists of battery storage at the J864 collector station. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2026-09-05 | 69 |  | 800000
MTEP25 | West | OTTER TAIL POWER COMPANY | 50520 | OTP Donaldson - Donaldson South J1575 Network Upgrades | Network upgrades to accommodate interconnection customer J1575 to the Donaldson to Warsaw 115 kV transmission line. | MN | GIP |  | Network upgrades required to accommodate interconnection customer J1575. |  |  |  | 2028-12-31 | 115 |  | 776292
MTEP25 | West | ITC MIDWEST | 50235 | J1444 Generator Interconnection - TOIF - DAEC 345kV Terminal | To interconnect projects J1444 to the ITC Midwest (“ITCM”) system at the Interconnection Customer’s requested point of interconnection, the DAEC 345 kV bus will need to be converted to a breaker and ½ to allow for the new 345 kV terminal. The Interconnection Customer, MISO, and ITCM entered into Generator Interconnection Agreement (“GIA”). Network Upgrades and Transmission Owner Interconnection Facilities (“TOIF”) are expected to be constructed at the DAEC Substation for project J1444, a 200 MW solar generating facility, under a Generator Interconnection Agreement (“GIA”) as a condition of the project’s Interconnection Service. | IA | GIP |  | The Facilities Study for J1444 identified Network Upgrades and TOIF necessary for the interconnection of the project to ITCM’s DAEC 345 kV Substation. Project J1444 and the impact to the transmission system was evaluated as part of the DPP 2019 West Area Study. |  |  |  | 2025-09-01 | 345 |  | 760648
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50327 | Raun: Tekamah 161 kV Line Relay Replacement SPP DISIS-2017 | Replace relaying at Raun Substation on Tekamah 161 kV line terminal | IA | GIP |  | SPP Gen-2017-105 network upgrade |  |  |  | 2028-09-01 | 161 |  | 750000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50318 | Adams County-Creston 161 kV Line Uprate for DPP 2020 | Replace line structures to increase line rating. | IA | GIP |  | DPP 2020 West identified network upgrade. |  |  |  | 2027-09-01 | 161 |  | 700000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 25371 | Lake Yankton SVC Retirement | Retire Lake Yankton SVC. | MN | Other | Age and Condition | SVC at Lake Yankton is due for repairs but is no longer required to support the area. |  |  |  | 2025-12-01 | 115 |  | 700000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50423 | Essig Substation Rebuild | Rebuild end of life Essig substation at neighboring site, converting old 2.4 kV system to standard 12.47kV | MN | Other | Age and Condition | Substation is at end of life and is showing deterioration and is non standard 2.4 kV |  |  |  | 2027-08-31 | 69 |  | 681832
MTEP25 | West | OTTER TAIL POWER COMPANY | 50510 | OTP Bellingham 115 kV Delivery | New 115 kV delivery for town of Bellingham by tapping the Big Stone to Marietta 115 kV line. | MN | Other | Age and Condition | Age and condition issues causing need to rebuild Bellingham distribution, so moving to new 115 kV delivery to better serve. |  |  |  | 2030-12-31 | 115 |  | 650000
MTEP25 | West | MINNESOTA MUNICIPAL POWER AGENCY | 50234 | MN River Breaker Install (position 5M518) | Install breaker on MN River Substation ring bus (position 5M518) | MN | Other | Local Reliability | Fault on generator bus can result in partial loss of load |  |  |  | 2027-02-15 | 115 |  | 625800
MTEP25 | West | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | 50465 | Pella Underground Conversion | Rebuild a section of overhead line (~1,135 linear feet of transmission line) to underground line (~800 feet of underground cable). | IA | Other | Local Needs | This conversion from overhead to underground is a results of a local park project |  |  |  | 2026-01-01 | 69 |  | 500000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50451 | Magic City Reactor | Install new reactor at Magic City | ND | BRP |  | Remediates observed high voltages under FAC-011 required monitoring |  |  |  | 2028-09-01 | 230 |  | 500000
MTEP25 | West | ITC MIDWEST | 50232 | J1359 Generator Interconnection - Network Upgrades - PCI 69kV Bus | The 69 kV straight bus at PCI will be extended to accommodate an additional position for the J1359 project. The Interconnection Customer, Alliant Energy, has proposed connection of a 95 MW combustion turbine generating facility to the PCI 69 kV bus. ITCM will TO-Fund the Network Upgrades and recover and earn on costs under a Facilities Service Agreement. | IA | GIP |  | The Facilities Study for J1359 identified Network Upgrades and TOIF necessary for the interconnection of the project to ITCM’s PCI 69 kV Substation. Project J1359 and the impact to the transmission system was evaluated as part of the DPP 2019 West Area Study |  |  |  | 2026-03-01 | 69 |  | 401708
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50325 | NE Ankeny - Ames 161 kV relay replacements | Replace 161 kV line relaying for ITC substation cut-in | IA | Other | Local Reliability | Compliance |  |  |  | 2025-10-01 | 161 |  | 400000
MTEP25 | West | OTTER TAIL POWER COMPANY | 50471 | OTP Ivanhoe 41.6kV Line Recloser | Install line recloser near Ivanhoe 41.6 kV. | MN | Other | Local Reliability | Reduce 41.6 kV line exposure and improve reliability |  |  |  | 2025-12-31 | 42 |  | 350000
MTEP25 | West | OTTER TAIL POWER COMPANY | 50487 | OTP Bemidji Nymore Circuit Breaker | New 69 kV breaker at Bemidji Nymore substation. | MN | Other | Local Reliability | Improve reliability by adding circuit breaker. |  |  |  | 2026-12-31 | 69 |  | 350000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50330 | Plymouth-Merrill 69 kV Line Uprate | Replace structures on the Plymouth-Merrill 69 kV line to increase line's rating. | IA | Other | Local Reliability | Reliability improvement |  |  |  | 2026-06-01 | 69 |  | 325000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50333 | Franklin: Replace Nuthatch Line Relaying | Replace primary and secondary line and breaker failure relaying on Franklin 161 kV Breaker 9920 to ITC Midwest’s Nuthatch Substation | IA | Other | Local Reliability | ITC Midwest plans to upgrade relays at Nuthatch Substation to SEL-411L by the fourth quarter of 2025. MidAmerican has agreed to replace line relays at Franklin Substation on the line terminal to Nuthatch to SEL-411L relays and add redundant pilot protection at the same time as ITC Midwest’s relay replacement. |  |  |  | 2025-06-19 | 161 |  | 300000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50655 | R1049/R5061 Edgewater SS, Network Upgrades and Interconnection Facilities | Supporting R1049/R5061 interconnection via 345 kV CT contributions, bus 3 differential relay panel, wiring updates in the bus 3 differential relay panels, and System Protection Setting Modifications and Supporting Activities. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2026-09-30 | 345 |  | 260000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50516 | S1017 Tennyson SS Network Upgrades | S1017 is a 100 MW Surplus project in Grant County, WI. The S1017 project consists of the installation of 100MW of battery storage at the J947 collector station. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2025-04-30 | 138 |  | 225000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50542 | S1025 Sheepskin SS Network Upgrades | S1025 is a 25 MW Surplus project in Rock County, WI. The S1025 project consists of battery storage at the J1188 collector station. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2027-06-15 | 69 |  | 225000
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50431 | Line 0846 Relocation | Relocate structures on line 0846 High Bridge - Daytons Bluff 115kV | MN | Other | Local Needs | Relocation request from Ramsey County to promote new development |  |  |  | 2024-12-01 | 115 |  | 200000
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50505 | J1793 Holland SS Network Upgrades | J1793 is a 75 MW solar facility in Sheboygan County, WI. There are no TOIF upgrades required as a part of the J1793 interconnection request as the J1793 generator lead line will utilize the J1153 Generator Lead Line to the same TOIF equipment covered under the J1153 GIA. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2025-12-09 | 138 |  | 142000
MTEP25 | West | GREAT RIVER ENERGY | 50392 | Elk River Muni West | Remove and upgrade 600-amp switches EWSM11 and EWS10 with live parts to 1200 amp. The span of 266 ACSR transmission conductor between the two switch poles should be removed and upgraded to 477 ACSS. Switch EWS14 is 1200-amp and owned by Elk River Municipal and nothing needs to be done to this switch. | MN | Other | Local Reliability | Thermal overloading The short span of 266 ACSR transmission between switches EWSM11 and EWS14 will overload for the loss of Liberty – Thompson Lake 69 kV line in the near-term with very little expected load growth until overloading. Switches EWSM11 and EWS10 will overload for the loss of Liberty – Thompson Lake 69 kV line after the 134 MW subsystem has grown by 40 MW. Assuming a CAGR of 1-2%, the switches will need to be replaced in 14-28 years. The subsystem is described furthermore at the end of the document. | Load Growth |  |  | 2026-10-30 | 69 |  | 68811
MTEP25 | West | NORTHERN STATES POWER COMPANY | 50494 | Knight Substation | Install new 115/34.5kV substation in the Dayton area to meet area load growth. | MN | Other | Load Growth | Required for load growth in the area. |  |  |  | 2026-12-01 | 115 |  | 29600
MTEP25 | West | AMERICAN TRANSMISSION COMPANY | 50515 | J1779 Rockdale SS Interconnection Facilities | J1779 is a 200 MW solar facility in Dane County, WI. Per the GIA, there are no network upgrades associated with project, only TOIFs. | WI | GIP |  | Generation Interconnection Project |  |  |  | 2027-10-31 | 345 |  | 25000
MTEP25 | West | OTTER TAIL POWER COMPANY | 50467 | OTP Maple River Reactor Retirements | Retire 2 x 25 MVAR reactors off transformer tertiaries at Maple River 345 kV substation. | ND | Other | Age and Condition | Reactors failed and will be retired. |  |  |  | 2025-12-31 | 35 |  | 1
MTEP25 | West | OTTER TAIL POWER COMPANY | 50469 | OTP Big Stone South Reactor Retirement | Retire 25 MVAR reactor off tertiary winding of Big Stone South transformer #1. | SD | Other | Age and Condition | Reactor failed and is going to be retired. |  |  |  | 2025-12-31 | 35 |  | 1
MTEP25 | Central | PRAIRIE POWER, INC. | 50381 | Rebuild Riverside-Hardin Tap 69 kV line | Rebuild Riverside-Hardin Tap 69 kV Line | IL | Other | Local Reliability | Reliability. Increase rating from 35 MVA to 50 MVA to mitigate throughflow overloads |  |  |  | 2026-12-01 | 69 |  | 5940000
MTEP25 | Central | PRAIRIE POWER, INC. | 50405 | Relocate Berlin-Amos 69 kV line | Reroute Berlin-Amos 69 kV Line out of creek bottom | IL | Other | Age and Condition | Age and condition. Replace 1966 line. Provide feed for new Knoles distribution station. |  |  |  | 2029-12-01 | 69 |  | 11175000
MTEP25 | Central | PRAIRIE POWER, INC. | 50406 | Rebuild Breiner-Kington 69 kV line | Rebuild Breiner-Kington 69 kV Line | IL | Other | Age and Condition | Age and condition. Replace 1968 line. |  |  |  | 2027-12-01 | 69 |  | 5665000
MTEP25 | Central | PRAIRIE POWER, INC. | 50407 | Rebuild Macomb-Spring Lake Junction 69 kV line | 1) Rebuild Macomb Bkr-Woodland 69 kV Line 2) Rebuild Woodland-Spring Lake Jct 69 kV Line | IL | Other | Age and Condition | Age and condition. Replace 1962 line. |  |  |  | 2027-12-01 | 69 |  | 2010000
MTEP25 | Central | PRAIRIE POWER, INC. | 50408 | Rebuild El Dara Junction-Hadley 69 kV line | Rebuild El Dara Jct-Hadley 69 kV Line | IL | Other | Age and Condition | Age and condition. Replace 1967 line. |  |  |  | 2029-12-01 | 69 |  | 2820000
MTEP25 | Central | PRAIRIE POWER, INC. | 50409 | New Andrew-Salisbury Tap 69 kV line | Add 2nd circuit to existing Andrew-Salisbury Tap to 69 kV Line for dedicated feed to Salisbury | IL | Other | Local Reliability | Solves low voltage issues for P6 contingency |  |  |  | 2028-12-01 | 69 |  | 1100000
MTEP25 | Central | PRAIRIE POWER, INC. | 50411 | New Tice-Virginia 69 kV line | 1) New Tice-Petersburg 69 kV Line 2) New Petersburg-Virginia 69 kV Line | IL | Other | Local Reliability | Solves low voltage issues for P6 contingency |  |  |  | 2030-12-01 | 69 |  | 20085000
MTEP25 | Central | PRAIRIE POWER, INC. | 50412 | New Paragon-Grove City 69 kV line | 1) New Paragon-Dunkel 69 kV Line 2) New Dunkel-Owaneco 69kV Line 3) New Owaneco-Velma 69 kV Line 4) New Velma-Grove City 69 kV Line | IL | Other | Local Reliability | Provide network service to Grove City, Velma, and Owaneco |  |  |  | 2030-12-01 | 69 |  | 19890000
MTEP25 | Central | PRAIRIE POWER, INC. | 50413 | New Edinburg 69 kV breaker station | New 3 terminal Breaker Station | IL | Other | Local Reliability | Sectionalize 69 kV lines to East Lanesville, Pleasant View and Paragon |  |  |  | 2030-12-01 | 69 |  | 3400000
MTEP25 | Central | PRAIRIE POWER, INC. | 50414 | New Henton 69 kV breaker station | 1) New 3 terminal Breaker Station 2) New 4.8 MVAR Capacitor Bank | IL | Other | Local Reliability | Sectionalize 69 kV lines to East Lanesville, Pleasant View and Paragon. Solves low voltage issues for P6 contingency |  |  |  | 2029-12-01 | 69 |  | 3400000
MTEP25 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 50399 | Line 35A Rebuild | A complete rebuild of Line 35A (Benndale – Benndale GT 69kV) is recommended at 161kV insulation with more reliable structural designs and OPGW. This project will increase reliability of the transmission system and provide an additional OPGW communication link between Benndale and Benndale GT. | MS | Other | Local Reliability | Line 35A (Benndale - Benndale GT 69kV) is overloading during the outage of L71A (Benndale - Benndale GT 69kV). L35A was constructed in 1969 and is reaching the end of its useful life and is in need of being rebuilt in order to maintain reliability and avoid overloading. |  |  |  | 2028-06-01 | 69 |  | 900000
MTEP25 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 50400 | Ovett 69kV Delivery Point | Tap Line 114A (Ellisville - NW Perry 69kV) with a 69kV GOAB and build a new transmission line to the delivery point. | MS | Other | Load Growth | A member distribution cooperative, Dixie Electric, has requested a new 69kV delivery point near Ovett in Jones County, MS. |  |  |  | 2026-10-01 | 69 |  | 2100000
MTEP25 | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 50404 | Lake Walthall 115kV Delivery Point | Tap the Entergy owned 115kV line (Tylertown - Dexter) with a 115kV switching station and build a new transmission line to the delivery point. | MS | Other | Load Growth | A member distribution cooperative, Magnolia Electric, has requested a new 115kV delivery point south of Tylertown, MS. |  |  |  | 2026-12-01 | 115 |  | 2830000
MTEP25 | South | ENTERGY ARKANSAS, LLC | 50541 | El Dorado 500/345kV Autotransformer Upgrade | EAL is proposing to upgrade the El Dorado 500/345kV Autotransformer including associated station equipment. | AR | BRP |  | These facilities were identified as needed to maintain NERC compliance during Entergy’s studies with the addition of the Mount Olive to Sarepta 500 kV project. This project is being submitted as an EPR due to the long lead time of Autotransformers and the timing of the submittal being after the September 2024 cutoff for inclusion into MTEP25. | Large Industrial (BRP) |  |  | 2028-12-01 | 500 |  | 35725000 | EAL BRP $36M; mitigates Cargas violations
MTEP25 | South | ENTERGY SERVICES, LLC. | 50540 | Sarepta to Mount Olive 500 kV Project | Entergy is proposing to construct • Sarepta 500 kV station including a Sarepta 500-345 kV Autotransformer • New ~60 mile Mt Olive to Sarepta 500 kV line. • Upgrade existing Mt Olive 500-230 kV Autotransformer | LA | BRP |  | Entergy received a request from a customer adding new load in Holly Ridge, LA. These facilities were identified as needed to maintain NERC compliance during Entergy’s studies. Entergy is observing the following thermal violations which require the need for this project: • P6 loss of Sterlington to El Dorado 500 kV and MT Olive to El Dorado 500 kV lines. o Marion – Huttig 115 kV line o Marion – Sterlington 115 kV line o El Dorado E – T.E.P S/F 115 kV line o El Dorado E – El Dorado 115 kV line o J1612 – Strong 115 kV line o J1612 – Huttig115 kV line o El Dorado D – El Dorado M 115 kV line o T.E.P S/F – Strong 115 kV line o Vienna – Bernice 115 kV line o Sarepta – Minden 115 kV line o Minden LG – Minden LA 115 kV line o Bernice – Junction City 115 kV line o Upland – Junction City 115 kV line o Parnell – Newell 115 kV line o Newell – Upland 115 kV line o Wyatt – Parnell 115 kV line o El Dorado Mon – El Dorado | Large Industrial (BRP) |  |  | 2028-12-01 | 500 |  | 470100002 | BRP: Sarepta-Mt Olive 500kV ($470M) mitigating thermal violations from Cargas load in Holly Ridge LA
MTEP25 | South | ENTERGY SERVICES, LLC. | 50360 | War Eagle 138 kV: Construct New Substation and Lines | Construct a new War Eagle 138 kV substation approximately 0.3 miles north of the Oak Ridge 138 kV substation that cuts into the Oak Ridge – Metro 138 kV. Construct a new 138 kV line from Porter to the new War Eagle substation. Energize the abandoned 138 kV L-403 by terminating into the War Eagle and Forest 138 kV substations and rebuild. | TX | BRP |  | The P6 contingency involving the loss of any two of the three 138 kV lines listed below results in non-consequential load loss in the Woodlands area due to the overload of the remaining line over 125%. Lewis Creek – Alden Conroe – Forest Porter – Oak Ridge No reconfiguration of the system or redispatch was found to reduce all loading below applicable ratings. |  |  |  | 2029-06-01 | 138 |  | 110000002
MTEP25 | Central | Southern Illinois Power Cooperative | 50637 | Big Muddy Solar - J1303 Generator Interconnection | Installation of a new 161 kV switchyard on the SIPC Jackson to Campbell Hill line. | IL | GIP | [5 empty] | 2026-10-01 | 161 |  | 9389000
MTEP25 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 50241 | Replace Boonville T1 69 kV | Replace transformer #1 with new 20MVA. | IN | Other | Age and Condition | Aging infrastructure |  |  |  | 2027-12-31 | 69 |  | 2360000
MTEP25 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 50245 | Replace Culley 138kV CCVT Boxes | Replace existing line, breaker, and bus relaying panels. Replace existing CCVT junction boxes with new stainless-steel boxes. | IN | Other | Age and Condition | Aging infrastructure |  |  |  | 2027-12-31 | 138 |  | 1600000
MTEP25 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 50247 | Rebuild Elliott Transformer and Substation 69 kV | Replace existing ‘Transformer #1’ & ‘Transformer #2’ with new 100MVA transformers. Add new transformer protective relaying. Replace existing 138kV circuit breakers ‘1000’ & ‘3000’ and 69kV circuit breakers ‘100’, ‘200’, ‘300’ & ‘600’. Replace breaker foundations, breaker/line switches, and protective relaying. Replace two (2) existing 69kV capacitor banks. | IN | Other | Local Reliability | Local Reliability |  |  |  | 2027-12-31 | 138 |  | 15700000
MTEP25 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 50248 | Replace Newburgh Circuit Switcher 69 kV | Remove existing 69kV high-side fuses and associated switch ‘199’ and replace with new 69kV circuit switcher. Install an auto-sectionalizing and RTU panels. Replace existing 7200V voltage regulators. | IN | Other | Age and Condition | Aging Infrastructure |  |  |  | 2027-12-31 | 69 |  | 1550000
MTEP25 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 50249 | Rebuild Dubois T2 138/69 kV Transformer | Replace existing 100MVA, 138/69kV ‘Transformer #1’. Replace existing 69kV breakers ‘100’, ‘200’, ‘300’, ‘400’ and ‘500’. Replace existing 138kV and 69kV CCVTs. Install new transformer, 138kV and 69kV breaker and line relaying panels. | IN | Other | Local Reliability | Local Reliability |  |  |  | 2027-12-31 | 138 |  | 7870000
MTEP25 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 50316 | Rebuild Z84 Duff to Petersburgh 138 kV | Complete rebuild of Z84 from Duff to IPL Petersburgh plant. Total rebuild distance is 19.9 miles and involves replacing wood h-frame structures with galvanized steel monopole structures. The existing 765 Drake ACSR conductor to be replaced with new 2-bundled 954 Rail conductor. | IN | Other | Age and Condition | Aging Infrastructure |  |  |  | 2028-12-31 | 138 |  | 38040000
MTEP25 | Central | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | 50326 | Rebuild Z95 Northwest to AB Brown 138kV | Rebuild aging portions of the Z95 Northwest to AB Brown 138kV transmission line. The first section is approximately 1.57 miles long and the second section is approximately 3.47 miles long. Both sections have 795 Drake conductor, which will be replaced with 954 Rail conductor. Aging wood poles will be replaced with tubular steel structures. | IN | Other | Age and Condition | Aging infrastructure |  |  |  | 2027-12-31 | 138 |  | 8700000
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50320 | E. 17th & Washington 69 kV bus expansion and line breaker installations | Expand E. 17th & Washington Substation steel to accommodate two 69 kV line breakers | IA | Other | Local Reliability | Reliability improvement |  |  |  | 2028-06-01 | 69
MTEP25 | West | MIDAMERICAN ENERGY CO. | 50321 | E. 17th & Broadway 69 kV breaker installations | Install three 69 kV line breakers at E. 17th & Broadway Substation | IA | Other | Local Reliability | Reliability improvement |  |  |  | 2028-10-01 | 69
MTEP25 | West | OTTER TAIL POWER COMPANY | 50603 | OTP Big Stone South Load Addition | OTP has a new customer requesting to be served near Big Stone, SD. OTP will serve the new customer by building a new 230/34.5 kV distribution substation connecting to the Big Stone South to Crowned Ridge 230 kV line right near the Big Stone South substation. | SD | Other | Load Growth | A new customer has requested to interconnect to OTP's system. This project is required to serve the new load and maintain transmission system reliability. |  |  |  | 2025-09-19 | 230
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50691 | LEAP Phase 2 EPR Mitigations | Reactive and thermal project mitigations for LEAP Phase 2 (MTEP 50208) area large load. | IN | BRP |  | Reactive and thermal project mitigations for LEAP Phase 2 area large load | Data Center (BRP) | Y |  | 2029-06-29 | 345 |  | 45000000 | BRP: Reactive/thermal mitigations for LEAP Phase 2 (50208) data center load
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50728 | Add 3rd 345/138kV Bank at Edwards Sub | This is part of LEAP Phase 2 EPR mitigations. This will add a third 606MVA bank to Edwards substation, as well as updating normal and emergency line ratings for the LEAP 138kV lines | IN | BRP |  | Part of LEAP Phase 2 EPR mitigations; adds 3rd 606MVA bank to Edwards substation | Data Center (BRP) | Y |  | 2029-06-30 | 345 |  | 15000000 | BRP driven by LEAP data center EPR. Add 3rd 345/138kV bank at Edwards Sub
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50208 | New LEAP Transmission Network | A large customer has committed to the LEAP District, an innovation district west of Lebanon, IN in Boone County. This data center customer will be ramping to 600 MW of total demand. To meet the load requirements, WVPA will connect into the Whitestown-Hortonville 345kV line and construct a new 345/138kV substation, approximately 10 miles of double circuit 345kV, two 138kV stations and approximately 25 miles of 138kV transmission. | IN | Other | Load Growth | Large customer committed to LEAP District, Innovation district west of Lebanon IN. Data center customer ramping to 600 MW total demand. New 345/138kV sub, ~10mi double-circuit 345kV, two 138kV stations, ~25mi 138kV. | Data Center | Y | 600 | 2026-12-31 | 345 |  | 222200000 | LEAP Innovation District data center, Lebanon IN. 600 MW Phase 1. Total district demand 1200 MW (Phase 1+2)
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50286 | Lebanon Industrial 2nd 69kV Source | Build approximately 13 miles of new 69kV transmission between new Rosston Substation and Eli Lilly facility | IN | Other | Local Reliability | Lebanon Industrial 2nd 69kV Source; near LEAP district | Pharmaceutical (Eli Lilly) |  |  | 2027-10-01 | 69 |  | 30311869 | DEI $30M; likely Eli Lilly manufacturing
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50287 | Gessie 69kV Rebuild | Rebuild the entire 3.5 miles of 69kV line due to age and condition. It will be rebuilt in two stages to minimize outages to the substation. This project will also support Warren's needed distribution underbuild. | IN | Other | Age and Condition | Age and condition |  |  |  | 2026-07-06 | 69 |  | 7194654
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50292 | Fishback Creek 69/12kV Substation | New substation near Whitestown Parkway to alliveiate heavy loading on existing Royalton substation | IN | Other | Load Growth | Load Growth |  |  |  | 2028-12-31 | 69 |  | 6000000
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50293 | 6923 69kV Ring Bus | The 6923 line from Huntington North Junction to North Manchester is an 18.8 mile long line. In order to improve reliability, a 3-breaker ring bus substation will be added at the midpoint of this line at the tap point for Heartland’s Bippus Substation. | IN | Other | Local Reliability | Reliability |  |  |  | 2029-12-31 | 69 |  | 6800000
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50294 | Romine 69kV Switching Station | Currently the 6936 lines goes from Attica 230kV substation to Cayuga (43.6 miles), and a new 3-breaker ring bus would be added at the Flexel junction point to segment the line and improve reliability. This point has been agreed upon with Duke. | IN | Other | Local Reliability | Reliability |  |  |  | 2028-12-31 | 69 |  | 6800000
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50295 | 69154 69kV Ring Bus | A 4-position ring bus will be installed at the Cherry Grove substation along Duke’s 69154 transmission line. The line has a lot of mileage exposure and has multiple member delivery points served off it so the project will break up the line and improve the reliability of those delivery points. | IN | Other | Local Reliability | Reliability |  |  |  | 2030-12-31 | 69 |  | 6800000
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50296 | Dover 69/12kV Substation | Build new substation next to existing Dover substation to serve construction power for the LEAP district and other expected growth in the area. The sub will be built with a single transformer with provisions for a 2nd and the line will be looped through the station. Construction power requests have been between 6-12MW of load. | IN | Other | Load Growth | Load growth |  |  | 12 | 2027-12-31 | 69 |  | 5500000
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50297 | Milnon 69/12kV Substation | Construct new 69/12kV substation between the NIPSCO Monon and Milroy delivery points and retire member meter points | IN | Other | Load Growth | Load growth |  |  |  | 2027-11-24 | 69 |  | 6649226
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50298 | Four Corners 69/12kV Substation | Build a new 69kV substation to serve load near Hanna, IN | IN | Other | Load Growth | Load growth |  |  |  | 2027-12-01 | 69 |  | 14052130
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50300 | Hayworth 69/12kV Substation | Build a new 69kV substation to retire the Morocco meter point and provide reliability to existing Berthaville & Colfax South substation | IN | Other | Load Growth | Reliability & load growth |  |  |  | 2027-12-01 | 69 |  | 10249426
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50301 | Maple Leaf 69kV Line | WVPA will build approximately 6 miles of new 69kV transmission line to provide a second transmission source to the existing Maple Leaf substation in Milford, IN. NIPSCO’s 69kV transmission line 6941 will be tapped just East of their Royal Outdoor substation in Milford, IN. | IN | Other | Local Reliability | Reliability |  |  |  | 2027-12-31 | 69 |  | 15000000
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50302 | Lacrosse 69/12kV Substation | Install new 14 MVA substation in LaCrosse, IN, near Dome substation to support the Lena Park and Kouts substations during switching orders and outages. | IN | Other | Load Growth | Load growth |  |  | 14 MVA | 2029-12-31 | 69 |  | 12500000
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50303 | Jacob Mack 2nd Bank & Source | A 22.4MVA transformer will be installed at Jacob Mack sub to serve member load and relieve the existing older bank. In addition to the bank work, the substation 69kV side will be built out for a looped transmission feed. Jacob Mack is currently radially fed with a normal feed from NIPSCO’s 6939 line out of Green Acres and a normally open point from circuit 6934, both lines will be looped into the station and the normally open point moved inside the fence. | IN | Other | Local Reliability | Jacob Mack 2nd Bank & Source for load growth and reliability | Load Growth + Reliability |  |  | 2027-12-31 | 69 |  | 8594249 | System Need: "Load growth & reliability"
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50371 | Lee Hanna 69/12kV Rebuild | Rebuild the existing Lee Hanna 69/12kV Substation to increase the capacity of the station to two 33.6MVA transformers for load growth, back-feeding, and construction power. | IN | Other | Load Growth | Load growth |  |  | 6 MVA | 2027-11-01 | 69 |  | 10000000
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50551 | New Stillwell to Elderberry 345kV Line | The project is to construct a 345kV line from AEP’s Elderberry Substation to NIPSCO’s Stillwell substation. | IN | Other | Local Reliability | Increased system reliability, integration of assets, and delivery of energy to the MISO market. |  |  |  | 2028-12-31 | 345 |  | 75000000
MTEP25 | Central | WABASH VALLEY POWER ASSOCIATION, INC. | 50628 | Upgrade LEAP Transmission Network Phase 2 | Additional load has committed to the LEAP District, an innovation district west of Lebanon, IN in Boone County. The total demand in the district is estimated to be 1200MW. This represents a 600MW increase to a prior approved submission. To meet the additional load requirements, WVPA will connect into the Qualitech-Whitestown 345kV line and construct a new 345kV ring bus and approx. 12 miles of 345kV line to the west side of Lebanon where WVPA will construct a 345/138kV substation. Approx. 15 miles of 345kV line will be built to network this 345/138kV station to a planned 345/138kV station on the north side of the LEAP district. WVPA will also connect into the Nucor-Whitestown 345kV line and construct a new 345kV ring and approx. 6 miles of new 345kV line to the new step down substation. | IN | Other | Load Growth | Additional load committed to LEAP District. Total demand estimated 1200MW. 600MW increase. New 345kV ring bus, 12mi 345kV, new 345/138kV sub, 15mi 345kV. | Data Center | Y | 600 | 2029-06-30 | 345 |  | 345000000 | LEAP Phase 2: additional 600 MW data center load. Total LEAP ecosystem ~$852M+
MTEP25 | East | ITC | 18192 | Rebuild Hines - Levan 120 kV Line | Rebuild the 954 ACSR sections (~0.5 mile) from structure #5680A to Levan and from structure #5686 to Hines with 1431 ACSR using 120 kV, double-circuit construction. Install OPGW on the rebuilt sections. Also, upgrade the 954 ACSR bus (line drop) at Levan “HD” to at least 375 MVA for summer emergency rating. Terminate fiber at both ends. | MI | BRP |  | The Hines – Levan circuit is projected to become overloaded in MISO’s MTEP24 study. |  |  |  | 2031-06-01 | 120 |  | 1935000
MTEP25 | East | METC | 50372 | Upgrade Dupont-White Lake 138 kV line | Upgrade line from Dupont to White Lake (~5.094 miles) from 336 ACSR to 954 ACSR. Also, upgrade buses at Dupont positions “199” and “177” to at least 332 MVA for summer emergency rating. | MI | BRP |  | The overloads identified were found in MISO’s MTEP24 Annual Deliverability Study. |  |  |  | 2030-06-01 | 138 |  | 8298000
MTEP25 | East | ITC | 50590 | Upgrade Sunset 120 kV Switch | Upgrade the 1200A switch "HI" at Sunset 120 kV station. | MI | BRP |  | MISO identified the overload on Sunset2-Sunset3 120kV bus-tie (HH) in the MTEP24 study. |  |  |  | 2030-06-01 | 120 |  | 168000
MTEP25 | East | ITC | 50591 | Install Phoenix 120 kV Capacitor | Install a 50 Mvar capacitor with 40 kA synchronous breaker and associate switch at Phoenix 120 kV bus 103. | MI | BRP |  | MISO identified voltage issues at Phoenix 120 kV bus in the MTEP24 study. |  |  |  | 2030-06-01 | 120 |  | 1500000

## MTEP25 (App B)
MTEP Year | Planning Region | Utility/TO | Project ID | Project Name | Project Description | State | Project Type | Other Type | System Need / Rationale | Project Driver | Data Center Flag | Load (MW) | Expected ISD | Max kV | Min kV | Estimated Cost ($) | Report Notes
MTEP25 (App B) | Central | AMEREN MISSOURI | 22850 | Upgrade Miner 161 kV Substation | Add line breakers on Sikeston and Charleston positions | MO | Other | Age and Condition | Increased reliability and age/condition |  |  |  | 2028-12-01 | 161 |  | 5600000
MTEP25 (App B) | Central | AMEREN MISSOURI | 22793 | Upgrade Arnold 138 kV substation | Line breaker at Arnold on TYSN-ARNO-3 | MO | Other | Local Reliability | increased reliability and modularity during outages |  |  |  | 2028-12-01 | 138 |  | 2100000
MTEP25 (App B) | Central | AMEREN MISSOURI | 23128 | Reconductor Sioux-Maline 138 kV lines 3&4 | Reconductor the Sioux-Brickhouse-Maline-3 & 4 138 kV lines with conductors capable of carrying 2,000 amps at Summer Emergency Conditions. Replace both shield wires with new OPGW. | MO | Other | Age and Condition | The existing shield wires between structure 42-Maline Sub are historically poor performing Copperweld wires that are susceptible to failure under heavy wind/ice conditions. The shield wires from Sioux-Str. 42 are 60 years old and in open, flat terrain, which makes them significant targets for lightning strikes that weaken their strength and increase the likelihood of failure. In addition, the 2156 ACSR Bluebird conductors are approaching end of life, |  |  |  | 2029-12-01 | 138 |  | 21000000
MTEP25 (App B) | Central | AMEREN MISSOURI | 23066 | New Point Prairie 161 kV line breakers | Line breakers at Point Prairie | MO | Other | Local Reliability | Increased reliability |  |  |  | 2028-12-01 | 161 |  | 8700000
MTEP25 (App B) | Central | AMEREN TRANSMISSION COMPANY OF ILLINOIS | 50632 | Missouri Multi-Entity New Transmission (MoMENT) Project (Alternate) | New 40 mile 345 kV line from Loose Creek to Barnett. New 345/161 kV substation at Barnett. New 38 mile 345 and 161 kV double circuit line from Overton to Barnett. New 65 mile single circuit 345 kV line from Barnett to Clinton. New Clinton substation. New 50 mile single circuit 345 kV line from Clinton to LaCygne. | MO | Other | Local Reliability | This program is the result of a joint effort between ATXI, AECI and Evergy to identify a portfolio of projects which would increase reliability to all customers across the Central and Western Missouri region. Benefits include Increased transfer capability between regions and increased reliability to multiple substations. Future benefits include potential interconnection points for generators and load customers. |  |  |  | 2030-12-01 | 345 |  | 499000001
MTEP25 (App B) | West | AMERICAN TRANSMISSION COMPANY | 50629 | Birnanwood – Brookes Corners 69kV (Y-86), Partial Rebuild | Rebuild ~9.3 out of 28.4 miles of Y-86 | WI | Other | Age and Condition | Asset Renewal - Transmission Line |  |  |  | 2031-12-31 | 69 |  | 19000000
MTEP25 (App B) | West | AMERICAN TRANSMISSION COMPANY | 50537 | Dam Heights – Sauk City Oak St 69 kV (Y-14), Partial Rebuild & OPGW | Rebuild and install poles, conductor, and OPGW on approximately 2.0 miles out of 2.4 miles between Dam Heights SS to Sauk City Oak St SS. | WI | Other | Age and Condition | Asset Renewal |  |  |  | 2029-06-01 | 69 |  | 14000000
MTEP25 (App B) | West | AMERICAN TRANSMISSION COMPANY | 50122 | Columbia SS Power Transformer Asset Renewal | Replace T21/T23 with one 500MVA transformer & associated yard equipment. | WI | Other | Age and Condition | Asset Renewal |  |  |  | 2028-12-01 | 345 |  | 12329000
MTEP25 (App B) | West | AMERICAN TRANSMISSION COMPANY | 50123 | Highway V SS Power Transformers Asset Renewal | Replacement of two transformers at Highway V SS. Replacement of two gas breakers and disconnects. Reconfigure bus to facilitate xfmr, breaker, and disconnect installation. Install two breaker/differential relay panels. Modify ground grid in alignment with site expansion. Asset renewal of two station power transformers. | WI | Other | Age and Condition | Asset Renewal |  |  |  | 2028-12-01 | 138 |  | 21439000
MTEP25 (App B) | West | AMERICAN TRANSMISSION COMPANY | 50129 | Silver River - North Lake 138 kV (NLKG31), Rebuild | T-line rebuild of line NLKG31 from Silver River SS to North Lake SS. | MI | Other | Age and Condition | Asset Renewal |  |  |  | 2029-12-01 | 138 |  | 88000000
MTEP25 (App B) | West | AMERICAN TRANSMISSION COMPANY | 50131 | Dam Heights - Kirkwood 69 kV (Y-75), Partial Rebuild | Rebuild and install poles, conductor, and OPGW on approximately 7.7 miles out of 16.6 miles between various sections from Kirkwood SS to Dam Heights SS. | WI | Other | Age and Condition | Asset Renewal |  |  |  | 2028-11-30 | 69 |  | 25700000
MTEP25 (App B) | West | AMERICAN TRANSMISSION COMPANY | 50132 | Riverside (ALTE) - Erdman 69 kV (Y-82/X-64/X-37), Partial Rebuild & OPGW | Rebuild and install poles, conductor, and OPGW on approximately 3.6 miles from Erdman substation to Structure 97 (X-64/Y-82) and 1 mile from Structure 81 to Structure 65 (Y-82/X-37), and to also install OPGW on portions not being rebuilt to complete the fiber path. | WI | Other | Age and Condition | Asset Renewal & Communication |  |  |  | 2028-05-30 | 69 |  | 29000000
MTEP25 (App B) | West | AMERICAN TRANSMISSION COMPANY | 50133 | Zenda - Katzenberg 69 kV (Y-51 ALE), Partial Rebuild | Rebuild and install poles, conductor, and OPGW on approximately 8.2 miles of Y-51 ALE from Zenda Tap switch structure to Katzenberg SS and rebuild approximately 2 miles from Zenda Tap to Zenda. | WI | Other | Age and Condition | Asset Renewal |  |  |  | 2028-05-30 | 69 |  | 22300000
MTEP25 (App B) | West | AMERICAN TRANSMISSION COMPANY | 50578 | Indian Lake – Hiawatha, 69 kV New Line and 138 kV Conversion | Construct a new 69 kV circuit from Indian Lake to Hiawatha. Convert Existing 69 kV Line from Indian Lake – Hiawatha to 138 kV operation. | MI | BRP |  | BRP |  |  |  | 2029-09-01 | 138 |  | 43100000
MTEP25 (App B) | West | AMERICAN TRANSMISSION COMPANY | 50694 | Highland – Verona 69 kV (Y-138/Y-36/Y-209/Y-136), Partial Rebuild | Partial rebuild of select portions of 69 kV line sections between Highland and Verona (Y-138/Y-36/Y-209/Y-136) and fix limiters in their respective substations, to achieve a rating of T2 Hawk 477 kcmil. | WI | Other | Age and Condition | Asset Renewal - Transmission Line |  |  |  | 2031-12-31 | 69 |  | 78400000
MTEP25 (App B) | West | AMERICAN TRANSMISSION COMPANY | 50692 | Badger West 69kV 20ohm Series Reactor | Install 69kV 20ohm series reactor at Badger West on line Badger West – Saratoga 69kV (Y-302). | WI | Other | Local Reliability | Reliability |  |  |  | 2027-12-31 | 69 |  | 5000000
MTEP25 (App B) | West | AMERICAN TRANSMISSION COMPANY | 50346 | Huebner SS, DIC, Transformer Addition | WPL will add a 3rd 138/24.9 kV, 20/26/33 MVA transformer to Huebner Substation. ATC will relocate the C1 cap bank equipment to make room for 138 kV bus expansion. Reconnect C1 to Bus 1. ATC will expand 138 kV bus 1 to the east to interconnect the 3rd Huebner transformer. ATC will install two 138 kV line breakers to the existing loop-through configuration. Project team to ensure we make provisions for two future bus-tie breakers to be installed if more load is put on the station. ATC will install two 138 kV bus-side disconnect switches and remove the whips and supervisory control from the line-side disconnect switches. | WI | Other | Load Growth | Load Interconnection |  |  | 33 MVA | 2027-12-31 | 138 |  | 3200000
MTEP25 (App B) | West | AMERICAN TRANSMISSION COMPANY | 50509 | Racine - St. Rita 138 kV (8531), Partial Rebuild | Rebuild wood h-frame portion for asset renewal needs (~7.9 miles) and also assumes for cost estimate to rebuild the steel lattice tower section (~1.6 miles). Engineering/scope review to see if steel lattice towers can handle upgraded conductor as planning is also needs driver as well for larger (T2 Hawk). Include 48 fiber from end to end. Listing it as partial rebuild in case engineering evaluation shows that lattice towers can be reconductored instead of replaced. | WI | Other | Age and Condition | Asset Renewal, Reliability |  |  |  | 2033-12-31 | 138 |  | 33000000
MTEP25 (App B) | West | Central Minnesota Municipal Power Agency | 50276 | Blue Earth North Substation Upgrade 1st 161/69 Transformer to 45-60-75 MVA | Blue Earth North Substation Upgrade 1st 161/69 Transformer to 45-60-75 MVA | MN | Other | Load Growth | Load growth |  |  | 75 MVA | 2034-05-31 | 161 |  | 3700000
MTEP25 (App B) | West | Central Minnesota Municipal Power Agency | 50277 | Blue Earth Northeast Sub Upgrade 1st transformer to 20-37.3 MVA | Blue Earth Northeast Sub Upgrade 1st transformer to 20-37.3 MVA | MN | Other | Load Growth | Load growth |  |  | 3 MVA | 2034-05-31 | 69 |  | 3000000
MTEP25 (App B) | West | Central Minnesota Municipal Power Agency | 50278 | Blue Earth new North to Northeast 69 kV line | new North Sub to Northeast Sub 69 kV line | MN | Other | Load Growth | Load growth |  |  |  | 2034-05-31 | 69 |  | 12800000
MTEP25 (App B) | East | METC | 50592 | Rebuild Latson-Dean Road-Oakland 138 kV Line | Rebuild 138 kV sections (~13.3 miles) from Latson to Dean Road to Oakland using 954 ACSR conductor. | MI | BRP |  | MISO identified thermal overloads on the Latson-Dean Road-Oakland 138 kV sections for P2 contingency in the MTEP24 study. |  |  |  | 2030-06-01 | 138 |  | 23500000
MTEP25 (App B) | East | METC | 50309 | Rebuild Eureka 138kV Station | Rebuild the Eureka 138kV Station to a breaker-and-a-half configuration just south of the existing station. This station will include five (5) 138kV 3000 A breakers with at least 63 kA interrupting capability and all associated equipment. | MI | Other | Local Needs | Expanding this station would ensure that power is being reliably supplied to the customer (Fitzner) while adding additional benefits to the system in this area. |  |  |  | 2030-06-01 | 138 |  | 11257400
MTEP25 (App B) | East | METC | 50446 | Rebuild Beals Road 138 kV Station | Construct a new 138 kV station (tentatively named Badger) approximately 1 mile south of Beals Road substation with 4 row (expandable to 6 rows) breaker-and-a-half configuration. Relocate all 138 kV connections at existing Beals Road substation to the new Badger station. | MI | Other | Age and Condition | The Beals Road 138 kV station is a late 1940’s legacy station that was acquired from Consumers Energy as part of the METC acquisition. Much of the equipment has been in-service for several decades and has been identified as being in poor condition, a source of failure, and a safety hazard by the Asset Management department at ITC. In addition to the issues primary equipment issues mentioned, there are several protection and control related issues including having maintenance, safety, and human performance concerns due to the buildings’ age and space constraints. Most of METC’s relaying and controls require high operations and maintenance expenses due to their age.. |  |  |  | 2030-06-01 | 138 |  | 24540000
MTEP25 (App B) | West | MINNESOTA POWER INC. | 50344 | Haines Road Substation Modernization | Rebuild Haines Road 115 kV substation into a 5-position ring bus. Add 115/34.5 kV Transformer to provide better backup capacity for area distribution load. | MN | Other | Age and Condition | Age and Condition and extra source for local distribution. |  |  |  | 2029-12-31 | 115 |  | 5836050
MTEP25 (App B) | West | MINNESOTA POWER INC. | 50348 | 181 Line Rebuild | Rebuild 115 kV Thomson - Mahtowa (181 Line) Transmission Line. | MN | Other | Age and Condition | Age and Condistion |  |  |  | 2033-12-31 | 115 |  | 14200000
MTEP25 (App B) | West | NORTHERN STATES POWER COMPANY | 25398 | King Transmission Connection | New 230kV ~30mi transmission line, 2 switching stations with capacitors, and associated substation upgrades including 2 230/345kV transformers to bring radial renewable generation to AS King substation to replace existing generation. | MN | Other | Local Reliability | Project needed to bring renewable generation in WI to AS King substation to replace existing coal generation. |  |  |  | 2027-06-01 | 345 |  | 146000000
MTEP25 (App B) | West | NORTHERN STATES POWER COMPANY | 25282 | Minnesota Energy Connection | New radial double circuit line from SherCo to wind generation collector sites. Voltage support at end of radial line and midpoint substation. Upgrades at SherCo to accommodate new line. | MN | Other | Local Reliability | Required to deliver wind generation to SherCo to replace retiring coal generation at SherCo. |  |  |  | 2028-09-30 | 345 |  | 1075000000
MTEP25 (App B) | South | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | 50499 | Purvis Bulk Transformer Bonus Rating | The Purvis Bulk transformers are causing constraints in the generator deliverability analysis. | MS | Other | Local Reliability | Increase the Purvis Bulk transformer bonus rating to 520 MVA. |  |  |  | 2026-03-01 | 230 |  | 10000