## Merged
Upgrade Id | Region | Transmission Owner | State | Location | Description | Project Type | Voltage | Equipment | Driver | csv_driver_category | driver_consistency | is_data_center | csv_data_center | csv_driver_detail | csv_notes | csv_sources | csv_doc_dates | csv_record_count | Cost Estimate | TEAC Cost | Initial TEAC Date | Latest TEAC Date | Required Date | Projected In Service Date | Actual In Service Date | Status | Percent Complete | Task | Immediate Need | Proposal IDs | Schedule12 Location | (Non-Load Ratio Share) Cost Allocation Percent | (Load Ratio Share) Cost Allocation Percent | ISA In-Service Date | Revised In-Service Date | TEAC Materials | Last Updated
b2668.1 | PJM WEST | AEP | IN | Dequine | Replace the bus/risers at Dequine 345 kV station | Baseline | 345 | Bus | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 2.3 | 2.3 | 2021-11-02 | 11/2/2021 | 6/1/2020 | 3/20/2023 | 3/20/2023 | IS | 100 | Replace | No |  | Appendix A | AEP:100
b2779.6 | PJM WEST | AEP | IN | Dunton Lake, SDI Varner | Construct a 345 kV ring bus at Dunton Lake to serve SDI load at 345 kV via two circuits | Baseline | 345 | Ring Bus | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Construction of new 138 kV station (Sowers) tapping into Grabill-South Hicksville 138 kV line to serve Steel Dynamics, Inc. (SDI) Varner station (~300+ MW demand). Scope change to split load at SDI: furnaces via 345 kV from Dunton Lake, segregated load via 138 kV from Auburn and Sowers; avoids prolonged outage of Collingwood 345 kV line and eliminates flicker exposure. Cost increased from $107.7M to $135M (previously approved project, scope change). |  | 20210209-february-board-whitepaper.json | 2021-01-01 | 1 | 23.4 | 23.4 | 2020-12-01 | 12/1/2020 | 6/1/2016 | 11/15/2021 | 11/3/2021 | IS | 100 | Construct | Yes |  | Appendix A | AEP:100
b2779.7 | PJM WEST | AEP | IN | Collingwood | Retire Collingwood 345 kV station | Baseline | 345 | Substation | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Construction of new 138 kV station (Sowers) tapping into Grabill-South Hicksville 138 kV line to serve Steel Dynamics, Inc. (SDI) Varner station (~300+ MW demand). Scope change to split load at SDI: furnaces via 345 kV from Dunton Lake, segregated load via 138 kV from Auburn and Sowers; avoids prolonged outage of Collingwood 345 kV line and eliminates flicker exposure. Cost increased from $107.7M to $135M (previously approved project, scope change). |  | 20210209-february-board-whitepaper.json | 2021-01-01 | 1 | 1.4 | 1.4 | 2020-12-01 | 12/1/2020 | 6/1/2016 | 12/15/2021 | 11/29/2021 | IS | 100 | Retire | Yes |  | Appendix A | AEP:100
b3131.1 | PJM WEST | AEP | OH | Haviland and East Lima | Rebuild approximately 12.3 miles of remaining Lark conductor on the double circuit line between Haviland and East Lima with 1033 54/7 ACSR conductor. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Winter Generator Deliverability and Basecase Analysis: Haviland–East Lima 138kV line overloaded for 15 N-1 and generator deliverability contingencies. Additional scope added to replace 500 MCM Cu risers and bus conductors at Haviland 138kV after they were identified as elements with ratings between existing and desired facility ratings. |  | 20200602-teac-appendix-basline-material-upgrade-recommend-july-2020-pjm-board-review.json | 2020-01-01 | 1 | 25.9 | 25.9 | 2021-01-15 | 1/15/2021 | 12/1/2024 | 6/14/2024 | 6/17/2024 | IS | 100 | Rebuild | No |  | Appendix A | AEP:100
b3221 | PJM MA | PPL | PA | Steel City | Replace terminal equipment (bus conductor) on the 230 kV side of the Steel City 500/230 kV transformer #1 | Baseline | 230 | Bus | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.09 | 0.09 | 2020-11-04 | 11/4/2020 | 6/1/2025 | 11/27/2024 | 6/6/2024 | IS | 100 | Reconductor | No |  | Appendix A | PPL:100
b3223.1 | PJM SOUTH | Dominion | VA |  | Install a 2nd 230kV circuit with a minimum summer emergency rating of 1047 MVA between Lanexa and Northern Neck Substations. The 2nd circuit will utilize the vacant arms on the double-circuit structures that are being installed on the Line #224 (Lanexa-Northern Neck) End-of-Life rebuild project (b3089). | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Increases in load and a shift in the load profile in Dominion to match winter peaking condition, resulting in accelerated load growth in this area, leading to N-1-1 voltage and thermal violations and >300 MW load loss in the 2022/2023 timeframe based on 2020 PJM load forecast. |  | 20201201-pjm-teac-board-whitepaper-december-2020.json | 2020-01-01 | 1 | 14 | 14 | 2020-09-01 | 10/6/2020 | 6/1/2023 | 12/31/2025 | 9/14/2025 | IS | 100 | Install | Yes |  | Appendix A | Dominion:100
b3223.2 | PJM SOUTH | Dominion | VA |  | Expand the Northern Neck terminal from a 230kV, 4-breaker ring bus to a 6-breaker ring bus. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Increases in load and a shift in the load profile in Dominion to match winter peaking condition, resulting in accelerated load growth in this area, leading to N-1-1 voltage and thermal violations and >300 MW load loss in the 2022/2023 timeframe based on 2020 PJM load forecast. |  | 20201201-pjm-teac-board-whitepaper-december-2020.json | 2020-01-01 | 1 | 5 | 5 | 2020-09-01 | 10/6/2020 | 6/1/2023 | 12/31/2025 | 10/23/2025 | IS | 100 | Modify | Yes |  | Appendix A | Dominion:100
b3223.3 | PJM SOUTH | Dominion | VA |  | Expand the Lanexa terminal from a 6-breaker ring bus to a breaker-and-a-half arrangement. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Increases in load and a shift in the load profile in Dominion to match winter peaking condition, resulting in accelerated load growth in this area, leading to N-1-1 voltage and thermal violations and >300 MW load loss in the 2022/2023 timeframe based on 2020 PJM load forecast. |  | 20201201-pjm-teac-board-whitepaper-december-2020.json | 2020-01-01 | 1 | 4 | 4 | 2020-09-01 | 10/6/2020 | 6/1/2023 | 7/31/2025 | 10/23/2025 | IS | 100 | Modify | Yes |  | Appendix A | Dominion:100
b3224 | PJM MA | DPL | DE |  | Replace a disconnect switch and reconductor a short span of Mt. Pleasant - Middletown Tap line | Baseline | 138 | Conductor | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.43 | 0.42 | 2020-11-18 | 11/18/2020 | 6/1/2025 | 12/31/2027 |  | EP | 10 | Replace | No |  | Appendix A | DPL:100
b3226 | PJM MA | AEC | NJ | Swainton substation | Add 10 MVAR 69 kV capacitor bank at Swainton substation | Baseline | 69 | Capacitor | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 3.86 | 2.9 | 2020-11-18 | 11/18/2020 | 6/1/2025 | 5/31/2025 | 5/16/2025 | IS | 100 | Install | No |  | Appendix A | AEC:100
b3227 | PJM MA | AEC | NJ | Corson-Court 69 kV line | Rebuild the Corson-Court 69 kV line to achieve ratings equivalent to 795 ACSR conductor or better | Baseline | 69 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 45.3 | 13.2 | 2020-11-18 | 11/18/2020 | 6/1/2025 | 6/1/2026 |  | EP | 60 | Rebuild | No |  | Appendix A | AEC:100
b3228 | PJM MA | BGE | MD |  | Replace two relays at Center Substation to increase ratings on the 110552 circuit | Baseline | 115 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2020-11-18 | 11/18/2020 | 6/1/2025 | 6/1/2025 | 12/12/2024 | IS | 100 | Replace | No |  | Appendix A | BGE:100
b3233 | PJM MA | PENELEC | PA |  | Install one 34 MVAR 115 kV shunt reactor and breaker. Install one 115 kV circuit breaker to expand the substation to a 4 breaker ring bus. | Baseline | 115 | Reactive Device | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 4.9 | 4.9 | 2020-11-18 | 11/18/2020 | 6/1/2025 | 12/31/2027 |  | EP | 3 | Install | No |  | Appendix A | PENELEC:100
b3240 | PJM WEST | APS | WV |  | Upgrade Cherry Run and Morgan terminals to make the Transmission Line the limiting component. Morgan: Wave Trap Cherry Run: Substation conductor, relays, CT | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.1 | 0.23 | 2020-11-20 | 10/5/2021 | 6/1/2024 | 6/18/2024 | 6/1/2024 | IS | 100 | Upgrade | No |  | Appendix A | APS:100
b3241 | PJM WEST | APS | WV |  | Install 138 kV, 36 MVAR capacitor and a 5 uF reactor protected by a 138 kV capacitor switcher. Install a breaker on the 138 kV Junction terminal. Install a 138 kV 3.5 uF reactor on the existing Hardy 138 kV capacitor. | Baseline | 138 | Capacitor | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 2.85 | 2.85 | 2020-11-20 | 12/18/2020 | 6/1/2025 | 5/30/2025 | 6/13/2025 | IS | 100 | Install | No |  | Appendix A | APS:100
b3242 | PJM WEST | APS | VA |  | Reconfigure Stonewall 138 kV substation from its current configuration to a six-breaker breaker-and-a-half layout and add two 36 MVAR capacitors with capacitor switchers. | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 13.3 | 13.3 | 2020-11-20 | 12/18/2020 | 6/1/2025 | 6/1/2027 |  | EP | 30 | Modify | No |  | Appendix A | APS:100
b3245 | PJM MA | PENELEC | PA |  | Construct a new breaker-and-a-half substation near Tiffany substation. All transmission assets and lines will be relocated to the new substation. The two distribution transformers will be fed via two dedication 115 kV feeds to the existing Tiffany substation. | Baseline | 115 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Williams 115 kV bus has voltage drop issue in 2025 RTEP winter case for line fault stuck breaker contingency: loss of Williams-Tiffany-Laurel Lake-Westover 115 kV circuit. Excluded from competitive window via below-200 kV exemption. |  | 20210209-february-board-whitepaper.json | 2021-01-01 | 1 | 23.2 | 23.2 | 2020-11-18 | 11/18/2020 | 6/1/2025 | 6/5/2026 |  | UC | 40 | Construct | No |  | Appendix A | PENELEC:100
b3246.1 | PJM SOUTH | Dominion | VA |  | Convert 115 kV Line #172 Liberty-Lomar and 115 kV Line #197 Cannon Branch-Lomar to 230 kV to provide a new 230 kV source between Cannon Branch and Liberty. The majority of 115 kV Line #172 Liberty-Lomar and Line #197 Cannon Branch-Lomar is adequate for 230 kV operation. Lines to have a summer rating of 1047 MVA/1047 MVA (SN/SE) | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Manassas area of northern Virginia experiencing significant load growth due to introduction of multiple new load locations and increases to existing load exceeding 500 MW. N-1-1 analysis shows load drop violations for multiple 230 kV contingency pairs; violations expected in 2022/2023 timeframe due to reverse-power relay scheme interactions. |  | 20210209-february-board-whitepaper.json | 2021-01-01 | 1 | 10 | 8 | 2020-12-01 | 8/31/2021 | 6/1/2023 | 8/14/2026 |  | UC | 80 | Modify | Yes |  | Appendix A | Dominion:100
b3246.2 | PJM SOUTH | Dominion | VA |  | Perform substation work for the 115 kV to 230 kV Line conversion at Liberty, Wellington, Godwin, Pioneer, Sandlot and Cannon Branch. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Manassas area of northern Virginia experiencing significant load growth due to introduction of multiple new load locations and increases to existing load exceeding 500 MW. N-1-1 analysis shows load drop violations for multiple 230 kV contingency pairs; violations expected in 2022/2023 timeframe due to reverse-power relay scheme interactions. |  | 20210209-february-board-whitepaper.json | 2021-01-01 | 1 | 40 | 16 | 2020-12-01 | 8/31/2021 | 6/1/2023 | 12/18/2026 |  | UC | 70 | Modify | Yes |  | Appendix A | Dominion:100
b3246.3 | PJM SOUTH | Dominion | VA |  | Extend 230kV Line #2011 Cannon Branch – Clifton to Winters Branch by removing the existing Line #2011 termination at Cannon Branch and extending the line to Brickyard creating 230kV Line #2011 Brickyard-Clifton. Extend a new 230kV line between Brickyard and Winters Branch with a summer rating of 1572MVA/1572MVA (SN/SE) | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Manassas area of northern Virginia experiencing significant load growth due to introduction of multiple new load locations and increases to existing load exceeding 500 MW. N-1-1 analysis shows load drop violations for multiple 230 kV contingency pairs; violations expected in 2022/2023 timeframe due to reverse-power relay scheme interactions. |  | 20210209-february-board-whitepaper.json | 2021-01-01 | 1 | 8 | 10 | 2020-12-01 | 12/1/2020 | 6/1/2023 | 8/9/2025 | 8/19/2025 | IS | 100 | Modify | Yes |  | Appendix A | Dominion:100
b3246.4 | PJM SOUTH | Dominion | VA |  | Perform substation work at Cannon Branch, Brickyard and Winters Branch for the 230kV Line #2011 extension. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Manassas area of northern Virginia experiencing significant load growth due to introduction of multiple new load locations and increases to existing load exceeding 500 MW. N-1-1 analysis shows load drop violations for multiple 230 kV contingency pairs; violations expected in 2022/2023 timeframe due to reverse-power relay scheme interactions. |  | 20210209-february-board-whitepaper.json | 2021-01-01 | 1 | 14.1 | 4 | 2020-12-01 | 12/1/2020 | 6/1/2023 | 8/9/2025 | 8/19/2025 | IS | 100 | Modify | Yes |  | Appendix A | Dominion:100
b3246.5 | PJM SOUTH | Dominion | VA |  | Replace the Gainesville 230kV 40kA breaker “216192” with a 50kA breaker. | Baseline | 230 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Manassas area of northern Virginia experiencing significant load growth due to introduction of multiple new load locations and increases to existing load exceeding 500 MW. N-1-1 analysis shows load drop violations for multiple 230 kV contingency pairs; violations expected in 2022/2023 timeframe due to reverse-power relay scheme interactions. |  | 20210209-february-board-whitepaper.json | 2021-01-01 | 1 | 0.5 | 0.5 | 2020-12-01 | 12/1/2020 | 6/1/2023 | 5/19/2023 | 5/15/2023 | IS | 100 | Replace | Yes |  | Appendix A | Dominion:100
b3249 | PJM WEST | AEP | OH | Chatfield-Melmore | Rebuild the Chatfield-Melmore 138kV line (~ 10 miles) to 1033 ACSR conductor. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In the summer 2025 RTEP case, the Chatfield-Melmore 138 kV line is overloaded due to a line with stuck breaker contingency. Identified through AEP's FERC 715 Planning Criteria. |  | 20210406-pjm-teac-board-whitepaper-april-2021.json | 2021-01-01 | 1 | 27.2 | 27.2 | 2021-02-17 | 2/17/2021 | 6/1/2025 | 2/24/2026 |  | UC | 85 | Rebuild | No |  | Appendix A | AEP:100
b3263 | PJM SOUTH | Dominion | VA |  | Cut existing 115kV Line#5 between Bremo and Cunningham substations and loop in and out of Fork Union Substation. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 2.5 | 2.5 | 2020-11-04 | 1/14/2021 | 12/1/2025 | 12/1/2025 | 2/24/2022 | IS | 100 | Modify | No |  | Appendix A | Dominion:100
b3300 | PJM SOUTH | Dominion | VA | Brambleton, Evergreen Mills | Reconductor 230kV Line #2172 from Brambleton to Evergreen Mills along with upgrading the line leads at Brambleton to achieve a summer emergency rating of 1574 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 6.5 | 2.32 | 2020-12-01 | 1/6/2021 | 6/1/2025 | 2/26/2027 |  | UC | 60 | Reconductor | No | 2020_W1-26 | Appendix A | Dominion:100
b3301 | PJM SOUTH | Dominion | VA | Brambleton, Evergreen Mills | Reconductor 230kV Line #2210 from Brambleton to Evergreen Mills along with upgrading the line leads at Brambleton to achieve a summer emergency rating of 1574 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 4.2 | 2.26 | 2020-12-01 | 1/6/2021 | 6/1/2025 | 1/14/2027 |  | UC | 60 | Reconductor | No | 2020-W1-735 | Appendix A | Dominion:100
b3302 | PJM SOUTH | Dominion | VA | Cabin Run, Yardley Ridge | Reconductor 230kV Line #2213 from Cabin Run to Yardley Ridge along with upgrading the line leads at Yardley to achieve a summer emergency rating of 1574 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.75 | 1.75 | 2020-12-01 | 1/6/2021 | 6/1/2025 | 12/15/2026 | 12/15/2026 | UC | 30 | Reconductor | No | 2020-W1-134 | Appendix A | Dominion:100
b3303.1 | PJM SOUTH | Dominion | VA | Nimbus, Farmwell | Extend a new single circuit 230KV line (#9250) from Farmwell Substation to Nimbus Substation. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 6 | 5.65 | 2020-12-01 | 1/6/2021 | 6/1/2025 | 4/23/2026 |  | EP | 20 | Build | No | 2020_W1-704 | Appendix A | Dominion:100
b3303.2 | PJM SOUTH | Dominion | VA | Beaumeade | Remove Beaumeade 230kV Line #2152 line switch. | Baseline | 230 | Disconnect Switch | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.05 | 0.05 | 2020-12-01 | 1/6/2021 | 6/1/2025 | 6/1/2023 | 5/16/2023 | IS | 100 | Modify | No | 2020_W1-704 | Appendix A | Dominion:100
b3304 | PJM SOUTH | Dominion | VA | Midlothian, Trabue, Winterpock | Midlothian Area 300 MW Load Drop Relief Area Improvements | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 6.22 | 6.22 | 2020-12-01 | 1/6/2021 | 6/1/2025 | 10/30/2026 |  | EP | 20 | Modify | No | 2020_W1-860 | Appendix A | Dominion:100
b3304.1 | PJM SOUTH | Dominion | VA | Trabue | Cut 230kV Line #2066 at Trabue junction | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0 |  | 2020-12-01 | 1/6/2021 | 6/1/2025 | 10/30/2026 |  | EP | 20 | Modify | No | 2020_W1-860 | Appendix A | Dominion:100
b3304.2 | PJM SOUTH | Dominion | VA | Midlothian, Trabue, Winterpock | Reconductor idle 230kV Line #242 (radial from Midlothian to Trabue junction) to allow a minimum summer rating of 1047 MVA and connect to the section of 230kV Line #2066 between Trabue junction and Winterpock; re-number 230kV Line #242 structures to #2066; | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0 |  | 2020-12-01 | 1/6/2021 | 6/1/2025 | 10/30/2026 |  | EP | 20 | Modify | No | 2020_W1-860 | Appendix A | Dominion:100
b3304.3 | PJM SOUTH | Dominion | VA | Midlothian, Trabue, Winterpock | Use the section of idle 115kV Line #153, between Midlothian and Trabue junction to connect to the section of (former) 230kV Line #2066 between Trabue junction and Trabue to create new Midlothian-Trabue lines with new line numbers #2218 and #2219 | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0 |  | 2020-12-01 | 1/6/2021 | 6/1/2025 | 10/30/2026 |  | EP | 20 | Modify | No | 2020_W1-860 | Appendix A | Dominion:100
b3304.4 | PJM SOUTH | Dominion | VA | Midlothian | Create new line terminations at Midlothian for the new Midlothian-Trabue lines. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 2.27 |  | 2020-12-01 | 1/6/2021 | 6/1/2025 | 10/30/2026 |  | EP | 30 | Modify | No | 2020_W1-860 | Appendix A | Dominion:100
b3305 | PJM MA | BGE | MD | Pumphrey | Replace Pumphrey 230/115kV transformer | Baseline | 230/115 | Transformer | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Replacement of Pumphrey 230/115 kV transformer cancelled. No longer needed based on retool analysis performed by PJM. | Project cancelled. Cost decrease of $4.69M to RTEP. | 20230711-pjm-teac-board-whitepaper-july-2023-public.json | 2023-01-01 | 1 | 4.69 | 4.69 | 2020-12-01 | 12/1/2020 | 6/1/2025 | 6/1/2025 |  | Cancelled | 0 | Replace | No | 2020_W1-494 | Appendix A | BGE:100
b3306 | PJM MA | PENELEC | PA | Pierce Brook | Install a second 125 MVAR 345 kV shunt reactor and associated equipment at Pierce Brook Substation. Install a 345 kV breaker on the high side of the #1 345/230 kV transformer | Baseline | 345 | Reactive Device | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 8.08 | 8.08 | 2020-12-01 | 12/1/2020 | 6/1/2025 | 6/30/2027 |  | EP | 0 | Install | No | 2020_W1-855 | Appendix A | PENELEC:100
b3342 | PJM WEST | AEP | OH | Muskingum | Replace the 2156 ACSR & 2874 ACSR bus and risers with 2-bundled 2156 ACSR at Muskingum River 345 kV station to address loading issues on Muskingum-Waterford 345 kV line. | Baseline | 345 | Bus | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.53 | 0.53 | 2021-11-02 | 11/2/2021 | 6/1/2026 | 9/1/2025 | 4/25/2023 | IS | 100 | Replace | No |  | Appendix A | AEP:100
b3664 | PJM MA | PPL | PA | Juniata | Juniata: Replace the limiting 230 kV T2 transformer leads, bay conductor and bus conductor with double bundle 1590 ACSR. Replace the limiting 1200 A MODs on the Bus tie breaker with 3000 A MODs | Baseline | 500/230 | Transformer | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.68 | 0.68 | 2021-11-02 | 11/2/2021 | 6/1/2026 | 8/1/2025 | 7/21/2025 | IS | 100 | Replace | No |  | Appendix A | PPL:100
b3665 | PJM MA | PENELEC | PA | East Towanda | Replace several pieces of 1033.5 AAC substation conductor at East Towanda 230 kV Substation (on East Towanda-Canyon 230 kV Line terminal) | Baseline | 230 | Conductor | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.41 | 0.41 | 2021-11-02 | 11/2/2021 | 6/1/2026 | 5/31/2025 | 5/27/2025 | IS | 100 | Replace | No |  | Appendix A | PENELEC:100
b3666 | PJM MA | PENELEC | PA | Marshall | Marshall 230 kV Substation: Install dual reactors and expand existing ring bus | Baseline | 230 | Reactive Device | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 5.83 | 5.83 | 2021-11-02 | 11/2/2021 | 6/1/2026 | 12/31/2027 |  | EP | 3 | Install | No | 2021_1-745 | Appendix A | PENELEC:100
b3667 | PJM MA | PENELEC | PA | Pierce Brook | Pierce Brook Substation: Install second 230/115 kV transformer | Baseline | 230/115 | Transformer | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 5.07 | 5.07 | 2021-11-02 | 11/2/2021 | 6/1/2026 | 12/17/2027 |  | EP | 10 | Install | No | 2021_1-101 | Appendix A | PENELEC:100
b3668 | PJM MA | BGE | MD | Windy Edge | Upgrade Windy Edge 115 kV substation conductor to increase ratings of the Windy Edge-Chesco Park 110501 circuit. | Baseline | 115 | Conductor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Windy Edge - Chesco Park 110501 115kV circuit overloaded for N-1-1 contingency in 2026 RTEP summer case |  | 20220111-teac-appendix-february-2022-board-teac-review.json | 2022-01-01 | 1 | 0.5 | 0.5 | 2021-11-18 | 11/18/2021 | 6/1/2026 | 10/1/2025 |  | EP | 0 | Replace | No |  | Appendix A | BGE:100
b3669.1 | PJM MA | DPL | MD | Church | Replace terminal equipment (stranded bus, disconnect switch and circuit breaker) at Church substation (Townsend-Church 138 kV). | Baseline | 138 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | generation_interconnection | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:generation_interconnection | FALSE | 0 | Townsend-Church 138kV circuit overloaded for towerline contingency under Winter Generator Deliverability in 2026 RTEP winter case |  | 20220111-teac-appendix-february-2022-board-teac-review.json | 2022-01-01 | 1 | 1 | 1 | 2021-11-18 | 11/18/2021 | 12/1/2026 | 12/1/2026 |  | EP | 0 | Replace | No |  | Appendix A | DPL:100
b3669.2 | PJM MA | DPL | DE | Townsend | Replace terminal equipment (circuit breaker) at Townsend substation (Townsend-Church 138 kV). | Baseline | 138 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | generation_interconnection | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:generation_interconnection | FALSE | 0 | Townsend-Church 138kV circuit overloaded for towerline contingency under Winter Generator Deliverability in 2026 RTEP winter case |  | 20220111-teac-appendix-february-2022-board-teac-review.json | 2022-01-01 | 1 | 0.45 | 0.45 | 2021-11-18 | 11/18/2021 | 12/1/2026 | 12/1/2026 |  | EP | 0 | Replace | No |  | Appendix A | DPL:100
b3670 | PJM MA | DPL | MD | Loretto/Fruitland | Upgrade terminal equipment on the Loretto-Fruitland 69 kV circuit: Replace the 477 ACSR stranded bus on the 6711 line terminal inside Loretto substation and the 500 SDCU stranded bus on the 6711 line terminal inside Fruitland substation with 954 ACSR conductor. | Baseline | 69 | Bus | Baseline Load Growth Deliverability & Reliability | generation_interconnection | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:generation_interconnection | FALSE | 0 | Loretto - Fruitland 69kV circuit overloaded for line fault stuck breaker contingency under Summer Generator Deliverability in 2026 RTEP summer case |  | 20220111-teac-appendix-february-2022-board-teac-review.json | 2022-01-01 | 1 | 0.8 | 0.8 | 2021-11-18 | 11/18/2021 | 6/1/2026 | 6/1/2026 |  | EP | 0 | Replace | No |  | Appendix A | DPL:100
b3672 | PJM MA | PENELEC | PA | East Towanda/North Meshoppen | East Towanda-North Meshoppen 115 kV line: Rebuild 2.5 miles of 636 ACSR with 1113 ACSS conductor using single circuit construction. Upgrade all terminal equipment to the rating of 1113 ACSS. | Baseline | 115 |  | Baseline Load Growth Deliverability & Reliability | generation_interconnection | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:generation_interconnection | FALSE | 0 | East Towanda – North Meshoppen 115kV overloaded for N-1 contingency under Summer Generator Deliverability in 2026 RTEP summer case |  | 20220111-teac-appendix-february-2022-board-teac-review.json | 2022-01-01 | 1 | 6.66 | 6.66 | 2021-11-18 | 11/18/2021 | 6/1/2026 | 12/31/2025 | 12/19/2025 | IS | 100 | Rebuild | No |  | Appendix A | PENELEC:100
b3677 | PJM WEST | ComEd | IL | LaSalle-Mazon | Rebuild a 13 mile section of 138 kV line 0108 between LaSalle and Mazon with 1113 ACSR or higher rated conductor. The 13 mile portion of line 7713 from Oglesby (future Corbin) to Mazon that shares double circuit towers with line 0108 will also be reconductored due to the rebuild. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | LaSalle-Mazon 138kV line overloaded for N-2 outage under Generator Deliverability in 2026 Light Load RTEP case (FG: GD-LL36) ¦ In 2026 RTEP light load case, LaSalle-Mazon 138 kV line overloaded for an N-2 outage. |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json | 2022-01-01 | 2 | 54.4 | 42.06 | 2021-11-19 | 11/19/2021 | 11/1/2026 | 6/1/2025 |  | IS | 100 | Rebuild | No |  | Appendix A | ComEd:100
b3680 | PJM WEST | ATSI | OH | Ashtabula - Sanborn Q3 138 kV line | At Sanborn, replace limiting substation conductors on Ashtabula 138 kV exit to make transmission line conductor the limiting element. | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Ashtabula to Sanborn Q3 138kV line overloaded due to N-1-1 in 2026 Summer RTEP case (FG: N2-ST3) |  | 20220111-teac-appendix-february-2022-board-teac-review.json | 2022-01-01 | 1 | 0.3 | 0.3 | 2021-11-19 | 11/19/2021 | 6/1/2026 | 11/4/2022 | 11/2/2022 | IS | 100 | Replace | No |  | Appendix A | ATSI:100
b3681 | PJM WEST | APS | PA | Shingletown 230 kV substation | Upgrade the Shingletown #82 230-46 kV transformer circuit by installing a 230 kV breaker and disconnect switches, removing existing 230 kV switches, replacing 46 kV disconnect switches, replacing limiting substation conductor, and installing/replacing relays. | Baseline | 230 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.66 | 1.66 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 5/13/2026 |  | UC | 75 | Install | No | 2021_1-919 | Appendix A | APS:100
b3682 | PJM WEST | ATSI | OH | Hayes 345 substation | Install a second 345/138 kV transformer at Hayes, 448 MVA nameplate rating. Add one 345 kV circuit breaker (3000A) to provide transformer high-side connection between breaker B-18 and the new breaker. Connect the new transformer low side to the 138 kV bus. Add one 138 kV circuit breaker (3000A) at Hayes 138 kV substation between B-42 and the new breaker. Relocate the existing 138 kV No. 1 capacitor bank between B-42 and the new breaker. Protection per FE standard. | Baseline | 345 | Transformer | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 7.59 | 7.59 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 6/1/2026 |  | UC | 2 | Install | No | 2021_1-549 | Appendix A | ATSI:100
b3683 | PJM WEST | APS | WV | Ridgley to Messick 138 kV | Reconductor the existing 556.5 ACSR line segments (3.49 miles) on the Messick Road-Ridgeley WC4 138 kV line with 954 45/7 ACSR to achieve 308/376 MVA SN/SE and 349/445 MVA WN/WE ratings. Replace the remote end equipment for the Messick Road-Ridgeley WC4 138 kV line. The total length of the line is 5.02 miles. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Messick Road to Ridgeley 138kV line overloaded due to multiple breaker contingencies under Generation Deliverability in 2026 Summer RTEP case (FG: GD-S446 and GD-S448) ¦ In 2026 RTEP summer case, Messick Road-Ridgeley 138 kV line overloaded for multiple N-2 outage combinations. |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json | 2022-01-01 | 2 | 11.2 | 11.2 | 2021-12-17 | 12/17/2021 | 6/1/2026 | 6/30/2028 |  | EP | 10 | Reconductor | No |  | Appendix A | APS:100
b3684 | PJM SOUTH | Dominion | NC | Earleys, Kelford | Rebuild 12.4 miles of 115 line #126 segment from Earleys to Kelford with a summer emergency rating of 262 MVA. Replace structures as needed to support the new conductor. Upgrade breaker switch 13668 at Earleys from 1200 A to 2000 A. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | 115kV Line #126 segment from Earleys to Kelford overloaded for a tower contingency under Generator Deliverability (FG: GD-S710) ¦ In 2026 RTEP summer case, 115 kV line No. 126 segment from Earleys to Kelford overloaded for an N-2 outage. |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json | 2022-01-01 | 2 | 50.7 | 18.75 | 2021-11-18 | 11/18/2021 | 6/1/2026 | 3/1/2027 |  | UC | 30 | Rebuild | No |  | Appendix A | Dominion:100
b3687 | PJM SOUTH | Dominion | VA | Bristers, Ox | Rebuild approximately 15.1-mile-long line segment between 115 kV line #183 Bristers and Minnieville D.P. with 2-768 ACSS and 4000 A supporting equipment from Bristers to Ox to allow for future 230 kV capability of 115 kV line #183. The continuous summer normal rating will be 523 MVA from Ox-Minnieville. The continuous summer normal rating will be 786 MVA from Minnieville-Bristers. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | generation_interconnection | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:generation_interconnection | FALSE | 0 | Bristers 230/115kV transformer overloaded for single contingency under Generator Deliverability and Dominion Stress Case; 115kV Line #183 Sowego–Independent Hill overloaded for multiple contingencies under GD, N-1, N-1-1, and Dominion Stress Case ¦ In 2026 RTEP summer case, Bristers 230/115 kV transformer overloaded for N-1 outage under generator deliverability study and Dominion's Stress Case (FERC 715). 115 kV line No. 183 (Sowego-Independent Hill) overloaded for N-1 and N-2 outages and multip |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json | 2022-01-01 | 2 | 30 | 30 | 2021-11-18 | 11/18/2021 | 6/1/2026 | 12/17/2025 | 12/13/2025 | IS | 50 | Rebuild | No |  | Appendix A | Dominion:100
b3688 | PJM MA | DPL | DE | Todd | Replace the 4/0 SDCU stranded bus with 954 ACSR and a 600 A disconnect switch with a 1200 A disconnect switch on the 6716 line terminal inside Todd substation (on the Preston-Todd 69 kV circuit). | Baseline | 69 | Disconnect Switch | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.75 | 0.75 | 2021-12-20 | 12/20/2021 | 6/1/2026 | 6/1/2025 | 1/29/2024 | IS | 100 | Replace | No |  | Appendix A | DPL:100
b3689.1 | PJM SOUTH | Dominion | VA | Remington CT, Elk Run, Gainesville | Reconductor approximately 24.42 miles of 230 kV line #2114 Remington CT-Elk Run-Gainesville to achieve a summer rating of 1574 MVA by fully reconductoring the line and upgrading the wave trap and substation conductor at Remington CT and Gainesville. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | 230kV Line #2114 Remington CT – Gainesville overloaded for tower contingency under N-1 and single & tower contingencies under Generator Deliverability in 2026 RTEP summer case ¦ In 2026 RTEP summer case, Remington CT-Gainesville 230 kV line (No. 2114) overloaded for multiple N-1 and N-2 outages. |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json | 2022-01-01 | 2 | 52 | 28.99 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 6/1/2025 | 5/19/2025 | IS | 100 | Reconductor | No | Proposal #2021_1-445 | Appendix A | Dominion:100
b3689.2 | PJM SOUTH | Dominion | VA | Brambleton | Replace 230 kV breakers SC102, H302, H402 and 218302 at Brambleton substation with 4000A 80 kA breakers and associated equipment including breaker leads as necessary to address breaker duty issues identified in short circuit analysis. | Baseline | 230 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | 230kV Line #2114 Remington CT – Gainesville overloaded for tower contingency under N-1 and single & tower contingencies under Generator Deliverability in 2026 RTEP summer case ¦ In 2026 RTEP summer case, Remington CT-Gainesville 230 kV line (No. 2114) overloaded for multiple N-1 and N-2 outages. |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json | 2022-01-01 | 2 | 4.88 | 1.69 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 3/31/2027 |  | UC | 40 | Replace | No | Proposal #2021_1-445 | Appendix A | Dominion:100
b3690 | PJM SOUTH | Dominion | VA | Cub Run, Walney | Reconductor approximately 1.07 miles of 230 kV line #2008 segment from Cub Run-Walney to achieve a summer rating of 1574 MVA. Replace line switch 200826 with a 4000A switch. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | 230kV Line #2008 Cub Run to Walney overloaded for a breaker contingency under N-1 in 2026 RTEP summer case |  | 20220111-teac-appendix-february-2022-board-teac-review.json | 2022-01-01 | 1 | 2.03 | 1.93 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 11/15/2024 |  | IS | 100 | Reconductor | No | Proposal #2021_1-600 | Appendix A | Dominion:100
b3691 | PJM SOUTH | Dominion | NC | Lakeview, Carolina | Reconductor approximately 1.4 miles of 230 kV line #2141 from Lakeview-Carolina to achieve a summer rating of 1047 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | generation_interconnection | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:generation_interconnection | FALSE | 0 | 230kV Line #2141 Lakeview to Carolina overloaded for a single contingency under Generator Deliverability in 2026 RTEP summer case |  | 20220111-teac-appendix-february-2022-board-teac-review.json | 2022-01-01 | 1 | 1.19 | 1.18 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 5/31/2022 | 5/31/2022 | IS | 100 | Reconductor | No | Proposal #2021_1-414 | Appendix A | Dominion:100
b3692.2 | PJM SOUTH | Dominion | VA | Elmont | Switch to 5/2 H-frame structures and install approximately 27.7 miles of 230kV transmission line (but not be terminated) from Elmont to Chickahominy. String up approximately 8 miles of new 230kV conductor on the open arms of the structures of 230kV Line #2075 that runs parallel to 500kV Line #557. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | 500kV Line #557 Elmont to Chickahominy constructed in 1971 with ACAR conductor and 5-series Corten towers that need to be rebuilt to current standards based on Dominion's End-of-Life Criteria ¦ Elmont-Chickahominy 500 kV line (No. 557) constructed in 1971 with 2500 ACAR conductor and 5-series Corten towers. Needs to be rebuilt to current standards based on Dominion's End-of-Life Criteria. ¦ Scope and cost change: structure changed from lattice to H-frame due to ~8 miles of heavy swamp terrain re |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ dec2022_projects.json | 2022-01-01 ¦ 2025-07-01 ¦ 2025-01-01 | 4 | 74.5 | 74.5 | 2025-05-06 | 5/6/2025 | 6/1/2026 | 6/30/2028 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3693 | PJM SOUTH | Dominion | VA | Lexington, Bath County | Expand substation and install approximately 294 MVAR cap bank at 500 kV Lexington substation along with a 500 kV breaker. Adjust the tap positions associated with the two 230/69 kV transformers at Harrisonburg to neutral position and lock them. | Baseline | 500 | Capacitor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Voltage magnitude and voltage drop violations at 500kV buses of Lexington and Bath County for single and breaker contingencies under N-1 in 2026 RTEP light load case |  | 20220111-teac-appendix-february-2022-board-teac-review.json | 2022-01-01 | 1 | 5.86 | 5.86 | 2021-11-30 | 11/30/2021 | 11/1/2026 | 11/1/2026 |  | EP | 20 | Install | No | 2021_1-722 | Appendix A | Dominion:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3694.1 | PJM SOUTH | Dominion | VA | Aquia Harbor, Possum Point | Convert line #29 Aquia Harbor to Possum Point to 230 kV (Extended line #2104) and swap line #2104 and converted line #29 at Aquia Harbor backbone termination. Upgrade terminal equipment at Possum Point to terminate converted line 29 (now extended line #2104). (Line #29 from Fredericksburg to Aquia Harbor is being rebuilt under baseline b2981 to 230kV standards.) | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple Generator Deliverability violations and Dominion stress case violations at Fredericksburg (Line #2104), Carson (Tx#2 and Line #249), and Hopewell (Lines #211 and #228) in 2026 RTEP summer case ¦ In 2026 RTEP summer case: Fredericksburg area — Cranes Corner-Stafford 230 kV line overloaded for N-1 and N-2 and Dominion stress case with 307 MW load loss for N-1; Carson area — Carson 500/230 kV transformer No. 2 overloaded for N-2 and Carson-Chaparral 230 kV line overloaded for N-1; Hopewell |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2022-01-01 ¦ 2024-01-01 | 3 | 8.8 | 9.39 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 9/28/2029 |  | UC | 30 | Modify | No | Proposal #2021_1-224 | Appendix A | Dominion:100
b3694.10 | PJM SOUTH | Dominion | VA | Chesterfield, Hopewell | Reconductor approximately 2.9 miles of 230 kV line #211 Chesterfield-Hopewell to achieve a minimum summer emergency rating of 1046 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple Generator Deliverability violations and Dominion stress case violations at Fredericksburg (Line #2104), Carson (Tx#2 and Line #249), and Hopewell (Lines #211 and #228) in 2026 RTEP summer case ¦ In 2026 RTEP summer case: Fredericksburg area — Cranes Corner-Stafford 230 kV line overloaded for N-1 and N-2 and Dominion stress case with 307 MW load loss for N-1; Carson area — Carson 500/230 kV transformer No. 2 overloaded for N-2 and Carson-Chaparral 230 kV line overloaded for N-1; Hopewell |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2022-01-01 ¦ 2024-01-01 | 3 | 18 | 4.91 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 5/30/2025 | 5/30/2025 | IS | 100 | Reconductor | No | Proposal #2021_1-224 | Appendix A | Dominion:100
b3694.11 | PJM SOUTH | Dominion | VA | Chesterfield, Hopewell | Reconductor approximately 2.9 miles of 230 kV line #228 Chesterfield-Hopewell to achieve a minimum summer emergency rating of 1046 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple Generator Deliverability violations and Dominion stress case violations at Fredericksburg (Line #2104), Carson (Tx#2 and Line #249), and Hopewell (Lines #211 and #228) in 2026 RTEP summer case ¦ In 2026 RTEP summer case: Fredericksburg area — Cranes Corner-Stafford 230 kV line overloaded for N-1 and N-2 and Dominion stress case with 307 MW load loss for N-1; Carson area — Carson 500/230 kV transformer No. 2 overloaded for N-2 and Carson-Chaparral 230 kV line overloaded for N-1; Hopewell |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2022-01-01 ¦ 2024-01-01 | 3 | 18 | 4.91 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 5/30/2025 | 5/30/2025 | IS | 100 | Reconductor | No | Proposal #2021_1-224 | Appendix A | Dominion:100
b3694.12 | PJM SOUTH | Dominion | VA | Chesterfield | Upgrade equipment at Chesterfield substation to not limit ratings on lines 211 and 228. | Baseline | 230 | Disconnect Switch | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple Generator Deliverability violations and Dominion stress case violations at Fredericksburg (Line #2104), Carson (Tx#2 and Line #249), and Hopewell (Lines #211 and #228) in 2026 RTEP summer case ¦ In 2026 RTEP summer case: Fredericksburg area — Cranes Corner-Stafford 230 kV line overloaded for N-1 and N-2 and Dominion stress case with 307 MW load loss for N-1; Carson area — Carson 500/230 kV transformer No. 2 overloaded for N-2 and Carson-Chaparral 230 kV line overloaded for N-1; Hopewell |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2022-01-01 ¦ 2024-01-01 | 3 | 18 | 0.76 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 5/30/2025 | 5/30/2025 | IS | 100 | Upgrade | No | Proposal #2021_1-224 | Appendix A | Dominion:100
b3694.13 | PJM SOUTH | Dominion | VA | Hopewell | Upgrade equipment at Hopewell substation to not limit ratings on lines 211 and 228. | Baseline | 230 | Disconnect Switch | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple Generator Deliverability violations and Dominion stress case violations at Fredericksburg (Line #2104), Carson (Tx#2 and Line #249), and Hopewell (Lines #211 and #228) in 2026 RTEP summer case ¦ In 2026 RTEP summer case: Fredericksburg area — Cranes Corner-Stafford 230 kV line overloaded for N-1 and N-2 and Dominion stress case with 307 MW load loss for N-1; Carson area — Carson 500/230 kV transformer No. 2 overloaded for N-2 and Carson-Chaparral 230 kV line overloaded for N-1; Hopewell |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2022-01-01 ¦ 2024-01-01 | 3 | 18 | 1.71 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 5/30/2025 | 5/30/2025 | IS | 100 | Upgrade | No | Proposal #2021_1-224 | Appendix A | Dominion:100
b3694.2 | PJM SOUTH | Dominion | VA | Aquia Harbor | Upgrade Aquia Harbor terminal equipment to not limit 230 kV line #9281 conductor rating. | Baseline | 230 | Wave Trap | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple Generator Deliverability violations and Dominion stress case violations at Fredericksburg (Line #2104), Carson (Tx#2 and Line #249), and Hopewell (Lines #211 and #228) in 2026 RTEP summer case ¦ In 2026 RTEP summer case: Fredericksburg area — Cranes Corner-Stafford 230 kV line overloaded for N-1 and N-2 and Dominion stress case with 307 MW load loss for N-1; Carson area — Carson 500/230 kV transformer No. 2 overloaded for N-2 and Carson-Chaparral 230 kV line overloaded for N-1; Hopewell |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2022-01-01 ¦ 2024-01-01 | 3 | 0.8 | 0.63 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 6/16/2028 |  | UC | 30 | Upgrade | No | Proposal #2021_1-224 | Appendix A | Dominion:100
b3694.3 | PJM SOUTH | Dominion | VA | Fredericksburg | Upgrade Fredericksburg terminal equipment by rearranging 230 kV bus configuration to terminate converted line 29 (now becoming 9281). The project will add a new breaker at the 230 kV bay and reconfigure line termination of 230 kV lines #2157, #2090 and #2083. | Baseline | 230 | Disconnect Switch | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple Generator Deliverability violations and Dominion stress case violations at Fredericksburg (Line #2104), Carson (Tx#2 and Line #249), and Hopewell (Lines #211 and #228) in 2026 RTEP summer case ¦ In 2026 RTEP summer case: Fredericksburg area — Cranes Corner-Stafford 230 kV line overloaded for N-1 and N-2 and Dominion stress case with 307 MW load loss for N-1; Carson area — Carson 500/230 kV transformer No. 2 overloaded for N-2 and Carson-Chaparral 230 kV line overloaded for N-1; Hopewell |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2022-01-01 ¦ 2024-01-01 | 3 | 5 | 2.72 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 2/16/2028 |  | EP | 20 | Upgrade | No | Proposal #2021_1-224 | Appendix A | Dominion:100
b3694.4 | PJM SOUTH | Dominion | VA | Cranes Corner, Stafford | Reconductor/rebuild approximately 7.6 miles of 230 kV line #2104 Cranes Corner-Stafford to achieve a summer rating of 1047 MVA(1). Reconductor/rebuild approximately 0.34 miles of 230 kV line #2104 Stafford-Aquia Harbor to achieve a summer rating of 1047 MVA. Upgrade terminal equipment at Cranes Corner to not limit the new conductor rating. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple Generator Deliverability violations and Dominion stress case violations at Fredericksburg (Line #2104), Carson (Tx#2 and Line #249), and Hopewell (Lines #211 and #228) in 2026 RTEP summer case ¦ In 2026 RTEP summer case: Fredericksburg area — Cranes Corner-Stafford 230 kV line overloaded for N-1 and N-2 and Dominion stress case with 307 MW load loss for N-1; Carson area — Carson 500/230 kV transformer No. 2 overloaded for N-2 and Carson-Chaparral 230 kV line overloaded for N-1; Hopewell |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2022-01-01 ¦ 2024-01-01 | 3 | 5.4 | 19.6 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 4/17/2026 |  | EP | 20 | Reconductor | No | 2021_1-224 | Appendix A | Dominion:100
b3694.5 | PJM SOUTH | Dominion | VA | Ladysmith CT | Upgrade wave trap and line leads at 230 kV line #2090 Ladysmith CT terminal to achieve 4000A rating. | Baseline | 230 | Wave Trap | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple Generator Deliverability violations and Dominion stress case violations at Fredericksburg (Line #2104), Carson (Tx#2 and Line #249), and Hopewell (Lines #211 and #228) in 2026 RTEP summer case ¦ In 2026 RTEP summer case: Fredericksburg area — Cranes Corner-Stafford 230 kV line overloaded for N-1 and N-2 and Dominion stress case with 307 MW load loss for N-1; Carson area — Carson 500/230 kV transformer No. 2 overloaded for N-2 and Carson-Chaparral 230 kV line overloaded for N-1; Hopewell |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2022-01-01 ¦ 2024-01-01 | 3 | 0.15 | 0.15 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 12/15/2027 |  | EP | 20 | Upgrade | No | 2021_1-224 | Appendix A | Dominion:100
b3694.6 | PJM SOUTH | Dominion | VA | Fuller Road, Quantico | Upgrade Fuller Road substation to feed Quantico substation via 115 kV radial line. Install four-breaker ring and break 230 kV line #252 into two new lines: 1) #252 between Aquia Harbor to Fuller Road and 2) #9282 between Fuller Road and Possum Point. Install a 230/115 kV transformer which will serve Quantico substation. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple Generator Deliverability violations and Dominion stress case violations at Fredericksburg (Line #2104), Carson (Tx#2 and Line #249), and Hopewell (Lines #211 and #228) in 2026 RTEP summer case ¦ In 2026 RTEP summer case: Fredericksburg area — Cranes Corner-Stafford 230 kV line overloaded for N-1 and N-2 and Dominion stress case with 307 MW load loss for N-1; Carson area — Carson 500/230 kV transformer No. 2 overloaded for N-2 and Carson-Chaparral 230 kV line overloaded for N-1; Hopewell |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2022-01-01 ¦ 2024-01-01 | 3 | 44 | 24.16 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 1/2/2029 |  | EP | 20 | Upgrade | No | 2021_1-224 | Appendix A | Dominion:100
b3694.7 | PJM SOUTH | Dominion | VA | Carson | Energize in-service spare 500/230 kV Carson Tx#1. | Baseline | 500/230 | Transformer | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple Generator Deliverability violations and Dominion stress case violations at Fredericksburg (Line #2104), Carson (Tx#2 and Line #249), and Hopewell (Lines #211 and #228) in 2026 RTEP summer case ¦ In 2026 RTEP summer case: Fredericksburg area — Cranes Corner-Stafford 230 kV line overloaded for N-1 and N-2 and Dominion stress case with 307 MW load loss for N-1; Carson area — Carson 500/230 kV transformer No. 2 overloaded for N-2 and Carson-Chaparral 230 kV line overloaded for N-1; Hopewell |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2022-01-01 ¦ 2024-01-01 | 3 | 0 | 0 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 6/1/2025 | 5/3/2025 | IS | 100 | Provide | No | Proposal #2021_1-224 | Appendix A | Dominion:100
b3694.8 | PJM SOUTH | Dominion | VA | Carson, Chaparral, Locks | Partial wreck and rebuild 10.34 miles of 230 kV line #249 Carson-Locks to achieve a minimum summer emergency rating of 1047 MVA. Upgrade terminal equipment at Carson and Locks to not limit the new conductor rating. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple Generator Deliverability violations and Dominion stress case violations at Fredericksburg (Line #2104), Carson (Tx#2 and Line #249), and Hopewell (Lines #211 and #228) in 2026 RTEP summer case ¦ In 2026 RTEP summer case: Fredericksburg area — Cranes Corner-Stafford 230 kV line overloaded for N-1 and N-2 and Dominion stress case with 307 MW load loss for N-1; Carson area — Carson 500/230 kV transformer No. 2 overloaded for N-2 and Carson-Chaparral 230 kV line overloaded for N-1; Hopewell |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2022-01-01 ¦ 2024-01-01 | 3 | 26.3 | 25.6 | 2021-11-30 | 1/9/2024 | 6/1/2026 | 6/1/2025 | 5/3/2025 | IS | 100 | Rebuild | No | Proposal #2021_1-224, only CRL was accepted in 202 | Appendix A | Dominion:100 |  |  | 6/30/2025
b3694.9 | PJM SOUTH | Dominion | VA | Locks, Harrowgate | Wreck and rebuild 5.4 miles of 115 kV line #100 Locks-Harrowgate to achieve a minimum summer emergency rating of 393 MVA. Upgrade terminal equipment at Locks and Harrowgate to not limit the new conductor rating and perform line #100 Chesterfield terminal relay work. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple Generator Deliverability violations and Dominion stress case violations at Fredericksburg (Line #2104), Carson (Tx#2 and Line #249), and Hopewell (Lines #211 and #228) in 2026 RTEP summer case ¦ In 2026 RTEP summer case: Fredericksburg area — Cranes Corner-Stafford 230 kV line overloaded for N-1 and N-2 and Dominion stress case with 307 MW load loss for N-1; Carson area — Carson 500/230 kV transformer No. 2 overloaded for N-2 and Carson-Chaparral 230 kV line overloaded for N-1; Hopewell |  | 20220111-teac-appendix-february-2022-board-teac-review.json ¦ 20220208-pjm-teac-board-whitepaper-february-2022.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2022-01-01 ¦ 2024-01-01 | 3 | 9.1 | 9.1 | 2021-11-30 | 11/30/2021 | 6/1/2026 | 2/7/2025 |  | IS | 100 | Rebuild | No | Proposal #2021_1-224 | Appendix A | Dominion:100
b3708 | Not Specified | PENELEC | PA | Shawville | Replace the Shawville 230/115/17.2 kV transformer with a new Shawville 230/115 kV transformer and associated facilities. Replace the plant’s No. 2B 115/17.2 kV transformer with a larger 230/17.2 kV transformer. | Baseline | 230/115/17.2 | Transformer | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 8.78 | 8.78 | 2022-03-08 | 3/8/2022 | 6/1/2026 | 12/31/2026 |  | EP | 15 | Replace | No | 2021_1-100 | Appendix A | PENELEC:100
b3711 | PJM WEST | ComEd | IL | Dresden | Install 345 kV bus tie 5-20 circuit breaker in the ring at Dresden station in series with existing bus tie 5-6. | Baseline | 345 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 4.6 | 4.26 | 2022-04-12 | 4/12/2022 | 12/1/2026 | 12/31/2025 | 11/14/2025 | IS | 100 | Install | No | 2021_2-408 | Appendix A | ComEd:100
b3715.1 | PJM MA | PPL | PA | Williams Grove | At the existing PPL Williams Grove substation, install a new 300 MVA 230/115 kV transformer. | Baseline | 230/115 | Transformer | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 6.3 | 6.3 | 2022-05-10 | 5/10/2022 | 6/1/2026 | 5/6/2026 |  | UC | 50 | Install | No | 2021_1-99 | Appendix A | ME:100
b3715.2 | PJM MA | PPL | PA | Williams Grove-Allen | Construct a new ~3.4 mile 115 kV single circuit transmission line from Williams Grove to Allen substation. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 5.11 | 5.11 | 2022-05-10 | 5/10/2022 | 6/1/2026 | 3/6/2026 |  | UC | 50 | Build | No | 2021_1-99 | Appendix A | ME:100
b3715.3 | PJM MA | ME | PA | Allen | Install a new Allen four breaker ring bus within the existing MetEd Allen substation. Terminate the Round Top-Allen and the Allen-PPGI (PPG Industries) 115 kV lines into the new switchyard. | Baseline | 115 | Ring Bus | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 11.73 | 6.41 | 2022-05-10 | 5/10/2022 | 6/1/2026 | 6/1/2026 |  | UC | 50 | Modify | No | 2021_1-99 | Appendix A | ME:100
b3718.1 | PJM SOUTH | Dominion | VA | Wishing Star | Install one 500/230kV 1440MVA transformer at a new substation called Wishing Star. Cut and extend 500 kV Line #546 (Brambleton-Mosby) and 500 kV Line #590 (Brambleton-Mosby) to the proposed Wishing Star substation. Lines to terminate in a 500 kV breaker and a half configuration. | Baseline | 500/230 | Transformer | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Dominion zone experiencing load growth in the Data Center Alley area around Dulles airport. Forecasted data center additions for the 2022 Load Forecast provided by Dominion and NOVEC were noticeably higher than in the prior year. Numerous reliability violations (thermal overloads and load loss) observed in the 2024 and 2025 time frames. ¦ Driven by unprecedented data center load growth in northern Virginia. PJM directed as an immediate need project in July 2022 to enable integration of forecaste |  | 20221004-pjm-teac-board-whitepaper-october-2022.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json | 2022-01-01 ¦ 2023-12-08 | 2 | 342.3 | 111.28 | 2022-09-06 | 9/6/2022 | 6/1/2025 | 4/30/2026 |  | UC | 50 | Install | Yes |  | Appendix A | Dominion:100
b3718.10 | PJM SOUTH | Dominion | VA | Sojourner, Mars | Reconductor ~1.61 miles of 230 kV line #9349 (Sojourner-Mars) to achieve a summer rating of 1574 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Dominion zone experiencing load growth in the Data Center Alley area around Dulles airport. Forecasted data center additions for the 2022 Load Forecast provided by Dominion and NOVEC were noticeably higher than in the prior year. Numerous reliability violations (thermal overloads and load loss) observed in the 2024 and 2025 time frames. ¦ Driven by unprecedented data center load growth in northern Virginia. PJM directed as an immediate need project in July 2022 to enable integration of forecaste |  | 20221004-pjm-teac-board-whitepaper-october-2022.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json | 2022-01-01 ¦ 2023-12-08 | 2 | 1.4 | 1.43 | 2022-09-06 | 9/6/2022 | 6/1/2025 | 6/1/2025 | 1/29/2024 | IS | 100 | Reconductor | Yes |  | Appendix A | Dominion:100
b3718.11 | PJM SOUTH | Dominion | VA | Loudoun, Mosby | Upgrade 4-500 kV breakers (total) to 63kA on either end of 500 kV Line #502 (Loudoun-Mosby) | Baseline | 500 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Dominion zone experiencing load growth in the Data Center Alley area around Dulles airport. Forecasted data center additions for the 2022 Load Forecast provided by Dominion and NOVEC were noticeably higher than in the prior year. Numerous reliability violations (thermal overloads and load loss) observed in the 2024 and 2025 time frames. ¦ Driven by unprecedented data center load growth in northern Virginia. PJM directed as an immediate need project in July 2022 to enable integration of forecaste |  | 20221004-pjm-teac-board-whitepaper-october-2022.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json | 2022-01-01 ¦ 2023-12-08 | 2 | 0 | 6.27 | 2022-09-06 | 9/6/2022 | 6/1/2025 | 6/30/2028 |  | EP | 20 | Reconductor | Yes |  | Appendix A | Dominion:100
b3718.12 | PJM SOUTH | Dominion | VA | Loudoun, Mosby | Upgrade 4-500 kV breakers (total) to 63 kA on either end of 500 kV Line #584 (Loudoun-Mosby) | Baseline | 500 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Dominion zone experiencing load growth in the Data Center Alley area around Dulles airport. Forecasted data center additions for the 2022 Load Forecast provided by Dominion and NOVEC were noticeably higher than in the prior year. Numerous reliability violations (thermal overloads and load loss) observed in the 2024 and 2025 time frames. ¦ Driven by unprecedented data center load growth in northern Virginia. PJM directed as an immediate need project in July 2022 to enable integration of forecaste |  | 20221004-pjm-teac-board-whitepaper-october-2022.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json | 2022-01-01 ¦ 2023-12-08 | 2 | 0 | 6.38 | 2022-09-06 | 9/6/2022 | 6/1/2025 | 6/30/2028 |  | EP | 10 | Reconductor | Yes |  | Appendix A | Dominion:100
b3718.13 | PJM SOUTH | Dominion | VA | Sterling Park, Dranesville | Cut and loop 230 kV Line #2079 (Sterling Park-Dranesville) into Davis Drive substation and install two GIS 230 kV breakers. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Dominion zone experiencing load growth in the Data Center Alley area around Dulles airport. Forecasted data center additions for the 2022 Load Forecast provided by Dominion and NOVEC were noticeably higher than in the prior year. Numerous reliability violations (thermal overloads and load loss) observed in the 2024 and 2025 time frames. ¦ Driven by unprecedented data center load growth in northern Virginia. PJM directed as an immediate need project in July 2022 to enable integration of forecaste |  | 20221004-pjm-teac-board-whitepaper-october-2022.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json | 2022-01-01 ¦ 2023-12-08 | 2 | 0 | 15 | 2022-09-06 | 9/6/2022 | 6/1/2025 | 11/30/2026 |  | EP | 0 | Modify | Yes |  | Appendix A | Dominion:100
b3718.14 | PJM SOUTH | Dominion | VA | Wishing Star, Mars | Construct a new 230 kV transmission line for ~3.5 miles along with substation upgrades at Wishing Star and Mars. New right-of-way will be needed and will share same structures with the 500 kV line. New conductor to have a minimum summer normal rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Dominion zone experiencing load growth in the Data Center Alley area around Dulles airport. Forecasted data center additions for the 2022 Load Forecast provided by Dominion and NOVEC were noticeably higher than in the prior year. Numerous reliability violations (thermal overloads and load loss) observed in the 2024 and 2025 time frames. ¦ Driven by unprecedented data center load growth in northern Virginia. PJM directed as an immediate need project in July 2022 to enable integration of forecaste |  | 20221004-pjm-teac-board-whitepaper-october-2022.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json | 2022-01-01 ¦ 2023-12-08 | 2 | 40 | 78.68 | 2022-09-06 | 9/6/2022 | 6/1/2025 | 12/19/2025 |  | UC | 50 | Construct | Yes |  | Appendix A | Dominion:100
b3718.2 | PJM SOUTH | Dominion | VA | Mars | Install one 500/230 kV 1440 MVA transformer at a new substation called Mars near Dulles International Airport. | Baseline | 500/230 | Transformer | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Dominion zone experiencing load growth in the Data Center Alley area around Dulles airport. Forecasted data center additions for the 2022 Load Forecast provided by Dominion and NOVEC were noticeably higher than in the prior year. Numerous reliability violations (thermal overloads and load loss) observed in the 2024 and 2025 time frames. ¦ Driven by unprecedented data center load growth in northern Virginia. PJM directed as an immediate need project in July 2022 to enable integration of forecaste |  | 20221004-pjm-teac-board-whitepaper-october-2022.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json | 2022-01-01 ¦ 2023-12-08 | 2 | 290 | 114.04 | 2022-09-06 | 9/6/2022 | 6/1/2025 | 4/30/2026 |  | UC | 50 | Install | Yes |  | Appendix A | Dominion:100
b3718.3 | PJM SOUTH | Dominion | VA | Wishing Star, Mars | Construct a new 500 kV transmission line for ~ 3.5 miles along with substation upgrades at Wishing Star and Mars. New right-of-way will be needed and will share same structures with the line. New conductor to have a minimum summer normal rating of 4357 MVA. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Dominion zone experiencing load growth in the Data Center Alley area around Dulles airport. Forecasted data center additions for the 2022 Load Forecast provided by Dominion and NOVEC were noticeably higher than in the prior year. Numerous reliability violations (thermal overloads and load loss) observed in the 2024 and 2025 time frames. ¦ Driven by unprecedented data center load growth in northern Virginia. PJM directed as an immediate need project in July 2022 to enable integration of forecaste |  | 20221004-pjm-teac-board-whitepaper-october-2022.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json | 2022-01-01 ¦ 2023-12-08 | 2 | 40 | 267 | 2022-09-06 | 9/6/2022 | 6/1/2025 | 2/28/2026 |  | UC | 50 | Construct | Yes |  | Appendix A | APS:9.04,Dominion:90.96 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3718.4 | PJM SOUTH | Dominion | VA | Buttermilk, Roundtable | Reconductor ~0.62 miles of 230 kV line #2214 (Buttermilk-Roundtable) to achieve a summer rating of 1574 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Dominion zone experiencing load growth in the Data Center Alley area around Dulles airport. Forecasted data center additions for the 2022 Load Forecast provided by Dominion and NOVEC were noticeably higher than in the prior year. Numerous reliability violations (thermal overloads and load loss) observed in the 2024 and 2025 time frames. ¦ Driven by unprecedented data center load growth in northern Virginia. PJM directed as an immediate need project in July 2022 to enable integration of forecaste |  | 20221004-pjm-teac-board-whitepaper-october-2022.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json | 2022-01-01 ¦ 2023-12-08 | 2 | 4.8 | 4.79 | 2022-09-06 | 9/6/2022 | 6/1/2025 | 6/1/2025 |  | UC | 100 | Reconductor | Yes |  | Appendix A | Dominion:100
b3718.5 | PJM SOUTH | Dominion | VA | Enterprise, Greenway, Roundtable | Reconductor ~1.52 miles of 230 kV line #2031 (Enterprise-Greenway-Roundtable) to achieve a summer rating of 1574 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Dominion zone experiencing load growth in the Data Center Alley area around Dulles airport. Forecasted data center additions for the 2022 Load Forecast provided by Dominion and NOVEC were noticeably higher than in the prior year. Numerous reliability violations (thermal overloads and load loss) observed in the 2024 and 2025 time frames. ¦ Driven by unprecedented data center load growth in northern Virginia. PJM directed as an immediate need project in July 2022 to enable integration of forecaste |  | 20221004-pjm-teac-board-whitepaper-october-2022.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json | 2022-01-01 ¦ 2023-12-08 | 2 | 0 | 5.89 | 2022-09-06 | 9/6/2022 | 6/1/2025 | 3/13/2026 |  | UC | 90 | Reconductor | Yes |  | Appendix A | Dominion:100
b3718.6 | PJM SOUTH | Dominion | VA | Enterprise, Shellhorn | Reconductor ~0.64 miles of 230 kV line #2186 (Enterprise-Shellhorn) to achieve a summer rating of 1574 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Dominion zone experiencing load growth in the Data Center Alley area around Dulles airport. Forecasted data center additions for the 2022 Load Forecast provided by Dominion and NOVEC were noticeably higher than in the prior year. Numerous reliability violations (thermal overloads and load loss) observed in the 2024 and 2025 time frames. ¦ Driven by unprecedented data center load growth in northern Virginia. PJM directed as an immediate need project in July 2022 to enable integration of forecaste |  | 20221004-pjm-teac-board-whitepaper-october-2022.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json | 2022-01-01 ¦ 2023-12-08 | 2 | 0 | 3.96 | 2022-09-06 | 9/6/2022 | 6/1/2025 | 6/1/2025 | 9/3/2025 | IS | 100 | Reconductor | Yes |  | Appendix A | Dominion:100
b3718.7 | PJM SOUTH | Dominion | VA | Lockridge, Greenway, Shellhorn | Reconductor ~2.17 miles of 230 kV line #2188 (Lockridge-Greenway-Shellhorn) to achieve a summer rating of 1574 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Dominion zone experiencing load growth in the Data Center Alley area around Dulles airport. Forecasted data center additions for the 2022 Load Forecast provided by Dominion and NOVEC were noticeably higher than in the prior year. Numerous reliability violations (thermal overloads and load loss) observed in the 2024 and 2025 time frames. ¦ Driven by unprecedented data center load growth in northern Virginia. PJM directed as an immediate need project in July 2022 to enable integration of forecaste |  | 20221004-pjm-teac-board-whitepaper-october-2022.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json | 2022-01-01 ¦ 2023-12-08 | 2 | 0 | 3.8 | 2022-09-06 | 9/6/2022 | 6/1/2025 | 6/1/2025 | 8/27/2025 | IS | 100 | Reconductor | Yes |  | Appendix A | Dominion:100
b3718.8 | PJM SOUTH | Dominion | VA | Lockridge, Roundtable | Reconductor ~0.84 miles of 230 kV line #2223 (Lockridge-Roundtable) to achieve a summer rating of 1574 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Dominion zone experiencing load growth in the Data Center Alley area around Dulles airport. Forecasted data center additions for the 2022 Load Forecast provided by Dominion and NOVEC were noticeably higher than in the prior year. Numerous reliability violations (thermal overloads and load loss) observed in the 2024 and 2025 time frames. ¦ Driven by unprecedented data center load growth in northern Virginia. PJM directed as an immediate need project in July 2022 to enable integration of forecaste |  | 20221004-pjm-teac-board-whitepaper-october-2022.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json | 2022-01-01 ¦ 2023-12-08 | 2 | 0 | 2.59 | 2022-09-06 | 9/6/2022 | 6/1/2025 | 3/13/2026 |  | UC | 90 | Reconductor | Yes |  | Appendix A | Dominion:100
b3718.9 | PJM SOUTH | Dominion | VA | Sojourner, Runway, Shellhorn | Reconductor ~3.98 miles of 230 kV line #2218 (Sojourner-Runway-Shellhorn) to achieve a summer rating of 1574 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Dominion zone experiencing load growth in the Data Center Alley area around Dulles airport. Forecasted data center additions for the 2022 Load Forecast provided by Dominion and NOVEC were noticeably higher than in the prior year. Numerous reliability violations (thermal overloads and load loss) observed in the 2024 and 2025 time frames. ¦ Driven by unprecedented data center load growth in northern Virginia. PJM directed as an immediate need project in July 2022 to enable integration of forecaste |  | 20221004-pjm-teac-board-whitepaper-october-2022.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json | 2022-01-01 ¦ 2023-12-08 | 2 | 8 | 6.51 | 2022-09-06 | 9/6/2022 | 6/1/2025 | 3/10/2025 | 8/27/2025 | IS | 100 | Reconductor | Yes |  | Appendix A | Dominion:100
b3719 | PJM MA | PSEG | NJ | Bergeb | Replace the two existing 1200A Bergen 138 kV Circuit Switchers with two (2) 138 kV Disconnect Switches to achieve a minimum summer normal device rating of 298 MVA and a minimum summer emergency rating of 454 MVA. | Baseline | 138 | Circuit Switcher | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.2 | 1.2 | 2022-09-15 | 9/15/2022 | 12/31/2022 | 3/31/2024 |  | IS | 100 | Replace | Yes |  | Appendix A | PSEG:100
b3721 | PJM WEST | ATSI | OH | Avery - Hayes | Rebuild and reconductor the Avery-Hayes 138 kV line (approx. 6.5 miles) with 795 kcmil 26/7 ACSR. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Canceled because superseded by project b3925.3 (2024 RTEP Window 1, proposal 605) which provides higher ratings. Cost decrease of $10.4M. ¦ In the 2027 RTEP summer case, the Avery-Hayes 138 kV line is overloaded for an N-2 outage. Flow gate posted as part of 2022 RTEP Window 1 but excluded from competition due to below 200 kV exclusion. |  | 20250204-pjm-board-whitepaper-february-2025.json ¦ informational-only---pjm-teac-board-whitepaper-december-2022-public.json | 2025-01-01 | 2 | 19.49 | 10.4 | 2022-10-14 | 10/14/2022 | 6/1/2027 | 6/1/2027 |  | Cancelled | 0 | Reconductor | No |  | Appendix A | ATSI:100
b3723 | PJM WEST | AEP | WV | George Washington - Kammer | Rebuild the George Washington – Kammer 138 kV circuit, except for 0.1-mile of previously-upgraded T-line outside each terminal station (6.7 miles of total upgrade scope). Remove the existing 6-wired steel lattice towers and supplement the right-of-way as needed. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In the 2027 RTEP summer case, the George Washington-Kammer 138 kV line is overloaded for an N-2 outage. Flow gate posted as part of 2022 RTEP Window 1 but excluded from competition due to below 200 kV exclusion. |  | informational-only---pjm-teac-board-whitepaper-december-2022-public.json |  | 1 | 18.3 | 18.3 | 2022-10-14 | 10/14/2022 | 6/1/2027 | 6/1/2024 | 4/14/2025 | IS | 100 | Rebuild | No |  | Appendix A | AEP:100
b3725 | PJM WEST | ComEd | IL | Goodings Grove | Replace the 1600A bus disconnect switch at Goodings Grove on L11622 Elwood-Goodings Grove 345 kV. | Baseline | 345 | Disconnect Switch | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.5 | 0.5 | 2022-10-04 | 10/4/2022 | 12/1/2027 | 12/1/2027 |  | On Hold | 0 | Replace | No |  | Appendix A | ComEd:100
b3726 | PJM WEST | APS | WV | Black Oak | Install two new 500 kV breakers on the existing open SVC string to create a new bay position. Relocate & Reterminate facilities as necessary to move the 500 kV SVC into the new bay position and Install a 500 kV breaker on the 500/138 kV #3 transformer. Upgrade relaying at Black Oak substation. | Baseline | 500 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In the 2027 RTEP summer and winter case, there are several voltage drop violations at the Black Oak 500 kV substation for N-1 outage combinations. Flow gates posted as part of 2022 RTEP Window 1; PJM received one proposal. |  | informational-only---pjm-teac-board-whitepaper-december-2022-public.json |  | 1 | 17.37 | 17.37 | 2022-11-01 | 11/1/2022 | 6/1/2025 | 1/30/2026 | 2/4/2026 | IS | 100 | Install | No | 2022_1-21 | Appendix A | APS:100
b3728.1 | PJM MA | BGE | MD | Conastone | Upgrade two Breaker bushings on the 500 kV Line 5012 (Conastone-Peach Bottom) at Conastone substation. | Baseline | 500 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | CANCELLED. No longer required due to recently approved 2022 Window 3 solution. The Conastone-Peach Bottom 500 kV scope will be addressed under b3800. Net decrease of $5.8M. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 2 | 2 | 2022-10-04 | 2/6/2024 | 12/1/2027 | 12/1/2027 |  | Cancelled | 0 | Replace | No |  | Appendix A | APS:3.98,ATSI:0.03,BGE:20.98,DL:0.01,Dominion:32.06,DPL:0.02,JCPL:7.05,Neptune:0.81,PEPCO:17.70,PPL:2.72,PSEG:14.07,RE:0.57 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3728.2 | PJM MA | PECO | PA | Peach Bottom | Replace 4 meters and bus work inside Peach Bottom substation on the 500 kV Line 5012 (Conastone-Peach Bottom). | Baseline | 500 | Meter | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | CANCELLED. No longer required due to recently approved 2022 Window 3 solution. The Conastone-Peach Bottom 500 kV scope will be addressed under b3800. Net decrease of $5.8M. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 3.8 | 3.8 | 2022-10-04 | 2/6/2024 | 12/1/2027 | 12/1/2027 |  | Cancelled | 0 | Replace | No |  | Appendix A | APS:3.94,ATSI:0.03,BGE:20.78,DL:0.01,Dominion:31.75,DPL:0.02,JCPL:6.99,Neptune:0.80,PECO:0.98,PEPCO:17.52,PPL:2.69,PSEG:13.93,RE:0.56 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3729 | PJM MA | DPL | MD | Colora, Conowingo | To increase the Maximum Operating Temperature of DPL Circuit 22088 (Colora-Conowingo 230 kV), install cable shunts on each phase, on each side of four (4) dead-end structures and replace existing insulator bells. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Accelerated from June 2027 to June 2026 due to estimated annual congestion benefit of $0.8M. No additional cost. Upgrade of dead-end structures, installation of cable shunts, and replacement of existing insulator bells. |  | 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2024-01-01 | 1 | 0.26 | 0.26 | 2022-10-04 | 1/9/2024 | 6/1/2027 | 6/1/2026 |  | EP | 0 | Upgrade | No | 2022_1-236, only CRL was accpeted in 2022, just se | Appendix A | DPL:100 |  |  | 6/1/2026
b3730 | PJM MA | PPL | PA | Lackawanna | Reterminate the Lackawanna T3 and T4 500/230 kV transformers on the 230 kV side to remove them from the 230 kV buses and bring them into dedicated bay positions that are not adjacent to one another. | Baseline | 500/230 | Transformer | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In the 2027 RTEP summer case, the Lackawanna No. T3 transformer is overloaded for an N-2 outage. Flow gate posted as part of 2022 RTEP Window 1; PJM received three proposals. |  | informational-only---pjm-teac-board-whitepaper-december-2022-public.json |  | 1 | 10.7 | 10.7 | 2022-10-04 | 11/1/2022 | 6/1/2027 | 12/19/2025 |  | UC | 60 | Modify | No | 2022_1-127 | Appendix A | PPL:100
b3737.47 | PJM MA | Transource | PA | North Delta | Build New North Delta 500 kV substation (four bay breaker and half configuration ) - the substation will include 12 - 500kV breakers and one 500/230 kV transformer, will allow the termination of six - 500 kV lines | Baseline | 500/230 | Substation | Public Policy,Baseline Load Growth Deliverability & Reliability | state_policy | consistent (public policy aligns) | FALSE | 0 | New Jersey State Agreement Approach (SAA) project. Scope/cost increase: constructing Larrabee Collector station AC switchyard and procuring/preparing adjacent land (+$72.2M); MOAD pre-build infrastructure evaluation study (+$0.29M). ¦ New Jersey State Agreement Approach (SAA) additional scope to accommodate new 500/230 kV lines. Removes approximately 7.7 miles of existing E83 line along Larrabee-Smithburg ROW (not in service). ¦ New Jersey State Agreement Approach (SAA) additional scope. Removes | Change to previously approved project. Part of NJ SAA project b3737. Net cost increase for entire NJ SAA project is $127.34M. ¦ Change to previously approved SAA project b3737. ¦ Scope reduction to previously approved SAA project b3737. ¦ Original scope estimate was $76.27M (Transource-proposed); ex | 20230711-pjm-teac-board-whitepaper-july-2023-public.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json ¦ 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250204-pjm-board-whitepaper-february-2025.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json ¦ informational-only---pjm-teac-board-whitepaper-december-2022-public.json | 2023-01-01 ¦ 2023-12-08 ¦ 2024-01-01 ¦ 2025-01-01 ¦ 2025-07-01 ¦ 2026-02-01 | 21 | 104.1 | 104.1 | 2022-11-04 | 12/5/2023 | 6/1/2027 | 10/6/2027 |  | EP | 25 | Build | No | 2021_SAA-63 | Appendix A & C | Reliability driver (26.73%): PECO:100 PublicPolicy driver (73.27%): AEC:13.80,JCPL:31.95,PSEG:52.10,RE:2.15 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3738 | PJM WEST | APS | PA | Charleroi - Dry Run 138 kV | Charleroi - Dry Run 138 kV Line: Replace Limiting Terminal Equipment | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.38 | 0.38 | 2022-11-18 | 11/18/2022 | 6/1/2027 | 6/1/2027 |  | EP | 10 | Replace | No |  | Appendix A | APS:100
b3739 | PJM WEST | APS | PA | Dry Run - Mitchell 138 kV | Dry Run - Mitchell 138 kV Line: Replace Limiting Terminal Equipment | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.4 | 0.4 | 2022-11-18 | 11/18/2022 | 6/1/2027 | 6/1/2027 |  | EP | 2 | Replace | No |  | Appendix A | APS:100
b3740 | PJM WEST | APS | PA | Glen Falls - Bridgeport 138 kV | Glen Falls - Bridgeport 138 kV Line: Replace Limiting Terminal Equipment | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.88 | 1.88 | 2022-11-18 | 11/18/2022 | 6/1/2027 | 6/5/2026 |  | EP | 39 | Replace | No |  | Appendix A | APS:100
b3741 | PJM WEST | APS | PA | Yukon - Charleroi No.1 138 kV | Yukon - Charleroi No.1 138 kV Line: Replace Limiting Terminal Equipment | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.7 | 0.7 | 2022-11-18 | 11/18/2022 | 6/1/2027 | 4/14/2026 |  | EP | 39 | Replace | No |  | Appendix A | APS:100
b3742 | PJM WEST | APS | PA | Yukon - Charleroi No.1 138 kV | Yukon - Charleroi No.1 138 kV Line: Replace Limiting Terminal Equipment | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.7 | 0.45 | 2022-11-18 | 11/18/2022 | 6/1/2027 | 9/26/2025 | 10/1/2025 | IS | 100 | Replace | No |  | Appendix A | APS:100
b3743 | PJM WEST | APS | WV | Cherry Run - Harmony Jct Tap 138 kV | At Bedington Substation: Replace substation conductor, wavetrap, CT's and upgrade relaying At Cherry Run Substation: Replace substation conductor, wavetrap, CT's, disconnect switches, circuit breaker and upgrade relaying At Marlowe: Replace substation conductor, wavetrap, CT's and upgrade relaying. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 4.66 | 4.6 | 2022-11-18 | 11/18/2022 | 6/1/2027 | 6/1/2027 | 11/9/2023 | IS | 100 | Replace | No |  | Appendix A | APS:100
b3744 | PJM WEST | APS | PA | Shanor – Krendale 138 kV | Replace one span of 1272 ACSR from Krendale substation to structure 35 (~630 ft) Replace one span of 1272 ACSR from Shanor Manor to structure 21 (~148 ft) Replace 1272 ACSR risers at Krendale & Shanor Manor Substations Replace 1272 ACSR Substation Conductor at Krendale Substation Replace relaying at Krendale Substation Revise Relay Settings at Butler & Shanor Manor Substations. | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.75 | 1.75 | 2022-11-18 | 11/18/2022 | 6/1/2027 | 12/1/2023 | 11/9/2023 | IS | 100 | Replace | No |  | Appendix A | APS:100
b3745 | PJM WEST | APS | PA | Carbon Center 230 kVSubstation | Carbon Center Substation - Install Redundant Relaying | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.57 | 0.57 | 2022-11-18 | 11/18/2022 | 6/1/2027 | 6/1/2026 |  | EP | 2 | Replace | No |  | Appendix A | APS:100
b3746 | PJM WEST | APS | WV | Meadow Brook 500 kV Substation | Meadow Brook Substation - Install Redundant Relaying | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.21 | 0.21 | 2022-11-18 | 11/18/2022 | 6/1/2027 | 6/1/2027 |  | EP | 1 | Replace | No |  | Appendix A | APS:100
b3747 | PJM WEST | APS | WV | Bedington 500 kV Substation | Bedington Substation - Install Redundant Relaying | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.28 | 0.28 | 2022-11-18 | 11/18/2022 | 6/1/2027 | 5/29/2026 |  | EP | 1 | Replace | No |  | Appendix A | APS:100
b3748 | PJM WEST | AEP | IN | Clifty Creek | Replace four Clifty Creek 345 kV 3000A switches with 5000 A 345 kV switches. | Baseline | 345 | Disconnect Switch | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.85 | 0.85 | 2022-11-01 | 11/1/2022 | 6/1/2027 | 6/28/2024 | 6/11/2024 | IS | 100 | Replace | No | 2022_1-965 | Appendix A | AEP:100
b3749 | PJM MA | DPL | MD | New Church - Piney Grove | Rebuild the New Church - Piney Grove 138 kV line | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2027 RTEP case, New Church-Piney 138 kV circuit is overloaded for line fault stuck breaker contingency (N-1-1). |  | 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json | 2023-01-01 | 1 | 77 | 63 | 2022-10-13 | 11/17/2022 | 6/1/2027 | 6/15/2027 |  | EP | 12 | Rebuild | No |  | Appendix A | DPL:100
b3750 | PJM MA | PENELEC | PA | Seward | Upgrade Seward Terminal Equipment of the Seward-Blairsville 115 kV Line to increase the line rating such that the Transmission Line conductor is the limiting component. | Baseline | 115 | Disconnect Switch | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.43 | 0.43 | 2022-10-13 | 11/17/2022 | 6/1/2027 | 5/1/2026 |  | EP | 20 | Upgrade | No |  | Appendix A | PENELEC:100
b3751 | PJM MA | PENELEC | PA | Roxbury to the AE1-071 | Rebuild 6.4 miles of the Roxbury - Shade Gap 115 kV line from Roxbury to the AE1-071 115 kV ring bus with single circuit 115 kV construction | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2027 RTEP case, Roxbury-AE1-071 115 kV line is overloaded for multiple N-1 contingencies. |  | 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json | 2023-01-01 | 1 | 15.03 | 15.03 | 2022-10-13 | 11/17/2022 | 6/1/2027 | 6/29/2027 |  | EP | 5 | Rebuild | No |  | Appendix A | PENELEC:100
b3752 | PJM MA | PENELEC | PA | Shade Gap - AE1-071 115 | Rebuild 7.2 miles of the Shade Gap - AE1-071 115 kV line section of the Roxbury - Shade Gap 115 kV line | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2027 RTEP case, AE1-071-Shade Gap 115 kV line is overloaded for multiple N-1 contingencies. |  | 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json | 2023-01-01 | 1 | 17.43 | 17.43 | 2022-10-13 | 11/17/2022 | 6/1/2027 | 12/10/2026 |  | EP | 5 | Rebuild | No |  | Appendix A | PENELEC:100
b3759 | PJM SOUTH | Dominion | VA | Bell Ave, Suffolk | * Wreck and rebuild approximately 10.5 miles of 115kV Line #23 segment from Oak Ridge to AC2-079 Tap to minimum emergency ratings of 393 MVA Summer / 412 MVA Winter. Structures to be rebuilt to current 115kV standards. Transmission Estimated Cost: $37.1M * Reconductor 115kV Line #44 segment from Oak Ridge to AC2-079 Tap which also shares the same structures to minimum emergency ratings of 393 MVA Summer / 412 MVA Winter. Existing conductor is about 70 years old. Transmission Estimated Cost: $3.9M | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2027 RTEP case, failed breaker contingencies isolating Poe 115 kV Bus No. 1 overload the Oak Ridge to AC2-079 segment of 115 kV Line No. 23 Bell Ave-Suffolk. ¦ Scope expanded from reconductor to full wrecking and rebuilding of ~10.5 miles of 115 kV line No. 23 and reconductoring of line No. 44 on shared structures, due to inadequate clearances, ~80% of towers needing foundation modifications, and structural failures under ice/wind loading. Cost increased from $23.5M to $41M. |  | 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json ¦ 20250204-pjm-board-whitepaper-february-2025.json | 2023-01-01 ¦ 2025-01-01 | 2 | 39.5 | 41 | 2022-11-17 | 12/12/2024 | 6/1/2027 | 10/12/2027 |  | EP | 20 | Reconductor | No |  | Appendix A | Dominion:100
b3761 | PJM WEST | APS | PA | Ridgway 138/46 kV | Install 138 kV Breaker on the Ridgway 138/46 kV #2 Transformer | Baseline | 138 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.1 | 1.1 | 2022-12-16 | 12/16/2022 | 6/1/2027 | 6/1/2027 |  | EP | 0 | Install | No |  | Appendix A | APS:100
b3765 | PJM MA | PENELEC | PA | Mainesburg | Purchase one 80 MVAR 345 kV spare reactor, to be located at the Mainesburg station. | Baseline | 345 | Reactive Device | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 6.44 | 6.44 | 2022-11-04 | 12/6/2022 | 12/1/2022 | 12/30/2026 |  | UC | 50 | Provide | No |  | Appendix A | PENELEC:100
b3766.1 | PJM WEST | AEP | OH | Hayes - New Westville | Hayes – New Westville 138 kV line: Build ~0.19 miles of 138 kV line to the Indiana/ Ohio State line to connect to AES’s line portion of the Hayes – New Westville 138 kV line with the conductor size 795 ACSR26/7 Drake. The following cost includes the line construction and ROW. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; also addresses Dayton supplemental needs Dayton-2020-011, Dayton-2021-001, Dayton-2021-008. Converted from supplemental project S2585.2. ¦ Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; replaces 3302 line feeding New Westville; 3302 line to be retired as part of project. Converted from supplemental project S2585.3. ¦ Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; AES Ohio |  | 20230110-final-review-and-recommendation---2022-rtep-window-1---cluster-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json | 2023-01-01 | 7 | 0.38 | 0.38 | 2022-12-06 | 12/6/2022 | 6/1/2027 | 10/18/2027 |  | EP | 5 | Build | No |  | Appendix A | AEP:100
b3766.2 | PJM WEST | AEP | OH | Hayes-Hodgin | Hayes – Hodgin 138 kV line: Build ~0.05 miles of 138 kV line with the conductor size 795 ACSR26/7 Drake. The following cost includes the line construction, ROW, and fiber. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; also addresses Dayton supplemental needs Dayton-2020-011, Dayton-2021-001, Dayton-2021-008. Converted from supplemental project S2585.2. ¦ Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; replaces 3302 line feeding New Westville; 3302 line to be retired as part of project. Converted from supplemental project S2585.3. ¦ Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; AES Ohio |  | 20230110-final-review-and-recommendation---2022-rtep-window-1---cluster-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json | 2023-01-01 | 7 | 1.22 | 1.22 | 2022-12-06 | 12/6/2022 | 6/1/2027 | 10/18/2027 |  | EP | 5 | Build | No |  | Appendix A | AEP:100
b3766.3 | PJM WEST | AEP | OH | Hayes | Hayes 138 kV: Build a new 4-138 kV circuit breaker ring bus. The following cost includes the new station construction, property purchase, metering, station fiber and the College Corner –Randolph 138 kV line connection. | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; also addresses Dayton supplemental needs Dayton-2020-011, Dayton-2021-001, Dayton-2021-008. Converted from supplemental project S2585.2. ¦ Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; replaces 3302 line feeding New Westville; 3302 line to be retired as part of project. Converted from supplemental project S2585.3. ¦ Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; AES Ohio |  | 20230110-final-review-and-recommendation---2022-rtep-window-1---cluster-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json | 2023-01-01 | 7 | 7.44 | 7.44 | 2022-12-06 | 12/6/2022 | 6/1/2027 | 10/18/2027 |  | EP | 5 | Build | No |  | Appendix A | AEP:100
b3766.4 | PJM WEST | Dayton | OH | New Westville – AEP Hodgin 138kV Line | New Westville – AEP Hodgin 138kV Line: Construct a 138kV 1.86-mile single circuit transmission line. This transmission line will help loop the radial load served at New Westville as part of the overall effort to improve reliability in this area. Also, it provides a source to feed New Westville load while the 138kV tie built back into the AES Ohio system | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; also addresses Dayton supplemental needs Dayton-2020-011, Dayton-2021-001, Dayton-2021-008. Converted from supplemental project S2585.2. ¦ Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; replaces 3302 line feeding New Westville; 3302 line to be retired as part of project. Converted from supplemental project S2585.3. ¦ Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; AES Ohio |  | 20230110-final-review-and-recommendation---2022-rtep-window-1---cluster-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json | 2023-01-01 | 7 | 3.7 | 3.7 | 2022-12-06 | 12/6/2022 | 6/1/2027 | 4/30/2027 |  | EP | 20 | Construct | No |  | Appendix A | Dayton:100
b3766.5 | PJM WEST | Dayton | OH | New Westville – West Manchester 138kV Line | New Westville – West Manchester 138kV Line: Construct a new approximate 11-mile single circuit 138kV line from New Westville to the Lewisburg tap off 6656. Convert a portion of 6656 West Manchester – Garage Rd 69kV line between West Manchester - Lewisburg to 138kV operation (circuit is built to 138kV). This will utilize part of the line already built to 138kV and will take place of the 3302 that currently feeds New Westville. The 3302 line will be retired as part of this project. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; also addresses Dayton supplemental needs Dayton-2020-011, Dayton-2021-001, Dayton-2021-008. Converted from supplemental project S2585.2. ¦ Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; replaces 3302 line feeding New Westville; 3302 line to be retired as part of project. Converted from supplemental project S2585.3. ¦ Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; AES Ohio |  | 20230110-final-review-and-recommendation---2022-rtep-window-1---cluster-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json | 2023-01-01 | 7 | 16 | 16 | 2022-12-06 | 12/6/2022 | 6/1/2027 | 11/15/2028 |  | EP | 20 | Construct | No |  | Appendix A | Dayton:100
b3766.6 | PJM WEST | Dayton | OH | West Manchester Substation | West Manchester Substation: The West Manchester Substation will be expanded to a double bus double breaker design where AES Ohio will install one 138kV circuit breaker, a 138/69kV transformer, and eight new 69kV circuit breakers. These improvements will improve help improve a non-standard bus arrangement where there is only one bus tie today and will improve the switching arrangement for the West Sonora Delivery Point. | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; also addresses Dayton supplemental needs Dayton-2020-011, Dayton-2021-001, Dayton-2021-008. Converted from supplemental project S2585.2. ¦ Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; replaces 3302 line feeding New Westville; 3302 line to be retired as part of project. Converted from supplemental project S2585.3. ¦ Thermal violations on 138kV flowgates 2022W1-GD-S586 and 2022W1-GD-W377; AES Ohio |  | 20230110-final-review-and-recommendation---2022-rtep-window-1---cluster-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json | 2023-01-01 | 7 | 9.9 | 9.9 | 2022-12-06 | 12/6/2022 | 6/1/2027 | 11/15/2028 |  | UC | 26 | Modify | No |  | Appendix A | Dayton:100
b3768 | PJM MA | ME | PA | Lincoln,Germantown and Straban | Rebuild/Reconductor the Germantown - Lincoln 115 kV Line. Approximately 7.6 miles. Upgrade limiting terminal equipment at Lincoln, Germantown and Straban | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2027 RTEP summer case, Lincoln-Straban-Germantown 115 kV circuit is overloaded for multiple N-1 contingencies. ¦ Pre-existing baseline project to rebuild/reconductor the Germantown–Lincoln 115 kV line. Canceled because the recommended Window 3 solution (Proposal 837 by FirstEnergy – new Hunterstown–Carroll 230 kV line rebuild plus Lincoln–Orrtanna 115 kV reconductor and other PJM-identified upgrades) supersedes this need. ¦ No longer required with the recommended 2022 Window 3 solution | Cancellation yields net RTEP decrease of $17.36M | 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json ¦ 20231205-2022-rtep-window-3-reliability-analysis-report.json ¦ 20231205-pjm-teac-board-whitepaper-december-2023.json | 2023-01-01 ¦ 2023-12-08 | 3 | 20 | 17.36 | 2022-12-06 | 12/5/2023 | 6/1/2027 | 6/1/2027 |  | Cancelled | 0 | Rebuild | No |  | Appendix A | ME:100
b3769 | PJM MA | ME | PA | TMI | Install second TMI 500/230kV Transformer with additional 500 and 230 bus expansions | Baseline | 500/230 | Transformer | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2027 RTEP summer case, TMI 500/230 kV transformer is overloaded for multiple N-1 contingencies. |  | 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json | 2023-01-01 | 1 | 30.19 | 30.19 | 2022-12-06 | 1/6/2023 | 6/1/2027 | 6/1/2027 |  | EP | 15 | Install | No | 2022-W1-880 | Appendix A | ME:45.74,PPL:54.26
b3770 | PJM MA | BGE | PA | Graceton - Brunner Island | Rebuild 1.4 miles of existing single circuit 230 kV tower line between BGE's Graceton substation to the Brunner Island PPL tie-line at the MD/PA state line to double circuit steel pole line with one (1) circuit installed to uprate 2303 circuit | Baseline | 230 | Transmission Structures | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 11.4 | 8.4 | 2022-12-06 | 1/6/2023 | 6/1/2027 | 6/1/2027 |  | UC | 30 | Rebuild | No | 2022-W1-912 | Appendix A | BGE:99.98,ME:0.01,PPL:0.01
b3771 | PJM MA | BGE | MD | Conastone - North West | Reconductor two (2) 230 kV circuits from Conastone to Northwest #2 | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | 230 kV circuits from Conastone to Northwest No. 2 reconductored to address thermal overload. (Note: detail section of document contained copy-paste text from b3772; cost taken from summary table at $37.8M.) |  | 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json | 2023-01-01 | 1 | 90.06 | 37.76 | 2022-12-06 | 1/6/2023 | 6/1/2027 | 6/1/2027 |  | UC | 30 | Reconductor | No | 2022-W1-94 | Appendix A | BGE:70.70,PEPCO:29.30
b3772 | PJM SOUTH | APS | MD | Messick Road - Morgan | Reconductor 27.3 miles of the Messick Road - Morgan 138 kV Line from 556 ACSR to 954 ACSR. At Messick Road Substation: Replace 138 kV wave trap, circuit breaker, CT's, disconnect switch, and substation conductor and upgrade relaying. At Morgan Substation: Upgrade Relaying | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2027 RTEP summer and winter cases, Messick Road-Morgan 138 kV line is overloaded due to two breaker contingencies (N-2). |  | 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json | 2023-01-01 | 1 | 49.23 | 49.23 | 2022-12-06 | 1/6/2023 | 6/1/2027 | 6/15/2029 |  | EP | 4 | Reconductor | No |  | Appendix A | APS:100
b3773 | PJM WEST | APS | PA | McConnellsburg | Install (1) 31.7 MVAR switched capacitor, 138 kV breaker, and associated relaying at Warfordsburg Substation | Baseline | 138 | Reactive Device | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 3.05 | 3.05 | 2022-12-06 | 4/11/2025 | 6/1/2027 | 6/1/2027 |  | EP | 4 | Install | No |  | Appendix A | APS:100
b3774 | PJM MA | PPL | PA | Brunner Island | Upgrade terminal equipment at Brunner Island (on the Brunner Island - Yorkana 230 kV circuit) | Baseline | 230 | Conductor | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 2.5 | 2.5 | 2022-12-06 | 1/6/2023 | 6/1/2027 | 6/1/2027 |  | EP | 10 | Replace | No |  | Appendix A | PPL:100
b3775.1 | PJM WEST | NEET | IL | St. John-Green Acres-Olive, University Park N-Olive | Outside of the Green Acres substation, swap the NIPSCO Green Acre Tap towers from the St. John-Green Acres-Olive 345 kV line to the University Park N-Olive 345 kV line to create a University Park N-Green Acres-Olive and St. John-Olive 345 kV lines. | Baseline | 345 | Transmission Line | Congestion Relief - Economic,Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Winter generator deliverability flowgates on Crete-St. John 345 kV (MDW1-GD-W172 etc.), E. Frankfort-Crete 345 kV (MDW1-GD-W332/W331), University Park N-Olive 345 kV (MDW1-GD-W392/W393), and Stillwell-Dumont 345 kV (MDW1-GD-S1620). Also addresses market efficiency congestion (COMED-NIPSCO-AEP area). Additional benefit: remediation of aging/EOL infrastructure on ComEd and NEET sections of the affected 345 kV double circuits; Joliet units 6/7/8 deactivation (1,381 MW) reflected as sensitivity. ¦ I | {'source_document': 'Final Review and Recommendation - 2022 Multi-Driver Proposal Window No. 1 (January 11, 2023)', 'subcomponents': [{'id': 'B3775.1', 'description': 'Swap NIPSCO Green Acre Tap towers from St. John-Green Acres-Olive to Uni Park N-Olive 345 kV line', 'entity': 'NEET', 'cost_million' | 20230110-final-review-and-recommendation---2022-multi-driver-proposal-window-no-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json ¦ 20230711-pjm-teac-board-whitepaper-july-2023-public.json | 2023-01-01 | 5 | 2.5 | 1.98 | 2023-01-10 | 1/10/2023 | 12/1/2026 | 3/30/2027 |  | EP | 15 | Modify | No | 2022_MD-644 (modified) | Appendix A | Economic driver (52.75%): AEC:0.87,AEP:24.07,APS:3.95,BGE:4.30,Dayton:3.52,DEOK:5.35,Dominion:20.09,DPL:1.73,DL:2.11,ECP:0.17,EKPC:1.73,ATSI:11.04,HTP:0.07,JCPL:1.98,ME:1.63,Neptune:0.43,OVEC:0.07,PECO:3.59,PENELEC:1.68,PEPCO:3.91,PPL:3.64,PSEG:3.93,RE:0.14 Reliability driver (47.25%): ComEd:54.45,Dayton:45.55
b3775.10 | PJM WEST | AEP | IL | Olive-University Park N | Perform a sag study on the Olive – University Park 345kV line to increase the operating temperature to 225 F. Remediation work includes two tower replacements on the line. | Baseline | 345 | Transmission Line | Congestion Relief - Economic,Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Winter generator deliverability flowgates on Crete-St. John 345 kV (MDW1-GD-W172 etc.), E. Frankfort-Crete 345 kV (MDW1-GD-W332/W331), University Park N-Olive 345 kV (MDW1-GD-W392/W393), and Stillwell-Dumont 345 kV (MDW1-GD-S1620). Also addresses market efficiency congestion (COMED-NIPSCO-AEP area). Additional benefit: remediation of aging/EOL infrastructure on ComEd and NEET sections of the affected 345 kV double circuits; Joliet units 6/7/8 deactivation (1,381 MW) reflected as sensitivity. ¦ I | {'source_document': 'Final Review and Recommendation - 2022 Multi-Driver Proposal Window No. 1 (January 11, 2023)', 'subcomponents': [{'id': 'B3775.1', 'description': 'Swap NIPSCO Green Acre Tap towers from St. John-Green Acres-Olive to Uni Park N-Olive 345 kV line', 'entity': 'NEET', 'cost_million' | 20230110-final-review-and-recommendation---2022-multi-driver-proposal-window-no-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json ¦ 20230711-pjm-teac-board-whitepaper-july-2023-public.json | 2023-01-01 | 5 | 1.5 | 1.5 | 2023-01-10 | 1/10/2023 | 12/1/2026 | 12/1/2026 |  | EP | 0 | Sag Study | No | 2022_MD-908 | Appendix A | Economic driver (52.75%): AEC:0.87,AEP:24.07,APS:3.95,ATSI:11.04,BGE:4.30,Dayton:3.52,DEOK:5.35,DL:2.11,Dominion:20.09,DPL:1.73,ECP:0.17,EKPC:1.73,HTP:0.07,JCPL:1.98,ME:1.63,Neptune:0.43,OVEC:0.07,PECO:3.59,PENELEC:1.68,PEPCO:3.91,PPL:3.64,PSEG:3.93,RE:0.14 Reliability driver (47.25%): AEP:100
b3775.11 | PJM WEST | AEP | IL | Stillwell | Upgrade the limiting element at Stillwell substation to increase the rating of the Stillwell-Dumont 345 kV line to match conductor rating. | Baseline | 345 | Substation | Congestion Relief - Economic,Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Winter generator deliverability flowgates on Crete-St. John 345 kV (MDW1-GD-W172 etc.), E. Frankfort-Crete 345 kV (MDW1-GD-W332/W331), University Park N-Olive 345 kV (MDW1-GD-W392/W393), and Stillwell-Dumont 345 kV (MDW1-GD-S1620). Also addresses market efficiency congestion (COMED-NIPSCO-AEP area). Additional benefit: remediation of aging/EOL infrastructure on ComEd and NEET sections of the affected 345 kV double circuits; Joliet units 6/7/8 deactivation (1,381 MW) reflected as sensitivity. ¦ I | {'source_document': 'Final Review and Recommendation - 2022 Multi-Driver Proposal Window No. 1 (January 11, 2023)', 'subcomponents': [{'id': 'B3775.1', 'description': 'Swap NIPSCO Green Acre Tap towers from St. John-Green Acres-Olive to Uni Park N-Olive 345 kV line', 'entity': 'NEET', 'cost_million' | 20230110-final-review-and-recommendation---2022-multi-driver-proposal-window-no-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json ¦ 20230711-pjm-teac-board-whitepaper-july-2023-public.json | 2023-01-01 | 5 | 0.14 | 1.78 | 2023-04-11 | 4/11/2023 | 12/1/2026 | 12/1/2026 |  | EP | 15 | Upgrade | No | 2022_MD-644 (modified) | Appendix A | Economic driver (52.75%): AEC:0.87,AEP:24.07,APS:3.95,ATSI:11.04,BGE:4.30,Dayton:3.52,DEOK:5.35,DL:2.11,Dominion:20.09,DPL:1.73,ECP:0.17,EKPC:1.73,HTP:0.07,JCPL:1.98,ME:1.63,Neptune:0.43,OVEC:0.07,PECO:3.59,PENELEC:1.68,PEPCO:3.91,PPL:3.64,PSEG:3.93,RE:0.14 Reliability driver (47.25%): AEP:90.58,ComEd:9.42
b3775.2 | PJM WEST | NEET | IL | Crete-St. John | Reconductor NEET’s section of Crete(IN/IL border)-St. John 345 kV line (6.95 miles). | Baseline | 345 | Transmission Line | Congestion Relief - Economic,Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Winter generator deliverability flowgates on Crete-St. John 345 kV (MDW1-GD-W172 etc.), E. Frankfort-Crete 345 kV (MDW1-GD-W332/W331), University Park N-Olive 345 kV (MDW1-GD-W392/W393), and Stillwell-Dumont 345 kV (MDW1-GD-S1620). Also addresses market efficiency congestion (COMED-NIPSCO-AEP area). Additional benefit: remediation of aging/EOL infrastructure on ComEd and NEET sections of the affected 345 kV double circuits; Joliet units 6/7/8 deactivation (1,381 MW) reflected as sensitivity. ¦ I | {'source_document': 'Final Review and Recommendation - 2022 Multi-Driver Proposal Window No. 1 (January 11, 2023)', 'subcomponents': [{'id': 'B3775.1', 'description': 'Swap NIPSCO Green Acre Tap towers from St. John-Green Acres-Olive to Uni Park N-Olive 345 kV line', 'entity': 'NEET', 'cost_million' | 20230110-final-review-and-recommendation---2022-multi-driver-proposal-window-no-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json ¦ 20230711-pjm-teac-board-whitepaper-july-2023-public.json | 2023-01-01 | 5 | 7.24 | 1.99 | 2023-01-10 | 1/10/2023 |  | 12/1/2026 | 5/9/2023 | IS | 100 | Reconductor | No | 2022_MD-644 (modified) | Appendix A | Economic driver (52.75%): AEC:0.87,AEP:24.07,APS:3.95,ATSI:11.04,BGE:4.30,Dayton:3.52,DEOK:5.35,DL:2.11,Dominion:20.09,DPL:1.73,ECP:0.17,EKPC:1.73,HTP:0.07,JCPL:1.98,ME:1.63,Neptune:0.43,OVEC:0.07,PECO:3.59,PENELEC:1.68,PEPCO:3.91,PPL:3.64,PSEG:3.93,RE:0.14 Reliability driver (47.25%): ComEd:100
b3775.3 | PJM WEST | ComEd | IL | Crete-St. John, Olive-University Park N-E. Frankfort | Rebuild ComEd’s section of 345 kV double circuit in IL from St. John to Crete (5 miles) with twin bundled 1277 ACAR conductor. | Baseline | 345 | Transmission Line | Congestion Relief - Economic,Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Winter generator deliverability flowgates on Crete-St. John 345 kV (MDW1-GD-W172 etc.), E. Frankfort-Crete 345 kV (MDW1-GD-W332/W331), University Park N-Olive 345 kV (MDW1-GD-W392/W393), and Stillwell-Dumont 345 kV (MDW1-GD-S1620). Also addresses market efficiency congestion (COMED-NIPSCO-AEP area). Additional benefit: remediation of aging/EOL infrastructure on ComEd and NEET sections of the affected 345 kV double circuits; Joliet units 6/7/8 deactivation (1,381 MW) reflected as sensitivity. ¦ I | {'source_document': 'Final Review and Recommendation - 2022 Multi-Driver Proposal Window No. 1 (January 11, 2023)', 'subcomponents': [{'id': 'B3775.1', 'description': 'Swap NIPSCO Green Acre Tap towers from St. John-Green Acres-Olive to Uni Park N-Olive 345 kV line', 'entity': 'NEET', 'cost_million' | 20230110-final-review-and-recommendation---2022-multi-driver-proposal-window-no-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json ¦ 20230711-pjm-teac-board-whitepaper-july-2023-public.json | 2023-01-01 | 5 | 31 | 16.64 | 2023-01-10 | 1/10/2023 | 12/1/2026 | 12/1/2026 |  | UC | 25 | Rebuild | No | 2022_MD-253 | Appendix A | Economic driver (52.75%): AEC:0.87,AEP:24.07,APS:3.95,ATSI:11.04,BGE:4.30,Dayton:3.52,DEOK:5.35,DL:2.11,Dominion:20.09,DPL:1.73,ECP:0.17,EKPC:1.73,HTP:0.07,JCPL:1.98,ME:1.63,Neptune:0.43,OVEC:0.07,PECO:3.59,PENELEC:1.68,PEPCO:3.91,PPL:3.64,PSEG:3.93,RE:0.14 Reliability driver (47.25%): ComEd:100
b3775.4 | PJM WEST | ComEd | IL | Crete-E. Frankfort, Olive-University Park N-E. Frankfort | Rebuild 12.7 miles of 345 kV double circuit extending from Crete to E. Frankfort with twin bundled 1277 ACAR conductor. | Baseline | 345 | Transmission Line | Congestion Relief - Economic,Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Winter generator deliverability flowgates on Crete-St. John 345 kV (MDW1-GD-W172 etc.), E. Frankfort-Crete 345 kV (MDW1-GD-W332/W331), University Park N-Olive 345 kV (MDW1-GD-W392/W393), and Stillwell-Dumont 345 kV (MDW1-GD-S1620). Also addresses market efficiency congestion (COMED-NIPSCO-AEP area). Additional benefit: remediation of aging/EOL infrastructure on ComEd and NEET sections of the affected 345 kV double circuits; Joliet units 6/7/8 deactivation (1,381 MW) reflected as sensitivity. ¦ I | {'source_document': 'Final Review and Recommendation - 2022 Multi-Driver Proposal Window No. 1 (January 11, 2023)', 'subcomponents': [{'id': 'B3775.1', 'description': 'Swap NIPSCO Green Acre Tap towers from St. John-Green Acres-Olive to Uni Park N-Olive 345 kV line', 'entity': 'NEET', 'cost_million' | 20230110-final-review-and-recommendation---2022-multi-driver-proposal-window-no-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json ¦ 20230711-pjm-teac-board-whitepaper-july-2023-public.json | 2023-01-01 | 5 | 80.63 | 42.28 | 2023-01-10 | 1/10/2023 | 12/1/2026 | 12/1/2026 |  | UC | 25 | Rebuild | No | 2022_MD-253 | Appendix A | Economic driver (52.75%): AEC:0.87,AEP:24.07,APS:3.95,ATSI:11.04,BGE:4.30,Dayton:3.52,DEOK:5.35,DL:2.11,Dominion:20.09,DPL:1.73,ECP:0.17,EKPC:1.73,HTP:0.07,JCPL:1.98,ME:1.63,Neptune:0.43,OVEC:0.07,PECO:3.59,PENELEC:1.68,PEPCO:3.91,PPL:3.64,PSEG:3.93,RE:0.14 Reliability driver (47.25%): ComEd:100
b3775.5 | PJM WEST | ComEd | IL | E. Frankfort | Replace E. Frankfort 345 kV circuit breaker “9-14” with 3150A SF6 circuit breaker. | Baseline | 345 | Circuit Breaker | Congestion Relief - Economic,Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Winter generator deliverability flowgates on Crete-St. John 345 kV (MDW1-GD-W172 etc.), E. Frankfort-Crete 345 kV (MDW1-GD-W332/W331), University Park N-Olive 345 kV (MDW1-GD-W392/W393), and Stillwell-Dumont 345 kV (MDW1-GD-S1620). Also addresses market efficiency congestion (COMED-NIPSCO-AEP area). Additional benefit: remediation of aging/EOL infrastructure on ComEd and NEET sections of the affected 345 kV double circuits; Joliet units 6/7/8 deactivation (1,381 MW) reflected as sensitivity. ¦ I | {'source_document': 'Final Review and Recommendation - 2022 Multi-Driver Proposal Window No. 1 (January 11, 2023)', 'subcomponents': [{'id': 'B3775.1', 'description': 'Swap NIPSCO Green Acre Tap towers from St. John-Green Acres-Olive to Uni Park N-Olive 345 kV line', 'entity': 'NEET', 'cost_million' | 20230110-final-review-and-recommendation---2022-multi-driver-proposal-window-no-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json ¦ 20230711-pjm-teac-board-whitepaper-july-2023-public.json | 2023-01-01 | 5 | 4.17 | 3.27 | 2023-01-10 | 1/10/2023 | 12/1/2026 | 12/1/2025 | 10/6/2025 | IS | 100 | Replace | No | 2022_MD-253 | Appendix A | Economic driver (52.75%): AEC:0.87,AEP:24.07,APS:3.95,ATSI:11.04,BGE:4.30,Dayton:3.52,DEOK:5.35,DL:2.11,Dominion:20.09,DPL:1.73,ECP:0.17,EKPC:1.73,HTP:0.07,JCPL:1.98,ME:1.63,Neptune:0.43,OVEC:0.07,PECO:3.59,PENELEC:1.68,PEPCO:3.91,PPL:3.64,PSEG:3.93,RE:0.14 Reliability driver (47.25%): ComEd:100
b3775.6 | PJM WEST | AEP | IN | Dumont-Stillwell | Perform sag study mitigation work on the Dumont-Stillwell 345 kV line (remove a center-pivot irrigation system from under the line, allowing for the normal and emergency ratings of the line to increase, replace two structures and modify a third structure). | Baseline | 345 | Transmission Line | Congestion Relief - Economic,Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Winter generator deliverability flowgates on Crete-St. John 345 kV (MDW1-GD-W172 etc.), E. Frankfort-Crete 345 kV (MDW1-GD-W332/W331), University Park N-Olive 345 kV (MDW1-GD-W392/W393), and Stillwell-Dumont 345 kV (MDW1-GD-S1620). Also addresses market efficiency congestion (COMED-NIPSCO-AEP area). Additional benefit: remediation of aging/EOL infrastructure on ComEd and NEET sections of the affected 345 kV double circuits; Joliet units 6/7/8 deactivation (1,381 MW) reflected as sensitivity. ¦ I | {'source_document': 'Final Review and Recommendation - 2022 Multi-Driver Proposal Window No. 1 (January 11, 2023)', 'subcomponents': [{'id': 'B3775.1', 'description': 'Swap NIPSCO Green Acre Tap towers from St. John-Green Acres-Olive to Uni Park N-Olive 345 kV line', 'entity': 'NEET', 'cost_million' | 20230110-final-review-and-recommendation---2022-multi-driver-proposal-window-no-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json ¦ 20230711-pjm-teac-board-whitepaper-july-2023-public.json | 2023-01-01 | 5 | 2.22 | 2.22 | 2023-01-10 | 4/11/2023 | 12/1/2026 | 11/20/2026 |  | EP | 15 | Sag Study | No | 2022_MD-644 (modified) | Appendix A | Economic driver (52.75%): AEC:0.87,AEP:24.07,APS:3.95,ATSI:11.04,BGE:4.30,Dayton:3.52,DEOK:5.35,DL:2.11,Dominion:20.09,DPL:1.73,ECP:0.17,EKPC:1.73,HTP:0.07,JCPL:1.98,ME:1.63,Neptune:0.43,OVEC:0.07,PECO:3.59,PENELEC:1.68,PEPCO:3.91,PPL:3.64,PSEG:3.93,RE:0.14 Reliability driver (47.25%): AEP:90.58,ComEd:9.42
b3775.7 | PJM WEST | AEP | IN | Dumont | Upgrade the limiting element at Dumont substation to increase the rating of the Stillwell-Dumont 345 kV line to match conductor rating. | Baseline | 345 | Substation | Congestion Relief - Economic,Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Winter generator deliverability flowgates on Crete-St. John 345 kV (MDW1-GD-W172 etc.), E. Frankfort-Crete 345 kV (MDW1-GD-W332/W331), University Park N-Olive 345 kV (MDW1-GD-W392/W393), and Stillwell-Dumont 345 kV (MDW1-GD-S1620). Also addresses market efficiency congestion (COMED-NIPSCO-AEP area). Additional benefit: remediation of aging/EOL infrastructure on ComEd and NEET sections of the affected 345 kV double circuits; Joliet units 6/7/8 deactivation (1,381 MW) reflected as sensitivity. ¦ I | {'source_document': 'Final Review and Recommendation - 2022 Multi-Driver Proposal Window No. 1 (January 11, 2023)', 'subcomponents': [{'id': 'B3775.1', 'description': 'Swap NIPSCO Green Acre Tap towers from St. John-Green Acres-Olive to Uni Park N-Olive 345 kV line', 'entity': 'NEET', 'cost_million' | 20230110-final-review-and-recommendation---2022-multi-driver-proposal-window-no-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json ¦ 20230711-pjm-teac-board-whitepaper-july-2023-public.json | 2023-01-01 | 5 | 2 | 2 | 2023-01-10 | 4/11/2023 | 12/1/2026 | 12/1/2026 |  | EP | 15 | Upgrade | No | 2022_MD-644 (modified) | Appendix A | Economic driver (52.75%): AEC:0.87,AEP:24.07,APS:3.95,ATSI:11.04,BGE:4.30,Dayton:3.52,DEOK:5.35,DL:2.11,Dominion:20.09,DPL:1.73,ECP:0.17,EKPC:1.73,HTP:0.07,JCPL:1.98,ME:1.63,Neptune:0.43,OVEC:0.07,PECO:3.59,PENELEC:1.68,PEPCO:3.91,PPL:3.64,PSEG:3.93,RE:0.14 Reliability driver (47.25%): AEP:90.58,ComEd:9.42
b3775.8 | PJM WEST | NEET | IL | St. John | Upgrade the existing terminal equipment (substation conductor) at St. John on the existing Crete to St. John 345 kV line with bundled 2x1590 ACSR Lapwing | Baseline | 345 | Substation | Congestion Relief - Economic,Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Winter generator deliverability flowgates on Crete-St. John 345 kV (MDW1-GD-W172 etc.), E. Frankfort-Crete 345 kV (MDW1-GD-W332/W331), University Park N-Olive 345 kV (MDW1-GD-W392/W393), and Stillwell-Dumont 345 kV (MDW1-GD-S1620). Also addresses market efficiency congestion (COMED-NIPSCO-AEP area). Additional benefit: remediation of aging/EOL infrastructure on ComEd and NEET sections of the affected 345 kV double circuits; Joliet units 6/7/8 deactivation (1,381 MW) reflected as sensitivity. ¦ I | {'source_document': 'Final Review and Recommendation - 2022 Multi-Driver Proposal Window No. 1 (January 11, 2023)', 'subcomponents': [{'id': 'B3775.1', 'description': 'Swap NIPSCO Green Acre Tap towers from St. John-Green Acres-Olive to Uni Park N-Olive 345 kV line', 'entity': 'NEET', 'cost_million' | 20230110-final-review-and-recommendation---2022-multi-driver-proposal-window-no-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json ¦ 20230711-pjm-teac-board-whitepaper-july-2023-public.json | 2023-01-01 | 5 | 2.34 | 2 | 2023-01-10 | 1/10/2023 | 12/1/2026 | 3/30/2027 |  | EP | 15 | Upgrade | No | 2022_MD-644 (modified) | Appendix A | Economic driver (52.75%): AEC:0.87,AEP:24.07,APS:3.95,BGE:4.30,Dayton:3.52,DEOK:5.35,Dominion:20.09,DPL:1.73,DL:2.11,ECP:0.17,EKPC:1.73,ATSI:11.04,HTP:0.07,JCPL:1.98,ME:1.63,Neptune:0.43,OVEC:0.07,PECO:3.59,PENELEC:1.68,PEPCO:3.91,PPL:3.64,PSEG:3.93,RE:0.14 Reliability driver (47.25%): ComEd:62.41,Dayton:37.59
b3775.9 | PJM WEST | NEET | IL | Green Acres | Upgrade the existing terminal equipment (substation conductor) at Green Acres on the existing St. John to Green Acres 345 kV line with bundled 2x1590 ACSR Lapwing | Baseline | 345 | Substation | Congestion Relief - Economic,Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Winter generator deliverability flowgates on Crete-St. John 345 kV (MDW1-GD-W172 etc.), E. Frankfort-Crete 345 kV (MDW1-GD-W332/W331), University Park N-Olive 345 kV (MDW1-GD-W392/W393), and Stillwell-Dumont 345 kV (MDW1-GD-S1620). Also addresses market efficiency congestion (COMED-NIPSCO-AEP area). Additional benefit: remediation of aging/EOL infrastructure on ComEd and NEET sections of the affected 345 kV double circuits; Joliet units 6/7/8 deactivation (1,381 MW) reflected as sensitivity. ¦ I | {'source_document': 'Final Review and Recommendation - 2022 Multi-Driver Proposal Window No. 1 (January 11, 2023)', 'subcomponents': [{'id': 'B3775.1', 'description': 'Swap NIPSCO Green Acre Tap towers from St. John-Green Acres-Olive to Uni Park N-Olive 345 kV line', 'entity': 'NEET', 'cost_million' | 20230110-final-review-and-recommendation---2022-multi-driver-proposal-window-no-1.json ¦ 20230207-informational-only---pjm-teac-board-whitepaper-february-2023-public.json ¦ 20230711-pjm-teac-board-whitepaper-july-2023-public.json | 2023-01-01 | 5 | 2.34 | 2 | 2023-01-10 | 1/10/2023 | 12/1/2026 | 3/30/2027 |  | EP | 15 | Upgrade | No | 2022_MD-644 (modified) | Appendix A | Economic driver (52.75%): AEC:0.87,AEP:24.07,APS:3.95,BGE:4.30,Dayton:3.52,DEOK:5.35,Dominion:20.09,DPL:1.73,DL:2.11,ECP:0.17,EKPC:1.73,ATSI:11.04,HTP:0.07,JCPL:1.98,ME:1.63,Neptune:0.43,OVEC:0.07,PECO:3.59,PENELEC:1.68,PEPCO:3.91,PPL:3.64,PSEG:3.93,RE:0.14 Reliability driver (47.25%): ComEd:54.45,Dayton:45.55
b3779 | PJM SOUTH | Dominion | VA | Poland, Evergreen Mills, Brambleton | Cut existing 230 kV line #2183 and extend from Poland Road substation to Evergreen Mills substation. Approximately 0.59 miles of new line will be built from the cut-in to the Evergreen Mills substation. Cut and extend the existing 230 kV line #2183 creating a new line #2210 from Brambleton substation to be terminated at Evergreen Mills substation. Approximately 0.59 miles of new line will be built from the cut-in to the Evergreen Mills substation. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 7.71 | 7.71 | 2023-04-11 | 4/11/2023 | 6/1/2027 | 6/1/2027 |  | EP | 20 | Modify | No | 2022_2-648 | Appendix A | Dominion:100
b3785.1 | PJM WEST | AEP | WV | Mountaineer--(38.9761,-81.9418)-{025BB5E3-5A02-446C-9CBB-CBE3B1E1D244} | Replace existing 3000A wave trap at Mountaineer 765 kV, on the Belmont-Mountaineer 765 kV line, with a new 5000 A wave trap. | Baseline | 765 | Wave Trap | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.46 | 0.46 | 2023-12-05 | 12/5/2023 | 6/1/2028 | 1/14/2027 |  | EP | 5 | Replace | No |  | Appendix A | AEP:100
b3788.1 | PJM WEST | AEP | OH | Kyger Creek--(38.9122,-82.131)-{3C9F378E-8BA4-4FA8-8960-B7E684E56A48} | Replace AEP-owned station takeoff riser and breaker BB risers at OVEC-owned Kyger Creek station. | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.41 | 0.41 | 2023-12-05 | 12/5/2023 | 6/1/2028 | 4/3/2028 |  | EP | 5 | Replace | No |  | Appendix A | AEP:100
b3788.2 | PJM WEST | OVEC | WV | Kyger Creek--Sporn | Replace OVEC-owned breaker AA risers, bus work, and breaker AA disconnect switches at OVEC-owned Kyger Creek station. | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.75 | 0.75 | 2023-12-05 | 12/5/2023 | 6/1/2028 | 6/1/2028 |  | EP | 0 | Replace | No |  | Appendix A | OVEC:100
b3791.0 | PJM MA | PENELEC |  | Meshoppen - Mehoopany | Rebuild the North Meshoppen-Mehoopany No. 1 115 kV line with 795 ACSR 26/7 STR conductor. Upgrade terminal equipment to exceed transmission line ratings. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In the 2028 RTEP summer case, the North Meshoppen-Mehoopany 115 kV line No. 1 segment is overloaded under one N-1 and multiple N-2 outages. |  | 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2024-01-01 | 1 | 17.4 | 17.4 | 2023-10-19 | 11/16/2023 | 6/1/2028 | 6/11/2027 |  | EP | 3 | Rebuild | No | 2023-W1-746 | Appendix A | PENELEC:100
b3792.0 | PJM MA | PENELEC |  | Meshoppen - Mehoopany | Rebuild the North Meshoppen-Mehoopany No. 2 115 kV line using 795 ACSR 26/7 STR conductor, and upgrade terminal equipment to exceed the transmission line rating. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In the 2028 RTEP summer case, the North Meshoppen-Mehoopany 115 kV line No. 2 segment is overloaded under one N-1 and multiple N-2 outages. |  | 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2024-01-01 | 1 | 17.7 | 17.7 | 2023-10-19 | 11/16/2023 | 6/1/2028 | 12/17/2027 |  | EP | 3 | Rebuild | No | 2023-W1-158 | Appendix A | PENELEC:100
b3793.1 | PJM MA | DPL | MD | Silver Run - Cedar Creek | Reconductor Silver Run-Cedar Creek 230 kV line. Reconductor 8.8 miles of 230 kV circuit with 1594-T11/ACCR “Lapwing” conductor and replace all insulators with high-temp. hardware. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Administrative reassignment: project ID b3793.3 cancelled and reassigned as b3793.4 to correct Designated Entity from Exelon to LS Power. No cost change. ¦ New project ID replacing b3793.3; administrative reassignment to correct Designated Entity to LS Power. No cost change. ¦ Administrative reassignment: project was incorrectly assigned to Exelon; new ID b3793.4 assigned with Designated Entity corrected to LS Power. No cost change. |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 3 | 7.68 | 7.68 | 2023-10-31 | 12/5/2023 | 6/1/2028 | 6/1/2028 |  | EP | 0 | Reconductor | No | 2023-W1-573 | Appendix A | DPL:100
b3793.2 | PJM MA | DPL | MD | Cedar Creek | Replace three (3) standalone CTs, disconnect switch, stranded bus and rigid bus to achieve higher rating at Cedar Creek. | Baseline | 230 | Disconnect Switch | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Administrative reassignment: project ID b3793.3 cancelled and reassigned as b3793.4 to correct Designated Entity from Exelon to LS Power. No cost change. ¦ New project ID replacing b3793.3; administrative reassignment to correct Designated Entity to LS Power. No cost change. ¦ Administrative reassignment: project was incorrectly assigned to Exelon; new ID b3793.4 assigned with Designated Entity corrected to LS Power. No cost change. |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 3 | 0.45 | 0.45 | 2023-10-31 | 12/5/2023 | 6/1/2028 | 6/1/2028 |  | EP | 0 | Replace | No | 2023-W1-573 | Appendix A | DPL:100
b3793.3 | PJM MA | DPL | MD | Silver Run | Replace three (3) 1-1590 ACSR jumpers and one (1) air disconnect switch at Silver Run. | Baseline | 230 | Disconnect Switch | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Administrative reassignment: project ID b3793.3 cancelled and reassigned as b3793.4 to correct Designated Entity from Exelon to LS Power. No cost change. ¦ New project ID replacing b3793.3; administrative reassignment to correct Designated Entity to LS Power. No cost change. ¦ Administrative reassignment: project was incorrectly assigned to Exelon; new ID b3793.4 assigned with Designated Entity corrected to LS Power. No cost change. |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 3 | 0.58 | 0.58 | 2023-10-31 | 12/5/2023 | 6/1/2028 | 6/1/2028 |  | Cancelled | 0 | Replace | No | 2023-W1-573 | Appendix A | DPL:100
b3793.4 | PJM MA | DPL | MD | Silver Run | Replace three (3) 1-1590 ACSR jumpers and one (1) air disconnect switch at Silver Run 230 kV substation. | Baseline | 230 | Disconnect Switch | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Administrative reassignment: project ID b3793.3 cancelled and reassigned as b3793.4 to correct Designated Entity from Exelon to LS Power. No cost change. ¦ New project ID replacing b3793.3; administrative reassignment to correct Designated Entity to LS Power. No cost change. ¦ Administrative reassignment: project was incorrectly assigned to Exelon; new ID b3793.4 assigned with Designated Entity corrected to LS Power. No cost change. |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 3 | 0.58 | 0.58 | 2025-05-06 | 5/6/2025 | 6/1/2028 |  |  | EP | 0 | Replace | No | 2023-W1-573 | Appendix A | DPL:100
b3794.1 | PJM MA | PSEG | NJ | Waldwick | Replace existing Waldwick 230 kV 50 MVAR fixed shunt reactor with a 230 kV 150 MVAR variable shunt reactor. | Baseline | 230 | Reactive Device | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In the 2028 RTEP light load case, Hinchmans, Hawthorne, Waldwick and Fairlawn 230 kV and Waldwick 345 kV buses are observing high voltage violations under one N-1 and multiple N-2 outages. |  | 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2024-01-01 | 1 | 32.8 | 13.6 | 2023-10-31 | 12/5/2023 | 6/1/2028 | 6/1/2028 |  | UC | 44 | Replace | No | 2023-W1-107 | Appendix A | PSEG:100
b3794.2 | PJM MA | PSEG | NJ | Waldwick | Replace existing Waldwick 345 kV 100 MVAR fixed shunt reactor with a 345 kV 150 MVAR variable shunt reactor. | Baseline | 345 | Reactive Device | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In the 2028 RTEP light load case, Hinchmans, Hawthorne, Waldwick and Fairlawn 230 kV and Waldwick 345 kV buses are observing high voltage violations under one N-1 and multiple N-2 outages. |  | 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2024-01-01 | 1 | 0 | 16 | 2023-10-31 | 12/5/2023 | 6/1/2028 | 6/1/2028 |  | UC | 44 | Replace | No | 2023-W1-107 | Appendix A | PSEG:100
b3796.0 | PJM WEST | APS | WV | Belmont | Replace the Belmont 765/500 kV transformer No. 5 with a new transformer bank consisting of three single-phase transformers and an additional single phase spare transformer. The project will also replace 500 kV disconnect switches at the Belmont substation. | Baseline | 765/500 | Transformer | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In the 2028 RTEP summer case, the Belmont 765/500 kV transformer is overloaded under one N-1 and multiple N-2 outages. |  | 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2024-01-01 | 1 | 42.05 | 42.05 | 2024-01-09 | 1/9/2024 | 6/1/2028 | 6/1/2028 |  | EP | 0 | Replace | No | 2023-W1-903 | Appendix A | AEP:0.28,APS:0.15,Dayton:0.10,DEOK:0.18,DL:6.57,Dominion:92.68,EKPC:0.04 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.1 | PJM MA | PPL | PA |  | Build New Otter Creek 500 kV (Collinsville) - (switching station -Two bay three breaker configuration). | Baseline | 500 | Circuit Switcher | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 32.76 | 32.76 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 4/23/2027 |  | EP | 5 | Build | No | 2022-W3-374 | Appendix A | APS:13.16,BGE:0.71,Dominion:74.28,DPL:0.36,PECO:0.68,PEPCO:10.59,PPL:0.22 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.10 | PJM MA | ME | PA |  | Rebuild the Germantown-Lincoln 115 kV line for 230 kV double circuit construction. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 30.1 | 30.1 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | EP | 0 | Rebuild | No | 2022-W3-837 | Appendix A | ME:100
b3800.100 | PJM WEST | AEP | VA | Cloverdale | Establish a new 500 kV breaker position for the low-side of the existing 765/500 kV transformer at Cloverdale Station. The new position will be between two new 500 kV circuit breakers located in a new breaker string, electrically converting the 500 kV yard to "double-bus double-breaker" configuration. | Baseline | 500 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 11.59 | 11.59 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2027 |  | EP | 10 | Install | No | 2022-W3-410 | Appendix A | AEP:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.101 | PJM WEST | APS | PA | 502 Junction | 502 Junction substation two 500 kV circuit breaker expansion. | Baseline | 500 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 30.6 | 30.6 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/1/2028 |  | EP | 30 | Upgrade | No | 2022-W3-853 | Appendix A | APS:25.59,BGE:9.79,Dominion:51.94,PEPCO:12.68 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.102 | PJM WEST | NEET | VA | Woodside | New 500 kV line from existing 502 Junction substation to the demarcation point between FE/NEET around Gore substation (bypass Black Oak) (NEET Portion). | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 719.6 | 632.6 | 2023-12-05 | 1/6/2026 | 6/1/2027 | 12/31/2031 |  | EP | 7 | Build | No | 2022-W3-853 | Appendix A | APS:25.59,BGE:9.79,Dominion:51.94,PEPCO:12.68 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.103 | PJM WEST | APS | VA | Woodside | Rebuild ~16 miles of the Gore-Stonewall 138 kV line with 500 kV overbuild (502 Jct to Woodside 500 kV line section). | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 158.8 | 151.72 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | EP | 30 | Build | No | 2022-W3-853 | Appendix A | APS:25.59,BGE:9.79,Dominion:51.94,PEPCO:12.68 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.104 | PJM WEST | APS | WV | Woodside | Rebuild ~15 miles of the Stonewall-Millville 138 kV line with 500 kV overbuild (502 Jct to Woodside 500 kV line section). | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 165.23 | 136.93 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2030 |  | EP | 30 | Build | No | 2022-W3-853 | Appendix A | APS:9.18,BGE:7.21,Dominion:72.52,PEPCO:11.09 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.105 | PJM WEST | APS | VA | Woodside | Rebuild Millville-Doubs 138 kV for ~16 miles from structure MVF1-39 to structure MVF1-101(outside of Doubs Substation) with 500 kV overbuild | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 162.11 | 147.45 | 2023-12-06 | 12/6/2023 | 6/1/2027 | 6/1/2028 |  | EP | 30 | Build | No | 2022-W3-853 | Appendix A | APS:9.18,BGE:7.21,Dominion:72.52,PEPCO:11.09 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.106 | PJM WEST | NEET | VA | Woodside | Woodside 500 kV substation (Except terminations, Transformer, Cap Banks and Statcom). | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 86.2 | 77.6 | 2023-12-05 | 1/6/2026 | 6/1/2027 | 12/31/2028 |  | EP | 7 | Build | No | 2022-W3-853 | Appendix A | APS:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.107 | PJM WEST | NEET | VA | Woodside | Line Termination cost at Woodside 500 kV for 502 Jct to Woodside 500 kV line. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.8 | 0.7 | 2023-12-05 | 1/6/2026 | 6/1/2027 | 12/31/2031 |  | EP | 7 | Modify | No | 2022-W3-853 | Appendix A | APS:25.59,BGE:9.79,Dominion:51.94,PEPCO:12.68 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.108 | PJM WEST | NEET | VA | Woodside | Line Termination cost at Woodside 500 kV for Woodside to Aspen 500 kV line. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.8 | 0.7 | 2023-12-05 | 1/6/2026 | 6/1/2027 | 12/31/2031 |  | EP | 7 | Modify | No | 2022-W3-853 | Appendix A | APS:9.18,BGE:7.21,Dominion:72.52,PEPCO:11.09 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.109 | PJM WEST | NEET | VA | Woodside | Termination work for two 500/138 kV transformer at Woodside 500 kV substation | Baseline | 500/138 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 1.9 | 1.7 | 2023-12-05 | 1/6/2026 | 6/1/2027 | 12/31/2028 |  | EP | 7 | Build | No | 2022-W3-853 | Appendix A | APS:100
b3800.11 | PJM MA | ME | PA |  | Rebuild the Hunterstown-Lincoln 115 kV line for 230 kV double circuit construction. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 11.48 | 11.48 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | EP | 0 | Rebuild | No | 2022-W3-837 | Appendix A | ME:100
b3800.110 | PJM WEST | NEET | VA | Woodside | Two 500/138 kV transformers at Woodside 500 kV substation. | Baseline | 500/138 | Transformer | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 56.7 | 49.4 | 2023-12-05 | 1/6/2026 | 6/1/2027 | 12/31/2028 |  | EP | 7 | Install | No | 2022-W3-853 | Appendix A | APS:100
b3800.111 | PJM WEST | APS | VA | Woodside | Construct the Woodside-Stonewall 138 kV No. 1 line. | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 6.28 | 6.28 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2027 |  | EP | 30 | Build | No | 2022-W3-853 | Appendix A | APS:100
b3800.112 | PJM WEST | APS | VA | Woodside | Construct the Woodside-Stonewall 138 kV No. 2 line. | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 6.31 | 6.31 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2027 |  | EP | 30 | Build | No | 2022-W3-853 | Appendix A | APS:100
b3800.113 | PJM WEST | NEET | VA | Woodside | Two 150 MVAR Cap banks and one +500/-500 MVAR STATCOM at Woodside 500 kV substation. | Baseline | 500 | Capacitor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 92.6 | 80.7 | 2023-12-05 | 1/6/2026 | 6/1/2027 | 12/31/2028 |  | EP | 7 | Install | No | 2022-W3-853 | Appendix A | APS:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.114 | PJM WEST | APS | VA | Woodside | Stonewall 138 kV substation two 138kV breaker expansion. | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 8.3 | 8.3 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2027 |  | UC | 30 | Upgrade | No | 2022-W3-853 | Appendix A | APS:100
b3800.115 | PJM WEST | NEET | VA | Woodside | Line work for terminating Doubs to Bismark line for Doubs side for Woodside 500 kV substation. (NEET Portion) | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.8 | 0.7 | 2023-12-05 | 1/6/2026 | 6/1/2027 | 12/31/2028 |  | EP | 7 | Modify | No | 2022-W3-853 | Appendix A | APS:27.49,BGE:9.83,Dominion:53.78,PEPCO:8.90 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.116 | PJM WEST | APS | VA | Woodside | Line work for terminating Doubs to Bismark line for Doubs side for Woodside 500 kV substation. (FE Portion) | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.06 | 0.06 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2027 |  | EP | 0 | Modify | No | 2022-W3-853 | Appendix A | APS:27.49,BGE:9.83,Dominion:53.78,PEPCO:8.90 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.117 | PJM WEST | NEET | VA | Woodside | Line work for terminating Doubs to Bismark line for Bismark side for Woodside 500 kV substation. (NEET Portion) | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.8 | 0.7 | 2023-12-05 | 1/6/2026 | 6/1/2027 | 12/31/2028 |  | EP | 7 | Modify | No | 2022-W3-853 | Appendix A | APS:21.09,BGE:6.55,Dominion:64.94,PEPCO:7.42 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.118 | PJM WEST | Dominion | VA | Woodside | Line work for terminating Doubs to Bismark line into Woodside 500 kV substation. (DOM Portion) | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 5.1 | 5.1 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | EP | 10 | Modify | No | 2022-W3-853 | Appendix A | APS:21.09,BGE:6.55,Dominion:64.94,PEPCO:7.42 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.119 | PJM WEST | NEET | VA | Woodside | New 500 kV transmission line from Woodside substation to Aspen substation (in DOM zone). (NEET Portion) | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 71.72 | 71.72 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/31/2028 |  | Cancelled | 0 | Build | No | 2022-W3-853 | Appendix A | APS:9.18,BGE:7.21,Dominion:72.52,PEPCO:11.09 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.12 | PJM MA | ME | PA |  | Rebuild the Germantown-Carroll 138 kV line for 230 kV double circuit construction (MAIT). | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 12.16 | 12.16 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | EP | 15 | Rebuild | No | 2022-W3-837 | Appendix A | ME:100
b3800.120 | PJM SOUTH | Dominion | VA | Aspen | Terminate new NextEra 500 kV line from Woodside into Goose Creek substation (instead of termination at the new Aspen substation). The Goose Creek 500 kV cap bank will be moved to Aspen substation | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 30.49 | 30.49 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 9/30/2030 |  | EP | 10 | Build | No | 2022-W3-853 | Appendix A | APS:9.18,BGE:7.21,Dominion:72.52,PEPCO:11.09 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.121 | PJM WEST | AEP | PA | 502 Junction | Kammer to 502 Junction 500 kV line: Conduct LIDAR Sag Study to assess SE rating and needed upgrades. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.1 | 0.1 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2027 |  | EP | 0 | Sag Study | No | 2022-W3-853 | Appendix A | AEP:21.66,APS:0.01,BGE:7.14,DEOK:0.01,Dominion:62.25,PEPCO:8.93 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.122 | PJM SOUTH | APS | VA | Doubs | Rebuild 500 kV line No. 514 from Doubs-Goose Creek 500 kV line. The Doubs-Goose Creek 500 kV line will be rebuilt (APS Portion) | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 103.27 | 103.27 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2030 |  | EP | 0 | Build | No | 2022-W3-837 | Appendix A | APS:0.08,Dominion:99.90,PEPCO:0.02 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.123 | PJM SOUTH | APS | VA | Doubs | Doubs substation work - Re-terminate the rebuilt Doubs-Goose Creek 500 kV line in its existing bay, Terminate the new Doubs-Aspen 500 kV line in the open bay at Doubs, Replace three 500 kV breakers, Replace 500 kV terminal equipment including disconnect switches, CTs and substation conductor & Replace relaying. (APS Portion) | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 31.7 | 31.7 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2030 |  | EP | 0 | Build | No | 2022-W3-837 | Appendix A | APS:0.08,Dominion:99.90,PEPCO:0.02 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.124 | PJM SOUTH | APS | VA | Doubs | New Doubs to Aspen 500 kV line - Aspen substation is not yet constructed but is a component in Dominion's proposal 2022-W3-692. (APS Portion) | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 68.8 | 68.8 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2030 |  | EP | 0 | Build | No | 2022-W3-837 | Appendix A | APS:0.09,Dominion:99.89,PEPCO:0.02 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.125 | PJM SOUTH | APS | VA | Doubs | Rebuild the Doubs-Dickerson 230 kV line. This will be underbuilt on the new Doubs-Goose Creek 500 kV line. (APS Portion) | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 13.04 | 13.04 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2030 |  | EP | 0 | Modify | No | 2022-W3-837 | Appendix A | PEPCO:100
b3800.126 | PJM SOUTH | APS | VA | Doubs | Rebuild the Doubs-Aqueduct 230 kV line. This will be underbuilt on the new Doubs-Aspen 500 kV line. (APS Portion) | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 11.35 | 11.35 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2030 |  | EP | 3 | Modify | No | 2022-W3-837 | Appendix A | PEPCO:100
b3800.127 | PJM SOUTH | APS | VA | Doubs | Rebuild the Dickerson-Aqueduct 230 kV line. This will be underbuilt on the new Doubs-Aspen 500 kV line. (APS Portion) | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 6.8 | 6.8 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2030 |  | EP | 0 | Modify | No | 2022-W3-837 | Appendix A | PEPCO:100
b3800.128 | PJM WEST | APS | MD | Doubs | Construct new Woodside-Goose Creek 500 kV line for ~15 miles on single circuit monopole structures within the Doubs-Goose Creek Corridor. (FE Portion) | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 115.3 | 115.3 | 2024-07-10 | 7/10/2024 | 6/1/2027 | 12/31/2031 |  | EP | 30 | Construct | No | 2022-W3-853 | Appendix A | APS:9.26,BGE:7.30,Dominion:72.31,PEPCO:11.13 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.129 | PJM WEST | APS | MD | Doubs | Construct 500 kV line from existing structure MVF1-101 on the Doubs-Millville 138 kV line around Doubs substation and into the entrance of the Doubs-Goose Creek corridor. (~2 miles) | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 13.2 | 13.2 | 2024-07-10 | 7/10/2024 | 6/1/2027 | 6/1/2031 |  | EP | 30 | Construct | No | 2022-W3-853 | Appendix A | APS:9.26,BGE:7.30,Dominion:72.31,PEPCO:11.13 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.13 | PJM MA | APS | MD |  | Rebuild the Germantown-Carroll 138 kV line to 230 kV double circuit construction (APS-PE Section). | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 47.31 | 47.31 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | EP | 0 | Rebuild | No | 2022-W3-837 | Appendix A | APS:82.49,ME:17.51
b3800.14 | PJM MA | ME | PA |  | Construct New 230 kV Hunterstown-Carroll line (MAIT section). | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 17.37 | 17.37 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | EP | 0 | Construct | No | 2022-W3-837 | Appendix A | APS:99.86,ME:0.14
b3800.15 | PJM MA | APS | MD |  | Construct New 230 kV Hunterstown-Carroll line (APS-PE Section). | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 6.71 | 6.71 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | UC | 50 | Construct | No | 2022-W3-837 | Appendix A | APS:99.86,ME:0.14
b3800.16 | PJM MA | APS | MD |  | Expand Carroll 230 kV substation to ring bus. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 7.62 | 7.62 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | EP | 0 | Modify | No | 2022-W3-837 | Appendix A | APS:99.86,ME:0.14
b3800.17 | PJM MA | APS | MD |  | Network upgrade at Caroll substation. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.43 | 0.43 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | EP | 0 | Upgrade | No | 2022-W3-837 | Appendix A | APS:99.86,ME:0.14
b3800.18 | PJM MA | ME | PA |  | Add a new 230 kV Breaker at the Hunterstown 230 kV substation for the new Hunterstown-Carroll 230 kV termination. | Baseline | 230 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 2.31 | 2.31 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | EP | 0 | Build | No | 2022-W3-837 | Appendix A | APS:99.86,ME:0.14
b3800.19 | PJM MA | ME | PA |  | Reconductor Lincoln-Orrtanna 115 kV line. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 10.98 | 10.98 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | UC | 50 | Reconductor | No | 2022-W3-837 | Appendix A | ME:100
b3800.2 | PJM MA | ME | PA |  | Break the existing TMI-Peach Bottom line within the existing right-of-way and install new structures rerouting the line toward Chanceford switchyard taps being constructed by PPL. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 7.43 | 7.43 | 2023-12-06 | 5/1/2024 | 6/1/2027 | 6/1/2027 |  | EP | 3 | Modify | No | 2022-W3-374, DENL | Appendix A | APS:13.16,BGE:0.71,Dominion:74.28,DPL:0.36,PECO:0.68,PEPCO:10.59,PPL:0.22 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.20 | PJM MA | APS | MD |  | Fayetteville-Grand Point 138 kV – Replace line trap at Grand Point 138 kV. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.4 | 0.4 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2027 |  | EP | 10 | Reconductor | No | 2022-W3-837 | Appendix A | APS:100
b3800.200 | PJM SOUTH | Dominion | VA | Aspen, Golden | Build a new 500kV line from Aspen - Golden on 500/230kV double circuit structures with substation upgrades at Aspen and Golden. New conductor to have a minimum summer normal rating of 4357MVA. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 176.02 | 176.02 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2027 |  | EP | 20 | Build | No | 2022-W3-692 | Appendix A | Dominion:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.201 | PJM SOUTH | Dominion | VA | Golden | Install (2) 500-230kV transformer banks at Golden substation | Baseline | 500/230 | Transformer | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 70 | 70 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2027 |  | EP | 20 | Install | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.202 | PJM SOUTH | Dominion | VA | Aspen | Install (1) 500-230kV transformer bank at Aspen substation | Baseline | 500/230 | Transformer | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 42 | 42 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2027 |  | EP | 20 | Install | No | 2022-W3-692 | Appendix A | Dominion:86.28,PEPCO:13.72
b3800.203 | PJM SOUTH | Dominion | VA | Mars | Install a 2nd 500-230 kV 1440MVA transformer at Mars substation | Baseline | 500/230 | Transformer | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 42.19 | 42.19 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 5/20/2027 |  | UC | 50 | Install | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.204 | PJM SOUTH | Dominion | VA | Golden, Paragon Park | Reconductor 0.5 mile section of 230kV Line #2150 Golden - Paragon Park Circuit 1 to achieve a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 1.44 | 1.44 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 8/2/2027 |  | EP | 0 | Rebuild | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.205 | PJM SOUTH | Dominion | VA | Golden, Paragon Park | Reconductor 0.5 mile section of 230kV Line #2081 Golden - Paragon Park Circuit 2 to achieve a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 1.44 | 1.44 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 8/2/2027 |  | EP | 0 | Rebuild | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.206 | PJM SOUTH | Dominion | VA | Paragon Park | Upgrade Paragon Park substation line conductors to 4000A continuous current rating for 230kV Lines #2081 & Line #2150. | Baseline | 230 | Conductor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.09 | 0.09 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 8/2/2027 |  | EP | 0 | Upgrade | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.207 | PJM SOUTH | Dominion | VA | Paragon Park, BECO | Reconductor 230kV Line #2207 Paragon Park - Beco to achieve a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 3.36 | 3.36 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 8/2/2027 |  | EP | 0 | Rebuild | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.208 | PJM SOUTH | Dominion | VA | Paragon Park | Upgrade Paragon Park substation conductor and line leads to 4000A continuous current rating for 230kV Line #2207. | Baseline | 230 | Conductor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.1 | 0.1 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 5/28/2027 |  | EP | 0 | Upgrade | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.209 | PJM SOUTH | Dominion | VA | BECO | Upgrade BECO substation equipment to 4000A continuous current rating for 230kV Line #2207. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 1.86 | 1.86 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 5/28/2027 |  | EP | 0 | Upgrade | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.21 | PJM MA | APS | MD |  | Reid-Ringgold 138 kV – Replace line trap, substation conductor, breaker, relaying and CTs at Ringgold. | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 3.8 | 3.8 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2027 |  | EP | 30 | Replace | No | 2022-W3-837 | Appendix A | APS:100
b3800.210 | PJM SOUTH | Dominion | VA | Mars, Lockridge | Build a new 230kV line from Mars - Prentice Drive on 500/230kV double circuit structures to achieve a summer rating of 1573 MVA. Install 230kV equipment at Mars and Prentice Drive. Remove 230 kV line No. 2095 Mars-Shellhorn and 230 kV line No. 2292 Mars-Sojourner in the existing transmission corridor between Sojourner and Mars substations so that they can be rerouted to the south side of Mars substation, adding approximately 2 miles of new conductor. This is to allow for termination of the line No.2413 and 5003 Golden-Mars 230 and 500 kV circuits into Mars substation. Cut 230 kV line No. 2095 Mars-Shellhorn into Sojourner substation, creating 230 kV line No. 2427 (Mars-Sojourner) and 230 kV line No. 2095 (Sojourner-Shellhorn). Upgrade 4 230 kV breakers at Sojourner substation from 63 kA to 80 kA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 150.8 | 150.8 | 2023-10-31 | 12/8/2025 | 6/1/2027 | 6/1/2027 |  | EP | 10 | Build | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.211 | PJM SOUTH | Dominion | VA | Lockridge, Golden | Build a new 230kV line from Prentice Drive - Golden on 500/230kV double circuit structures to achieve a summer rating of 1573 MVA. Install 230kV equipment at Golden and Prentice. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 52.78 | 52.78 | 2023-10-31 | 12/8/2025 | 6/1/2027 | 6/1/2027 |  | EP | 10 | Build | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.212 | PJM SOUTH | Dominion | VA | Mars, Golden | Build a new 500kV Line from Mars-Golden on 500/230kV double circuit structures with substation upgrades at Golden and Mars. New conductor to have a monimum summer normal rating of 4357 MVA. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 228.04 | 228.04 | 2023-10-31 | 4/1/2025 | 6/1/2027 | 6/1/2028 |  | EP | 10 | Build | No | 2022-W3-692 | Appendix A | APS:99.96,Dominion:0.04 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.213 | PJM SOUTH | Dominion | VA | Brambleton, Goose Creek | Cut 500kV Line # 558 Brambleton - Goose Creek into Aspen substation. Upgrade 500kV terminal equipment at Aspen and Goose Creek to 5000A continuous rating current. At Goose Creek, replace circuit breakers 59582 and 55882, and associated disconnect switches, breaker leads, bus, and line risers to accommodate 5000A rating. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 50.12 | 50.12 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2027 |  | EP | 25 | Modify | No | 2022-W3-692 | Appendix A | APS:99.39,Dominion:0.61 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.214 | PJM SOUTH | Dominion | VA | Aspen, Goose Creek | Build a new 500kV Line from Aspen - Goose Creek to achieve a summer rating of 4357 MVA. Install new 500kV terminal equipment at Aspen. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 38.53 | 38.53 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2027 |  | EP | 20 | Build | No | 2022-W3-692 | Appendix A | APS:99.39,Dominion:0.61 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.215 | PJM SOUTH | Dominion | VA | Sterling Park, Paragon Park | Cut 230kV Line #2150 Sterling Park - Paragon Park Circuit 1 into Golden substation and install 230kV equipment at Golden. Upgrade relay settings at Golden substation for upgrading 230kV Line #2150 to 4000A continuous current rating. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 57.62 | 57.62 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2027 |  | EP | 20 | Modify | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.216 | PJM SOUTH | Dominion | VA | Sterling Park, Paragon Park | Cut 230kV Line #2081 Sterling Park - Paragon Park Circuit 2 into Golden substation and install 230kV equipment at Golden. Upgrade relay settings at Golden substation for upgrading 230kV Line #2081 to 4000A continuous current rating. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 57.62 | 57.62 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2027 |  | EP | 20 | Modify | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.217 | PJM SOUTH | Dominion | VA | Aspen, Sycolin Creek | Build a new 230kV line from Aspen - Sycolin Creek on 500/230kV double circuit structures to achieve a summer rating of 1573 MVA. Install 230kV equipment at Golden and Sycolin Creek. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 60.42 | 60.42 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2027 |  | EP | 20 | Rebuild | No | 2022-W3-692 | Appendix A | Dominion:86.28,PEPCO:13.72
b3800.218 | PJM SOUTH | Dominion | VA | Sycolin Creek, Golden | Build a new 230kV line from Sycolin Creek - Golden on 500/230kV double circuit structures to achieve a summer rating of 1573 MVA. Install 230kV equipment at Golden and Sycolin Creek. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 69.83 | 69.83 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2027 |  | EP | 20 | Rebuild | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.22 | PJM MA | ME | PA |  | Install DTT relaying at Straban substation. | Baseline | 115 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.67 | 0.67 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | EP | 0 | Install | No | 2022-W3-837 | Appendix A | ME:100
b3800.225 | PJM SOUTH | Dominion | VA | Brambleton | Change 500kV Line #558 destination at Brambleton to Aspen Substation and upgrade line protection relays | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.23 | 0.23 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2027 |  | EP | 20 | Modify | No | 2022-W3-692 | Appendix A | APS:5.20,DL:0.46,Dominion:91.40,ME:0.59,PEPCO:2.35 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.226 | PJM SOUTH | Dominion | VA | Paragon Park | Change 230kV Lines # 2081 and 2150 at Paragon Park substation destination to Golden Substation and upgrade line protection relays | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.3 | 0.3 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2027 |  | EP | 20 | Modify | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.227 | PJM SOUTH | Dominion | VA | Sterling Park | Change 230kV Lines # 2081 and 2150 at Sterling Park substation destination to Golden Substation and upgrade line protection relays | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.3 | 0.3 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2027 |  | EP | 20 | Modify | No | 2022-W3-692 | Appendix A | Dominion:100
b3800.228 | PJM SOUTH | Dominion | VA | Sterling Park, Golden | Reconductor 1.47 miles of 230kV circuits 2081 and 2150 from Sterling Park to Golden substation. Upgrade terminal equipment at Sterling Park to 4000A continuous current | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 7.97 | 7.97 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 8/2/2027 |  | EP | 0 | Reconductor | No | Additional Identified Upgrades | Appendix A | Dominion:100
b3800.229 | PJM SOUTH | Dominion | VA | Davis Drive, Sterling Park | Reconductor 0.67 miles of 230kV circuits 2194 and 9231 from Davis Drive to Sterling Park substation. Terminal equipment at remote end substations will be installed or upgraded to 4000A continuous current rating to support new conductor ratings | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 5.53 | 5.53 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 9/19/2027 |  | EP | 0 | Reconductor | No | Additional Identified Upgrades | Appendix A | Dominion:100
b3800.23 | PJM MA | ME | PA |  | Revise Relay Settings at Lincoln substation. | Baseline | 115 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.31 | 0.31 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | EP | 0 | Modify | No | 2022-W3-837 | Appendix A | ME:100
b3800.230 | PJM SOUTH | Dominion | VA | Breezy Knoll | Reset relays at Breezy Knoll for the revised current rating of 230kV Line #2098 Plesant View - Hamilton | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.02 | 0.02 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 9/13/2030 |  | EP | 10 | Modify | No | 2022-W3-516 | Appendix A | Dominion:100
b3800.231 | PJM SOUTH | Dominion | VA | Dry Mill | Reset relays at Dry Mill for the revised current rating of 230kV Line #2098 Plesant View - Hamilton | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.02 | 0.02 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 9/13/2030 |  | EP | 10 | Modify | No | 2022-W3-516 | Appendix A | Dominion:100
b3800.232 | PJM SOUTH | Dominion | VA | Hamilton | Reset relays at Hamilton for the revised current rating of 230kV Line #2098 Plesant View - Hamilton | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.01 | 0.01 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 9/13/2030 |  | EP | 10 | Modify | No | 2022-W3-516 | Appendix A | Dominion:100
b3800.233 | PJM SOUTH | Dominion | VA | Pleasant View | Upgrade equipment to 4000A continuous current rating at Pleasant View substation in support of 230kV Line #2098 wreck and rebuild. Replace circuit breakers 274T2098 & 2098T2180 and associated disconnect switches, breaker leads, bus, and line risers to accommodate 4000A rating | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 6.24 | 1.81 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 9/13/2030 |  | EP | 10 | Modify | No | 2022-W3-516 | Appendix A | Dominion:100
b3800.234 | PJM SOUTH | Dominion | VA | Pleasant View | Wreck and rebuild approximately one (1) mile of 230kV Line #2098 between Pleasant View and structure 2098/9, where Line #2098 turn towards Hamilton substation | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 3.44 | 3.44 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 9/13/2030 |  | EP | 10 | Reconductor | No | 2022-W3-516 | Appendix A | Dominion:100
b3800.238 | PJM SOUTH | Dominion | VA | Pleasant View | Upgrade equipment to 4000A continuous current rating at Pleasant View substation in support of 230kV Line #203 rebuild. Replace circuit breakers 203T274 & L3T203 and associated disconnect switches, breaker leads, bus, and line risers to accommodate 4000A rating | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 1.81 | 1.81 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 9/13/2030 |  | EP | 0 | Modify | No | 2022-W3-516 | Appendix A | APS:8.09,BGE:8.25,Dominion:64.87,PEPCO:18.79
b3800.239 | PJM SOUTH | Dominion | VA | Pleasant View | Wreck and rebuild 230kV Line #203 between Pleasant View and structure 203/15 using double circuit 500/230kV structures. The 500kV line is from Aspen - Doubs. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 6.87 | 6.87 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 9/13/2030 |  | EP | 0 | Rebuild | No | 2022-W3-516 | Appendix A | APS:8.09,BGE:8.25,Dominion:64.87,PEPCO:18.79
b3800.24 | PJM MA | ME | PA |  | Revise Relay Settings at Germantown substation. | Baseline | 115 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.47 | 0.47 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | EP | 0 | Modify | No | 2022-W3-837 | Appendix A | ME:100
b3800.240 | PJM SOUTH | Dominion | VA | Aspen, Doubs | Build a new 500kV line from Aspen - Doubs using double circuit 500/230kV structures. The 230kV line is from Pleasant View - structure 203/15. Install terminal equipment at Aspen for a 5000A line to Doubs (First Energy). This includes GIS breakers, GIS-to-AIS transition equipment, and metering CCVTs and CTs for the tie line. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 41.68 | 41.68 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 9/13/2030 |  | EP | 0 | Build | No | 2022-W3-516 | Appendix A | APS:0.09,Dominion:99.89,PEPCO:0.02 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.241 | PJM SOUTH | Dominion | VA | Goose Creek | Rebuild 500kV Line #514 from Goose Creek - Doubs using 500/230kV double circiut structures. The new double circuit towers will accommodate 230kV Line #2098 between Pleasant View substation and structure 2098/9. Upgrade equipment at Goose Creek to 5000A continuous current rating in support of Line #514 wreck and rebuild. Replace circuit breakers 514T595 & 51482 and associated disconnect switches, breaker leads, bus, and line risers to accommodate 5000A rating. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 16.11 | 16.11 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 9/13/2030 |  | EP | 0 | Rebuild | No | 2022-W3-516 | Appendix A | APS:0.08,Dominion:99.90,PEPCO:0.02 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.242 | PJM SOUTH | Dominion | VA | Edwards Ferry | Upgrading switches 20366M and 20369M and line leads to 4000A continuous current rating of 230kV Line #203 at Edwards Ferry substation | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.51 | 0.51 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 9/13/2030 |  | EP | 0 | Modify | No | 2022-W3-516 | Appendix A | APS:11.45,BGE:14.14,Dominion:42.82,PEPCO:31.59
b3800.243 | PJM SOUTH | PEPCO | VA | Dickerson, Edwards Ferry | Rebuild 7.26 miles of existing 500 kV circuit from Dickerson Station H to Ed's Ferry area to accommodate the new 500 kV circuit between Doubs and Aspen. (The 500 kV portion of the work) | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 37.2 | 37.2 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Rebuild | No | 2022-W3-660 | Appendix A | APS:0.09,Dominion:99.89,PEPCO:0.02 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.244 | PJM SOUTH | PEPCO | VA | Dickerson, Edwards Ferry | Rebuild 7.26 miles of existing 230 kV circuit from Dickerson Station H to Ed's Ferry area to accommodate the new 500 kV circuit between Doubs and Aspen. (The 230kV portion of the project) | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 18.6 | 18.6 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Rebuild | No | 2022-W3-660 | Appendix A | APS:9.78,BGE:12.07,Dominion:51.18,PEPCO:26.97
b3800.245 | PJM SOUTH | PEPCO | VA | Dickerson | Reconfigure Dickerson H 230 kV Substation and upgrade terminal equipment. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 10.58 | 10.58 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Modify | No | 2022-W3-660 | Appendix A | APS:9.78,BGE:12.07,Dominion:51.18,PEPCO:26.97
b3800.25 | PJM MA | APS | MD |  | Taneytown substation terminal upgrade. | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.53 | 0.53 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | EP | 0 | Upgrade | No | 2022-W3-837 | Appendix A | APS:100
b3800.26 | PJM MA | BGE | MD |  | Build High Ridge 500 kV substation - Three bay breaker and half configuration. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0 | 0 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Build | No | 2022-W3-660
b3800.27 | PJM MA | BGE | MD |  | High Ridge 500 kV substation (cut into Brighton-Waugh Chapel 500 kV line) - Waugh Chapel side. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 33.67 | 33.67 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Build | No | 2022-W3-660 | Appendix A | BGE:70.66,PEPCO:29.34 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.28 | PJM MA | BGE | MD |  | High Ridge 500 kV substation (cut into Brighton-Waugh Chapel 500 kV line) -Brighton side. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 33.67 | 33.67 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Build | No | 2022-W3-660 | Appendix A | APS:0.68,BGE:97.41,Dominion:1.91 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.29 | PJM MA | BGE | MD |  | High Ridge termination for the North Delta-High Ridge 500 kV line. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 33.67 | 33.67 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Build | No | 2022-W3-660 | Appendix A | BGE:2.58,Dominion:59.28,DPL:0.02,PEPCO:28.48,PSEG:9.24,RE:0.40 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.3 | PJM MA | PPL | PA |  | Build New 500kV AC line from the new Otter Creek (Chanceford) 500 kV switchyard – towards PA/MD border ~12.5 miles Ø Rebuild the existing Otter Creek - Conastone 230 kV line to become a double-circuit 500 kV line, operate Conastone circuit at 230 kV initially | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 102.8 | 102.8 | 2023-12-06 | 5/1/2024 | 6/1/2027 | 4/30/2027 |  | EP | 5 | Build | No | 2022-W3-374 | Appendix A | APS:13.16,BGE:0.71,Dominion:74.28,DPL:0.36,PECO:0.68,PEPCO:10.59,PPL:0.22 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.30 | PJM MA | BGE | MD |  | High Ridge - Install two 500/230 kV transformers. | Baseline | 500/230 | Transformer | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 22.11 | 22.11 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Install | No | 2022-W3-660 | Appendix A | BGE:62.75,PEPCO:37.25
b3800.300 | PJM SOUTH | Dominion | VA | Hollymeade Junction, Cash's Corner | Wreck/Rebuild 230kV Line #2135 segment Hollymeade Junction – Cash’s Corner using double-circuit capable 230 kV poles. (The second 230kV circuit will be wired but not have terminal ends.) | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 32.45 | 19.42 | 2023-10-31 | 5/6/2025 | 6/1/2027 | 6/30/2028 |  | EP | 0 | Rebuild | No | 2022-W3-211 | Appendix A | Dominion:100
b3800.301 | PJM SOUTH | Dominion | VA | Cash's Corner, Gordonsville | Wreck/Rebuild 230kV Line #2135 Cash’s Corner – Gordonsville using double-circuit capable 230 kV poles. (The second 230kV circuit will be wired but not have terminal ends.) | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 21.51 | 12.57 | 2023-10-31 | 5/6/2025 | 6/1/2027 | 6/30/2028 |  | EP | 10 | Rebuild | No | 2022-W3-211 | Appendix A | Dominion:100
b3800.302 | PJM SOUTH | Dominion | VA | Cash's Corner | Upgrade Cash's Corner switches 213576 and 213579 and line leads to 4000A continuous current rating of 230kV Line #2135. | Baseline | 230 | Disconnect Switch | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.51 | 0.51 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2028 |  | EP | 10 | Upgrade | No | 2022-W3-211 | Appendix A | Dominion:100
b3800.303 | PJM SOUTH | Dominion | VA | Gordonsville | Upgrade Gordonsville substation line leads to 4000A continuous current rating of 230kV Line #2135. | Baseline | 230 | Conductor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.08 | 0.08 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2028 |  | EP | 10 | Upgrade | No | 2022-W3-211 | Appendix A | Dominion:100
b3800.304 | PJM SOUTH | Dominion | VA | Hollymeade | Upgrade Charlottesville substation switch 205415 and line leads to 4000A continuous current rating of 230 kV line No. 2054 | Baseline | 230 | Disconnect Switch | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.3 | 0.3 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/30/2028 |  | EP | 10 | Upgrade | No | 2022-W3-211 | Appendix A | Dominion:100
b3800.305 | PJM SOUTH | Dominion | VA | Beaumeade | Install one (1) 300 MVAR Static synchronous Compensator (STATCOM) & associated equipment at Beaumeade substation. | Baseline | 230 | Reactive Device | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 52 | 43.57 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2027 |  | EP | 5 | Install | No | 2022-W3-231 | Appendix A | Dominion:100
b3800.306 | PJM SOUTH | Dominion | VA | Morrisville | Install one (1) 500KV, 150 MVAr Shunt Capacitor Bank & associated equipment at Morrisville substation. This addition will require a control house expansion to accommodate for two new panels. | Baseline | 500 | Capacitor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 3.63 | 3.63 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/29/2028 |  | EP | 10 | Install | No | 2022-W3-231 | Appendix A | Dominion:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.307 | PJM SOUTH | Dominion | VA | Mars | Install one (1) 500kV, 300 MVAR Static synchronous Compensator (STATCOM) & associated equipment at Mars substation. | Baseline | 500 | Reactive Device | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 50 | 41.27 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2027 |  | EP | 5 | Install | No | 2022-W3-231 | Appendix A | Dominion:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.308 | PJM SOUTH | Dominion | VA | Mars | Install one (1) 230kV, 150MVAr Shunt Capacitor Bank & associated equipment at Mars substation. | Baseline | 230 | Capacitor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 7 | 5.26 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/20/2027 |  | EP | 5 | Install | No | 2022-W3-231 | Appendix A | Dominion:100
b3800.309 | PJM SOUTH | Dominion | VA | Wishing Star | Install one (1) 230kV, 150MVAr Shunt Capacitor Bank & associated equipment at Wishing Star Substation. | Baseline | 230 | Capacitor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 6.09 | 6.09 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/29/2028 |  | EP | 10 | Install | No | 2022-W3-231 | Appendix A | Dominion:100
b3800.31 | PJM MA | PECO | PA |  | Build new North Delta-High Ridge 500 kV line. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 42.06 | 13.36 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/15/2030 |  | EP | 6 | Build | No | 2022-W3-344 | Appendix A | Dominion:60.85,DPL:0.01,PECO:0.01,PEPCO:29.24,PSEG:9.48,RE:0.41 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.310 | PJM SOUTH | Dominion | VA | Wishing Star | install one (1) 500kV, 293.8MVAr Shunt Capacitor Bank & associated equipment at Wishing Star Substation. | Baseline | 500 | Capacitor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 3.97 | 3.97 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/28/2029 |  | EP | 10 | Install | No | 2022-W3-231 | Appendix A | Dominion:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.311 | PJM SOUTH | Dominion | VA | Bristers, Morrisville | Rebuild 500kV Line #545 Bristers - Morrisville as a single circuit monopole line to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 4357 MVA. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 65.86 | 65.86 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/14/2028 |  | EP | 10 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:91.07,PEPCO:8.93 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.312 | PJM SOUTH | Dominion | VA | Loudoun, Morrisville | Rebuild 500kV Line #569 Loudoun - Morrisville to accommodate the new 500 kV line in the existing right-of-way. New conductor to have a summer rating of 4357 MVA. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 175.62 | 175.62 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 10 | Rebuild | No | 2022-W3-711 | Appendix A | APS:11.72,Dominion:88.28 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.313 | PJM SOUTH | Dominion | VA | Meadow Brook, Loudoun | Rebuild approximately 10.29 miles line segment of Line #535 (Meadow Brook to Loudoun) to accommodate the new 500 kV line in the existing ROW. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 65.86 | 65.86 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | APS:13.93,BGE:6.86,Dominion:70.92,PEPCO:8.29 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.314 | PJM SOUTH | Dominion | VA | Mosby, Wishing Star | Rebuild approximately 4.83 miles of 500kV Line #546 Mosby - Wishing Star to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 4357 MVA. Upgrade and install equipment at Mosby substation to upgrade terminal equipment to be rated for 5000A for 500kV Lines #546. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 49.78 | 49.78 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | EP | 10 | Rebuild | No | 2022-W3-711 | Appendix A | APS:41.98,Dominion:34.03,PEPCO:23.99 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.315 | PJM SOUTH | Dominion | VA | Mosby, Wishing Star | Rebuild approximately 4.59 miles of 500kV Line #590 Mosby - Wishing Star to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 4357 MVA. Upgrade and install equipment at Mosby substation to upgrade terminal equipment to be rated for 5000A for 500kV Lines #590. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 49.78 | 49.78 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | EP | 10 | Rebuild | No | 2022-W3-711 | Appendix A | APS:41.98,Dominion:34.03,PEPCO:23.99 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.316 | PJM SOUTH | Dominion | VA | Gainesville, Mint Springs | Rebuild approximately 6.17 miles of 230kV Line #2030 Gainesville - Mint Springs to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 13.98 | 13.98 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.317 | PJM SOUTH | Dominion | VA | Mint Springs, Loudoun | Rebuild approximately 1.58 miles of 230kV Line #2030 Mint Springs - Loudoun to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 3.59 | 3.59 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.318 | PJM SOUTH | Dominion | VA | Loudoun, North Star | Rebuild approximately 4.2 miles of 230kV Line #2045 Loudoun - North Star to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 14.52 | 14.52 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 10 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.319 | PJM SOUTH | Dominion | VA | North Star, Brambleton | Rebuild approximately 0.88 miles of 230kV Line #2045 North Star - Brambleton to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 3.04 | 3.04 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 10 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.32 | PJM MA | BGE | MD |  | Build new North Delta-High Ridge 500 kV line. (~59 miles). | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 407.11 | 407.11 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Build | No | 2022-W3-660 | Appendix A | BGE:2.58,Dominion:59.28,DPL:0.02,PEPCO:28.48,PSEG:9.24,RE:0.40 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.320 | PJM SOUTH | Dominion | VA | Brambleton, Racefield | Rebuild approximately 1.22 miles of 230kV Line #2227 Brambleton - Racefield to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 4.36 | 4.36 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 10 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.321 | PJM SOUTH | Dominion | VA | Racefield, Loudoun | Rebuild approximately 3.69 miles of 230kV Line #2094 Racefield - Loudoun to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 13.2 | 13.2 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 10 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.322 | PJM SOUTH | Dominion | VA | Bristers, Nokesville | Rebuild approximately 9.16 miles of 230kV Line #2101 Bristers - Nokesville to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 12.99 | 12.99 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2028 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.323 | PJM SOUTH | Dominion | VA | Nokesville, Vint Hill TP | Rebuild approximately 2.89 miles of 230kV Line #2101 Nokesville - Vint Hill TP to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 4.1 | 4.1 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2029 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.324 | PJM SOUTH | Dominion | VA | Vint Hill TP, Vint Hill | Rebuild approximately 0.33 miles of 230kV Line #2101 Vint Hill TP - Vint Hill to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.47 | 0.47 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2028 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.325 | PJM SOUTH | Dominion | VA | Rollins Ford, Vint Hill | Rebuild approximately 3.32 miles of 230kV Line #2114 Rollins Ford - Vint Hill to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 4.35 | 4.35 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2029 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.326 | PJM SOUTH | Dominion | VA | Vint Hill, Elk Run | Rebuild approximately 10.09 miles of 230kV Line #2114 Vint Hill - Elk Run to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 13.21 | 13.21 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2029 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.327 | PJM SOUTH | Dominion | VA | Heathcote, Catharpin | Rebuild approximately 4.43 miles of 230kV Line #2140 Heathcote - Catharpin to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 10.64 | 10.64 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2029 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.328 | PJM SOUTH | Dominion | VA | Catharpin, Loudoun | Rebuild approximately 2.88 miles of 230kV Line #2140 Catharpin - Loudoun to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 6.92 | 6.92 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2029 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.329 | PJM SOUTH | Dominion | VA | Railroad DP, Gainesville | Rebuild approximately 0.25 miles of 230kV Line #2151 Railroad DP - Gainesville to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 4.39 | 4.39 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2029 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.33 | PJM MA | PEPCO | MD |  | Replace/upgrade terminal limitations and related equipment for Brighton 500 kV - on the existing Brighton-Waugh Chapel 500 kV (5053) or new Brighton-High Ridge 500 kV. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 4.13 | 4.13 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Replace | No | 2022-W3-660 | Appendix A | APS:0.68,BGE:86.77,Dominion:1.91,PEPCO:10.64 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.330 | PJM SOUTH | Dominion | VA | Vint Hill, Liberty | Rebuild approximately 4.14 miles of 230kV Line #2163 Vint Hill - Liberty to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 17.56 | 17.56 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2029 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.331 | PJM SOUTH | Dominion | VA | Heathcote, Gainesville | Rebuild approximately 0.48 miles of Line #2176 Heathcote - Gainesville to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 8.78 | 8.78 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 2/28/2027 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.332 | PJM SOUTH | Dominion | VA | Rollins Ford, Gainesville | Rebuild approximately 1.11 miles of Line #2222 Rollins Ford - Gainesville to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 13.17 | 13.17 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.333 | PJM SOUTH | Dominion | VA | Bristers, Ox | Rebuild approximately 1.65 miles of Line #183 Bristers - Ox to accommodate the new 500 kV line in the existing ROW. New conductor to have a summer rating of 1573 MVA. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 8.78 | 8.78 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2028 |  | EP | 0 | Rebuild | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.336 | PJM SOUTH | Dominion | VA | Bristers | Upgrade and install equipment at Bristers substation to support the new conductor 5000A rating for 500kV Line #545. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 5.72 | 5.72 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/14/2028 |  | EP | 10 | Upgrade | No | 2022-W3-711 | Appendix A | Dominion:91.07,PEPCO:8.93 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.337 | PJM SOUTH | Dominion | VA | Brambleton | Upgrade and install equipment at Brambleton substation to support the new conductor termination. All terminal equipment for 230kV Lines #2045 & #2094 to be rated for 4000A continuous current rating. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 4.65 | 4.65 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 10 | Upgrade | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.338 | PJM SOUTH | Dominion | VA | Dawkins Branch | Revise relay settings at Dawkins Branch | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.02 | 0.02 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2029 |  | EP | 0 | Modify | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.339 | PJM SOUTH | Dominion | VA | Gainesville | Upgrade and install equipment at Gainesville substation to support the new conductor termination. All terminal equipment for 230kV Line #2030 to be rated for 4000A continuous current rating. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 3.71 | 3.71 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2029 |  | EP | 0 | Upgrade | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.34 | PJM MA | BGE | MD |  | Rebuild 5012 (existing Peach Bottom-Conastone) (new Graceton-Conastone) 500 kV line on single circuit structures within existing ROW and cut into North Delta 500 kV and Gracetone 500 kV stations. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 70 | 70 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Rebuild | No | 2022-W3-660 | Appendix A | BGE:12.36,Dominion:24.57,DPL:25.17,JCPL:7.90,Neptune:0.88,PENELEC:1.60,PEPCO:12.32,PSEG:14.57,RE:0.63 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.340 | PJM SOUTH | Dominion | VA | Heathcote | Revise relay settings at Heathcote | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.02 | 0.02 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2029 |  | EP | 0 | Modify | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.341 | PJM SOUTH | Dominion | VA | Loudoun | Upgrade and install equipment at Loudoun substation for 230kV Line #2094 Loudoun - Racefield to be rated for 4000A continuous current rating. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 2.5 | 2.5 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Upgrade | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.342 | PJM SOUTH | Dominion | VA | Loudoun | Upgrade and install equipment at Loudoun substation for 230kV Line #2045 Loudoun - North Star to be rated for 4000A continuous current rating. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 2.5 | 2.5 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Upgrade | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.343 | PJM SOUTH | Dominion | VA | Loudoun | Upgrade and install equipment at Loudoun substation for 230kV Line #2030 Loudoun - Mint Springs to be rated for 4000A continuous current rating. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 1 | 1 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Upgrade | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.344 | PJM SOUTH | Dominion | VA | Loudoun | Upgrade and install equipment at Loudoun substation to support the new conductor 5000A rating for 500kV Line #569 Loudoun - Morrisville. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 10.7 | 10.7 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Upgrade | No | 2022-W3-711 | Appendix A | APS:11.72,Dominion:88.28 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.345 | PJM SOUTH | Dominion | VA | Mint Springs | Revise relay settings at Mint Springs | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.03 | 0.03 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2028 |  | EP | 0 | Modify | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.346 | PJM SOUTH | Dominion | VA | Morrisville | Terminal equipment at Morrisville substation to be rated for 5000 A for 500kV Line #545 & #569. Upgrade 500 kV bus 2 to 5000 A. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 12.54 | 12.54 | 2023-10-31 | 4/7/2026 | 6/1/2027 | 6/30/2028 |  | EP | 0 | Upgrade | No | 2022-W3-711 | Appendix A | APS:11.72,Dominion:88.28 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.347 | PJM SOUTH | Dominion | VA | North Star | Revise relay settings at North Star | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.03 | 0.03 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Modify | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.348 | PJM SOUTH | Dominion | VA | Racefield | Revise relay settings at Racefield | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.03 | 0.03 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Modify | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.349 | PJM SOUTH | Dominion | VA | Railroad | Revise relay settings at Railroad | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.02 | 0.02 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Modify | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.35 | PJM MA | PECO | PA |  | Rebuild 5012 (existing Peach Bottom-Conastone) (new North Delta-Graceton PECO) 500 kV line on single circuit structures within existing ROW and cut into North Delta 500 kV and Gracetone 500 kV stations. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 43.78 | 29.86 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 4/10/2028 |  | EP | 7 | Rebuild | No | 2022-W3-344 | Appendix A | BGE:49.42,Dominion:31.22,DPL:0.01,JCPL:0.01,PECO:3.75,PEPCO:15.57,PSEG:0.02 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.350 | PJM SOUTH | Dominion | VA | Vint Hill | Install terminal equipment at Vint Hill substation to support a 5000A line to Morrisville. Update relay settings for 230kV Lines #2101, #2163, and 500kV Line #535. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 23.64 | 23.64 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2029 |  | EP | 0 | Upgrade | No | 2022-W3-711 | Appendix A | APS:9.79,Dominion:90.21 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.351 | PJM SOUTH | Dominion | VA | Vint Hill | Update relay settings at Vint Hill for 230kV Line #2101 Vint Hill - Bristers | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.03 | 0.03 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Modify | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.352 | PJM SOUTH | Dominion | VA | Vint Hill | Update relay settings at Vint Hill for 230kV Line #2163 Vint Hill - Liberty | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.03 | 0.03 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2028 |  | EP | 0 | Modify | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.353 | PJM SOUTH | Dominion | VA | Vint Hill | Update relay settings at Vint Hill for 500kV Line #535 Vint Hill - Loudoun | Baseline | 500 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.03 | 0.03 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2029 |  | EP | 0 | Modify | No | 2022-W3-711 | Appendix A | APS:13.93,BGE:6.86,Dominion:70.92,PEPCO:8.29 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.354 | PJM SOUTH | Dominion | VA | Wishing Star | Install terminal equipment at Wishing Star substation to support a 5000A line to Vint Hill. Update relay settings for 500kV Lines #546 and #590. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 12.3 | 12.3 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Upgrade | No | 2022-W3-711 | Appendix A | APS:21.45,Dominion:78.55 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.355 | PJM SOUTH | Dominion | VA | Youngs Branch | Revise relay settings at Youngs Branch | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.02 | 0.02 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/31/2029 |  | EP | 0 | Modify | No | 2022-W3-711 | Appendix A | Dominion:100
b3800.356 | PJM SOUTH | Dominion | VA | Vint Hill, Wishing Star | Build a new 500kV line from Vint Hill to Wishing Star. The line will be supported on single circuit monopoles. New conductor to have a summer rating of 4357 MVA. Line length is approximately 16.59 miles. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 87.81 | 87.81 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Build | No | 2022-W3-711 | Appendix A | APS:21.45,Dominion:78.55 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.357 | PJM SOUTH | Dominion | VA | Morrisville, Vint Hill | Build a new 500kV line from Yeat to Vint Hill. New conductor to have a summer rating of 4357 MVA. Line length is approximately 27.21 miles. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 150.64 | 150.64 | 2023-10-31 | 4/7/2026 | 6/1/2027 | 6/30/2030 |  | EP | 0 | Build | No | 2022-W3-711 | Appendix A | APS:9.79,Dominion:90.21 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.358 | PJM SOUTH | Dominion | VA | Locks | Replace single unit Locks 230/115 kV 168MVA transformer TX #7 with new single unit transformer with a rating of 224 MVA. Lead lines at the 115 kV level will be upgraded to 2000 A. | Baseline | 230/115 | Transformer | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 7.14 | 7.14 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/30/2027 |  | EP | 0 | Replace | No | 2022-W3-731 | Appendix A | Dominion:100
b3800.359 | PJM SOUTH | Dominion | VA | Ladysmith CT, Summit DP | Wreck and rebuild Line #2090 Ladysmith CT – Summit D.P. segment as a double circuit 230kV line to achieve a summer rating of 1573 MVA. Only one circuit will be wired at this stage. Upgrade circuit breaker leads, switches and line leads at Ladysmith CT to 4000A | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 32 | 36.5 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 9/13/2029 |  | EP | 20 | Rebuild | No | 2022-W3-74 | Appendix A | Dominion:100
b3800.36 | PJM MA | BGE | MD |  | Rebuild 5012 (existing Peach Bottom-Conastone) (new North Delta-Graceton BGE) 500 kV line on single circuit structures within existing ROW and cut into North Delta 500 kV and Gracetone 500 kV stations. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 10.44 | 10.44 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Rebuild | No | 2022-W3-660 | Appendix A | BGE:51.35,Dominion:32.44,DPL:0.01,JCPL:0.01,PEPCO:16.17,PSEG:0.02 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.360 | PJM SOUTH | Dominion | VA | Charlottesville, Proffit | Wreck/Rebuild 230kV Line #2054 segment Charlottesville – Hollymeade Junction using double-circuit capable 230 kV poles. (The second 230kV circuit will be wired but not have terminal ends.) | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 70.14 | 46.53 | 2023-10-31 | 5/6/2025 | 6/1/2027 | 12/30/2028 |  | EP | 10 | Rebuild | No | 2022-W3-967 | Appendix A | Dominion:100
b3800.361 | PJM SOUTH | Dominion | VA | Charlottesville, Hydraulic Road, Barracks Road, Crozet, Dooms | Rebuild 230kV Line #233 Charlottesville – Hydraulic Rd – Barracks Road – Crozet – Dooms | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 54.54 | 54.54 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 11/30/2029 |  | EP | 20 | Rebuild | No | 2022-W3-967 | Appendix A | Dominion:100
b3800.362 | PJM SOUTH | Dominion | VA | Charlottesville, Barracks Road | Rebuild 230kV Line #291 segment from Charlottesville – Barracks Road | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 22.5 | 22.5 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 11/30/2029 |  | EP | 20 | Rebuild | No | 2022-W3-967 | Appendix A | Dominion:100
b3800.363 | PJM SOUTH | Dominion | VA | Barracks Road, Crozet | Rebuild 230kV Line #291 segment from Barracks Road – Crozet | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 20.81 | 20.81 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 11/30/2029 |  | EP | 20 | Rebuild | No | 2022-W3-967 | Appendix A | Dominion:100
b3800.364 | PJM SOUTH | Dominion | VA | Crozzet, Dooms | Rebuild 230kV Line #291 segment Crozet – Dooms | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 11.23 | 11.23 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 11/30/2029 |  | EP | 20 | Rebuild | No | 2022-W3-967 | Appendix A | Dominion:100
b3800.365 | PJM SOUTH | Dominion | VA | Charlottesville, Hollymeade | Hollymeade Substation Relay Revision for 230kV Line #2054 Charlottsville - Hollymeade | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.01 | 0.01 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/30/2028 |  | EP | 0 | Modify | No | 2022-W3-967 | Appendix A | Dominion:100
b3800.366 | PJM SOUTH | Dominion | VA | Charlottesville | Upgrade the terminal equipment at Charlottesville to 4000A for 230kV Line #2054 (Charlottsville – Hollymeade). | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.97 | 0.97 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/30/2028 |  | EP | 0 | Upgrade | No | 2022-W3-967 | Appendix A | Dominion:100
b3800.367 | PJM SOUTH | Dominion | VA | Proffit DP | Proffit DP Substation Relay Revision for 230kV Line #2054 Charlottesville - Hollymeade | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.02 | 0.02 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/30/2028 |  | EP | 0 | Modify | No | 2022-W3-967 | Appendix A | Dominion:100
b3800.368 | PJM SOUTH | Dominion | VA | Barracks Road | Barracks Rd Substation Relay Reset to accommodate the rebuilt line 230kV Lines #233 and #291. | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.03 | 0.03 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 11/30/2029 |  | EP | 20 | Modify | No | 2022-W3-967 | Appendix A | Dominion:100
b3800.369 | PJM SOUTH | Dominion | VA | Crozet | Crozet Substation Relay Reset to accommodate the rebuilt line 230kV Lines #233 and #291. | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.03 | 0.03 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 11/30/2029 |  | EP | 20 | Modify | No | 2022-W3-967 | Appendix A | Dominion:100
b3800.37 | PJM MA | BGE | MD |  | Replace terminal equipment limitations at Conastone 500 kV - on the (existing Peach Bottom-Conastone) or (new Graceton-Conastone) 500 kV line. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 4.93 | 4.93 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Replace | No | 2022-W3-660 | Appendix A | BGE:12.36,Dominion:24.57,DPL:25.17,JCPL:7.90,Neptune:0.88,PENELEC:1.60,PEPCO:12.32,PSEG:14.57,RE:0.63 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.370 | PJM SOUTH | Dominion | VA | Charlottesville | Charlottesville Substation Terminal Equipment Upgrade for 230kV Lines #233 & #291 Rebuild | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 1.5 | 1.5 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 11/30/2029 |  | EP | 20 | Upgrade | No | 2022-W3-967 | Appendix A | Dominion:100
b3800.371 | PJM SOUTH | Dominion | VA | Hydraulic Road | Upgrade Hydraulic Rd Substation Equipment for 230kV Line #233 & #291 Rebuild | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.65 | 0.65 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 11/30/2029 |  | EP | 20 | Upgrade | No | 2022-W3-967 | Appendix A | Dominion:100
b3800.372 | PJM SOUTH | Dominion | VA | Dooms | Dooms Substation Terminal Equipment Upgrade for 230kV Linex #233 & #291 Rebuild | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 1.06 | 1.06 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 11/30/2029 |  | EP | 20 | Upgrade | No | 2022-W3-967 | Appendix A | Dominion:100
b3800.373 | PJM SOUTH | Dominion | VA | St. Johns | Wreck and rebuild approximately 7.14 miles of 230kV line #256 from St. Johns to structure 256/108 to achieve a summer rating of 1573 MVA. Line switch 25666 at St. Johns to be upgraded to 4000A. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 21.69 | 21.75 | 2023-10-31 | 12/5/2023 | 6/1/2028 | 12/18/2026 |  | EP | 20 | Rebuild | No | Additional Identified Upgrades | Appendix A | Dominion:100
b3800.374 | PJM SOUTH | Dominion | VA | Ladysmith CT | Reconductor approximately 5.30 miles of 230kV line #256 from Ladysmith CT to structure 256/107 to achieve a summer rating of 1573 MVA. Terminal equipment at remote end substations will be upgraded to 4000A. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 10 | 16.14 | 2023-10-31 | 12/5/2023 | 6/1/2028 | 12/31/2027 |  | EP | 20 | Reconductor | No | Additional Identified Upgrades | Appendix A | Dominion:100
b3800.375 | PJM SOUTH | Dominion | MD | Goose Creek | Construct new Woodside-Goose Creek 500 kV line for ~3 miles on single circuit monopole structures within the Doubs-Goose Creek Corridor. (DOM Portion) | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 15.6 | 15.6 | 2024-07-10 | 7/10/2024 | 6/1/2029 | 9/30/2030 |  | EP | 10 | Construct | No | 2022-W3-853 | Appendix A | APS:9.26,BGE:7.30,Dominion:72.31,PEPCO:11.13 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.38 | PJM MA | PEPCO | MD |  | Chalk Point-Cheltanham 500 kV (5073) - Replace relay at Chalk Point 500 kV. | Baseline | 500 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0.34 | 0.34 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Replace | No | 2022-W3-660 | Appendix A | BGE:39.75,Dominion:59.03,PEPCO:1.22 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.39 | PJM MA | DPL | DE |  | Red Lion - Hope Creek 500 kV - Replace four 500kV breakers and the stranded bus at Red Lion 500 kV substation | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 6 | 6 | 2023-12-05 | 2/6/2024 | 6/1/2027 | 12/31/2030 |  | EP | 0 | Replace | No | 2022-W3-344 | Appendix A | AEC:0.02,BGE:22.89,Dominion:48.61,DPL:9.46,JCPL:0.03,PEPCO:18.96,PSEG:0.03 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.4 | PJM MA | BGE | MD |  | New Otter Creek to Doubs 500 kV line (MD Border-PSEG Demarcation Point). Rebuild and expand existing ~1.6 miles of Otter Creek-Conastone 230 kV line to become a double-circuit 500 and 230 kV lines. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 11.11 | 11.11 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2027 |  | UC | 0 | Build | No | 2022-W3-374 | Appendix A | APS:13.16,BGE:0.79,Dominion:74.28,DPL:0.41,PECO:0.77,PEPCO:10.59 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.40 | PJM MA | PEPCO | MD |  | Conastone-Brighton 500 kV (5011 circuit) - Replace terminal equipment limitations at Brighton 500 kV. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 4.13 | 4.13 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Replace | No | 2022-W3-660 | Appendix A | BGE:9.65,Dominion:63.04,DPL:0.02,PEPCO:27.29 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.41 | PJM MA | BGE | MD |  | Conastone-Brighton 500 kV (5011 circuit) - Replace terminal equipment limitations at Conastone 500 kV. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 7.16 | 7.16 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/31/2030 |  | UC | 0 | Replace | No | 2022-W3-660 | Appendix A | BGE:9.65,Dominion:63.04,DPL:0.02,PEPCO:27.29 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.42 | PJM MA | PECO | PA |  | Peach Bottom North bus upgrade - Replace 11 – Instances of strain bus conductor used for breaker drops or CT drops, 7 – 500 kV disconnect switches, 7 – Free Standing CTs, 1 – 500 kV breaker, 2 – Breaker relays or meters. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 7.27 | 2.7 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 12/1/2030 |  | EP | 26 | Upgrade | No | 2022-W3-344 | Appendix A | BGE:62.82,DPL:7.25,JCPL:0.09,Neptune:0.01,PECO:0.01,PEPCO:29.63,PSEG:0.18,RE:0.01 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.43 | Not Specified | PSEG | MD |  | Construct 31.6 miles of 500 kV overhead AC line between the Conastone vicinity and the Doubs substations (APS zone portion). | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 183.8 | 176.8 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/1/2027 |  | EP | 6 | Construct | No | 2022-W3-637 | Appendix A | APS:13.16,BGE:0.79,Dominion:74.28,DPL:0.41,PECO:0.77,PEPCO:10.59 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.44 | Not Specified | PECO | PA |  | North Delta termination for the North Delta-High Ridge 500 line (PECO work). | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 4.76 | 3.4 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/15/2030 |  | EP | 18 | Construct | No | 2022-W3-344 | Appendix A | Dominion:60.85,DPL:0.01,PECO:0.01,PEPCO:29.24,PSEG:9.48,RE:0.41 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.45 | PJM MA | PECO | PA |  | North Delta 500 kV termination for the Rock Springs 500 kV line (5034/5014 line) (PECO work). | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 1.45 | 0.8 | 2023-10-31 | 1/9/2024 | 6/1/2027 | 1/31/2028 |  | EP | 21 | Construct | No | 2022-W3-344, DENL | Appendix A | AEC:17.65,BGE:4.43,Dominion:9.87,DPL:22.25,JCPL:3.16,Neptune:0.36,PECO:2.98,PENELEC:0.44,PEPCO:3.80,PPL:5.99,PSEG:27.86,RE:1.21 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.46 | Not Specified | PECO | PA |  | North Delta 500 kV termination for the new Peach Bottom-North Delta 500 kV line (PECO work). | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 2.7 | 2.6 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/11/2029 |  | EP | 34 | Construct | No | 2022-W3-344 | Appendix A | AEC:11.03,BGE:37.40,DPL:22.91,PEPCO:28.66 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.47 | Not Specified | PECO | PA |  | Build new Peach Bottom South-North Delta 500 kV line – cut in to Peach Bottom tie No. 1 and extending line to North Delta (~1.25 miles new ROW). | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 8.4 | 5.5 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 1/14/2030 |  | EP | 15 | Construct | No | 2022-W3-344 | Appendix A | AEC:11.03,BGE:37.40,DPL:22.91,PEPCO:28.66 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.48 | Not Specified | Transource | PA |  | North Delta termination for the North Delta-High Ridge 500 line (Transource work). | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 4.38 | 0.96 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 12/15/2030 |  | EP | 25 | Construct | No | 2022-W3-344 | Appendix A | Dominion:60.85,DPL:0.01,PECO:0.01,PEPCO:29.24,PSEG:9.48,RE:0.41 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.49 | Not Specified | Transource | PA |  | North Delta 500 kV termination for the Calpine generator (Calpine/Transource work). | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 4.05 | 4.05 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 10/6/2027 |  | EP | 25 | Construct | No | 2022-W3-344 | Appendix A | PECO:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.5 | PJM MA | PECO | PA |  | Peach Bottom-TMI 500 kV – Replace terminal equipment at Peach Bottom (install new line terminal relays and communication infrastructure within Peach Bottom and along the 5007) | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 6.11 | 2.5 | 2023-12-07 | 5/1/2024 | 6/1/2027 | 5/1/2027 |  | EP | 4 | Replace | No | 2022-W3-374 | Appendix A | AEC:6.40,BGE:20.32,DPL:9.76,JCPL:17.57,Neptune:1.73,PECO:6.33,PEPCO:7.48,PSEG:29.15,RE:1.26 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.50 | Not Specified | Transource | PA |  | North Delta 500 kV termination for the Rock Springs 500 kV line (5034/5014 line) (Transource work). | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 3.55 | 0.49 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 1/23/2028 |  | EP | 25 | Construct | No | 2022-W3-344 | Appendix A | AEC:17.65,BGE:4.43,Dominion:9.87,DPL:22.25,JCPL:3.16,Neptune:0.36,PECO:2.98,PENELEC:0.44,PEPCO:3.80,PPL:5.99,PSEG:27.86,RE:1.21 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.51 | Not Specified | Transource | PA |  | North Delta 500 kV termination for the new Peach Bottom-North Delta 500 kV line (Transource work). | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 3.68 | 0.29 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 5/31/2028 |  | EP | 25 | Construct | No | 2022-W3-344 | Appendix A | AEC:11.03,BGE:37.40,DPL:22.91,PEPCO:28.66 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.52 | PJM MA | PECO | PA | Peach Bottom | Reconfigure Peach Bottom North and South yards to allow for termination of 500 kV lines from Peach Bottom to North Delta. North Delta 500 kV termination for the new Peach Bottom-North Delta 500 kV line. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 14.25 | 7.86 | 2023-10-31 | 1/9/2024 | 6/1/2027 | 12/1/2030 |  | EP | 31 | Modify | No | 2022-W3-344/660 | Appendix A | AEC:11.03,BGE:37.40,DPL:22.90,PEPCO:28.67 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.53 | PJM MA | PPL | PA | Voltage | Construct a double circuit 500 kV line from the existing TMI-Peach Bottom 500 kV right-of-way to the proposed Chanceford switchyard ~1.0 miles in length. | Baseline | 500 |  | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 12.59 | 12.59 | 2024-05-01 | 5/1/2024 | 6/1/2027 | 4/30/2027 |  | EP | 0 |  | No | 2022-W3-374 | Appendix A | APS:13.37,Dominion:75.27,PEPCO:11.36 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.6 | PJM MA | ME | PA |  | Peach Bottom-TMI 500 kV - Replace terminal equipment at TMI. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0 | 0 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2027 |  | Cancelled | 0 | Replace | No | 2022-W3-374 | Appendix A | APS:7.41,BGE:15.50,Dominion:45.08,DPL:2.46,JCPL:0.80,ME:0.34,Neptune:0.09,PECO:10.72,PEPCO:15.72,PPL:0.43,PSEG:1.39,RE:0.06 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.7 | PJM MA | PSEG | MD |  | Construct 35.8 miles of 500 kV overhead AC line between the Conastone vicinity and the Doubs substations (BGE zone portion). | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 206.5 | 213.2 | 2023-10-31 | 12/5/2023 | 6/1/2027 | 6/1/2027 |  | EP | 6 | Construct | No | 2022-W3-637 | Appendix A | APS:13.16,BGE:0.79,Dominion:74.28,DPL:0.41,PECO:0.77,PEPCO:10.59 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.8 | PJM MA | APS | MD |  | Reconfigure Doubs 500 kV station and upgrade terminal equipment to terminate new line. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 57.5 | 57.5 | 2023-12-06 | 12/6/2023 | 6/1/2027 | 6/1/2027 |  | EP | 3 | Rebuild | No | 2022-W3-637 | Appendix A | APS:13.16,BGE:0.79,Dominion:74.28,DPL:0.41,PECO:0.77,PEPCO:10.59 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3800.9 | PJM MA | APS | MD |  | Rebuild the existing Hunterstown-Carroll 115/138 kV Corridor as Double Circuit using 230 kV construction standards. New circuit will be operated at 230 kV. Existing circuit to remain at 115/138 kV. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | PJM identified new baseline reliability criteria violations; full details in 2022 RTEP Window 3 Reliability Analysis Report and Constructability & Financial Analysis Report ¦ 2022 RTEP Window 3 project. Break the existing TMI-Peach Bottom 500 kV line and reterminate into adjacent Otter Creek 500 kV switchyard. Cost estimate revised upward from $7.03M to $18.3M following detailed project review. ¦ 2022 RTEP Window 3 project. North Delta 500 kV termination for the Rock Springs 500 kV line (5034/50 | New project approved by Board on December 11, 2023 | 20231205-pjm-teac-board-whitepaper-december-2023.json ¦ 20240206-pjm-teac-board-whitepaper-feburary-2024.json ¦ 20240806-pjm-board-whitepaper-august-2024.json ¦ 20250708-pjm-board-whitepaper-july-2025.json ¦ 20260203-pjm-board-whitepaper-february-2026.json ¦ dec2022_projects.json | 2023-01-01 ¦ 2024-01-01 ¦ 2025-07-01 ¦ 2026-02-01 ¦ 2025-01-01 | 28 | 0 | 0 | 2023-12-05 | 12/5/2023 | 6/1/2027 | 6/1/2028 |  | Cancelled | 0 | Rebuild | No | 2022-W3-837
b3810.0 | PJM WEST | ComEd | IL | Cherry Valley | Add three 345 kV circuit breakers to Cherry Valley substation. | Baseline | 345 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 7.75 | 7.75 | 2024-01-09 | 1/9/2024 | 6/1/2028 | 6/1/2028 |  | EP | 5 | Install | No | 2023-W1-771, single zone allocation; DENL & CRL | Appendix A | ComEd:100
b3811.1 | PJM WEST | ComEd | IL | Haumesser Road | Expand Haumesser Road 138 kV substation as a four-circuit breaker ring bus. | Baseline | 138 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2023 RTEP Window 1 2028 winter case, Haumesser Road-West DeKalb tap-ESS H452 (Enbridge-DeKalb) tap 138 kV line is overloaded for N-1 and N-2 outages. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 15.91 | 15.91 | 2024-02-06 | 2/6/2024 | 12/1/2028 | 12/1/2028 |  | EP | 5 | Upgrade | No | 2023-W1-972 | Appendix A | ComEd:100
b3811.2 | PJM WEST | ComEd | IL | H-452 (Enridge-DeKalb) | Add one 138 kV circuit breaker at H-452 to complete a three-circuit breaker ring bus. | Baseline | 138 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2023 RTEP Window 1 2028 winter case, Haumesser Road-West DeKalb tap-ESS H452 (Enbridge-DeKalb) tap 138 kV line is overloaded for N-1 and N-2 outages. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 1.98 | 1.98 | 2024-02-06 | 2/6/2024 | 12/1/2028 | 12/1/2028 |  | EP | 5 | Install | No | 2023-W1-972 | Appendix A | ComEd:100
b3811.3 | PJM WEST | ComEd | IL | Haumesser Road-H-452 (Enridge-DeKalb) Tap | Rebuild 3 miles of 138 kV line 11323 from Haumesser Road to the H-452 tap with double circuit towers. Cut the H-452 tap over to the second circuit from Haumesser Road. Both circuits to use twisted pair 556 ACSR Parakeet conductor. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2023 RTEP Window 1 2028 winter case, Haumesser Road-West DeKalb tap-ESS H452 (Enbridge-DeKalb) tap 138 kV line is overloaded for N-1 and N-2 outages. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 10.22 | 10.22 | 2024-02-06 | 2/6/2024 | 12/1/2028 | 12/1/2028 |  | EP | 5 | Rebuild | No | 2023-W1-972 | Appendix A | ComEd:100
b3812.1 | PJM WEST | ComEd | IL | Elwood-Goodings Grove | Reconductor 345 kV lines 11620 and 11622 from Elwood to Goodings Grove. | Baseline | 345 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2023 RTEP Window 1 2028 summer case, Elwood-Goodings Grove 345 kV double circuit is overloaded in base case and for N-2 outages. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 56.18 | 56.18 | 2024-03-05 | 3/5/2024 | 6/1/2028 | 6/1/2028 |  | On Hold | 0 | Reconductor | No | 2023-W1-35 | Appendix A | ComEd:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3812.2 | PJM WEST | ComEd | IL | Goodings Grove | Upgrade Goodings Grove 345 kV circuit breakers, disconnects and associated equipment. | Baseline | 345 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2023 RTEP Window 1 2028 summer case, Elwood-Goodings Grove 345 kV double circuit is overloaded in base case and for N-2 outages. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 5.16 | 5.16 | 2024-03-05 | 3/5/2024 | 6/1/2028 | 6/1/2028 |  | On Hold | 0 | Upgrade | No | 2023-W1-35 | Appendix A | ComEd:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3812.3 | PJM WEST | ComEd | IL | Elwood | Upgrade station conductor at Elwood 345 kV. | Baseline | 345 | Conductor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2023 RTEP Window 1 2028 summer case, Elwood-Goodings Grove 345 kV double circuit is overloaded in base case and for N-2 outages. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 0.5 | 0.5 | 2024-03-05 | 3/5/2024 | 6/1/2028 | 6/1/2028 |  | On Hold | 0 | Upgrade | No | 2023-W1-35 | Appendix A | ComEd:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3812.4 | PJM WEST | ComEd | IL | Goodings Grove | Adjust reclosing cycle on for Goodings Grove 345 kV circuit breaker “116 9806” to eliminate the reclosing derating. | Baseline | 345 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2023 RTEP Window 1 2028 summer case, Elwood-Goodings Grove 345 kV double circuit is overloaded in base case and for N-2 outages. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 0 | 0 | 2024-03-05 | 3/5/2024 | 6/1/2028 | 6/1/2028 |  | On Hold | 0 | Modify | No | 2023-W1-35 | Appendix A | ComEd:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3844.1 | PJM MA | PECO |  | Macdade--(39.9018,-75.296)-{1AA69AA4-1A3D-450C-BFC8-277AC581AAE7} | Replacement of relays at Macdade, Printz and Morton to increase rating limits of transmission relay equipment. Line protection relays will be upgraded with latest standard relays used across the PECO system. | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.5 | 1.4 | 2023-12-05 | 12/5/2023 | 12/31/2026 | 6/30/2026 |  | EP | 30 | Upgrade | No |  | Appendix A | PECO:100
b3845.1 | PJM MA | PECO |  | Nottingham--(39.761,-76.0321)-{3C903188-014A-433C-9F7C-103F7D2849E0} | Add a second breaker next to Nottingham 895 circuit breaker to eliminate stuck breaker contingency. | Baseline | 230 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.28 | 1.28 | 2023-11-16 | 11/16/2023 | 5/31/2028 | 12/31/2027 |  | EP | 5 | Install | No |  | Appendix A | PECO:100
b3846.1 | PJM MA | DPL |  | Mardela--(38.4498,-75.7436)-{F3304B78-4D4B-4925-9A01-2DEE12DBCE9A}, Vienna--(38.4872,-75.8207)-{DCC13F75-DBA2-4D9D-ADBA-76852F0AAAA4} | Rebuild 6.25 miles of 69 kV circuit 6708 (Vienna-Mardela) with new single pole steel structures and with 954.0 45/7 "Rail" conductor. This new rebuild will be from the dead-end structure on the east side of the Nanticoke River to the Mardela tap. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In the 2028 RTEP summer case, the Vienna-Mardela 69 kV line is overloaded under multiple N-2 outages. |  | 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2024-01-01 | 1 | 18.63 | 18.63 | 2023-11-16 | 11/16/2023 | 6/1/2028 | 6/1/2028 |  | EP | 0 | Rebuild | No |  | Appendix A | DPL:100
b3846.2 | PJM MA | DPL |  | Vienna--(38.4872,-75.8207)-{DCC13F75-DBA2-4D9D-ADBA-76852F0AAAA4} | Upgrade disconnect switch at Vienna to increase ratings of existing Vienna-Mardela transmission facility. | Baseline | 230 | Switch | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In the 2028 RTEP summer case, the Vienna-Mardela 69 kV line is overloaded under multiple N-2 outages. |  | 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2024-01-01 | 1 | 1 | 1 | 2023-11-16 | 11/16/2023 | 6/1/2028 | 12/31/2026 |  | EP | 0 | Upgrade | No |  | Appendix A | DPL:100
b3846.3 | PJM MA | DPL |  | Mardela--(38.4498,-75.7436)-{F3304B78-4D4B-4925-9A01-2DEE12DBCE9A} | Upgrade three disconnect switches at Mardela to increase ratings of existing Vienna-Mardela transmission facility. | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In the 2028 RTEP summer case, the Vienna-Mardela 69 kV line is overloaded under multiple N-2 outages. |  | 20240206-pjm-teac-board-whitepaper-feburary-2024.json | 2024-01-01 | 1 | 1.75 | 1.75 | 2023-11-16 | 11/16/2023 | 6/1/2028 | 6/1/2028 |  | EP | 0 | Upgrade | No |  | Appendix A | DPL:100
b3851.1 | PJM WEST | AEP | IN | Allen - R.P. Mone | Rebuild Allen –R.P. Mone 345kV line (18.6 miles). | Baseline | 345 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | In 2023 RTEP Window 2 2028 summer and winter cases, R.P. Mone-Maddox Creek 345 kV line is overloaded for generator deliverability test for N-1 and N-2 outages; Allen-R.P. Mone 345 kV line overloaded for N-1 in 2028 winter. ISD consistent with AEP forecast of when 2028 load levels are expected to materialize. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 49.88 | 49.88 | 2024-07-10 | 7/10/2024 | 6/1/2027 | 6/1/2027 |  | EP | 5 | Rebuild | Yes | 2023-W2-819 | Appendix A | AEP:0.71,Dayton:99.28,OVEC:0.01
b3851.2 | PJM WEST | AEP | OH | R.P. Mone - Maddox Creek | Rebuild R.P. Mone – Maddox Creek 345kV line (9.4 miles). | Baseline | 345 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | In 2023 RTEP Window 2 2028 summer and winter cases, R.P. Mone-Maddox Creek 345 kV line is overloaded for generator deliverability test for N-1 and N-2 outages; Allen-R.P. Mone 345 kV line overloaded for N-1 in 2028 winter. ISD consistent with AEP forecast of when 2028 load levels are expected to materialize. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 39.03 | 39.03 | 2024-07-09 | 7/9/2024 | 6/1/2027 | 6/1/2027 |  | EP | 5 | Rebuild | Yes | 2023-W2-957 | Appendix A | AEP:78.50,Dayton:21.50
b3851.3 | PJM WEST | AEP | OH | Moddox Creek | Replace breakers 'B1' and 'B' at Maddox Creek. | Baseline | 345 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | In 2023 RTEP Window 2 2028 summer and winter cases, R.P. Mone-Maddox Creek 345 kV line is overloaded for generator deliverability test for N-1 and N-2 outages; Allen-R.P. Mone 345 kV line overloaded for N-1 in 2028 winter. ISD consistent with AEP forecast of when 2028 load levels are expected to materialize. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 1.8 | 1.8 | 2024-07-09 | 7/9/2024 | 6/1/2027 | 6/1/2027 |  | EP | 5 | Replace | Yes | 2023-W2-334 | Appendix A | AEP:80.97,Dayton:19.03
b3851.4 | PJM WEST | AEP | OH | East Lima | Replace two 345kV breakers 'M' and 'M2' at East Lima Station. | Baseline | 345 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | In 2023 RTEP Window 2 2028 summer and winter cases, R.P. Mone-Maddox Creek 345 kV line is overloaded for generator deliverability test for N-1 and N-2 outages; Allen-R.P. Mone 345 kV line overloaded for N-1 in 2028 winter. ISD consistent with AEP forecast of when 2028 load levels are expected to materialize. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 1.76 | 1.76 | 2024-07-09 | 7/9/2024 | 6/1/2027 | 6/1/2027 |  | EP | 5 | Replace | Yes | 2023-W2-334 | Appendix A | AEP:80.97,Dayton:19.03
b3852.1 | PJM WEST | AEP | OH | Vassell | Connect and energize a second 765/345 kV bank at Vassell station. | Baseline | 345 | Transformer | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | In 2023 RTEP Window 2 2028 summer/winter cases, multiple 138 kV and 345 kV lines (Genoa-Westar, Maliszewski-Polaris, Polaris-Westar, Marysville-Hyatt, Hyatt-Vassell, etc.) and Maliszewski 765/138 kV transformer are overloaded for N-1, N-2, and N-1-1 outages. ISD consistent with AEP forecast of when 2028 load levels are expected to materialize. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 30.83 | 30.83 | 2024-07-09 | 7/9/2024 | 6/1/2027 | 7/15/2026 |  | UC | 85 | Install | Yes | 2023-W2-117 | Appendix A | AEP:89.17,Dayton:6.19,DEOK:4.57,OVEC:0.07
b3852.2 | PJM WEST | AEP | OH | Maliszewski | Replace 765 kV breaker D at Maliszewski station. | Baseline | 345 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | In 2023 RTEP Window 2 2028 summer/winter cases, multiple 138 kV and 345 kV lines (Genoa-Westar, Maliszewski-Polaris, Polaris-Westar, Marysville-Hyatt, Hyatt-Vassell, etc.) and Maliszewski 765/138 kV transformer are overloaded for N-1, N-2, and N-1-1 outages. ISD consistent with AEP forecast of when 2028 load levels are expected to materialize. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 2.9 | 2.9 | 2024-07-09 | 7/9/2024 | 6/1/2027 | 6/1/2027 |  | EP | 0 | Replace | Yes | 2023-W2-117 | Appendix A | AEP:68.04,ATSI:9.61,Dayton:1.92,DL:3.35,Dominion:17.06,EKPC:0.02 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3855.1 | PJM MA | PSEG | NJ | Jackson Road | Build 4 miles new 230 kV XLPE circuit using (345 kV rated 5000 kcmil cable) from Jackson Road 230 kV station to Cedar Grove 230 kV station. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2023 RTEP Window 2 2028 summer and winter cases, multiple N-1-1 thermal violations in Northern New Jersey (Cedar Grove and Jackson area). Four 69 kV lines overloaded for several N-1-1 contingency combinations. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 82.7 | 77.15 | 2024-07-09 | 7/9/2024 | 6/1/2028 | 6/1/2028 |  | UC | 36 | Build | No | 2023-W2-627 | Appendix A | PSEG:95.85,RE:4.15
b3855.2 | PJM MA | PSEG | NJ | Cedar Grove | Expand a new 230 kV bay at the existing Cedar Grove station with one line position by adding two 230 kV circuit breakers and associated disconnect switches. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2023 RTEP Window 2 2028 summer and winter cases, multiple N-1-1 thermal violations in Northern New Jersey (Cedar Grove and Jackson area). Four 69 kV lines overloaded for several N-1-1 contingency combinations. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 6.8 | 6.61 | 2024-07-09 | 7/9/2024 | 6/1/2028 | 6/1/2028 |  | UC | 36 | Expand | No | 2023-W2-627 | Appendix A | PSEG:95.85,RE:4.15
b3855.3 | PJM MA | PSEG | NJ | Jackson Road | Replace the existing HPFF termination structure with a new XLPE termination structure to connect to spare GIS bay position at Jackson 230 kV. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | In 2023 RTEP Window 2 2028 summer and winter cases, multiple N-1-1 thermal violations in Northern New Jersey (Cedar Grove and Jackson area). Four 69 kV lines overloaded for several N-1-1 contingency combinations. |  | 20240806-pjm-board-whitepaper-august-2024.json | 2024-01-01 | 1 | 0.9 | 0.82 | 2024-07-09 | 7/9/2024 | 6/1/2028 | 6/1/2028 |  | UC | 36 | Replace | No | 2023-W2-627 | Appendix A | PSEG:95.85,RE:4.15
b3858.1 | PJM MA | ME | PA | Windsor | Rebuild the Windsor Substation 115 kV yard to convert from a straight bus configuration into a six-breaker ring bus configuration. Install two (2) 21.62 MVAR, 115 kV capacitor banks. | Baseline | 115 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Voltage magnitude and voltage drop violations in N-1 analysis at Yorkana and Windsor 115 kV substations for multiple contingencies in 2029 summer and winter cases; required ISD advanced to June 2028 to address reliability requirements; below 200 kV exclusion from competition |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 12.36 | 12.36 | 2024-11-14 | 11/14/2024 | 6/1/2028 | 6/1/2029 |  | EP | 1 | Rebuild | No |  | Appendix A | ME:100
b3858.2 | PJM MA | ME | PA | Yorkana | Rebuild the Yorkana Substation 115 kV yard converting from a straight bus configuration to a (9) breaker, breaker-and-a-half configuration. | Baseline | 115 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Voltage magnitude and voltage drop violations in N-1 analysis at Yorkana and Windsor 115 kV substations for multiple contingencies in 2029 summer and winter cases; required ISD advanced to June 2028 to address reliability requirements; below 200 kV exclusion from competition |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 20.8 | 20.8 | 2024-11-14 | 11/14/2024 | 6/1/2028 | 6/1/2029 |  | EP | 1 | Rebuild | No |  | Appendix A | ME:100
b3862.1 | PJM MA | PECO | PA | Elroy | Upgrade two (2) 500kV free standing CTs, one (1) disconnect switch, and four (4) sections of tube bus at Elroy 500kV Substation. | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.5 | 1.5 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 12/31/2028 |  | EP | 20 | Upgrade | No |  | Appendix A | PECO:100
b3864.1 | PJM MA | PECO | PA | Tacony | Replace station cable at Tacony 69kv Station | Baseline | 69 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.18 | 0.18 | 2024-11-14 | 11/14/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Upgrade | No |  | Appendix A | PECO:100
b3864.2 | PJM MA | PECO | PA | Richmond | Replace station cable at Richmond 230kV Station | Baseline | 69 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.18 | 0.18 | 2024-11-14 | 11/14/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Upgrade | No |  | Appendix A | PECO:100
b3865.1 | PJM MA | DPL | DE | Reybold | Upgrade 138/69kV autotransformer, a 69kV breaker, two disconnects and move a takeoff structure at Reybold Substation. These upgrades will require a substation expansion to move the takeoff structure and a control house expansion to move the 69kV breaker relays from the Delaware City control house to the Reybold control house. | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 9.48 | 9.48 | 2024-11-14 | 11/14/2024 | 12/1/2029 | 12/1/2029 |  | EP | 0 | Upgrade | No |  | Appendix A | DPL:100
b3866.1 | PJM MA | DPL | DE | Cedar Creek | Adjust relay setting at Cedar Creek 230kV Substation. | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0 | 0.1 | 2024-12-03 | 12/3/2024 | 12/31/2029 | 12/31/2029 | 7/8/2025 | IS | 100 | Modify | No |  | Appendix A | DPL:100
b3866.2 | PJM MA | DPL | DE | Milford | Change relay setting at Milford 230kV Substation | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0 | 0.1 | 2024-12-03 | 12/3/2024 | 12/31/2029 | 12/31/2029 | 7/8/2025 | IS | 100 | Modify | No |  | Appendix A | DPL:100
b3867.1 | PJM MA | ACE | NJ | Mickleton | Upgrade a circuit switcher at Mickleton substation. | Baseline | 230 | Circuit Switcher | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.03 | 1.03 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Replace | No |  | Appendix A | AEC:100
b3869.1 | PJM MA | PSEG | NJ | Bergen | Relocate the Bergen Gen #1 point of interconnection from Bergen 138kV to Bergen 345kV GIS through the existing 345/138kV transformer. | Baseline | 345 | Conductor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Bergen-Fairlawn (M-1339) and Bergen-East Rutherford 138 kV thermal violations from N-1 contingencies when Bergen series reactor bypass switches must be closed following reactor outage in 2029 winter case; below 200 kV exclusion from competition; solution relocates Bergen generator No. 1 interconnection from 138 kV to 345 kV bus and retires two series reactors ¦ Original scope: remove/retire two Bergen 138 kV series reactors and relocate Bergen generator No. 1 point of interconnection from Bergen |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json ¦ 20251104-pjm-board-whitepaper-november-2025.json | 2025-01-01 | 2 | 6.8 | 6.8 | 2024-11-14 | 11/14/2024 | 12/1/2029 | 9/1/2027 |  | Cancelled | 0 | Relocate | No |  | Appendix A | PSEG:100
b3869.2 | PJM MA | PSEG | NJ | Bergen | Remove and retire the two (2) existing Bergen 138kV Series Reactors and associated ancillary equipment. | Baseline | 138 | Series Reactor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Bergen-Fairlawn (M-1339) and Bergen-East Rutherford 138 kV thermal violations from N-1 contingencies when Bergen series reactor bypass switches must be closed following reactor outage in 2029 winter case; below 200 kV exclusion from competition; solution relocates Bergen generator No. 1 interconnection from 138 kV to 345 kV bus and retires two series reactors ¦ Original scope: remove/retire two Bergen 138 kV series reactors and relocate Bergen generator No. 1 point of interconnection from Bergen |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json ¦ 20251104-pjm-board-whitepaper-november-2025.json | 2025-01-01 | 2 | 5.7 | 5.7 | 2024-11-14 | 11/14/2024 | 12/1/2029 | 9/1/2027 |  | Cancelled | 0 | Remove | No |  | Appendix A | PSEG:100
b3869.3 | PJM MA | PSEG | NJ | Bergen | Replace the two Bergen 138 kV series reactors with two new dry type 138 kV series reactors. | Baseline | 138 | Series Reactor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Bergen-Fairlawn (M-1339) and Bergen-East Rutherford 138 kV thermal violations from N-1 contingencies when Bergen series reactor bypass switches must be closed following reactor outage in 2029 winter case; below 200 kV exclusion from competition; solution relocates Bergen generator No. 1 interconnection from 138 kV to 345 kV bus and retires two series reactors ¦ Original scope: remove/retire two Bergen 138 kV series reactors and relocate Bergen generator No. 1 point of interconnection from Bergen |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json ¦ 20251104-pjm-board-whitepaper-november-2025.json | 2025-01-01 | 2 | 12.77 | 12.77 | 2025-10-16 | 10/16/2025 | 12/1/2029 | 9/1/2027 |  | PL | 0 | Replace | No |  | Appendix A | PSEG:100
b3870.1 | PJM WEST | APS | PA | Federal St. | At Federal Street Substation: - Install (3) 138 kV CCVTs on the 138 kV bus. - Remove the Transformer 1 CO-6 138 kV Phase relay Overcurrent Relays. - Install (1) SEL-421 relay on the high side of Transformer 1. - Install foundations, conduit, and grounding for new CCVTs. - Install cables between CCVTs and relay. | Baseline | 138 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.69 | 0.69 | 2024-11-15 | 11/15/2024 | 6/1/2028 | 6/1/2029 |  | EP | 0 | Replace | No |  | Appendix A | APS:100
b3871.1 | PJM WEST | DL | PA | Brunot Island | Replace two 138 kV disconnect switches with 3000 amp disconnect switches and replace a portion of the stranded conductor on the #2 138 kV Bus with aluminum pipe bus. | Baseline | 138 | Bus | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 8 | 8 | 2024-11-15 | 11/15/2024 | 6/1/2029 | 12/31/2028 |  | EP | 0 | Modify | No |  | Appendix A | DL:100
b3877.1 | PJM WEST | AEP | OH | Beatty | Project will replace station conductor and switches in the 345 kV yard at Beatty that are currently limiting the 345 kV lines to Adkins and Chenoweth | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.5 | 0.5 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 2/1/2028 |  | EP | 0 | Replace | No |  | Appendix A | AEP:100
b3877.2 | PJM WEST | AEP | OH | Adkins | Project will upgrade 345 kV circuit breakers 'A' and 'A1' to 4000A 63 kA breakers at Adkins station along with some station conductor that is currently limiting the 345 kV line to Beatty. | Baseline | 345 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 4.5 | 4.5 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 8/1/2029 |  | EP | 0 | Replace | No |  | Appendix A | AEP:100
b3878.1 | PJM WEST | AEP | OH | Marysville | Proposal will upgrade 765 kV circuit breakers 'B' and 'B2' 'to 5000A 50 kA breakers at Marysville station. In addition, the project will upgrade the existing wavetrap towards Sorenson. | Baseline | 765 | Substation equipment | Baseline Load Growth Deliverability & Reliability | generation_interconnection | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:generation_interconnection | FALSE | 0 | Marysville 765 kV reactor lead toward Sorenson overloaded under generator deliverability test in 2029 summer case; substation equipment exclusion applied |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 10 | 10 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 11/12/2027 |  | EP | 0 | Replace | No |  | Appendix A | AEP:100
b3888.1 | PJM WEST | AEP | OH | East Leipsic,Lammer | Preform sag study and complete mitigations on the 138 kV line between East Leipsic and the AE2-072 tap (Lammer) to allow line's conductor to operate to its maximum operating temperature (MOT). | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 2.5 | 2.5 | 2024-11-15 | 11/15/2024 | 6/1/2029 | 3/8/2028 |  | EP | 0 | Sag Study | No |  | Appendix A | AEP:100
b3889.1 | PJM WEST | AEP | OH | Tiltonsville | Project will replace limiting station equipment at Tiltonsville station to increase the rating on the branch to Windsor | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.8 | 0.8 | 2024-11-15 | 11/15/2024 | 6/1/2029 | 6/28/2028 |  | EP | 0 | Replace | No |  | Appendix A | AEP:100
b3890.1 | PJM WEST | AEP | OH | South Coshocton | Replace station conductor at South Coshocton station currently limiting the branch to Ohio Central | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.2 | 0.2 | 2024-11-15 | 11/15/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Replace | No |  | Appendix A | AEP:100
b3891.1 | PJM WEST | AEP | OH | Kenny | Project will perform relay upgrades at Kenny 138 kV to raise the CT & Relay thermal limits that are currently limiting the line to Roberts. | Baseline | 138 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.4 | 0.4 | 2024-11-15 | 11/15/2024 | 6/1/2029 | 6/1/2026 |  | EP | 20 | Upgrade | No |  | Appendix A | AEP:100
b3894.1 | PJM WEST | AEP | OH | Tidd | Replace limiting station conductor at Tidd on the line to Carnegie (FE). | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.5 | 0.5 | 2024-11-15 | 11/15/2024 | 6/1/2029 | 4/18/2028 |  | EP | 0 | Replace | No |  | Appendix A | AEP:100
b3898.1 | PJM WEST | AEP | VA | Buchanan IPP | Upgrade the CT thermal limit at Buchanan station on the Buchanan-Keen Mountain 138 kV line. | Baseline | 138 | Current Transformer | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.1 | 0.1 | 2024-11-15 | 11/15/2024 | 12/1/2029 | 12/1/2029 |  | EP | 0 | Upgrade | No |  | Appendix A | AEP:100
b3899.1 | PJM WEST | OVEC | OH | Kyger Creek | Replace OVEC owned station equipment at Kyger Creek to raise the rating of the Kyger Creek-Sporn 345 kV line. Equipment to be replaced includes station conductor and a wavetrap at Kyger Creek. | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.8 | 0.8 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Replace | No |  | Appendix A | OVEC:100
b3900.1 | PJM WEST | ComEd | IL | Kewanee | Replace 300 copper conductor with 1113 kcmil ACSR conductor on Kewanee 138 kV Bus No. 1. | Baseline | 138 | Bus | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.2 | 0.2 | 2024-11-15 | 11/15/2024 | 4/1/2029 | 4/1/2029 |  | EP | 5 | Replace | No |  | Appendix A | ComEd:100
b3901.1 | PJM WEST | ComEd | IL | Electric Junction,W541 | Reconductor 138 kV line from Electric Junction to W541. | Baseline | 138 | Conductor | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.38 | 1.38 | 2024-11-15 | 11/15/2024 | 6/1/2029 | 12/31/2027 |  | EP | 10 | Reconductor | No |  | Appendix A | ComEd:100
b3901.2 | PJM WEST | ComEd | IL | Electric Junction | Replace 2" tubular bus, 2-500 KCMIL Cu and 1113 KCMIL ACSR/AA on bus 2 and line terminal of 138kV L11106 at TSS 111 Electric Junction with bus that meets or exceeds a minimum thermal capability of 2036/2236/2690A (487/534/643MVA) SN/SE/SLD. | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.28 | 0.28 | 2024-11-15 | 11/15/2024 | 6/1/2029 | 12/31/2027 |  | EP | 10 | Replace | No |  | Appendix A | ComEd:100
b3902.1 | PJM WEST | ComEd | IL | Wilton Ctr. | Replace the Wilton Center 345 kV BT 4-5 circuit breaker. | Baseline | 345 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 2.7 | 2.7 | 2024-12-03 | 12/3/2024 | 12/1/2029 | 12/1/2029 | 12/3/2024 | IS | 100 | Replace | No |  | Appendix A | ComEd:100
b3904.1 | PJM WEST | Dayton | OH | Rockford | Rebuild and reconductor 7.7 miles of 69kV line with our standard 1351 AAC conductor from Rockford substation to the POI. | Baseline | 69 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Rockford-Roller Creek 69 kV line overloaded for N-1 and N-2 outages in 2029 light load case; 7.7-mile Dayton-owned section rebuilt with standard 1351 AAC conductor; below 200 kV exclusion from competition |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 25 | 25 | 2025-01-17 | 1/17/2025 | 4/15/2029 | 6/1/2029 |  | EP | 0 | Rebuild | No |  | Appendix A | Dayton:100
b3906.1 | PJM MA | BGE | MD | Marley Neck | Construct new Marley Neck 115 kV substation. Marley Neck 115kV portion will accommodate 10 breaker-and-a-half bays, with only 6 bays planned for initial service while accommodating 4 future bays. Two Standard 230/115kV transformers will be connected between the 230 and 115 kV equipment with appropriate isolation methods. | Baseline | 230/115 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple facilities overloaded under N-1-1 analysis in 2029 summer case: Chestnut Hill-Frederick Rd. 115 kV lines No. 527 and 528, North East 230/115 kV transformers No. 1 and 2, Wagner 230/115 kV transformers No. 1 and 2, and Howard-Pumphrey 230 kV line |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 107.62 | 107.62 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 12/31/2029 |  | EP | 0 | Build | No | 2024-W1-295 | Appendix A | BGE:100
b3907.1 | PJM MA | PECO | PA | North Philadelphia | Reconductor entire 2.5 miles of North Philadelphia to Master 230 kV line | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | generation_interconnection | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:generation_interconnection | FALSE | 0 | Master-North Philadelphia-Waneeta-Richmond 230 kV line overloaded under generator deliverability test in 2029 summer and winter cases; reconductors 2.5 miles Master-North Philadelphia, 2.12 miles North Philadelphia-Waneeta, and rebuilds 3.18 miles Waneeta-Richmond; required ISD for Richmond segments advanced to June 2028 |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 6.49 | 6.49 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 8 | Rebuild | No | 2024-W1-12 | Appendix A | AEC:0.76,JCPL:1.45,PECO:94.22,PSEG:3.29,RE:0.13,Neptune:0.15
b3907.2 | PJM MA | PECO | PA | Richmond | Richmond to Waneeta 230kV Line: Rebuild entire 0.95 miles of existing UGT, and rebuild entire 2.23 miles of existing OHT | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | generation_interconnection | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:generation_interconnection | FALSE | 0 | Master-North Philadelphia-Waneeta-Richmond 230 kV line overloaded under generator deliverability test in 2029 summer and winter cases; reconductors 2.5 miles Master-North Philadelphia, 2.12 miles North Philadelphia-Waneeta, and rebuilds 3.18 miles Waneeta-Richmond; required ISD for Richmond segments advanced to June 2028 |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 29.4 | 29.4 | 2024-12-03 | 12/3/2024 | 6/1/2028 | 6/1/2029 |  | EP | 8 | Rebuild | No | 2024-W1-12 | Appendix A | AEC:9.99,JCPL:8.34,PECO:55.62,PSEG:24.31,RE:0.94,Neptune:0.80
b3907.3 | PJM MA | PECO | PA | Waneeta | Reconductor 2.12 miles of North Philadelphia to Waneeta 230 kV line | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | generation_interconnection | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:generation_interconnection | FALSE | 0 | Master-North Philadelphia-Waneeta-Richmond 230 kV line overloaded under generator deliverability test in 2029 summer and winter cases; reconductors 2.5 miles Master-North Philadelphia, 2.12 miles North Philadelphia-Waneeta, and rebuilds 3.18 miles Waneeta-Richmond; required ISD for Richmond segments advanced to June 2028 |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 7.33 | 7.33 | 2024-12-03 | 12/3/2024 | 6/1/2028 | 6/1/2029 |  | EP | 8 | Rebuild | No | 2024-W1-12 | Appendix A | AEC:10.75,JCPL:14.26,PECO:38.58,PSEG:33.62,RE:1.31,Neptune:1.48
b3908.1 | PJM MA | PPL | PA | Pocono | Install one 80 MVAr 230 kV capacitor bank at Pocono 230kV Substation | Baseline | 230 | Capacitor | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 4.97 | 4.93 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 4/1/2029 |  | EP | 0 | Install | No | 2024-W1-850 | Appendix A | PPL:100
b3909.1 | PJM MA | PPL | PA | Juniata | Juniata 500 kV yard expansion/reconfiguration to include one new bay and eliminate the line fault stuck breaker | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | generation_interconnection | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:generation_interconnection | FALSE | 0 | Juniata 500/230 kV transformer and Susquehanna-Glenbrook 230 kV line overloaded under generator deliverability test in 2029 summer and winter cases; required ISD advanced to June 2028; expands and reconfigures Juniata 500 kV substation with one new bay and eliminates line fault stuck breaker |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 23.73 | 22.2 | 2024-12-03 | 12/3/2024 | 6/1/2028 | 6/1/2028 |  | EP | 0 | Expand | No | 2024-W1-935 | Appendix A | PPL:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3910.1 | PJM MA | PPL | PA | Susquehanna | Susquehanna T10 230 kV Station Reconfiguration. Break the existing Susquehanna - Glen Brook 230 kV line and loop it 0.2 miles in and out of the Susquehanna T10 230 kV Station. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 10.07 | 9.5 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 12/31/2028 |  | EP | 0 | Reconfigure | No | 2024-W1-549 | Appendix A | PPL:100
b3911.1 | PJM WEST | AEP | OH | Canal - Gay | Rebuild the existing 1.1 mile Canal - Gay 138 kV oil filled pipe-type underground line to address overloads on the existing cable utilizing 5000 MCM XLPE cable. | Baseline | 138 | Transmission Line (Underground) | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | 1970s vintage oil-filled pipe-type cable (1.1-mile underground) identified as overloaded in N-1-1 analysis in 2029 summer case; AEP M-3 need ID AEP-2023-OH024 presented March 2023 |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 15.6 | 15.6 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Rebuild | No | 2024-W1-940 | Appendix A | AEP:100
b3912.1 | PJM WEST | AEP | OH | Canal - Mound | Rebuild the existing 2.2-mile Canal-Mound St 138 kV oil filled pipe-type underground line to address overloads on the existing cable utilizing 5000 MCM XLPE cable. | Baseline | 138 | Transmission Line (Underground) | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | 1926 vintage oil-filled pipe-type cable (2.2-mile underground); EOL/asset renewal concerns per AEP M-3 need ID AEP-2023-OH024; single remaining vendor for replacement parts; overloaded under generator deliverability test, N-1, and N-1-1 analysis in 2029 summer case |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 31.09 | 31.09 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Rebuild | No | 2024-W1-856 | Appendix A | AEP:100
b3913.1 | PJM WEST | AEP | OH | Beatty - White Road | Rebuild 138 kV line section between Beatty and White Road stations (approximately 4.5 miles). Update remote end relay settings as needed. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | AEP EOL list; overhead wood pole structures mostly from 1960s, conductor from 1967; overloaded under generator deliverability test, N-1, and N-1-1 analysis in 2029 summer case; approximately 7.84 miles total (Beatty-White Road: 4.5 mi; White Road-Cyprus: 3.34 mi) |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 18.8 | 18.8 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Rebuild | No | 2024-W1-769 | Appendix A | AEP:100
b3913.2 | PJM WEST | AEP | OH | White Road - Cyprus | Rebuild 138 kV line section between White Road and Cyprus stations (approximately 3.34 miles). Update remote end relay settings as needed. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | AEP EOL list; overhead wood pole structures mostly from 1960s, conductor from 1967; overloaded under generator deliverability test, N-1, and N-1-1 analysis in 2029 summer case; approximately 7.84 miles total (Beatty-White Road: 4.5 mi; White Road-Cyprus: 3.34 mi) |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 14.31 | 14.31 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Rebuild | No | 2024-W1-769 | Appendix A | AEP:100
b3914.1 | PJM WEST | ComEd | IL | Fisk | Change No-load Tap of 2 Autotransformers at Fisk from 338.25 kV to 346.5 kV. | Baseline | 345,138 | Transformer | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.03 | 0.03 | 2024-12-13 | 12/13/2024 | 4/15/2029 | 12/31/2026 |  | EP | 0 | Modify | No |  | Appendix A | ComEd:100
b3914.2 | PJM WEST | ComEd | IL | Crawford | Change No-load Tap of 4 Autotransformers at Crawford from 338.25 kV to 3456.5 kV. | Baseline | 138,345 | Transformer | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.07 | 0.07 | 2024-12-13 | 12/13/2024 | 4/15/2029 | 12/31/2026 |  | EP | 0 | Modify | No |  | Appendix A | ComEd:100
b3914.3 | PJM WEST | ComEd | IL | Elmhurst | Change No-load Tap of 3 Autotransformers at Elmhurst from 338.25kV to 346.5 kV. | Baseline | 345,138 | Transformer | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.05 | 0.05 | 2024-12-13 | 12/13/2024 | 4/15/2029 | 12/31/2026 |  | EP | 0 | Modify | No |  | Appendix A | ComEd:100
b3914.4 | PJM WEST | ComEd | IL | West Loop | Change No-load Tap of 2 Autotransformers at West Loop from 338.25kV to 346.5kV. | Baseline | 138,345 | Transformer | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.03 | 0.03 | 2024-12-13 | 12/13/2024 | 4/15/2029 | 12/31/2026 |  | EP | 0 | Modify | No |  | Appendix A | ComEd:100
b3914.5 | PJM WEST | ComEd | IL | Taylor | Change No-load Tap of 2 Autotransformers at Taylor from 338.25kV to 346.5kV. | Baseline | 345,138 | Transformer | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.03 | 0.03 | 2024-12-13 | 12/13/2024 | 4/15/2029 | 12/31/2026 |  | EP | 0 | Modify | No |  | Appendix A | ComEd:100
b3914.6 | PJM WEST | ComEd | IL | Skokie | Change No-load Tap of 4 Autotransformers at Skokie from 338.25 kV to 345.65 kV. | Baseline | 138,345 | Transformer | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.07 | 0.07 | 2024-12-13 | 12/13/2024 | 4/15/2029 | 12/31/2026 |  | EP | 0 | Modify | No |  | Appendix A | ComEd:100
b3915.1 | PJM WEST | ComEd | IL | Dresden-Mulberry | Reconductor 1.5 miles of 345 kV lines 1202 and 1227 from Dresden to Mulberry with two conductor bundled 1033.5 ACSS conductor. Modify and replace towers as necessary to accommodate the higher mechanical loads of the bundled conductor. | Baseline | 345 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Dresden-Mulberry 345 kV double circuit (lines 1202 and 1227, 1.5 miles) overloaded for N-1 and N-2 outages in 2029 summer and winter cases |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 12.33 | 12.33 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 5 | Reconductor | No | 2024-W1-135 | Appendix A | ComEd:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3915.2 | PJM WEST | ComEd | IL | Dresden | Install 345 kV circuit breaker on line 1202 (Dresden-Mulberry 345 kV) and upgrade disconnects and associated equipment at Dresden 345 kV substation. | Baseline | 345 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Dresden-Mulberry 345 kV double circuit (lines 1202 and 1227, 1.5 miles) overloaded for N-1 and N-2 outages in 2029 summer and winter cases |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 3.77 | 3.77 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 5 | Install | No | 2024-W1-135 | Appendix A | ComEd:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3915.3 | PJM WEST | ComEd | IL | Mulberry | Upgrade disconnects and associated equipment at Mulberry 345 kV substation. | Baseline | 345 | Disconnect Switch | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Dresden-Mulberry 345 kV double circuit (lines 1202 and 1227, 1.5 miles) overloaded for N-1 and N-2 outages in 2029 summer and winter cases |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 0.17 | 0.17 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 5 | Upgrade | No | 2024-W1-135 | Appendix A | ComEd:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b3916.1 | PJM WEST | ComEd | IL | Itasca | Install a new 420 MVA 345/138 kV autotransformer and associated 345 kV and 138 kV circuit breakers at Itasca substation. | Baseline | 345/138 | Transformer | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Busse-Des Plaines 138 kV line overloaded for N-1 contingency pairs in 2029 summer case; addresses M-3 need ID ComEd-2024-004; proposal scope represents half of M-3 supplemental solution at Itasca substation |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 14.31 | 14.31 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2028 |  | EP | 40 | Install | No | 2024-W1-816 | Appendix A | ComEd:100
b3919.1 | PJM WEST | AEP | OH | Maliszewski | Reconfigure Maliszewski 765 kV station from 2 breakers to a 6 breaker ring bus. Install a new 765/345 kV transformer. Establish new 345 kV breaker yard with 3 string breaker and a half to include a line exit to Hyatt and a line exit to Corridor. Loop the existing Hyatt - West Millersport 345 kV line into the new established 345 kV yard at the Maliszewski station. | Baseline | 765 | Substation | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Additional load increase in AEP area driving thermal violations; Genoa-Westar 138 kV and Maliszewski-Polaris 138 kV overloaded in N-1-1; Maliszewski-Vassell 765 kV overloaded in generator deliverability test in 2029 and 2032 summer cases; includes EOL asset renewal concerns on Maliszewski-Corridor, Bokes Creek-Marysville, and Hyatt-Marysville 345 kV lines (converted supplemental s3006) |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 79.74 | 79.74 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Reconfigure | No | 2024-W1-408 | Appendix A | AEP:85.10,Dayton:9.33,DEOK:5.48,OVEC:0.09
b3919.10 | PJM WEST | AEP | OH | Hyatt - Marysville | Rebuild ~19.0 miles of Hyatt - Marysville 345 kV line using 4-bundled 795 ACSR conductor Bold construction (This is an EOL rebuild) | Baseline | 345 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Additional load increase in AEP area driving thermal violations; Genoa-Westar 138 kV and Maliszewski-Polaris 138 kV overloaded in N-1-1; Maliszewski-Vassell 765 kV overloaded in generator deliverability test in 2029 and 2032 summer cases; includes EOL asset renewal concerns on Maliszewski-Corridor, Bokes Creek-Marysville, and Hyatt-Marysville 345 kV lines (converted supplemental s3006) |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 116.7 | 116.7 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2027 |  | EP | 0 | Rebuild | No | 2024-W1- Supplemental conversion | Appendix A | AEP:100
b3919.2 | PJM WEST | AEP | OH | Hyatt - Corridor - West Millersport | Establish a 0.18 mile double circuit 345 kV line extension to cut the existing Hyatt – West Millersport 345 kV line in and out of Corridor station. | Baseline | 345 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Additional load increase in AEP area driving thermal violations; Genoa-Westar 138 kV and Maliszewski-Polaris 138 kV overloaded in N-1-1; Maliszewski-Vassell 765 kV overloaded in generator deliverability test in 2029 and 2032 summer cases; includes EOL asset renewal concerns on Maliszewski-Corridor, Bokes Creek-Marysville, and Hyatt-Marysville 345 kV lines (converted supplemental s3006) |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 3.1 | 3.1 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Cut In | No | 2024-W1-408 | Appendix A | AEP:100
b3919.3 | PJM WEST | AEP | OH | Corridor | Install three new 345 kV breakers at Corridor station in order to accommodate the cut in of the Hyatt- West Millersport 345 kV line. | Baseline | 345 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Additional load increase in AEP area driving thermal violations; Genoa-Westar 138 kV and Maliszewski-Polaris 138 kV overloaded in N-1-1; Maliszewski-Vassell 765 kV overloaded in generator deliverability test in 2029 and 2032 summer cases; includes EOL asset renewal concerns on Maliszewski-Corridor, Bokes Creek-Marysville, and Hyatt-Marysville 345 kV lines (converted supplemental s3006) |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 5.52 | 5.52 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No | 2024-W1-408 | Appendix A | AEP:100
b3919.4 | PJM WEST | AEP | OH | Maliszewski - Corridor | Reconductor 10.2-mile of Maliszewski-Corridor 345 kV line. | Baseline | 345 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Additional load increase in AEP area driving thermal violations; Genoa-Westar 138 kV and Maliszewski-Polaris 138 kV overloaded in N-1-1; Maliszewski-Vassell 765 kV overloaded in generator deliverability test in 2029 and 2032 summer cases; includes EOL asset renewal concerns on Maliszewski-Corridor, Bokes Creek-Marysville, and Hyatt-Marysville 345 kV lines (converted supplemental s3006) |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 18.3 | 18.3 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Reconductor | No | 2024-W1-408 | Appendix A | AEP:100
b3919.5 | PJM WEST | AEP | OH | Bokes Creek - Marysville | Reconductor 4.75-miles of the existing Bokes Creek-Marysville 345 kV circuit. Update the associated relay settings. | Baseline | 345 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Additional load increase in AEP area driving thermal violations; Genoa-Westar 138 kV and Maliszewski-Polaris 138 kV overloaded in N-1-1; Maliszewski-Vassell 765 kV overloaded in generator deliverability test in 2029 and 2032 summer cases; includes EOL asset renewal concerns on Maliszewski-Corridor, Bokes Creek-Marysville, and Hyatt-Marysville 345 kV lines (converted supplemental s3006) |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 6.67 | 6.67 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Reconductor | No | 2024-W1-408 | Appendix A | AEP:100
b3919.6 | PJM WEST | AEP | OH | Marysville - Hyatt | Rebuild 4.4-miles of the existing Marysville - Hyatt 345 kV double circuit line where it extends into Marysville station. | Baseline | 345 | Transmission Line | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Additional load increase in AEP area driving thermal violations; Genoa-Westar 138 kV and Maliszewski-Polaris 138 kV overloaded in N-1-1; Maliszewski-Vassell 765 kV overloaded in generator deliverability test in 2029 and 2032 summer cases; includes EOL asset renewal concerns on Maliszewski-Corridor, Bokes Creek-Marysville, and Hyatt-Marysville 345 kV lines (converted supplemental s3006) |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 26.26 | 26.26 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Rebuild | No | 2024-W1-408 | Appendix A | AEP:100
b3919.7 | PJM WEST | AEP | OH | Hyatt | Upgrade 345 kV breakers K & K1 along with associated switches and conductor to 5000A at Hyatt Station. | Baseline | 345 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Additional load increase in AEP area driving thermal violations; Genoa-Westar 138 kV and Maliszewski-Polaris 138 kV overloaded in N-1-1; Maliszewski-Vassell 765 kV overloaded in generator deliverability test in 2029 and 2032 summer cases; includes EOL asset renewal concerns on Maliszewski-Corridor, Bokes Creek-Marysville, and Hyatt-Marysville 345 kV lines (converted supplemental s3006) |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 2.94 | 2.94 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Upgrade | No | 2024-W1-408 | Appendix A | AEP:100
b3919.8 | PJM WEST | AEP | OH | West Millersport | Upgrade the relaying and associated equipment at West Millersport stationto coordinate with the cut in work to Corridor station. | Baseline | 345 | Relay | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Additional load increase in AEP area driving thermal violations; Genoa-Westar 138 kV and Maliszewski-Polaris 138 kV overloaded in N-1-1; Maliszewski-Vassell 765 kV overloaded in generator deliverability test in 2029 and 2032 summer cases; includes EOL asset renewal concerns on Maliszewski-Corridor, Bokes Creek-Marysville, and Hyatt-Marysville 345 kV lines (converted supplemental s3006) |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 0.41 | 0.41 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Upgrade | No | 2024-W1-408 | Appendix A | AEP:100
b3919.9 | PJM WEST | AEP | OH | Marysville | Upgrade 3000A 345 kV breaker 'L2' along with associated terminal elements to 5000A at Marysville. | Baseline | 345 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | load_growth | consistent | FALSE | 0 | Additional load increase in AEP area driving thermal violations; Genoa-Westar 138 kV and Maliszewski-Polaris 138 kV overloaded in N-1-1; Maliszewski-Vassell 765 kV overloaded in generator deliverability test in 2029 and 2032 summer cases; includes EOL asset renewal concerns on Maliszewski-Corridor, Bokes Creek-Marysville, and Hyatt-Marysville 345 kV lines (converted supplemental s3006) |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 2.56 | 2.56 | 2024-12-03 | 12/3/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Upgrade | No | 2024-W1-408 | Appendix A | AEP:100
b3921.1 | PJM SOUTH | Dominion | VA | Merck,Elkton D.P. | Wreck and rebuild 115kV line 119 from structure 119/305 (Merck #5 substation) to 119/411A (Port Republic Substation). The existing structures shall be replaced one for one within the existing ROW using primarily custom engineered double circuit 115kV steel structures on concrete foundations. The line will be rebuilt with 3-phase 1-768.2 ACSS/TW/HS (20/7) 250 MOT “Maumee” conductor and two (2) DNO-11410 OPGW. The rebuild includes the installation of double circuit structures but assumes the second circuit will not be installed as part of this project, and that the vacant conductor arms should not be utilized without acquiring additional ROW. This scope assumes project GITAE2029C will be completed prior to the construction of this project. Project GITAE2029C serves to install Port Republic Substation, which will split Line 119 in between existing Structures 119/411 and 119/412. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Merck No.5-Port Republic 115 kV line No. 119 overloaded for multiple contingencies in 2029 summer and winter cases; below 200 kV exclusion from competition; rebuilt from structure 119/305 to 119/411A with ACSS/TW/HS conductor |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 44.84 | 41.87 | 2024-12-12 | 12/12/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Rebuild | No |  | Appendix A | Dominion:100
b3921.2 | PJM SOUTH | Dominion | VA | Merck | Uprate the 397.5 ACSR jumpers and associated equipment to meet the line conductor rating of 393MVA. | Baseline | 115 | Substation equipment | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Merck No.5-Port Republic 115 kV line No. 119 overloaded for multiple contingencies in 2029 summer and winter cases; below 200 kV exclusion from competition; rebuilt from structure 119/305 to 119/411A with ACSS/TW/HS conductor |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 0.49 | 0.46 | 2024-12-12 | 12/12/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Upgrade | No |  | Appendix A | Dominion:100
b3922.1 | PJM SOUTH | Dominion | NC | Pantego,Terra Ceia | This project serves to wreck and rebuild 115kV line 1031 from structure 1031/220 to structure 1031/329. The existing structures to be removed are primarily single circuit wood, steel or concrete monopoles. The existing structures to be removed were primarily constructed in 1993 with the weathering steel structures being constructed in 2011. See Figure 1 for the project location. The existing structures shall be replaced one for one within the existing ROW using single circuit steel monopoles on foundations. The line will be rebuilt with single circuit 3-phase 768.2 ACSS/TW/HS (20/7) “Maumee” conductor and single (1) DNO-11410 OPGW, respectively. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Pantego-Terra Ceia 115 kV line No. 1031 overloaded under N-1-1 analysis in 2029 summer case; below 200 kV exclusion from competition; rebuilt with steel monopoles and ACSS/TW/HS conductor |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 29.37 | 29.37 | 2024-12-12 | 12/12/2024 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Rebuild | No |  | Appendix A | Dominion:100
b3925.1 | PJM WEST | ATSI | OH | Avery - Shinrock | Rebuild the 7.46 miles of Avery - Shinrock 138 kV Line with 795 kcmil 26/7 ACSS (7.46 miles) | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple 138 kV lines overloaded for N-2 contingency pairs in 2029 summer and light load cases; two 345 kV lines overloaded for N-2 contingency pairs in 2029 summer case; existing lines originally constructed 60-100 years ago; flowgate drivers include summer generation deliverability and N-1/N-1-1 baseline; total ~59.46 miles of 138 kV rebuilt |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 15.2 | 15.2 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 12/10/2027 |  | EP | 0 | Rebuild | No | 2024-W1-605 | Appendix A | ATSI:100 |  | 6/1/2029
b3925.2 | PJM WEST | ATSI | OH | Greenfield - Lakeview | Rebuild the 13.45 miles of Greenfield - Lakeview 138 kV Line from 2 x 336.4 kcmil 26/7 ACSR to 1 x 795 kcmil 26/7 ACSS | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple 138 kV lines overloaded for N-2 contingency pairs in 2029 summer and light load cases; two 345 kV lines overloaded for N-2 contingency pairs in 2029 summer case; existing lines originally constructed 60-100 years ago; flowgate drivers include summer generation deliverability and N-1/N-1-1 baseline; total ~59.46 miles of 138 kV rebuilt |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 59.68 | 59.68 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Rebuild | No | 2024-W1-605 | Appendix A | ATSI:100 |  | 6/1/2029
b3925.3 | PJM WEST | ATSI | OH | Avery-Hayes | Rebuild the 6.5 miles of Avery-Hayes 138 kV Line with 795 kcmil 26/7 ACSS conductor | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple 138 kV lines overloaded for N-2 contingency pairs in 2029 summer and light load cases; two 345 kV lines overloaded for N-2 contingency pairs in 2029 summer case; existing lines originally constructed 60-100 years ago; flowgate drivers include summer generation deliverability and N-1/N-1-1 baseline; total ~59.46 miles of 138 kV rebuilt |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 11.01 | 11.01 | 2025-01-07 | 1/7/2025 | 6/1/2027 | 6/1/2027 |  | EP | 0 | Rebuild | No | 2024-W1-605 | Appendix A | ATSI:100 |  | 6/1/2027
b3925.4 | PJM WEST | ATSI | OH | Greenfield - Beaver Corridor | Rebuild the Greenfield - Beaver 138 kV corridor (32 miles) with 795 kcmil 26/7 ACSS. This corridor encompasses multiple 138 kV lines that are constructed on common towers. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Multiple 138 kV lines overloaded for N-2 contingency pairs in 2029 summer and light load cases; two 345 kV lines overloaded for N-2 contingency pairs in 2029 summer case; existing lines originally constructed 60-100 years ago; flowgate drivers include summer generation deliverability and N-1/N-1-1 baseline; total ~59.46 miles of 138 kV rebuilt |  | 20250304-2024-rtep-window-1-reliability-analysis-report.json | 2025-01-01 | 1 | 131.43 | 131.43 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Rebuild | No | 2024-W1-605 | Appendix A | ATSI:100 |  | 6/1/2029
b3928.1 | PJM SOUTH | Dominion | VA | Navy North | Install (1) 230kV, 50 MVAr Shunt Capacitor Bank & associated equipment including breaker at Navy North substation. | Baseline | 230 | Capacitor | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 3 | 3 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 4/24/2026 |  | EP | 0 | Install | No | 2024-W1-527 | Appendix A | Dominion:100
b3936.1 | PJM WEST | AEP | OH | P5 Substation: Location CEII | AEP Zone 2024W1 P5 Solution #1: Install battery chargers & associated equipment at AEP substation. Addresses the following FGs: 2024-P5-AEP07, 2024-P5-AEP08. | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.07 | 0.07 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | AEP:100
b3936.2 | PJM WEST | AEP | OH | P5 Substation: Location CEII | AEP Zone 2024W1 P5 Solution #2: Install battery chargers & associated equipment at AEP substation. Addresses the following FG's: 2024-P5-AEP03, 2024-P5-AEP04 | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.11 | 0.11 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | AEP:100
b3936.3 | PJM WEST | AEP | OH | P5 Substation: Location CEII | AEP Zone 2024W1 P5 Solution #3: Install battery chargers & associated equipment at AEP substation. Addresses the following FG's: 2024-P5-AEP09, 2024-P5-AEP10, 2024-P5-AEP11, 2024-P5-AEP12. | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.08 | 0.08 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | AEP:100
b3936.4 | PJM WEST | AEP | IN | P5 Substation: Location CEII | AEP Zone 2024W1 P5 Solution #4: Install battery chargers & associated equipment at AEP substation. Addresses the following FG's: 2024-P5-AEP05. | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.12 | 0.12 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | AEP:100
b3936.5 | PJM WEST | AEP | VA | P5 Substation: Location CEII | AEP Zone 2024W1 P5 Solution #5: Install battery chargers & associated equipment at AEP substation. Addresses the following FG's: 2024-P5-AEP01. | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.09 | 0.09 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | AEP:100
b3936.6 | PJM WEST | OVEC | OH | P5 Substation: Location CEII | OVEC Zone 2024W1 P5 Solution #6: Install battery chargers & associated equipment and upgrade protection equipment at OVEC substation. Addresses the following FG's: 2024-P5-AEP02. | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.58 | 0.58 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | AEP:100
b3936.7 | PJM WEST | AEP | WV | P5 Substation: Location CEII | AEP Zone 2024W1 P5 Solution #7: Install battery chargers & associated equipment at AEP substation. Addresses the following FG's: 2024-P5-AEP06. | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.15 | 0.15 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | AEP:100
b3937.1 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #1 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP01 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.10 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #10 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP10 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.11 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #11 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP11 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.12 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #12 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP12 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.13 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #13 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP13 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.14 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #14 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP14 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.15 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #15 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP15 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.16 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #16 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP16 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.17 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #17 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP17 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.18 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #18 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP18 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.19 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #19 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP19 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.2 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #2 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP02 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.20 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #20 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP20 | Baseline | 69 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.21 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #21 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP21 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.22 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #22 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP23 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.23 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #23 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP24 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.24 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #24 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP26 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.25 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #25 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP27 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.26 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #26 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP28 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.27 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #27 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP29 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.28 | PJM SOUTH | Dominion | WV | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #28 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP30 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.29 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #29 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP31 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.3 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #3 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP03 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.30 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #30 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP32 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.31 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #31 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP33 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.32 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #32 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP34 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.33 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #33 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP35 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.34 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #34 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP36 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.35 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #35 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP37 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.36 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #36 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP38 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.37 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #37 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP39 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.38 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #38 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP40 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.39 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #39 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP41 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.4 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #4 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP04 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.5 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #5 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP05 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.6 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #6 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP06 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.7 | PJM SOUTH | Dominion | WV | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #7 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP07 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.8 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #8 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP08 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3937.9 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution #9 - DC Supply Monitoring: Addressing FG # 2024-P5-DVP09 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No |  | Appendix A | Dominion:100
b3938.1 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution No. 40 – Replace and upgrade relay and associated equipment at DVP substation, addressing FG No. 2024-P5-DVP16. | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.19 | 0.19 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Replace | No
b3938.2 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution No. 41 – Replace and upgrade relay and associated equipment at DVP substation, addressing FG No. 2024-P5-DVP23. | Baseline | 500 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.11 | 0.11 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Replace | No
b3938.3 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution No. 42 – Replace and upgrade relay and associated equipment at DVP substation, addressing FG No. 2024-P5-DVP14. | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.18 | 0.18 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/30/2025 |  | PL | 0 | Replace | No
b3938.6 | PJM SOUTH | Dominion | VA | P5 Substation: Location CEII | 2024W1 DVP P5 Solution No. 45 – Replace and upgrade relay and associated equipment at DVP substation, addressing FG No. 2024-P5-DVP03. | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.2 | 0.2 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Replace | No
b3939.1 | PJM MA | PSEG | NJ | P5 Substation: Location CEII | 2024W1 PSEG P5 Solution #1 - Battery monitoring upgrades at PSEG substation. Addresses FG #2024-P5-PSEG01 | Baseline | 500 | Communication Equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.08 | 0.08 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2027 |  | PL | 0 | Install | No |  | Appendix A | PSEG:100
b3939.2 | PJM MA | PSEG | NJ | P5 Substation: Location CEII | 2024W1 PSEG P5 Solution #2 - Battery monitoring upgrades at PSEG substation. Addresses FG #2024-P5-PSEG02 | Baseline | 230 | Communication Equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.08 | 0.08 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2027 |  | PL | 0 | Install | No |  | Appendix A | PSEG:100
b3939.3 | PJM MA | PSEG | NJ | P5 Substation: Location CEII | 2024W1 PSEG P5 Solution #3 - Battery monitoring upgrades at PSEG substation. Addresses FG #2024-P5-PSEG03 | Baseline | 230 | Communication Equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.08 | 0.08 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2027 |  | PL | 0 | Install | No |  | Appendix A | PSEG:100
b3939.4 | PJM MA | PSEG | NJ | P5 Substation: Location CEII | 2024W1 PSEG P5 Solution #4 - Battery monitoring upgrades at PSEG substation. Addresses FG #2024-P5DYN-PSEG01 | Baseline | 230 | Communication Equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.08 | 0.08 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2027 |  | PL | 0 | Install | No |  | Appendix A | PSEG:100
b3939.5 | PJM MA | PSEG | NJ | P5 Substation: Location CEII | 2024W1 PSEG P5 Solution #5 - Battery monitoring upgrades at PSEG substation. Addresses FG #2024-P5DYN-PSEG02 | Baseline | 230 | Communication Equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.08 | 0.08 | 2025-07-08 | 7/8/2025 | 6/1/2029 | 6/1/2027 |  | PL | 0 | Install | No |  | Appendix A | PSEG:100
b3942.1 | PJM MA | PECO | PA | Chichester | Replace existing and install new relays at Chichester 230 kV substation to increase the rating on Chichester – Trainer 230 kV circuit. | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.69 | 0.69 | 2025-11-04 | 11/4/2025 | 6/1/2030 | 5/31/2030 |  | PL | 0 | Upgrade | No
b3943.1 | PJM WEST | ComEd | IN | Stateline (DOMENE) | Install a new 345/138 kV transformer TR 84, and associated equipment at State line substation. Install two 345 kV circuit breakers, one 138 kV circuit breaker and associated equipment; also replace the 138 kV BT 732 circuit breaker at State line substation. | Baseline | 345 | Transformer | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | State Line 345/138 kV transformer TR 82 is overloaded for N-2 outages in the 2030 winter case. Flowgates excluded from competition under below 200 kV exclusion. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 20.81 | 20.81 | 2025-11-14 | 11/14/2025 | 12/1/2030 | 12/1/2030 |  | PL | 0 | Install | No
b3945.1 | PJM WEST | AEP | WV | Mullens | Adjust Mullens 138 kV cap bank Vhi setting to 1.04. Adjust protection settings as needed at the station. | Baseline | 138 | Capacitor | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.1 | 0.1 | 2025-11-14 | 11/14/2025 | 12/1/2030 | 12/1/2030 |  | EP | 0 | Modify | No
b3952.1 | PJM WEST | AEP | VA | Joshua Falls | Replace 138 kV, 3000A circuit breakers H and H1 with 4000A circuit breakers. | Baseline | 765 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.51 | 1.51 | 2025-11-14 | 11/14/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 | Replace | No
b3971.1 | PJM WEST | AEP | OH | Haviland | At Haviland, reconductor bus No. 1 Sub cond 500 MCM CU 37 Str toward Haviland bus No. 2 and reconductor Haviland bus No. 2 500 KCM CU, 37-Str. and 795 KCM AAC, 37-Str. toward Timber SW 138 kV. | Baseline | 138 | Bus | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.47 | 1.47 | 2025-11-14 | 11/14/2025 | 12/1/2030 | 6/1/2030 |  | EP | 0 | Replace | No
b3972.1 | PJM WEST | AEP | OH | E. Lima,Haviland | Perform a ratings study and clearance mitigation on the ~5.55-mile section of sag derated 556.5 ACSR 26/7 DOVE conductor (East Lima-STR 28) between the East Lima-Haviland 138 kV circuit on the East Lima-West Lima 138 kV line. | Baseline | 345,138 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 6.8 | 6.8 | 2025-11-14 | 11/14/2025 | 4/15/2030 | 4/15/2030 |  | EP | 0 | Sag Study | No
b3976.1 | PJM WEST | APS | WV | Bedington | At Bedington: • Install foundation, conduit and grounding for new equipment. • Install three 138 kV surge arresters. • Replace one existing 138 kV CVT with three 138 kV CVTs. • Replace one lot of limiting conductor. • Install one lot of cables and grounding. • Replace one existing 138 kV Eagle line terminal relay panel and breaker failure, with one standard line relaying panel consisting of one SEL-421, one SEL-411L and one SEL-451. | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.96 | 1.96 | 2025-11-14 | 11/14/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 | Replace | No
b3977.1 | PJM WEST | APS | VA | Meadow Brook | At Meadow Brook: • Install conduit and grounding for new equipment. • Install one lot of cables and grounding for new equipment. • Replace one 138 kV wave trap on the West Winchester line terminal. | Baseline | 500 | Wave Trap | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.36 | 0.35 | 2025-11-14 | 11/14/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 | Replace | No
b3978.1 | PJM WEST | ATSI | OH | Lakeview,Ottowa | • Reconductor one span of transmission line outside Ottawa substation. • Reconductor one span of transmission line outside Lakeview substation. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.09 | 1.09 | 2025-11-14 | 11/14/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 | Reconductor | No
b3978.2 | PJM WEST | ATSI | OH | Lakeview | Replace limiting terminal equipment at Lakeview substation. • Two thermal relays • Two 138 kV disconnect switches • Limiting substation conductor | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.32 | 0.32 | 2025-11-14 | 11/14/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 | Replace | No
b3979.1 | PJM WEST | ATSI | OH | Johnson,Elyria | Abbe-Johnson No.1 69 kV line (Johnson-Elyria Water P.C.):[GE1.1][AH1.2] • Reconductor one span of transmission line between Johnson substation and Elyria Water P.C. • Replace one 69 kV disconnect switch. • Upgrade one thermal relay. • Modify Elyria Loop Tap configuration. • Install one 69 kV disconnect switch. | Baseline | 138,69 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 2.07 | 2.07 | 2025-11-14 | 11/14/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 | Reconductor | No
b3979.2 | PJM WEST | ATSI | OH | Elyria,Spring Valley | Abbe-Johnson No.1 69 kV line (Elyria Water P.C.-Spring Valley): • Replace one 69 kV disconnect switch. | Baseline | 69 | Switch | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.71 | 0.71 | 2025-11-14 | 11/14/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 | Replace | No
b3979.3 | PJM WEST | ATSI | OH | Spring Valley,Lorain County Community College | Abbe-Johnson No.1 69 kV line (Spring Valley-Lorain College): • Replace two 69 kV disconnect switches. | Baseline | 69 | Switch | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.44 | 0.44 | 2025-11-14 | 11/14/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 | Replace | No
b3980.1 | PJM WEST | ATSI | OH | Bellvue,Groton | Bellevue-Groton 69 kV line: • Rebuild 4 miles of the Bellevue-Groton 69 kV line. | Baseline | 69,138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Bellevue-Groton 69 kV line is overloaded for a N-1 outage in the 2030 summer case. Flowgate excluded from competition under below 200 kV exclusion. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 9.53 | 9.53 | 2025-11-14 | 11/14/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 | Rebuild | No
b3980.2 | PJM WEST | ATSI | OH | Bellvue | Bellevue substation: • Replace three 69 kV disconnect switches. • Revise relay settings. • Replace limiting substation conductor. | Baseline | 69 | Substation equipment | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Bellevue-Groton 69 kV line is overloaded for a N-1 outage in the 2030 summer case. Flowgate excluded from competition under below 200 kV exclusion. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 0.47 | 0.47 | 2025-11-14 | 11/14/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 | Replace | No
b3980.3 | PJM WEST | ATSI | OH | Groton | Groton substation: • Revise relay settings | Baseline | 138 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Bellevue-Groton 69 kV line is overloaded for a N-1 outage in the 2030 summer case. Flowgate excluded from competition under below 200 kV exclusion. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 0.1 | 0.1 | 2025-11-14 | 11/14/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 | Modify | No
b4000.1 | PJM WEST | AEP | WV | John Amos | Add two 765 kV breakers at Amos Substation to expand the breaker and a half scheme to accommodate the new Amos-Welton Spring 765 kV line. | Baseline | 765 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 30.87 | 30.87 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No | 2024-W1-708 | Appendix A | APS:14.67,BGE:8.11,Dominion:66.09,DPL:2.15,PEPCO:8.98 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.10 | PJM WEST | APS | MD | Rocky Point | Install four 250 MVAR cap banks (two on 765 and two on 500 kV side) and a +/-500 MVAR STATCOM on the 765 kV Rocky Point yard | Baseline | 765 | Capacitor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 121 | 121 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No | 2024-W1-708 | Appendix A | APS:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.11 | PJM WEST | APS | MD | Black Oak | Expand Black Oak Substation to accommodate the connection of the 502 Jct-Woodside 500 kV line and loop the 502 Jct-Woodside 500 kV line into the Black Oak substation by constructing ~0.85 miles of new 500 kV line into and out of Black Oak 500 kV substation | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 19.23 | 19.23 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Expand | No | 2024-W1-708 | Appendix A | APS:8.93,BGE:13.63,Dominion:61.66,PEPCO:15.78 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.12 | PJM WEST | APS | MD | Doubs | Upgrade the terminal equipment on the Doubs No. 1 500/230 kV transformer. | Baseline | 500/230 | Line and Terminal Equipment | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.43 | 0.43 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Upgrade | No | 2024-W1-708 | Appendix A | APS:74.10,PEPCO:25.90
b4000.13 | PJM WEST | APS | MD | Doubs area | Terminate the Woodside - Goose Creek 500 kV Line into Doubs Substation, creating the Woodside - Doubs #2 500 kV Line Remove the Chanceford-Doubs and Rocky Point-Doubs line terminations at the Doubs substation and connects the two lines through a 0.6 mile 500 kV bypass line around the Doubs substation | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 13.97 | 13.97 | 2025-01-07 | 1/7/2025 | 6/1/2032 | 6/1/2032 |  | EP | 0 | Build | No | 2024-W1-551 | Appendix A | AEC:0.20,APS:0.06,BGE:0.71,Dominion:89.06,DPL:0.36,JCPL:0.33,ME:0.15,PECO:0.73,PEPCO:7.93,PSEG:0.42,RE:0.02,Neptune:0.03 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.14 | PJM WEST | NEET | MD | Black Oak 500 kV substation | Install two new 500 kV dead-end structures near Black Oak substation to interconnect the 502 Junction – Woodside 500 kV transmission line. Adjust Woodside protection scheme for Black Oak loop-in and remove 502 Junction tie. (NEET Scope) | Baseline | 500 | Transmission Structures | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 3 | 3 | 2025-06-05 | 6/5/2025 | 6/1/2029 | 12/31/2031 |  | EP | 2 | Build | No | 2024-W1-PJM | Appendix A | APS:100
b4000.15 | PJM WEST | APS | WV | Welton Springs - Rocky Point | Construct a new 86 miles Welton Spring to Rocky Point 765 kV line (Welton Spring to DVP local area, roughly 50 miles) (WV Portion) | Baseline | 765 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 248.5 | 248.5 | 2025-06-05 | 6/5/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Build | No | 2024-W1-708 | Appendix A | APS:14.67,BGE:8.11,Dominion:66.09,DPL:2.15,PEPCO:8.98 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.2 | PJM WEST | APS | WV | John Amos - Welton Springs | Construct a new 175 miles Amos to Welton Spring 765 kV line. (AEP Section of the line is 30 miles) | Baseline | 765 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 150 | 150 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Build | No | 2024-W1-708 | Appendix A | APS:14.67,BGE:8.11,Dominion:66.09,DPL:2.15,PEPCO:8.98 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.200 | PJM WEST | AEP | OH | Broadford | Broadford 765 kV Upgrade: Replace Jackson's Ferry CB Q2 | Baseline | 765 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 4.5 | 4.5 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | Cancelled | 0 | Replace | No | 2024-W1-81 | Appendix A | AEP:21.60,APS:12.36,BGE:8.28,Dominion:46.81,PEPCO:10.95 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.201 | PJM WEST | AEP | OH | Smith Mountain | Smith Mountain 138 kV Upgrade: Replace 795 KCM AAC, 37-Str. 795 KCM AAC, 37-Str. PH A B2S1 B2S2 BS1 BS2 | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.4 | 0.4 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Replace | No | 2024-W1-81 | Appendix A | AEP:100
b4000.202 | PJM WEST | AEP | OH | Smith Mountain - Redeye | Rebuild 12.5 miles of Smith Mountain - Redeye 138 kV line | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 14.9 | 14.9 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Reconductor | No | 2024-W1-81 | Appendix A | AEP:100
b4000.203 | PJM WEST | AEP | OH | Redeye - Candler's Mountain | Rebuild 17.5 miles of Redeye - Candler's Mountain 138 kV line | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 21 | 21 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Reconductor | No | 2024-W1-81 | Appendix A | AEP:100
b4000.204 | PJM WEST | AEP | OH | Candler's Mountain - Opossum Creek | Rebuild 4 miles of Candler's Mountain - Opossum Creek 138 kV line | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 4.9 | 4.9 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Reconductor | No | 2024-W1-81 | Appendix A | AEP:100
b4000.205 | PJM WEST | AEP | OH | Candler's Mountain | Candler's Mountain 138 kV: Replace 1590 KCM AAC, 61-Str. Replace MOAB "Y" SMITH MTN LINE | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.2 | 0.2 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Replace | No | 2024-W1-81 | Appendix A | AEP:100
b4000.206 | PJM WEST | AEP | OH | Opposum Creek | Opposum Creek 138 kV: Replace Opossum Creek Switch | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.1 | 0.1 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Replace | No | 2024-W1-81 | Appendix A | AEP:100
b4000.207 | PJM WEST | AEP | OH | Leesville | Leesville Station Upgrade 138 kV: Replace 795 KCM AAC, 37-Str. IPS Sch. 40 1272 KCM AAC, 61-Str. 1272 KCM AAC, 61-Str. PH A,B,C ALTA VISTA CB-A BUS DISC ALTA VISTA CB-A LINE DISC Wavetrap (1200A) Relay Thermal Limit 1356 Amps | Baseline | 138 | Substation equipment,Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.6 | 0.6 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Replace | No | 2024-W1-81 | Appendix A | AEP:100
b4000.208 | PJM WEST | AEP | OH | Otter | Otter 138 kV Station Upgrade: Replace 795 KCM AAC, 37-Str. | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.1 | 0.1 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Replace | No | 2024-W1-81 | Appendix A | AEP:100
b4000.209 | PJM WEST | AEP | OH | Altavista - Otter - Johnson Mountain | Rebuild 0.9 miles of Altavista - Otter 138 kV line | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 1.2 | 1.2 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | Cancelled | 0 | Reconductor | No | 2024-W1-81 | Appendix A | AEP:100
b4000.210 | PJM WEST | AEP | OH | Otter - Johnson Mountain | Rebuild 7 miles of Otter - Johnson Mountain 138 kV line | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 8.4 | 8.4 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Reconductor | No | 2024-W1-81 | Appendix A | AEP:100
b4000.211 | PJM WEST | AEP | OH | Johnson Mountain - New London | Rebuild 6.5 miles of Johnson Mountain - New London 138 kV line | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 7.68 | 7.68 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Reconductor | No | 2024-W1-81 | Appendix A | AEP:100
b4000.251 | PJM WEST | AEP | OH | Cloverdale | Replace the wave trap and upgrade the relay at Cloverdale 765kV substation | Baseline | 765 | Wave Trap,Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 1 | 1 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Replace | No | 2024-W1-617 | Appendix A | AEP:3,APS:8.96,BGE:6.53,Dominion:72.75,PEPCO:8.76 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.252 | PJM WEST | AEP | OH | Joshua Falls | Replace the wave trap and upgrade the relay at Joshua Falls 765kV substation | Baseline | 765 | Wave Trap,Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 1 | 1 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Replace | No | 2024-W1-617 | Appendix A | AEP:3,APS:8.96,BGE:6.53,Dominion:72.75,PEPCO:8.76 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.3 | PJM WEST | APS | WV | John Amos - Welton Springs | Construct a new 175 miles Amos to Welton Spring 765 kV line. (APS/FE Section of the line is 145 miles) | Baseline | 765 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 725 | 725 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Build | No | 2024-W1-708 | Appendix A | APS:14.67,BGE:8.11,Dominion:66.09,DPL:2.15,PEPCO:8.98 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.300 | PJM SOUTH | Dominion | VA | Marsh Run, Remington CT | Rebuild approximately 1.71 miles of 230kV line 299 from the Marsh Run substation to the Remington CT substation. New conductor has a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 5.35 | 5.35 | 2025-01-07 | 1/7/2025 | 5/30/2029 | 5/30/2029 |  | EP | 10 | Reconductor | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.301 | PJM SOUTH | Dominion | VA | Marsh Run, Remington CT | Reconductor approximately 1.24 miles of 230kV line 280 from Remington - the Marsh Run CT substation to the Remington substation. New conductor has a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 3.89 | 3.89 | 2025-01-07 | 1/7/2025 | 5/30/2029 | 5/30/2029 |  | EP | 10 | Reconductor | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.302 | PJM SOUTH | Dominion | VA | Marsh Run | Uprate line #299 terminal equipment, line leads, and bus at Marsh Run substation to be rated to 4000A. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 2.53 | 2.53 | 2025-01-07 | 1/7/2025 | 5/30/2029 | 5/30/2029 |  | EP | 10 | Uprate | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.303 | PJM SOUTH | Dominion | VA | Remington CT | Uprate line #299 terminal equipment, line leads, and bus at Remington CT substation to be rated to 4000A. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 2.44 | 2.44 | 2025-01-07 | 1/7/2025 | 5/30/2029 | 5/30/2029 |  | EP | 0 | Uprate | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.304 | PJM SOUTH | Dominion | VA | Wheeler, Linton | Partial reconductor/partial wreck & rebuild of 230kV Line #2161 Gainesville – Wheeler. New conductor has a summer rating of 1573 MVA. (Wheeler - Linton Tap segment) | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 17.72 | 17.72 | 2025-01-07 | 1/7/2025 | 5/16/2029 | 5/30/2029 |  | EP | 10 | Reconductor | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.305 | PJM SOUTH | Dominion | VA | Linton, Atlantic | Partial reconductor/partial wreck & rebuild of 230kV Line #2161 Gainesville – Wheeler. New conductor has a summer rating of 1573 MVA. (Linton Tap - Atlantic segment) | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 3.49 | 3.49 | 2025-01-07 | 1/7/2025 | 5/16/2029 | 5/16/2029 |  | EP | 10 | Reconductor | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.306 | PJM SOUTH | Dominion | VA | Atlantic, Trident | Partial reconductor/partial wreck & rebuild of 230kV Line #2161 Gainesville – Wheeler. New conductor has a summer rating of 1573 MVA. (Atlantic - Trident segment) | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 1.72 | 1.72 | 2025-01-07 | 1/7/2025 | 5/16/2029 | 5/16/2029 |  | EP | 10 | Reconductor | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.307 | PJM SOUTH | Dominion | VA | Trident, Gainesville | Partial reconductor/partial wreck & rebuild of 230kV Line #2161 Gainesville – Wheeler. New conductor has a summer rating of 1573 MVA. (Trident - Gainesville segment) | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 6.16 | 6.16 | 2025-01-07 | 1/7/2025 | 5/16/2029 | 5/16/2029 |  | EP | 10 | Reconductor | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.308 | PJM SOUTH | Dominion | VA | Gainesville | Upgrade all line #2161 terminal equipment at Gainesville to 4000A. A CCVT will also be replaced due to aging. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 1.78 | 1.78 | 2025-01-07 | 1/7/2025 | 5/16/2029 | 5/16/2029 |  | EP | 10 | Upgrade | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.309 | PJM SOUTH | Dominion | VA | Wheeler | Upgrade all line #2161 terminal equipment Wheeler substation to 4000A. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 2.25 | 2.25 | 2025-01-07 | 1/7/2025 | 5/16/2029 | 5/16/2029 |  | EP | 10 | Upgrade | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.310 | PJM SOUTH | Dominion | VA | Trident | Revise relay settings at Trident substation. | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.03 | 0.03 | 2025-01-07 | 1/7/2025 | 5/16/2029 | 5/16/2029 |  | EP | 10 | Revise | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.311 | PJM SOUTH | Dominion | VA | Thelma, Lakeview | Rebuild 230kV Line #213 and #225 from Thelma – Lakeview. New conductor has a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 44.69 | 44.69 | 2025-01-07 | 1/7/2025 | 5/16/2029 | 5/16/2029 |  | EP | 0 | Rebuild | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.312 | PJM SOUTH | Dominion | VA | Thelma, Lakeview | At Thelma subsation, upgrade line lead, wave traps (213WT & 225WT), circuit breaker leads to 4000A. CB switches 22535, 23235, 23238 and 21335 will also be upgrade to 4000A DEB switches. CCVTs 213P1, 213P2 and 213P3 will be replaced due to aging. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 2.3 | 2.3 | 2025-01-07 | 1/7/2025 | 5/26/2029 | 5/26/2029 |  | EP | 0 | Upgrade | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.313 | PJM SOUTH | Dominion | VA | Lakeview | At Lakeview substation, upgrade wave traps 213WT and 225WT, line leads, and circuit breaker leads to 4000A. Upgrade CB switches 22565 and 22564 to 4000A double-end break switches. Replace CCVTs 225P1, 225P2, and 225P3 due to aging. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 1.72 | 1.72 | 2025-01-07 | 1/7/2025 | 5/26/2029 | 5/26/2029 |  | EP | 0 | Upgrade | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.314 | PJM SOUTH | Dominion | VA | Chesterfield, Tyler | Reconductor 230kV Line #2003 Chesterfield – Tyler segment. New conductor has a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 3.16 | 3.16 | 2025-01-07 | 1/7/2025 | 4/22/2030 | 4/22/2030 |  | EP | 0 | Reconductor | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.315 | PJM SOUTH | Dominion | VA | Tyler, Poe | Reconductor 230kV Line #2003 Tyler – Poe segment. New conductor has a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 20.61 | 20.61 | 2025-01-07 | 1/7/2025 | 4/22/2030 | 4/22/2030 |  | EP | 0 | Reconductor | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.316 | PJM SOUTH | Dominion | VA | Poe | At Poe substation, uprate all Line #2003 terminal equipment, line leads, and bus to be rated to 4000A. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 1.79 | 1.79 | 2025-01-07 | 1/7/2025 | 4/22/2030 | 4/22/2030 |  | EP | 0 | Uprate | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.317 | PJM SOUTH | Dominion | VA | Tyler | At Tyler substation, upgrade the necessary line terminal equipment to maintain 4000A at Tyler substation. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.54 | 0.54 | 2025-01-07 | 1/7/2025 | 4/22/2030 | 4/22/2030 |  | EP | 0 | Upgrade | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.318 | PJM SOUTH | Dominion | VA | Chesterfield | Revise relay settings at Chesterfield substation. | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.02 | 0.02 | 2025-01-07 | 1/7/2025 | 4/22/2030 | 4/22/2030 |  | EP | 0 | Revise | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.319 | PJM SOUTH | Dominion | VA | Carson, Poe | Reconductor 230kV Line #2002 Carson – Poe. New conductor has a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 30.29 | 30.29 | 2025-01-07 | 1/7/2025 | 3/20/2030 | 3/20/2030 |  | EP | 0 | Reconductor | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.320 | PJM SOUTH | Dominion | VA | Carson | At Carson substation, upgrade all line #2002 terminal equipment at Carson to 4000A. CCVTs will also be replaced due to aging. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.89 | 0.89 | 2025-01-07 | 1/7/2025 | 3/20/2030 | 3/20/2030 |  | EP | 0 | Upgrade | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.321 | PJM SOUTH | Dominion | VA | Poe | At Poe substation, upgrade all line #2002 terminal equipment at Carson to 4000A. CCVTs will also be replaced due to aging. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.81 | 0.81 | 2025-01-07 | 1/7/2025 | 3/20/2030 | 3/20/2030 |  | EP | 0 | Upgrade | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.322 | PJM SOUTH | Dominion | VA | Nokeville, Hornbaker | Build a new 230kV Line from Nokesville – Hornbaker using the vacant arms of the double circuit monopole structures installed as part of previous project 993027. New conductor has a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 15.28 | 15.28 | 2025-01-07 | 1/7/2025 | 7/9/2029 | 7/9/2029 |  | EP | 0 | Build | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.323 | PJM SOUTH | Dominion | VA | Nokesville | Upgrade terminal equipment at Nokesville substation. The project adds one more line to Nokesville, including the installation of one 230kV breaker and two 230kV switches. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 1.43 | 1.43 | 2025-01-07 | 1/7/2025 | 7/9/2029 | 7/9/2029 |  | EP | 0 | Upgrade | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.324 | PJM SOUTH | Dominion | VA | Hornbaker | Upgrade terminal equipment at Hornbaker substation. This project provides for installing a new 230kV 4000A rated line terminal at Hornbaker to accommodate the new line to Nokesville. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 1.43 | 1.43 | 2025-01-07 | 1/7/2025 | 7/9/2029 | 7/9/2029 |  | EP | 0 | Upgrade | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.325 | PJM SOUTH | Dominion | VA | Elmont, Ladysmith | Build a new 26.38mi 230kV Line from Elmont – Ladysmith on the existing 5-2 structures between the two stations. New conductor has a summer rating of 1573 MVA. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 26.09 | 26.09 | 2025-01-07 | 1/7/2025 | 2/24/2029 | 2/24/2029 |  | EP | 0 | Build | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.326 | PJM SOUTH | Dominion | VA | Elmont | At Elmont substation, install/upgrade associated equipment to accommodate a 4000A line rating for the new 230kV line between Elmont - Ladysmith. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 2.19 | 2.19 | 2025-01-07 | 1/7/2025 | 2/24/2029 | 2/24/2029 |  | EP | 0 | Upgrade | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.327 | PJM SOUTH | Dominion | VA | Ladysmith | Upgrade/install equipment at Ladysmith substation to 4000A. Expansion will be required to accommodate a total of three (3) new 230kV strings of breaker and a half scheme. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 8.72 | 8.72 | 2025-01-07 | 1/7/2025 | 2/24/2029 | 2/24/2029 |  | EP | 0 | Upgrade | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.328 | PJM SOUTH | Dominion | VA | Cloverhill, Ox | Construct a new 24.5-mile 230 kV line 9482 from Cloverhill substation to Ox substation. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 287.54 | 287.54 | 2025-01-07 | 1/7/2025 | 4/28/2029 | 4/28/2029 |  | EP | 0 | Build | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.329 | PJM SOUTH | Dominion | VA | Ox | At Ox substation, install the necessary associated equipment to accomdate the new line between Cloverhill - Ox. This project also includes expanding the substation with associated security level 1 fencing and super post structure needed. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 6.37 | 6.37 | 2025-01-07 | 1/7/2025 | 4/28/2029 | 4/28/2029 |  | EP | 0 | Install | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.330 | PJM SOUTH | Dominion | VA | Cloverhill | At Cloverhill substation, install the necessary associated equipment to accomdate the new line between Cloverhill - Ox. This project also includes demolishing and reconstructing the existing bus system and roadway. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 2.27 | 2.27 | 2025-01-07 | 1/7/2025 | 4/28/2029 | 4/28/2029 |  | EP | 0 | Install | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.331 | PJM SOUTH | Dominion | VA | Raines, Cloud | Construct a new 230kV single circuit line from Raines substation to Cloud substation to solve electrical violations cause by the significant load growth in South Hill, Virginia. The scope also includes an idle 230kV circuit being installed between these stations. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 77.5 | 77.5 | 2025-01-07 | 1/7/2025 | 11/8/2028 | 11/8/2028 |  | EP | 0 | Build | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.332 | PJM SOUTH | Dominion | VA | Cloud | At Cloud substation, upgrade substation terminal equipment to 4000A. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 1.43 | 1.43 | 2025-01-07 | 1/7/2025 | 11/8/2028 | 11/8/2028 |  | EP | 0 | Upgrade | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.333 | PJM SOUTH | Dominion | VA | Raines | At Raines substation, upgrade substation terminal equipment to 4000A. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 1.32 | 1.32 | 2025-01-07 | 1/7/2025 | 11/8/2028 | 11/8/2028 |  | EP | 0 | Upgrade | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.334 | PJM SOUTH | Dominion | VA | Poe, Prince George | Reconductor 115kV line #121 from Poe - Prince George. Specifically, line #121 will be reconductored and converted to 230kV from Poe substation to Prince George substation. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 14.62 | 14.62 | 2025-01-07 | 1/7/2025 | 1/10/2030 | 1/10/2030 |  | EP | 0 | Reconductor | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.335 | PJM SOUTH | Dominion | VA | Poe | At Poe substation, install a new 230kV six breaker ultimate ring bus which will fit the station to current 230kV standards. The substation scope includes the installation of 230kV breaker and half GIS bus. Work at Poe subsation is associated with line #121 reconductor. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 38.28 | 38.28 | 2025-01-07 | 1/7/2025 | 1/10/2030 | 1/10/2030 |  | EP | 0 | Install | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.336 | PJM SOUTH | Dominion | VA | Prince George | Build a new 230-115kV Prince George substation along the existing 115 or 230kV corridor. The substation scope includes the installation of 230kV breakers & 1-115kV breaker along with its associated terminal equipment initially but will have provision for making it a 6-breaker ring (both 230 & 115kV) in future. The existing 230-115kV transformer at Prince George will be relocated to serve this new substation. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 26.62 | 26.62 | 2025-01-07 | 1/7/2025 | 1/10/2030 | 1/10/2030 |  | EP | 0 | Build | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.337 | PJM SOUTH | Dominion | VA | Morrisville, Anderson Branch | Extend a new 230 kV line approximately 7.85 miles between the existing Morrisville and Anderson Branch substations. The existing tower structures currently supporting the Bristers to Morrisville 500 kV Line #545 will be used to support this new line as shared tower structures. | Baseline | 230 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 5.26 | 5.26 | 2025-01-07 | 1/7/2025 | 10/11/2028 | 6/14/2028 |  | EP | 5 | Build | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.338 | PJM SOUTH | Dominion | VA | Morrisville | At Morrisville substation, install/upgrade substation terminal equipment to 4000A. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.95 | 0.95 | 2025-01-07 | 1/7/2025 | 10/11/2028 | 6/14/2028 |  | EP | 5 | Install | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.339 | PJM SOUTH | Dominion | VA | Anderson Branch | At Anderson Branch substation, install/upgrade substation terminal equipment to 4000A. | Baseline | 230 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.95 | 0.95 | 2025-01-07 | 1/7/2025 | 10/11/2028 | 6/14/2028 |  | EP | 5 | Install | No | 2024-W1-24 | Appendix A | Dominion:100
b4000.340 | PJM SOUTH | Dominion | VA | Goose Creek | Uprate existing Goose Creek 500/230kV transformer to 1440 MVA. | Baseline | 500/230 | Transformer | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 34.01 | 34.01 | 2025-01-07 | 1/7/2025 | 9/15/2029 | 12/30/2026 |  | EP | 10 | Upgrade | No | 2024-W1-781 | Appendix A | Dominion:100
b4000.341 | PJM SOUTH | Dominion | VA | Vint Hill | Remove the 500 kV conductor previously planned to terminate into the Vint Hill 500 kV substation and extend approximately 0.2 miles of conductor to fly-over the site. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0 | 0 | 2025-01-07 | 1/7/2025 | 7/13/2029 | 7/13/2029 |  | EP | 0 | Remove | No | 2024-W1-781 | Appendix A | Dominion:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.342 | PJM SOUTH | Dominion | VA | Vint Hill | Remove the terminal equipment and substation work required for the termination of the Morrisville – Wishing Star 500 kV line into Vint Hill. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0 | 0 | 2025-01-07 | 1/7/2025 | 7/13/2029 | 7/13/2029 |  | EP | 0 | Remove | No | 2024-W1-781 | Appendix A | Dominion:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.343 | PJM SOUTH | Dominion | VA | Brambleton | Uprate bus at Brambleton to support 500kV Line #558 (Aspen to Brambleton) uprate. | Baseline | 500 | Bus | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0 | 0 | 2025-01-07 | 1/7/2025 | 11/28/2025 | 11/28/2025 |  | EP | 0 | Uprate | No | 2024-W1-781 | Appendix A | Dominion:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.344 | PJM SOUTH | Dominion | VA | North Anna, Kraken | Build a 500kV line from North Anna substation (bypassing Ladysmith Substation) to a new substation called Kraken. New conductor to have a minimum summer normal rating of 4357MVA. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 186.67 | 186.67 | 2025-01-07 | 1/7/2025 | 9/16/2030 | 9/16/2030 |  | EP | 10 | Build | No | 2024-W1-967 | Appendix A | Dominion:91.69,PEPCO:8.31 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.345 | PJM SOUTH | Dominion | VA | Kraken, Yeat | Build a 500kV line from a new substatoon called Kraken to Bristers. New conductor to have a minimum summer normal rating of 4357MVA. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 384.96 | 384.96 | 2025-01-07 | 4/7/2026 | 9/16/2030 | 9/16/2030 |  | EP | 10 | Build | No | 2024-W1-967 | Appendix A | Dominion:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.346 | PJM SOUTH | Dominion | VA | Kraken | Cut-in 500kV line from Kraken substation into Bristers substation | Baseline | 500 | Tie-in | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 5 | 5 | 2025-01-07 | 4/7/2026 | 6/1/2029 | 6/1/2029 |  | EP | 5 | Cut In | No | 2024-W1-967 | Appendix A | Dominion:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.347 | PJM SOUTH | Dominion | VA | North Anna | Upgrade/install equipment at North Anna substation to 5000A to support the new conductor rating. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 9.12 | 9.12 | 2025-01-07 | 1/7/2025 | 9/16/2030 | 9/16/2030 |  | EP | 10 | Upgrade | No | 2024-W1-967 | Appendix A | Dominion:91.69,PEPCO:8.31 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.348 | PJM SOUTH | Dominion | VA | Kraken | Build a new 500/230kV substation called Kraken. The 500kV, 5000A ring bus will be set up for a redundant breaker configuration. Install (2) 1400MVA 500/230 kV transformers. A new redundant breaker ring will be added at Kraken to accommodate the new 500kV line from North Anna to Kraken. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 84.41 | 84.41 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Build | No | 2024-W1-967 | Appendix A | Dominion:100
b4000.349 | PJM SOUTH | Dominion | VA | Ladysmith | Update relay settings at Ladysmith to change the destination of 500kV line #568 from Possum Point to Kraken. | Baseline | 500 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.04 | 0.04 | 2025-01-07 | 1/7/2025 | 9/16/2030 | 9/16/2030 |  | EP | 10 | Update | No | 2024-W1-967 | Appendix A | BGE:13.28,Dominion:64.48,PEPCO:22.24 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.350 | PJM SOUTH | Dominion | VA | Possum Point | Update relay settings at Possum Point to change the destination of 500kV line #568 from Ladysmith to Kraken. | Baseline | 500 | Relay | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 0.04 | 0.04 | 2025-01-07 | 1/7/2025 | 9/16/2030 | 9/16/2030 |  | EP | 10 | Update | No | 2024-W1-967 | Appendix A | BGE:8.30,Dominion:78.64,PEPCO:13.06 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.351 | PJM SOUTH | Dominion | VA | Ladysmith, Kraken | Cut in Line #568 Ladysmith - Possum Point into Kraken, creating Line #9517 Ladysmith to Kraken. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 3.6 | 3.6 | 2025-01-07 | 1/7/2025 | 9/16/2030 | 9/16/2030 |  | EP | 10 | Cut In | No | 2024-W1-967 | Appendix A | BGE:8.30,Dominion:78.64,PEPCO:13.06 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.352 | PJM SOUTH | Dominion | VA | Possum Point, Kraken | Cut in Line #568 Ladysmith - Possum Point into Kraken, creating new Line #568 Kraken to Possum Point. | Baseline | 500 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 3.6 | 3.6 | 2025-01-07 | 1/7/2025 | 9/16/2030 | 9/16/2030 |  | EP | 10 | Cut In | No | 2024-W1-967 | Appendix A | BGE:13.28,Dominion:64.48,PEPCO:22.24 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.353 | PJM SOUTH | Dominion | VA | Elmont | Upgrade 500kV terminal equipment at Elmont substation. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 6.8 | 8.9 | 2025-01-07 | 1/7/2025 | 11/14/2029 | 6/1/2030 |  | EP | 10 | Upgrade | No | 2024-W1-967 | Appendix A | APS:9.79,BGE:6.14,Dominion:75.61,PEPCO:8.46 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.354 | PJM SOUTH | Dominion | VA | Ladysmith | Expand Ladysmith substation to a add redundant circuit breakers to the middle breakers on both 500kV strings (574T575 and 568T581). The equipment including switches 57518, 57515, H115 will be replaced with 5000A equipment. | Baseline | 500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 8.24 | 8.24 | 2025-01-07 | 1/7/2025 | 11/14/2029 | 11/14/2029 |  | EP | 0 | Expand | No | 2024-W1-967 | Appendix A | APS:9.79,BGE:6.14,Dominion:75.61,PEPCO:8.46 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.355 | PJM SOUTH | AEP | VA | Joshua Falls, Yeat | Build a new 115 mile 765kV line from Joshua Falls – Yeat. (Roughly 5 miles in AEP section). | Baseline | 765 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 24.62 | 24.62 | 2025-01-07 | 4/7/2026 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Build | No | 2024-W1-820 | Appendix A | APS:9.11,BGE:6.49,Dominion:75.72,PEPCO:8.68 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.356 | PJM SOUTH | Dominion | VA | Joshua Falls, Yeat | Build a new 115 mile 765kV line from Joshua Falls – Yeat. (Roughly 110 miles in Dominion section). | Baseline | 765 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 541.54 | 541.54 | 2025-01-07 | 4/7/2026 | 6/1/2029 | 6/1/2029 |  | EP | 5 | Build | No | 2024-W1-820 | Appendix A | APS:9.11,BGE:6.49,Dominion:75.72,PEPCO:8.68 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.357 | PJM SOUTH | Dominion | VA | Yeat | Build a new 765/500KV substation called Yeat. Install (2) 765/500 kV transformers. Cut in 500kV line Spotsylvania – Morrisville into Yeat. | Baseline | 765 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 187.1 | 187.1 | 2025-01-07 | 4/7/2026 | 6/1/2029 | 6/1/2029 |  | EP | 5 | Build | No | 2024-W1-820 | Appendix A | Dominion:89.71,PEPCO:10.29 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.358 | PJM SOUTH | Dominion | VA | Yeat | Build a new 765/500/230kV substation called Yeat. Install (1) 500/230kV transformer. Cut in 230kV line Vint Hill – Elk Run into Yeat substation. | Baseline | 765 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 45.6 | 45.6 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 5 | Build | No | 2024-W1-820 | Appendix A | Dominion:100
b4000.359 | PJM SOUTH | AEP | VA | Joshua Falls | Add (2) 765kV breakers at Joshua Falls substation. Substation expansion is required to add the additional breakers. | Baseline | 765 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 99.19 | 99.19 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Add | No | 2024-W1-820 | Appendix A | APS:9.11,BGE:6.49,Dominion:75.72,PEPCO:8.68 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.360 | PJM SOUTH | Dominion | VA | Altavista | Replace two switches, a wave trap and leads to upgrade all related substation equipment to 2000A at Altavista 138 kV substation. | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 1 | 1 | 2025-05-06 | 5/6/2025 | 6/18/2028 | 12/31/2031 |  | EP | 0 | Replace | No |  | Appendix A | Dominion:100
b4000.4 | PJM WEST | APS | WV | Welton Springs | Construct a new 765 kV switchyard (Welton Spring) | Baseline | 765 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 92.28 | 92.28 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Build | No | 2024-W1-708 | Appendix A | APS:14.67,BGE:8.11,Dominion:66.09,DPL:2.15,PEPCO:8.98 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.5 | PJM WEST | APS | WV | Welton Springs | Install four 250 MVAR shunt capacitors, and a +/-500 MVAR STATCOM at Welton Spring 765 kV substation | Baseline | 765 | Capacitor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 121.54 | 121.54 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Install | No | 2024-W1-708 | Appendix A | APS:100 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.6 | PJM WEST | APS | WV | Welton Springs - Rocky Point | Construct a new 86 miles Welton Spring to Rocky Point 765 kV line (Welton Spring to DVP local area, roughly 21 miles) (VA Portion) | Baseline | 765 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 353.5 | 105 | 2025-01-07 | 6/5/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Build | No | 2024-W1-708 | Appendix A | APS:14.67,BGE:8.11,Dominion:66.09,DPL:2.15,PEPCO:8.98 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.7 | PJM WEST | APS | VA | Welton Springs - Rocky Point | Construct a new 86 miles Welton Spring to Rocky Point 765 kV line (in DVP local area/Millville to Lovettsville section, roughly 10.5 miles) | Baseline | 765 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 52.5 | 52.5 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Build | No | 2024-W1-708 | Appendix A | APS:14.67,BGE:8.11,Dominion:66.09,DPL:2.15,PEPCO:8.98 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.8 | PJM WEST | APS | MD | Welton Springs - Rocky Point | Construct a new 86 miles Welton Spring to Rocky Point 765 kV line (DVP local area to Rocky Point, roughly 4.8 miles) | Baseline | 765 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 24 | 24 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Build | No | 2024-W1-708 | Appendix A | APS:14.67,BGE:8.11,Dominion:66.09,DPL:2.15,PEPCO:8.98 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4000.9 | PJM WEST | APS | MD | Rocky Point | Construct a new substation called Rocky Point with a 765 kV and a 500 kV yard. Loop in the Doubs-Goose Creek 500 kV line, the Doubs-Aspen 500 kV line, and the Woodside-Goose Creek 500 kV line. Install two 765/500 kV transformer at Rocky Point substation | Baseline | 765/500 | Substation | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Scope addition to b4000.11; necessary to tie NextEra's planned 502 Junction-Woodside 500 kV line segment into Black Oak substation for loop-in completion ¦ Cost correction: original estimated cost incorrectly reflected future in-service year installed cost rather than current year cost. Previous cost: $11.5M; corrected cost: $10.6M (decrease of $0.9M) ¦ Scope addition to b4000.207; tie line between AEP and Dominion — Altavista side (Dominion) requires equipment upgrade to increase line rating on |  | 20250708-pjm-board-whitepaper-july-2025.json ¦ 20251104-pjm-board-whitepaper-november-2025.json ¦ dec2022_projects.json | 2025-07-01 ¦ 2025-01-01 | 9 | 254.7 | 254.7 | 2025-01-07 | 1/7/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 | Build | No | 2024-W1-708 | Appendix A | APS:14.99,BGE:8.29,Dominion:67.55,PEPCO:9.17 | AEC:1.63 ,AEP:14.27 ,APS:5.89 ,ATSI:7.62 ,BGE:3.96 ,ComEd:12.47 ,Dayton:2.04 ,DEOK:3.12 ,Dominion:14.85 ,DPL:2.53 ,DL:1.62 ,EKPC:2.26 ,JCPL:3.78 ,ME:1.81 ,OVEC:0.07 ,PECO:5.04 ,PENELEC:1.75 ,PEPCO:3.62 ,PPL:4.85 ,PSEG:6.16 ,RE:0.25 ,Neptune:0.41
b4001.1 | PJM WEST | APS |  |  | Construct the McCanns Rd. 138 kV switching station and interconnect the existing Redbud-West Winchester 138 kV line and Bartonville-Stephenson 138 kV line. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Redbud-West Winchester and Double Toll Gate-Greenwood 138 kV lines are overloaded for N-1-1 outages in 2030 summer and winter cases. Competitive proposal window (2025 RTEP Window 1); one proposal received from FirstEnergy. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 18.83 | 18.83 | 2025-11-04 | 11/4/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-631
b4001.2 | PJM WEST | APS |  | Redbud,McCanns Rd | Reconductor new Redbud McCanns Rd. 138 kV line with 795 kcmil 45/7 ACSS for 0.5 miles from Redbud 138 kV substation to Str. 175 of the existing Redbud-West Winchester 138 kV line at approximate coordinates (39.217478, -78.128621). | Baseline | 138 |  | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Redbud-West Winchester and Double Toll Gate-Greenwood 138 kV lines are overloaded for N-1-1 outages in 2030 summer and winter cases. Competitive proposal window (2025 RTEP Window 1); one proposal received from FirstEnergy. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 5.04 | 5.03 | 2025-11-04 | 11/4/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-631
b4002.1 | PJM WEST | APS |  | Garrett Substation,Penn Mar Substation,Deep Creek Substation | Garrett - Garrett Tap 115 kV Line Upgrade: • Rebuild approximately 1.9 miles of 115 kV line with larger conductor. • Install OPGW for the static. • Install one new SCADA-controlled 2000A disconnect with whips. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 9.02 | 9.01 | 2025-11-04 | 11/4/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 |  | No | 2025-W1-692
b4002.2 | PJM WEST | PENELEC |  |  | Adjust the relay settings at Penn Mar, Garrett and Deep Creek substations to accommodate the new ratings and impedance changes associates with the Garrett-Garrett tap 115 kV line rebuild. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.13 | 0.13 | 2025-11-04 | 11/4/2025 | 6/1/2029 | 6/1/2029 |  | EP | 0 |  | No | 2025-W1-692
b4003.1 | PJM WEST | DEOK |  | OH/IN State Line (Tower 10P-X1-129),Collinsville | Rebuild the College Corner (AEP)-Collinsville (DEOK) 138 kV circuit from the OH/IN state line (tower 10P-X1-129) to Collinsville substation. AEP owns approximately 0.1 miles of the line from College Corner substation to the OH/IN state line. DEOK owns the remaining 11.90 miles from the state line to Collinsville substation. The entire 11.90 mile section that DEOK owns will be rebuilt with 954ACSS/TW conductor (@ 200C) and new double-circuit structures. The College Corner (AEP)-Trenton (DEOK) line is on the other side of the double-circuit structure and will also be rebuilt. DEOK will be doing a route survey to see if easement updates and/or additional structures are required. | Baseline | 138 |  | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | College Corner-Collinsville 138 kV tie line between AEP and DEOK is overloaded for N-2 outages in the 2030 summer case. Competitive proposal window (2025 RTEP Window 1); one proposal received from DEOK. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 45.11 | 45.11 | 2025-11-04 | 11/4/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 |  | No | 2025-W1-156
b4003.2 | PJM WEST | DEOK |  | OH/IN State Line (Tower 10P-X1-129),Trenton | Rebuild parts of the College Corner (AEP)-Trenton (DEOK) 138 kV circuit that shares a common structure with the College Corner (AEP)-Collinsville (DEOK) circuit from the OH/IN state line (Tower 10P-X1-129) to Collinsville substation. AEP owns approximately 0.1 miles of the line from College Corner substation to the OH/IN state line. DEOK owns the remaining 24.19 miles from the state line to Trenton substation. Only the 11.90-mile DEOK section that shares a common structure with College Corner (AEP)-Collinsville (DEOK) will be rebuilt with 954ACSS/TW conductor (@ 200C) and new double-circuit structures. The remaining sections from Collinsville-Trenton will be left untouched. DEOK will be doing a route survey to see if easement updates and/or additional structures are required. | Baseline | 138 |  | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | College Corner-Collinsville 138 kV tie line between AEP and DEOK is overloaded for N-2 outages in the 2030 summer case. Competitive proposal window (2025 RTEP Window 1); one proposal received from DEOK. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 13.24 | 13.24 | 2025-11-04 | 11/4/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 |  | No | 2025-W1-156
b4003.3 | PJM WEST | AEP | IN | College Corner | Relay Settings at College Corner station needed due to Duke rebuilding their College Corner-Collinsville 138 kV line section. | Baseline | 138 |  | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | College Corner-Collinsville 138 kV tie line between AEP and DEOK is overloaded for N-2 outages in the 2030 summer case. Competitive proposal window (2025 RTEP Window 1); one proposal received from DEOK. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 0.06 | 0.06 | 2025-11-04 | 11/4/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-156
b4003.4 | PJM WEST | DEOK | OH | Collinsville | Update relay settings for the College Corner-Collinsville line at DEOK's Collinsville substation. | Baseline | 138 |  | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | College Corner-Collinsville 138 kV tie line between AEP and DEOK is overloaded for N-2 outages in the 2030 summer case. Competitive proposal window (2025 RTEP Window 1); one proposal received from DEOK. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 0.03 | 0.03 | 2025-11-04 | 11/4/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 |  | No | 2025-W1-156
b4003.5 | PJM WEST | DEOK | OH | Trenton | Update relay settings for the College Corner-Trenton line at DEOK's Trenton substation. | Baseline | 138 |  | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | College Corner-Collinsville 138 kV tie line between AEP and DEOK is overloaded for N-2 outages in the 2030 summer case. Competitive proposal window (2025 RTEP Window 1); one proposal received from DEOK. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 0.03 | 0.03 | 2025-11-04 | 3/19/2026 | 6/1/2030 | 6/1/2030 |  | Cancelled | 0 |  | No | 2025-W1-156
b4004.1 | PJM MA | DPL | DE | Claymont | Upgrade existing 1590 ACSR stranded bus at Claymont substation to increase the rating on the Claymont – Linwood 230 kV circuit. | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.03 | 0.03 | 2025-11-04 | 11/4/2025 | 6/1/2030 | 5/31/2030 |  | PL | 0 | Upgrade | No
b4005.1 | PJM MA | PSEG |  | Roseland,Livingston | Replace the existing 1590 ACSR single conductor on the Roseland to Livingston 230 kV line with a 1590 ACSS single conductor. | Baseline | 230 |  | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 4.87 | 4.87 | 2025-11-04 | 11/4/2025 | 6/1/2030 | 1/31/2028 |  | EP | 0 |  | No | 2025-W1-656
b4005.2 | PJM MA | PSEG |  | Roseland,Laurel | Replace the existing 1590 ACSR single conductor on the Roseland to Laurel Ave 230 kV line with a 1590 ACSS single conductor. | Baseline | 230 |  | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 5.06 | 5.06 | 2025-11-04 | 11/4/2025 | 6/1/2030 | 3/28/2028 |  | EP | 0 |  | No | 2025-W1-656
b4006.1 | PJM WEST | ComEd | IL | Wilton Center | Install 765/345 kV TR 91 and associated 765 kV and 345 kV circuit breakers at Wilton Center. | Baseline | 765,345 |  | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Wilton Center 765/345 kV transformers TR 93 and TR 94 are overloaded for N-1 and N-2 outages in the 2030 winter case. Competitive proposal window (2025 RTEP Window 1); one proposal received from Exelon. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 45.81 | 45.81 | 2025-11-04 | 11/4/2025 | 12/1/2030 | 12/1/2030 |  | EP | 0 |  | No | 2025-W1-906
b4007.1 | PJM MA | BGE | MD | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit battery monitoring: Addressing FG No. 2024-P5-BGE03 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-11-04 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4007.2 | PJM MA | BGE | MD | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit battery monitoring: Addressing FG No. 2024-P5-BGE07 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.06 | 0.06 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4007.3 | PJM MA | BGE | MD | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit battery monitoring: Addressing FG No. 2024-P5-BGE11 | Baseline | 115 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.04 | 0.04 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4007.4 | PJM MA | BGE | MD | P5 Substation: Location CEII | 2024W1 P5: Install trip coil monitors: Addressing FG No. 2024-P5-BGE14 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.1 | 0.1 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4007.5 | PJM MA | BGE | MD | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit battery monitoring: Addressing FG No. 2024-P5-BGE05 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4007.6 | PJM MA | BGE | MD | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit battery monitoring: Addressing FG No. 2024-P5-BGE04 | Baseline | 115 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.08 | 0.08 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4007.7 | PJM MA | BGE | MD | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit battery monitoring: Addressing FG No. 2024-P5-BGE13 | Baseline | 115 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4009.1 | PJM MA | PENELEC | PA | P5 Substation: Location CEII | 2024W1 P5: Modify relay wiring: Addressing FG No. 2024-P5-PN03 | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.33 | 0.33 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4011.1 | PJM MA | ME | PA | North Hanover | Install new 115 kV capacitor; replace limiting conductors, line relaying and disconnect switches at North Hanover on the Jackson terminal. | Baseline | 115 | Capacitor | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Jackson-North Hanover 115 kV line is overloaded, and low voltage violations are observed at North Hanover, Eisenhower, Gitts Run and Fairview 115 kV buses for N-1-1 outages in the 2030 summer case. Flowgates excluded from competition under below 200 kV exclusion. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 3.56 | 3.56 | 2025-11-13 | 11/13/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 | Install | No
b4011.2 | PJM MA | ME | PA | Jackson | Replace limiting conductors, line relaying, circuit breaker and two 115 kV disconnect switches at Jackson on the North Hanover terminal. | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Jackson-North Hanover 115 kV line is overloaded, and low voltage violations are observed at North Hanover, Eisenhower, Gitts Run and Fairview 115 kV buses for N-1-1 outages in the 2030 summer case. Flowgates excluded from competition under below 200 kV exclusion. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 0.57 | 0.57 | 2025-11-13 | 11/13/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 | Replace | No
b4011.3 | PJM MA | ME | PA | North Hanover | Rebuild the Jackson-North Hanover 115 kV 968 line as a double circuit, approximately 13.2 miles, using 954 ACSR 45/7. The line will be energized in a six-wire configuration. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Jackson-North Hanover 115 kV line is overloaded, and low voltage violations are observed at North Hanover, Eisenhower, Gitts Run and Fairview 115 kV buses for N-1-1 outages in the 2030 summer case. Flowgates excluded from competition under below 200 kV exclusion. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 57.65 | 57.65 | 2025-11-13 | 11/13/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 | Rebuild | No
b4022.1 | PJM MA | BGE | MD | Greene St.,Consitution Street | Replace approx. 2 miles per circuit of existing HPFF cables with new 3500 KCM CU LPP HPFF cables. | Baseline | 115 | Cable | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Greene Street-Constitution Street 115 kV line is overloaded for N-1-1 outages in the 2030 summer case. Flowgates excluded from competition under below 200 kV exclusion. Ancillary benefit of replacing aging cables installed in the 1970s. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 58.49 | 58.49 | 2025-11-13 | 11/13/2025 | 6/1/2030 | 6/1/2030 |  | PL | 0 | Reconductor | No
b4023.1 | PJM MA | DPL | MD | Vienna | Upgrade existing 500 and 750 SDCU on Vienna side of Vienna-Loretto facility with 2x954 ACSR. Replace three 138 kV 600A disconnect switches with 2000A rated units. | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.81 | 1.81 | 2025-11-04 | 11/13/2025 | 12/1/2030 | 5/31/2030 |  | PL | 0 | Upgrade | No
b4024.1 | PJM MA | DPL | DE,MD | Laurel,Sharptown | Rebuild existing Sharptown-Laurel 69 kV circuit utilizing 954 ACSR "Rail" 45/7 conductor. | Baseline | 69 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Sharptown-Laurel 69 kV line is overloaded for N-2 outages in the 2030 summer case. Flowgates excluded from competition under below 200 kV exclusion. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 36.55 | 36.55 | 2025-11-13 | 11/13/2025 | 6/1/2030 | 5/31/2030 |  | PL | 0 | Rebuild | No
b4024.2 | PJM MA | DPL | DE | Laurel | Upgrade breaker, rigid bus, relay and disconnect switch at Laurel substation on the Sharptown-Laurel facility. | Baseline | 69 | Substation equipment | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Sharptown-Laurel 69 kV line is overloaded for N-2 outages in the 2030 summer case. Flowgates excluded from competition under below 200 kV exclusion. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 1.7 | 1.7 | 2025-11-13 | 11/13/2025 | 6/1/2030 | 5/31/2030 |  | PL | 0 | Upgrade | No
b4025.1 | PJM WEST | ComEd | IL | Mendota,Sandwich | Build new 28-mile transmission line from Mendota to Sandwich. | Baseline | 138 | Transmission Line | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Waterman-Sandwich 138 kV and Steward-Haumesser 138 kV lines are overloaded for N-1 and N-2 outages in 2030 light load and winter cases. Area also faces real-time operational issues complicated by 85 MW of wind generation causing stability and voltage regulation challenges. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 159.57 | 159.57 | 2025-12-12 | 12/12/2025 | 4/15/2030 | 12/1/2030 |  | PL | 0 | Build | No
b4025.2 | PJM WEST | ComEd | IL | Mendota | Convert Mendota straight bus to ring by installing four new 138 kV circuit breakers. | Baseline | 138 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Waterman-Sandwich 138 kV and Steward-Haumesser 138 kV lines are overloaded for N-1 and N-2 outages in 2030 light load and winter cases. Area also faces real-time operational issues complicated by 85 MW of wind generation causing stability and voltage regulation challenges. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 10.37 | 10.37 | 2025-12-12 | 12/12/2025 | 4/15/2030 | 12/1/2030 |  | PL | 0 | Install | No
b4025.3 | PJM WEST | ComEd | IL | Sandwich | Install 138 kV BT circuit breaker and associated equipment at Sandwich. | Baseline | 138 | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Waterman-Sandwich 138 kV and Steward-Haumesser 138 kV lines are overloaded for N-1 and N-2 outages in 2030 light load and winter cases. Area also faces real-time operational issues complicated by 85 MW of wind generation causing stability and voltage regulation challenges. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 1.95 | 1.95 | 2025-12-12 | 12/12/2025 | 4/15/2030 | 12/1/2030 |  | PL | 0 | Install | No
b4027.1 | PJM WEST | AEP |  | Smith Mountain,Moneta,Rockcastle | Sag study the Smith Mountain-Moneta 138 kV line. Approximately 14 structures will need to be added in existing rights-of-way to increase the sag along the existing centerline such that the higher requested ampacity can be achieved along the corridor and maintain safety clearances. | Baseline | 138 |  | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 9.6 | 9.6 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-689
b4027.2 | PJM WEST | AEP |  |  | Replace the 2" IPS Sch. 40 conductor with 4" IPS Sch. 40 conductor at Smith Mountain station on the Smith Mountain-Rock Castle branch allowing the branch to exceed a summer emergency rating of 1765A. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.28 | 0.28 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-689
b4028.1 | PJM WEST | AEP |  | Mound Street Station,St Clair Avenue Station | Rebuild 2.3 miles of the Mound Street-St Clair Avenue 138 kV UG line with 5000 KCM XLPE cable. | Baseline | 138 |  | Baseline Load Growth Deliverability & Reliability | reliability_criteria | consistent (logic chain: load growth → reliability violation) | FALSE | 0 | Mound Street-Saint Clair Avenue 138 kV line is overloaded for N-1, N-2, and N-1-1 outages in 2030 summer and winter cases. Competitive proposal window (2025 RTEP Window 1); one proposal received from AEP. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 41.59 | 41.59 | 2025-12-12 | 12/12/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-195
b4029.1 | PJM MA | PPL |  |  | Expand existing Slykerville 230 kV station to add a 500 kV yard. Build a new Kelayres 500 kV breaker-and-a-half substation. Add two 750 MVA, 500/230 kV transformers at Kelayres. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 72.92 | 72.92 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 2/28/2030 |  | EP | 0 |  | No | 2025-W1-317
b4029.10 | PJM MA | PPL |  |  | At Glen Brook 230/69 kV substation, replace fourteen 230 kV, 2000A MODs with 230 kV, 3000A MODs. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 2.5 | 2.5 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 8/31/2029 |  | EP | 0 |  | No | 2025-W1-958
b4029.11 | PJM MA | PPL |  |  | At the Jenkins 230/69 kV substation, re-terminate the Jenkins 230/69 kV T2 and T4 transformers into bay positions in the 69 kV and 230 kV yards, respectively. Add one new 230 kV, 3000A circuit breaker, and two 230 kV, 3000A MODs to accommodate the retermination of the T4 transformer into the east bay position in the existing 230 kV breaker-and-a-half bay 2. Add two new 69 kV, 3000A circuit breakers and four 69 kV, 3000A switches to accommodate the retermination of the T2 transformer into a new 69 kV double- bus double-breaker bay 4. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 8.71 | 8.71 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 7/31/2029 |  | EP | 0 |  | No | 2025-W1-647
b4029.12 | PJM MA | PPL |  | Jenkins | Reterminate high side of T4 transformer into bay 2E of the 230 kV yard. | Baseline | 230 |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 1.46 | 1.46 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 7/31/2029 |  | EP | 0 |  | No | 2025-W1-647
b4029.13 | PJM MA | PPL |  | Glen Brook,Susquehanna | Reconductor 0.7 miles of Glen Brook - Susquehanna T10 1 & 2 DCT line with ACCC 1036/87/392 (2045 kcmil) conductor. | Baseline | 230 |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 2.63 | 2.63 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 10/31/2029 |  | EP | 0 |  | No | 2025-W1-588
b4029.14 | PJM MA | PPL |  | Susquehanna,Talen AWS | Susquehanna T10-Susquehanna 230 kV False. 3 line: Construct a new Susquehanna T10-Susquehanna 230 kV False. 3 line (~2.7 miles) using an approximately 75% brownfield route, with a short greenfield segment near the Susquehanna station. | Baseline | 230 |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 14.33 | 14.33 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 10/31/2029 |  | EP | 0 |  | No | 2025-W1-588
b4029.15 | PJM MA | PPL |  |  | Construct a new breaker-and-a-half bay at Susquehanna T10 230 kV station and initially populate with two 230 kV, 3000A circuit breakers and four 230 kV, 3000A MODs, leaving a position for a future breaker to be added. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 6.62 | 6.62 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 10/31/2029 |  | EP | 0 |  | No | 2025-W1-588
b4029.16 | PJM MA | PPL |  |  | Reuse existing bay and upgrade to 3000A. Existing bay at Susquehanna vacated by the former Sunbury line. Inspect all facilities, refurbish and insure bay rating of 3000A. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 1.24 | 1.24 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 10/31/2029 |  | EP | 0 |  | No | 2025-W1-588
b4029.2 | PJM MA | PPL |  |  | Add one 500 kV, 4000A circuit breaker, two 500 kV, 4000A MODs and a 750 MVA 500/230 kV T3 transformer at Kelayres. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 29.02 | 29.02 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 2/28/2030 |  | EP | 0 |  | No | 2025-W1-853
b4029.3 | PJM MA | PPL |  | Nescopeck,Harwood | Bifurcate the Sunbury-Susquehanna 500 kV line. From the bifurcation point, build a 13-mile extension to Kelayres, resulting in a Susquehanna-Kelayres 500 kV line. | Baseline | 230 |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 20.87 | 20.87 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 2/28/2030 |  | EP | 0 |  | No | 2025-W1-317
b4029.4 | PJM MA | PPL |  | Sunbury,Kelayres | Bifurcate the Sunbury-Susquehanna 500 kV line bringing both segments into a new Kelayres 500 kV station on separate towers. From the bifurcation point, build a 24-mile extension to Kelayres, resulting in a Sunbury-Kelayres 500 kV line. | Baseline | 500 |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 133.64 | 133.64 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 2/28/2030 |  | EP | 0 |  | No | 2025-W1-317
b4029.5 | PJM MA | PPL |  | Susquehanna,Tomhicken | Susquehanna-Tomhicken 230 kV 1 and 2 DCT line reconductor: Reconduct both circuits on the existing DCT tower with ACCC 1036/87/392 (2045 kcmil) conductor. | Baseline | 230 |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 29.73 | 29.73 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 6/30/2028 |  | EP | 0 |  | No | 2025-W1-824
b4029.6 | PJM MA | PPL |  |  | Upgrade the existing Monroe 230/138 kV substation to a two-bay breaker and a half on the 230 kV side (with space to accommodate two future bays), and a double-bus double-breaker design on the 138 kV side. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 30.95 | 30.95 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 10/31/2029 |  | EP | 0 |  | No | 2025-W1-688
b4029.7 | PJM MA | PPL |  | Monroe,Fox Hill,Martins Creek | Retermination of the Monroe-Fox Hill and Monroe-Martins Creek 230 kV lines into their new locations in the upgraded 230 kV breaker-and-a-half yard. | Baseline | 230 |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 8.27 | 8.27 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 10/31/2029 |  | EP | 0 |  | No | 2025-W1-688
b4029.8 | PJM MA | PPL |  | Juniata,Sunbury | Address end-of-life concerns by rebuilding the existing 38-mile Juniata-Sunbury 500 kV line using single-circuit design. | Baseline | 500 |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 162.89 | 162.89 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 4/30/2030 |  | EP | 0 |  | No | 2025-W1-16
b4029.9 | PJM MA | PPL |  | Montour,Glen Brook | The Montour-Glen Brook 230 kV 1 and 2 DCT line is 24.9 miles long. For this project, the developer will reconduct 0.70 miles of this route with ACCC 1036/87/392 (2045 kcmil) conductor. AFalsether 5.2 miles of the route will be rebuilt with new steel pole structures and double-bundle 1590 ACSR conductor. The remaining 19 miles of the route is being rebuilt and reconductored as part of supplemental project s2373 to address end of life for CORTEN structures. | Baseline | 230 |  | Baseline Load Growth Deliverability & Reliability | load_growth_data_center | consistent | TRUE | 1 | Multiple lines in the Susquehanna and Juniata area of PPL zone are overloaded for N-1, N-2, and N-1-1 outages with voltage violations under N-2 and N-1-1 conditions in 2030 seasons. PJM Mid-Atlantic Region summer load increased approximately 5 GW for 2030 compared to 2024 RTEP, with most of these load increases being data center loads primarily in the PPL zone. Juniata-Sunbury 500 kV line is also an End-of-Life candidate per PPL FERC Form 715 criteria. 29 proposals received from four entities. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 37.15 | 37.15 | 2025-12-02 | 12/2/2025 | 5/1/2030 | 8/31/2029 |  | EP | 0 |  | No | 2025-W1-958
b4030.1 | PJM SOUTH | Dominion |  | Chesterfield,Basin | Chesterfield-Basin 230 kV rebuild: Wreck and rebuild approximately 12.5 miles of Chesterfield-Basin 230 kV line. | Baseline | 230 |  | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 100.31 | 100.31 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-911
b4030.10 | PJM SOUTH | Dominion |  | Fork Union,Bremo | Fork Union-Bremo 230 kV rebuild: Wreck and Rebuild approximately 1.74 miles of Fork Union-Bremo 230 kV line. | Baseline | 230 |  | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 10.81 | 10.81 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-911
b4030.11 | PJM SOUTH | Dominion |  |  | Charlottesville 230 kV substation scope: Replace all terminal equipment at Charlottesville 230 kV substation to support the new line conductor ratings of the Charlottesville-Fork Union 230 kV rebuild. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 3.35 | 3.35 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-911
b4030.12 | PJM SOUTH | Dominion |  |  | Fork Union 230 kV substation scope: Replace all terminal equipment at Fork Union 230 kV substation to support the new line conductor ratings of the Charlottesville-Fork Union 230 kV rebuild. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 2.24 | 2.24 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-911
b4030.13 | PJM SOUTH | Dominion |  |  | Fork Union 230 kV substation scope: Replace all terminal equipment at Fork Union 230 kV substation to support the new conductor ratings of the Fork Union-Bremo 230 kV rebuild. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 1.6 | 1.6 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-911
b4030.14 | PJM SOUTH | Dominion |  |  | Bremo 230 kV substation scope: Replace all terminal equipment at Bremo 230 kV substation to support the new conductor ratings of the Fork Union-Bremo 230 kV rebuild. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 1.8 | 1.8 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-911
b4030.15 | PJM SOUTH | Dominion |  |  | Mt. Eagle tap 230 kV substation scope: Upgrade disconnect switches at Mt. Eagle tap 230 kV substation to 4000A. | Baseline |  | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 0.65 | 0.65 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 | Add | No | 2025-W1-911
b4030.16 | PJM SOUTH | Dominion |  |  | Sycamore Springs 230 kV substation scope: Reset relays at Sycamore Springs 230 kV substation. | Baseline |  |  | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 0.04 | 0.04 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-911
b4030.2 | PJM SOUTH | Dominion |  | Chesterfield,Hopewell | Chesterfield-Hopewell 230 kV reconductor: Reconductor 230 kV lines No. 211 and No. 228 between the existing Chesterfield-Hopewell 230 kV substation. Each line reconductor is ~3 miles long. | Baseline | 230 |  | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 6.34 | 6.34 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-911
b4030.3 | PJM SOUTH | Dominion |  |  | Basin 230 kV substation scope: Replace all terminal equipment, line leads and bus at Basin 230 kV substation to be rated to 4000A. | Baseline |  | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 1.96 | 1.96 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 | Add | No | 2025-W1-911
b4030.4 | PJM SOUTH | Dominion |  |  | Chesterfield 230 kV substation scope: Replace all terminal equipment, line leads and bus at Chesterfield 230 kV substation to be rated to 4000A. | Baseline |  | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 3.51 | 3.51 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 | Add | No | 2025-W1-911
b4030.5 | PJM SOUTH | Dominion |  |  | Chesterfield 230 kV substation scope: Install a new 230 kV, 80 kA 4000A circuit breaker at Chesterfield 230 kV substation. | Baseline |  | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 1.5 | 1.5 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 | Add | No | 2025-W1-911
b4030.6 | PJM SOUTH | Dominion |  | Suffolk,Yadkin | Suffolk-Yadkin 500 kV rebuild: Rebuild approximately 13.2 miles of Suffolk-Yadkin 500 kV line. | Baseline | 500 |  | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 68.86 | 68.86 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-911
b4030.7 | PJM SOUTH | Dominion |  |  | Suffolk 500 kV substation scope: Replace all terminal equipment at Suffolk 500 kV substation to be rated to 5000 A. | Baseline |  | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 5.23 | 5.23 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 | Add | No | 2025-W1-911
b4030.8 | PJM SOUTH | Dominion |  |  | Yadkin 500 kV substation scope: Replace all terminal equipment at Yadkin 500 kV substation to be rated to 5000A. | Baseline |  | Circuit Breaker | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 0.24 | 0.24 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 | Add | No | 2025-W1-911
b4030.9 | PJM SOUTH | Dominion |  | Charlottesville,Fork Union | Charlottesville-Fork Union 230 kV rebuild: Wreck and rebuild ~24 miles of Charlottesville-Fork Union 230 kV line. | Baseline | 230 |  | Baseline Load Growth Deliverability & Reliability | aging_infrastructure | TRUE MISMATCH xlsx:Baseline Load Growth Deliverability & Reliability ¦ csv:aging_infrastructure | FALSE | 0 | Three components: (1) Basin-Chesterfield-Hopewell 230 kV lines overloaded for N-1/N-2 outages in all 2030 seasons; (2) Charlottesville-Fork Union-Bremo 230 kV lines overloaded for N-1/N-2 outages in 2030 light load case; (3) Suffolk-Yadkin 500 kV 565 line violates FERC Form 715 C.2.9 EOL criteria – structures installed in 1970 are approaching end of service life, weathering-steel 5-series towers experiencing packout and deterioration, porcelain insulators have deteriorated significantly. |  | 20260106-2025-rtep-window-1-reliability-analysis-report.json | 2026-01-01 | 1 | 106.49 | 106.49 | 2025-12-08 | 12/8/2025 | 6/1/2030 | 6/1/2030 |  | EP | 0 |  | No | 2025-W1-911
b4031.1 | PJM SOUTH | Dominion | VA | Bremo,Fork Union | Wreck and rebuild 115kV line No. 5 using conductor with minimum summer rating of 393 MVA. | Baseline | 115 | Transmission Line | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 5 | 5 | 2025-12-11 | 12/11/2025 | 4/15/2030 | 4/15/2030 |  | PL | 0 | Rebuild | No
b4031.2 | PJM SOUTH | Dominion | VA | Bremo | At Bremo substation, upgrade relevant equipment below 2000A, such as line leads, breakers, switches and CTs to accommodate the upgraded 115kV line 5. | Baseline | 115 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1 | 1 | 2025-12-11 | 12/11/2025 | 4/15/2030 | 4/15/2030 |  | PL | 0 | Upgrade | No
b4031.3 | PJM SOUTH | Dominion | VA | Fork Union | At Fork Union substation, upgrade relevant equipment below 2000A, such as line leads, breakers, switches and CTs to accommodate the upgraded 115kV line 5. | Baseline | 115 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1 | 1 | 2025-12-11 | 12/11/2025 | 4/15/2030 | 4/15/2030 |  | PL | 0 | Upgrade | No
b4037.1 | PJM WEST | APS | PA | P5 Substation: Location CEII | 2024W1 P5: Install open battery monitoring and modify relay wiring: Addressing FG No. 2024-P5-APS25. | Baseline | 138 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.6 | 0.6 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4038.1 | PJM WEST | APS | WV | P5 Substation: Location CEII | 2024W1 P5: Modify relay wiring: Addressing FG No. 2024-P5-APS02 | Baseline | 500 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.66 | 0.66 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4039.1 | PJM WEST | APS | MD | P5 Substation: Location CEII | 2024W1 P5: Replace three relay panels and modify relay wiring. Addresses FG No. 2024-P5-APS24. | Baseline | 500 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 4.22 | 4.22 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4039.2 | PJM WEST | APS | WV | P5 Substation: Location CEII | 2024W1 P5: Replace one relay panel at a confidential substation connected to the substation associated with b4039.1. Addresses FG No. 2024-P5-APS24. | Baseline | 138 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0 | 0 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4039.3 | PJM WEST | APS | MD | P5 Substation: Location CEII | 2024W1 P5: Replace one relay panel at a confidential substation connected to the substation associated with b4039.1. Addresses FG No. 2024-P5-APS24. | Baseline | 138 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0 | 0 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4039.4 | PJM WEST | APS | WV | P5 Substation: Location CEII | 2024W1 P5: Replace one relay panel at a confidential substation connected to the substation associated with b4039.1. Addresses FG No. 2024-P5-APS24. | Baseline | 138 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0 | 0 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4043.1 | PJM MA | JCPL | NJ | P5 Substation: Location CEII | 2024W1 P5: Modify relay wiring: Addressing FG No. 2024-P5-JCPL06 | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.66 | 0.66 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4045.1 | PJM MA | JCPL | NJ | P5 Substation: Location CEII | 2024W1 P5: Install relay panel and modify relay wiring: Addressing FG No. 2024-P5-JCPL01 | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.66 | 0.66 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4047.1 | PJM MA | JCPL | NJ | P5 Substation: Location CEII | 2024W1 P5: Install open battery monitoring and modify relay wiring: Addressing FG No. 2024-P5-JCPL03 | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.64 | 0.64 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4050.1 | PJM WEST | ATSI | OH | P5 Substation: Location CEII | 2024W1 P5: Modify relay wiring: Addressing FG No. 2024-P5-ATSI05 | Baseline | 345 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.66 | 0.66 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4051.1 | PJM WEST | ATSI | OH | P5 Substation: Location CEII | 2024W1 P5: Install open battery monitoring and modify relay wiring: Addressing FG No. 2024-P5-ATSI09 | Baseline | 345 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.45 | 0.45 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4057.1 | PJM WEST | APS | PA | P5 Substation: Location CEII | 2024W1 P5: Install relay panel and modify relay wiring: Addressing FG No. 2024-P5-APS06 | Baseline | 500 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.36 | 0.36 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4058.1 | PJM MA | ME | PA | P5 Substation: Location CEII | 2024W1 P5: Install open battery monitoring and modify relay wiring: Addressing FG No. 2024-P5-ME04 | Baseline | 115 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.51 | 0.51 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4059.1 | PJM MA | ME | PA | P5 Substation: Location CEII | 2024W1 P5: Install open battery monitoring, install relay panel, modify relay wiring: Addressing FG No. 2024-P5-ME05 | Baseline | 230 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.69 | 0.69 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4061.1 | PJM WEST | APS | PA | P5 Substation: Location CEII | 2024W1 P5: Install open battery monitoring and modify relay wiring: Addressing FG No. 2024-P5-APS05 | Baseline | 500 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.97 | 0.97 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4063.1 | PJM WEST | APS | WV | P5 Substation: Location CEII | 2024W1 P5: Install battery monitoring, DC panel(s); replace bus differential scheme and modify relay wiring: Addressing FG No. 2024-P5-APS22 | Baseline | 138 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.29 | 1.29 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4064.1 | PJM WEST | APS | WV | P5 Substation: Location CEII | 2024W1 P5: Install battery monitoring, relay panels; modify relay wiring: Addressing FG No. 2024-P5-APS23 | Baseline | 138 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 1.94 | 1.94 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4065.1 | PJM MA | PENELEC | PA | P5 Substation: Location CEII | 2024W1 P5: Install battery monitoring system and replace two 115 kV line protection schemes. Addresses FG No. 2024-P5-PN04 | Baseline | 115 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 2.9 | 2.9 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4065.2 | PJM MA | PENELEC | PA | P5 Substation: Location CEII | 2024W1 P5: Install one relay panel at a confidential substation connected to the substation associated with b4065.1. Addresses FG No. 2024-P5-PN04 | Baseline | 115 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0 | 0 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4066.1 | PJM MA | PENELEC | PA | P5 Substation: Location CEII | 2024W1 P5: Install open battery monitoring and modify relay wiring: Addressing FG No. 2024-P5-PN05 | Baseline | 345 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 2.58 | 2.58 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4072.1 | PJM MA | ME | PA | P5 Substation: Location CEII | 2024W1 P5: Install open battery monitoring and modify relay wiring: Addressing FG No. 2024-P5-ME02 | Baseline | 500 | Relay | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.97 | 0.97 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 6/1/2029 |  | PL | 0 | Upgrade | No
b4073.1 | PJM WEST | ComEd | IL | P5 Substation: Location CEII | 2024W1 P5: Install battery monitoring: Addressing FG No. 2024-P5-COMED01 | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.25 | 0.25 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Install | No
b4073.2 | PJM WEST | ComEd | IL | P5 Substation: Location CEII | 2024W1 P5: Install battery monitoring: Addressing FG No. 2024-P5-COMED30 | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.1 | 0.1 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Install | No
b4073.3 | PJM WEST | ComEd | IL | P5 Substation: Location CEII | 2024W1 P5: Install battery monitoring: Addressing FG No. 2024-P5-COMED28 | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.05 | 0.05 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Install | No
b4073.4 | PJM WEST | ComEd | IL | P5 Substation: Location CEII | 2024W1 P5: Install battery monitoring: Addressing FG No. 2024-P5-COMED31 | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.1 | 0.1 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Install | No
b4073.5 | PJM WEST | ComEd | IL | P5 Substation: Location CEII | 2024W1 P5: Install battery monitoring: Addressing FG No. 2024-P5-COMED29 | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.1 | 0.1 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Install | No
b4073.6 | PJM WEST | ComEd | IL | P5 Substation: Location CEII | 2024W1 P5: Install battery monitoring: Addressing FG No. 2024-P5-COMED14 | Baseline | 345 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.1 | 0.1 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Install | No
b4074.1 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the control center: Addressing FG No. 2024-P5-PECO01 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.10 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO10 | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.11 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO11 | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.12 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO12 | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.13 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO13 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.14 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO14 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.15 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO15 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.16 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO16 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.17 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO17 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.05 | 0.05 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.18 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO18 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.19 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5DYN-PECO01 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.2 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO02 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.3 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO03 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.4 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO04 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.5 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO05 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.6 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG No. 2024-P5-PECO06 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.7 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO07 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.8 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO08 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.05 | 0.05 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4074.9 | PJM MA | PECO | PA | P5 Substation: Location CEII | 2024W1 P5: Replace existing battery charger; install auxiliary alarm relay board; install shunt enclosure; and connect alarm points to SCADA to monitor and report low-voltage and open-circuit conditions on the station DC supply to the Control Center: Addressing FG No. 2024-P5-PECO09 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4075.1 | PJM MA | ACE | NJ | P5 Substation: Location CEII | 2024W1 P5: Install open circuit battery monitoring: Addressing FG No. 2024-P5-AEC01 | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4075.2 | PJM MA | ACE | NJ | P5 Substation: Location CEII | 2024W1 P5: Install open circuit battery monitoring: Addressing FG No. 2024-P5-AEC02 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4075.3 | PJM MA | ACE | NJ | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit battery monitoring: Addressing FG No. 2024-P5-AEC03 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4075.4 | PJM MA | ACE | NJ | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit battery monitoring: Addressing FG No. 2024-P5-AEC04 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4075.5 | PJM MA | ACE | NJ | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit battery monitoring: Addressing FG No. 2024-P5-AEC05 | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4075.6 | PJM MA | ACE | NJ | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit battery monitoring: Addressing FG No. 2024-P5-AEC06 | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4075.7 | PJM MA | ACE | NJ | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit battery monitoring: Addressing FG No. 2024-P5-AEC07 | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4075.8 | PJM MA | ACE | NJ | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit battery monitoring: Addressing FG No. 2024-P5-AEC08 | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4076.1 | PJM MA | DPL | DE | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit monitoring. Addresses FG No. 2024-P5-DPL01 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4076.10 | PJM MA | DPL | MD | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit monitoring. Addresses FG No. 2024-P5DYN-DPL01 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability,Stability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4076.2 | PJM MA | DPL | DE | P5 Substation: Location CEII | 2024W1 P5: Install open circuit monitoring. Addresses FG No. 2024-P5-DPL02 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4076.3 | PJM MA | DPL | MD | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit monitoring. Addresses FG No. 2024-P5-DPL03 | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4076.4 | PJM MA | DPL | MD | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit monitoring. Addresses FG No. 2024-P5-DPL04 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4076.5 | PJM MA | DPL | VA | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit monitoring. Addresses FG No. 2024-P5-DPL05 | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4076.6 | PJM MA | DPL | MD | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit monitoring. Addresses FG No. 2024-P5-DPL07 | Baseline | 138 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4076.7 | PJM MA | DPL | MD | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit monitoring. Addresses FG No. 2024-P5-DPL08 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4076.8 | PJM MA | DPL | MD | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit monitoring. Addresses FG No. 2024-P5-DPL09 | Baseline | 230 | Substation equipment | Baseline Load Growth Deliverability & Reliability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No
b4076.9 | PJM MA | DPL | DE | P5 Substation: Location CEII | 2024W1 P5: Install open-circuit monitoring. Addresses FG No. 2024-P5-DPL10, 2024-P5DYN-DPL02 | Baseline | 500 | Substation equipment | Baseline Load Growth Deliverability & Reliability,Stability |  | no_csv_record | FALSE | [6 empty] | 0.02 | 0.02 | 2025-12-08 | 12/8/2025 | 6/1/2029 | 7/1/2029 |  | PL | 0 | Upgrade | No